## 0_Naslovnica
OPOZORILO! Vsi prevodi v angleščino so strojno izdelani in zgolj informativne narave. V primeru kakršnekoli nejasnosti ali dvoma izključno velja izvirno besedilo v slovenščini. WARNING! All translations into English have been produced by machine translation and are provided for informational purposes only. In the event of any ambiguity or uncertainty, the original Slovenian text shall prevail exclusively.
| / | / | [5 empty] | /
| Sprem./Rev.: | Opis spremembe/Description of Changes: | [5 empty] | Datum/Date: | Podpis/Signature:
| Investitor/Investor: |  |  |  |  | Gradnja/Facility
|  |  | Univerza v Ljubljani Kongresni trg 12 1000 Ljubljana, Slovenija |  |  | Fakulteta za strojništvo/Faculty of Mechanical Engineering
| Projektant/Design Engineer: |  |  |  |  | Del objekta/sistem/Building/System:
|  |  | IBE, svetovanje, projektiranje in inženiring Ljubljana, Slovenija |  |  | STAVBA FAKULTETE/FACULTY BUILDING
| Projektant/Design Engineer: |  |  |  |  | Vrsta načrta/Documentation:
|  |  | SADAR + VUGA d.o.o. Ljubljana, Slovenija |  |  | 1 NAČRT S PODROČJA ARHITEKTURE/ DOC. IN THE FIELD OF ARCHITECTURE
|  | Ime in priimek/Name and Surname: |  |  | Id. št./Id. No: | Vsebina risbe (dokumenta)/Document Title:
| Vodja proj./ Des. Manager: | Boštjan Vuga, univ. dipl. inž. arh., grad. dip. (AA) |  |  | ZAPS 0035 PA PPN | PROJEKTANTSKI POPIS GRADBENO OBRTNIŠKIH DEL, AKUSTIČNE CELICE/BOQ OF CONSTRUCTION AND CRAFT WORKS, ACUSTIC CELLS
| Poobl. strok./ Cert. Profess.: | Nina Janković, univ. dipl. inž. arh.
| Poobl. strok./ Cert. Profess.: | Matej Turk, mag. inž. arh. |  |  |  | Št. proj./ Proj. No.: | 362-19 |  | Vrsta dokument./ Document. Type: | DZR
| Izdelal/ Creator: | Boris Bruderman, univ. dipl. inž. vod. in kom. inž. |  |  |  | Klas. ozn./ Class. No.: | -- |  | Stran/ Page: | 1/*
| Datum/ Date: | maj/May 2026 |  | Merilo/ Scale: | / | Ident. ozn./ Id. No: | JULFS--6A1019P

## 0_Osebe
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | AKUSTIČNE CELICE | ACOUSTIC CELLS
POOBLAŠČENI STROKOVNJAKI, ODGOVORNI ZA IZDELAVO PROJEKTANTSKEGA POPISA:
Id. št. ZAPS/IZS | Pooblaščeni strokovnjak | Strokovno področje
ZAPS 0035 PA PPN | Boštjan Vuga, univ. dipl. inž. arh., grad. dip. (AA) | arhitektura
ZAPS 0028 PA PPN | Jurij Sadar, univ. dipl. inž. arh. | arhitektura
ZAPS 1632 PA* | Miha Čebulj, univ. dipl. inž. arh., m. arch. (BI) | arhitektura
ZAPS 1022 PA PPN | Damjan Holc, univ. dipl. inž. arh. | arhitektura
ZAPS 1781 PA* | Nina Janković, univ. dipl. inž. arh. | arhitektura
ZAPS 2334 PA | Matej Turk, mag. inž. arh. | arhitektura
SODELAVCI PRI IZDELAVI PROJEKTANTSKEGA POPISA:
/ | Boris Bruderman, univ. dipl. inž. vod. in kom. inž. | Izdelava popisa
ZAPS 1781 PA* | Andraž Seifert, univ. dipl. inž. arh. | Izdelava popisa
ZAPS 2143 PA | Matjaž Bahor, mag. inž. arh. | Izdelava popisa
/ | Maruša Dolenc, mag. inž. arh. | Izdelava popisa
/ | Belén Villán Fernández, mag. inž. arh. | Izdelava popisa
/ | Pavlina Šuligoj, mag. inž. arh. | Izdelava popisa
/ | Andreja Toporiš, mag. inž. arh. | Izdelava popisa
/ | Vladmir Bavdaž, gr. inž | Izdelava popisa
/ | Sebastjan Krempl | Izdelava popisa
CERTIFIED EXPERTS RESPONSIBLE FOR ELABORATING THE BILL OF QUANTITIES:
Id. No ZAPS/IZS | Certified Expert | Area of Expertise
ZAPS 0035 PA PPN | Boštjan Vuga, univ. dipl. inž. arh., grad. dip. (AA) | architecture
ZAPS 0028 PA PPN | Jurij Sadar, univ. dipl. inž. arh. | architecture
ZAPS 1632 PA* | Miha Čebulj, univ. dipl. inž. arh., m. arch. (BI) | architecture
ZAPS 1022 PA PPN | Damjan Holc, univ. dipl. inž. arh. | architecture
ZAPS 1781 PA* | Nina Janković, univ. dipl. inž. arh. | architecture
ZAPS 2334 PA | Matej Turk, mag. inž. arh. | architecture
COLABORATORS IN THE ELABORATING THE BILL OF QUANTITIES:
/ | Boris Bruderman, univ. dipl. inž. vod. in kom. inž. | elaborating the Bill of Quantities
ZAPS 1781 PA* | Andraž Seifert, univ. dipl. inž. arh. | elaborating the Bill of Quantities
ZAPS 2143 PA | Matjaž Bahor, mag. inž. arh. | elaborating the Bill of Quantities
/ | Maruša Dolenc, mag. inž. arh. | elaborating the Bill of Quantities
/ | Belén Villán Fernández, mag. inž. arh. | elaborating the Bill of Quantities
/ | Pavlina Šuligoj, mag. inž. arh. | elaborating the Bill of Quantities
/ | Andreja Toporiš, mag. inž. arh. | elaborating the Bill of Quantities
/ | Vladmir Bavdaž, gr. inž | elaborating the Bill of Quantities
/ | Sebastjan Krempl | elaborating the Bill of Quantities

## 0.1_Uvod-STP
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | AKUSTIČNE CELICE | ACOUSTIC CELLS
0.1 | SPLOŠNI TEHNIČNI POGOJI | GENERAL TECHNICAL CONDITIONS
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic operator with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
0.1.1 | Izvajalec se obveže, da bo upošteval veljavno zakonodajo, ki ureja graditev objektov v Republiki Sloveniji, vključno s povezanimi podzakonskimi akti, predpisi, tehničnimi smernicami, standardi, pravili stroke in dobro gradbeno prakso. Prav tako mora izvajalec upoštevati vse zahteve izdanega integralnega gradbenega dovoljenja in vsa dela izvesti skladno s projektno dokumentacijo ter ostalimi pogoji, objavljenimi v razpisni dokumentaciji. | The Contractor undertakes to comply with the applicable legislation governing the construction of buildings in the Republic of Slovenia, including related by-laws, regulations, technical guidelines, standards, professional rules and good construction practice. The Contractor shall also comply with all the requirements of the integral building permit issued and shall carry out all works in accordance with the project documentation and other conditions published in the tender documentation.
0.1.2 | Dela lahko izvaja samo izvajalec, ki je registriran za opravljanje gradbene dejavnosti in ima za tovrstna dela ustrezno zavarovanje za škodo, certifikate, tehnično izobražen kader, sredstva ter je usposobljen za samostojno pripravo in izvedbo del. | The work may only be carried out by a contractor who is registered to carry out construction work and who has the appropriate insurance for such work, certificates, technically trained staff, resources and is qualified to prepare and carry out the work independently.
0.1.3 | Izvajalec odgovarja za kakovost izvedbe vseh del. | The Contractor shall be responsible for the quality of the execution of all works.
0.1.4 | Izvajalec nosi vso odgovornost za nesreče in škodo, ki nastane na objektu ali v okolici zaradi njegovega dela. | The Contractor shall bear all liability for accidents and damage to the installation or the surrounding area caused by his work.
0.1.5 | Pred oddajo ponudbe se je izvajalec dolžan seznaniti z območjem predvidenim za gradnjo in temu prilagoditi vsa potrebna dela, kar mora biti zajeto v ponudbi. V neposredni bližini predvidene gradnje se nahajajo stavbe, v katerih potekajo izobraževalni in raziskovalni procesi. Zato bo izvajalec moral izvajati kontrolo hrupa in kontrolo vibracij. Dela, ki so hrupna in dela, ki povzročajo vibracije bo izvajalec moral preprečiti oziroma jih izvesti na način, da povzročajo minimalne vplive. Tehnologijo rušenja, pilotiranja in tehnologijo izvedbe ostalih del bo izvajalec moral prilagoditi tako, da bo vpliv minimalen. Izvajalec mora preprečiti in zmanjšati emisije delcev iz gradbišča na najmanjšo možno mero. | Before submitting a tender, the contractor is obliged to familiarise himself with the area to be constructed and to adapt any necessary works accordingly, which must be included in the tender. In the immediate vicinity of the proposed construction, there are buildings in which educational and research processes take place. The contractor will therefore be required to carry out noise and vibration control. Noise and vibration works will have to be avoided or carried out in such a way as to minimise the impact. Demolition, piling and other works will have to be adapted to minimise the impact. The contractor must avoid and minimise the emission of particulates emitted from the construction site as far as is reasonably practicable.
0.1.6 | Izvajalec je pred oddajo ponudbe dolžan pregledati projektno dokumentacijo in ostale pogoje, ki so del razpisne dokumentacije V primeru morebitnih napak in neskladij je izvajalec dolžan na to opozoriti naročnika pred oddajo ponudbe. | The Contractor is obliged to review the project documentation and other conditions forming part of the tender documentation before submitting the tender In case of any errors or inconsistencies, the Contractor is obliged to bring these to the attention of the Contracting Authority before submitting the tender.
0.1.7 | Pred oddajo ponudbe je izvajalec dolžan preveriti ustreznost popisov del in količin v teh popisih ter njihovo skladnost z ostalimi dokumenti projektne dokumentacije, ki so del razpisne dokumentacije. Prav tako je izvajalec dolžan preveriti vse detajle in sheme. Vse izmere je potrebno preveriti po posameznih projektih oz. načrtih, ki sestavljajo razpisno dokumentacijo. V primeru ugotovljenih neskladij je v času priprave ponudbe obvezan o tem obvestiti naročnika. | Before submitting a tender, the Contractor shall check the adequacy of the inventories of works and quantities in these Bills of Quantities and their conformity with the other documents of the project documentation forming part of the tender documentation. The Contractor shall also check all details and diagrams. All measurements shall be checked against the individual projects or plans forming part of the tender documentation. In the event of any discrepancies, the Contractor shall inform the Contracting Authority at the time of preparing the tender.
0.1.8 | Pred oddajo ponudbe je izvajalec dolžan v tem popisu preveriti zmnožke in seštevke ter prenose le-teh v rekapitulacijo. Izvajalec se s pripravo ponudbe obvezuje, da je prebral vse celice in elemente celotnega popisa, vključno z vsemi postavkami in splošnimi navodili ali določili in je preveril pravilnost preračuna ter s tem zagotavlja ponudbeno vrednost. | Before submitting a tender, the Contractor is required to check the products and totals in this Bill of Quantities (BoQ) and their transfer to the recapitulation. The Contractor undertakes, by preparing a tender, to have read all the cells and elements of the complete BoQ, including all headings and general instructions or provisions, and to have checked the correctness of the conversion, thereby guaranteeing the value of the tender.
0.1.9 | Dela bo izvajalec moral izvajati po predloženi projektni dokumentaciji, detajlih in z upoštevanjem navodil in potrditev projektanta, nadzornika in investitorja. Vso potrebno delavniško dokumentacijo zagotovi izvajalec del v okviru ponujene cene. | The Contractor shall carry out the works in accordance with the submitted design documents, details and subject to the instructions and approvals of the Designer, the Supervisor and the Investor. All necessary workshop documentation shall be provided by the Contractor within the scope of the price quoted.
0.1.10 | Pred izvedbo posameznih del je izvajalec dolžan pregledati projektno dokumentacijo za izvedbo gradnje (PZI) in elaborate. Na morebitne napake v dokumentaciji ali neskladja med posameznimi načrti ali deli načrtov (popisi del, tehnična poročila, lokacijski in tehnični prikazi) izvajalec opozori nadzornika in projektanta, in se z njima pravočasno uskladi. | The Contractor shall review the Detailed Design documentation (PZI) and the studies before carrying out the individual works. The Contractor shall draw the attention of the Supervisor and the Designer to any errors in the documentation or discrepancies between the individual designs or parts of designs (BoQ, technical reports, location and technical drawings) and shall coordinate with them in good time.
0.1.11 | Tehnični opisi, prikazi, detajli, sheme ter ostali dokumenti v PZI dokumentaciji predstavljajo dodaten opis popisnih postavk gradbeno obrtniških in inštalacijskih del ter jih je potrebno dosledno upoštevati skupaj s popisom del. | The technical descriptions, illustrations, details, diagrams and other documents in the Detailed Design documentation (PZI) are additional descriptions of the BoQ inventory items of the building, construction and installation works and must be strictly followed together with the BoQ.
0.1.12 | Specifikacije in zahteve, navedene v popisu, se ne smejo upoštevati kot edine zahteve. Izvajalec je dolžan v ceni zajeti in dobaviti vse elemente opreme ter opraviti dela in storitve, ki niso eksplicitno navedeni, a so bistvenega pomena za funkcionalnost, skladnost s predpisi ter kontinuirano, zanesljivo in varno obratovanje opreme. | The specifications and requirements set out in the BoQ shall not be taken as the only requirements. The Contractor shall be obliged to include in the price and supply all items of equipment and to carry out works and services which are not expressly mentioned but which are essential for the functionality, regulatory compliance and continuous, reliable and safe operation of the equipment.
0.1.13 | Vsa dela morajo biti izvedena kvalitetno in iz materialov z zahtevanimi lastnostmi, izvedena skladno z veljavno zakonodajo in z upoštevanjem navodil za vgradnjo za izbrane materiale in opremo, s predložitvijo predpisanih izjav o lastnostih in/ali certifikatov. Vsi gradbeni proizvodi (GP) morajo biti označeni s CE oznako. | All work shall be of good quality and be executed with materials of the required characteristics, in accordance with the applicable legislation and in compliance with the installation instructions for the materials and equipment selected, and shall be accompanied by the prescribed declarations of performance and/or certificates. All construction products (GP) shall bear the CE marking.
0.1.14 | Za vsako opisano delo v popisu je potrebno upoštevati celotno potrebno delo, ves osnovni in pomožni material, prevoz materiala in orodja na objekt, notranje transporte, delovne in pomožne odre, zaključno čiščenje in odstranitev odpadkov po dovršenem delu. | For each work described in the inventory, the total work required, all basic and ancillary materials, the transport of materials and tools to the site, internal transports, working and ancillary scaffolding, final cleaning and the disposal of waste after the work has been completed must be taken into account.
0.1.15 | Vsa delovna sredstva, organizacija in koordinacija del, pripravljalna, spremljajoča in zaključna dela, potrebni montažni in tesnilni materiali ter podkonstrukcije so sestavni del posameznih postavk. | All labour, organisation and coordination of the works, preparatory, accompanying and finishing works, necessary prefabrication and sealing materials and substructures are part of the individual items.
0.1.16 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - načrt organizacije gradbišča s podrobnim terminskim planom in izvedba vseh pripravljalnih del, postavitev, organizacija, zaščita in prijava gradbišča, gradbiščnih objektov, ureditev začasnih deponij, tekoče vzdrževanje, skupaj s plačilom splošnih stroškov pristojbin in davkov upravnih organov, pridobivanju raznih dovoljenj in soglasij za izvedbo, ograditev gradbišča in postavitev gradbene table in prometne signalizacije, zagotavljanje ustrezne varnosti na gradbišču, tekoče vzdrževanje in končna odstranitev gradbišča; - zagotovitev potrebnih začasnih površin za transportne poti in gradnjo izven območja gradbišča s plačilom stroškov za sanacijo in vzpostavitev okoliških zemljišč in objektov v prvotno stanje (soglasja, odškodnine, itd.); - začasni odvoz, deponiranje in vračanje izkopanega materiala, ki ga ne bo možno deponirati na gradbišču; - odvoz in zagotovitev odstranjevanja odpadnega gradbenega materiala skladno z zakonodajo na področju ravnanja z odpadki (odvoz na urejene deponije s plačilom komunalnih prispevkov in taks itd.); - oteženi izkop v mokrem terenu, izkop v vodi, odvod meteorne vode iz gradbene jame in vode, ki se izceja iz bočnih strani izkopov; - ustrezno varovanje izkopa gradbene jame za objekt in ostalih manjših posameznih izkopov za izvedbo komunalne infrastrukture brez posegov na sosednja zemljišča; - ustrezno varovanje obstoječih objektov, infrastrukture in okolice v času gradnje ter dokumentiranje vseh morebitnih škodnih dogodkov; - pripravljalna, spremljajoča in zaključna dela (zakoličbe, zagotovitev potrebnih komunalnih priključkov za potrebe izvajanja gradnje, izvedba začasnih inštalacij, označevanje podzemnih vodov, postavljanje in vzdrževanje zakoličbenih profilov, izvedba in označevanje novih in starih križanj ter morebitna zaščita križanj komunalnih vodov, geodetski posnetki in izdajanje vmesnih posnetkov izvedene infrastrukture naročniku, izdelava zbirnih kart, itd.), v kolikor ni to drugače določeno; - pridobivanje soglasij in izvedba morebitnih zapor na vseh cestah s plačilom stroškov, nadomestil in pristojbin; - zagotovitev oz. postavitev in končna odstranitev po zaključku gradnje začasnih skladišč in začasnega pisarniškega kontejnerskega objekta vključno z opremo za dve delovni mesti in za skupne operativne sestanke vel. ca. 40 m2 za potrebe naročnika, s tekočim vzdrževanjem in čiščenjem. | The following must also be included or taken into account in the uniform prices for individual items: - a construction site organisation plan with a detailed timetable and the execution of all preparatory works, the setting-up, organisation, protection and registration of the construction site, site facilities, the arrangement of temporary storage facilities, ongoing maintenance, including the payment of general costs of fees and taxes of the administrative authorities, the obtaining of various permits and consents for the execution, the fencing of the site and the erection of construction signs and traffic signals, the provision of adequate security on the site, ongoing maintenance and the final dismantling of the construction site; - provision of the necessary temporary areas for transport routes and off-site construction, with costs for restoration and reinstatement of surrounding land and buildings (consents, compensation, etc.); - temporary removal, storage and return of excavated material that cannot be stored on site; - removing and disposing of waste building materials in accordance with waste management legislation (removal to regulated landfill sites with payment of municipal fees and charges, etc.); - difficult excavation in wet ground, excavation in water, drainage of rainwater from the construction pit and water draining from the sides of excavations; - adequate protection of the excavation of the construction pit for the building and other small individual excavations for the implementation of the utility infrastructure without encroaching on neighbouring land; - adequate protection of existing facilities, infrastructure and the surrounding area during construction, and documentation of any damage incidents; - preparatory, accompanying and finishing works (stake-out, provision of the necessary utility connections for the needs of construction, execution of temporary installations, marking of underground lines, installation and maintenance of stake-out profiles, execution and marking of new and old crossings and possible protection of crossings of utility lines, geodetic surveys and issuing of intermediate images of the completed infrastructure to the client, production of summary maps, etc.), unless otherwise specified; - obtaining consents and implementing any road closures, with costs, compensation and fees; - provision or erection and final removal on completion of construction of temporary storage and temporary office container building including equipment for two workstations and for joint operational meetings of approx. 40 m2 for the needs of the client, with ongoing maintenance and cleaning.
0.1.17 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - izdelava montažne tehnične dokumentacije, detajlov izvedbe in vse druge potrebne delavniške dokumentacije (s področja arhitekture, gradbeništva, elektrotehnike, strojništva in zunanje ter krajinske ureditve) ter pridobitev obvezne potrditve s strani projektanta, nadzornika in investitorja; - odprava vseh vrst inštalacijskih kolizij z izvajanjem potrebnih premikov inštalacij in njihovim usklajevanjem na mestu montaže, vse v obsegu, ki ne vpliva na projektirano rešitev ali tip inštalacij oz. opreme; - zagotavljanje kompletnosti elektro-instalacijskih sistemov s področja avtomatike za doseganje njihove popolne funkcionalnosti delovanja; - stroški za nadzor in koordinacijo izvedbe vseh elektro napeljav, ki so predmet končne instalacije proizvoda (senčila, vrata, okna,…); - izdelava montažnih skic in detajlov za izvedbo v dogovoru z vodjo gradnje in nadzornikom; - izdelava in predstavitev vzorcev v ustrezni velikosti za potrditev projektanta, nadzornika in investitorja; - zagotavljanje varnosti in zdravja pri delu, zlasti izvajanje vseh del, ki izhajajo in ukrepov, ki izhajajo iz določil veljavnih predpisov varstva pri delu in zahtev Varnostnega načrta;- stroški garancij, ki jih mora izvajalec predložiti naročniku. | The following must also be included or taken into account in the uniform prices for individual items: - preparation of prefabricated technical documentation, construction details and all other necessary workshop documentation (architectural, civil, electrical, mechanical, exterior and landscaping) and obtaining the mandatory approval of the designer, the supervisor and the investor; - elimination of all types of installation conflicts by carrying out the necessary relocation of installations and their coordination at the installation site, all to the extent that it does not affect the design solution or the type of installation or equipment; - ensuring the completeness of electrical installation systems in the automation sector to achieve their full operational functionality; - the cost of supervising and coordinating the installation of all the electrical installations that are the subject of the final installation of the product (blinds, doors, windows, etc.); - preparation of erection drawings and details for implementation in agreement with the construction manager and supervisor; - production and presentation of samples in appropriate sizes for the approval of the designer, the supervisor and the investor; - ensuring health and safety at work, in particular the implementation of all the works arising from and the measures resulting from the provisions of the applicable occupational safety regulations and the requirements of the Safety Plan; - the cost of the guarantees to be provided by the contractor to the client.
0.1.18 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - strošek vodje del glavnega izvajalca, ki bo izvajal tudi koordinacijo s podizvajalci in z drugimi izvajalci, ki jih bo izbral naročnik in bo opravljal delo vodje gradbišča; - koordinacija del z ostalimi izvajalci oz. podizvajalci del, projektantom, nadzornikom in investitorjem pri medsebojnem usklajevanju organizacije gradbišča in časovnega načrta del ter pri usklajevanju izdelave plana montaže, potrjenih s strani vseh udeležencev gradnje; - stroški koordinacije, sodelovanja in usklajevanja z dobavitelji tehnološke, laboratorijske, eksperimentalne in vse ostale pohištvene ter multimedijske opreme ter z vsemi ostalimi dobavitelji oz. podizvajalci na objektu; - stroški izdelave situacij; - stroški zavarovanja objekta v času izvedbe del in delavcev ter materiala na gradbišču v času izvajanja del, od začetka del do pridobitve uporabnega dovoljenja za objekt. Zavarovanje mora biti sklenjeno pri ustrezni zavarovalni družbi najmanj v višini pogodbene vrednosti ali v zakonsko predpisani vrednosti (v kolikor zavarovanje v višini pogodbene vrednosti presega zakonsko dovoljeno), za ves čas trajanja izvedbe del do uspešne primopredaje objekta; - preizkušanje kvalitete materiala, ki se vgrajuje in dokazovanje kvalitete s certifikati oz. tehničnimi soglasji; - izvedba vseh zahtevanih testov in preizkusov (npr. tlačni preizkusi, termografski pregledi, meritve elektromagnetnega sevanja, hrupa, itd.), poskusnega obratovanja celotnega objekta s poudarkom na vseh inštalacijah ter izvajanje predpisanega monitoringa v skladu s Poročilom o vplivih na okolje (pred gradnjo, med gradnjo in po končani gradnji); - izdelava izkaza požarne varnosti, vključno s sprotnim spremljanjem gradnje in izvajanjem požarnovarnostnih zahtev ter izdelava Požarnega reda z obveznimi prilogami; - izdelava Izkaza zaščite pred hrupom v stavbah; - izdelava Izkaza energijskih lastnosti stavbe in energetske izkaznice; - sodelovanje z izvajalci gradbenega in projektantskega nadzora in investitorjem za izvedbo tehničnega pregleda in priprava primopredaje, ki mora vsebovati vso zahtevano dokumentacijo, predvsem pa: izjave o skladnosti, požarni izkaz in ostale izkaze ter obvezne tabele, dokazilo o zanesljivosti objekta (DZO), certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo in vzdrževanje ter vse ostale dokumente v skladu s predpisi in pogodbenimi določili. | The following must also be included or taken into account in the uniform prices of the individual items: - the cost of a works manager for the main contractor, who will also coordinate with subcontractors and other contractors selected by the client and act as site manager; - coordination of the works with other contractors or subcontractors, the designer, the supervisor and the investor in coordinating the organisation of the construction site and the timetable for the works, and in coordinating the production of an installation plan approved by all the participants in the construction; - the costs of coordination, cooperation and coordination with suppliers of technological, laboratory, experimental and all other furniture and multimedia equipment, as well as with all other suppliers or subcontractors on the site; - the cost of drawing up situations; - the cost of insuring the building during the execution of the works and the workers and materials on site during the execution of the works, from the start of the works until the building has been licensed for occupation. The insurance must be taken out with a suitable insurance company for at least the contract value or the legal value (if the insurance for the contract value exceeds the legal value), for the entire duration of the works until the successful handover of the building; - testing the quality of the material to be installed and proving it with certificates or technical approvals; - carrying out all required tests and trials (e.g. pressure tests, thermographic inspections, electromagnetic radiation measurements, noise measurements, etc.), trial operation of the entire building, with emphasis on all installations, and carrying out the required monitoring in accordance with the Environmental Impact Assessment Report (before, during and after construction); - preparation of a fire safety statement, including ongoing monitoring of construction and implementation of fire safety requirements, and preparation of a Fire Safety Order with mandatory annexes; - preparation of a Noise Protection Statement for buildings; - preparation of the Building Energy Performance Report and Energy Performance Certificate; - cooperation with the construction and design supervision contractors and the investor to carry out the technical inspection and prepare the handover, which must include all the required documentation, in particular: declarations of conformity, fire and other statements and mandatory tables, proof of reliability of the building (DZO), certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use and maintenance, and all other documents in accordance with the regulations and the contractual provisions.
0.1.19 | V enotnih cenah posameznih postavk, ki se nanašajo na opremo in posamezne sisteme, mora biti zajeto oz. upoštevano tudi naslednje: - dobava oz. transport, - stroški za vse delovne stroje za dvigovanje bremen in delovne košare za dostope do delovišč; - morebitni stroški povzročeni upravljavcem GJI, ki bi nastali v zvezi s predmetno gradnjo; - montaža, vključno s pomožnim montažnim materialom (vezni, tesnilni in pritrdilni material, sidra, nosilni profili, podkonstrukcije in podobno) in navodili proizvajalca, - odprava vseh kolizij sistemov s stenami in med sistemi, - izvedba vseh potrebnih tesnjenj, - priključitev in nastavitve, vključno z morebitnim kalibriranjem, - zagon, testiranje in meritve, vključno s poročili, - šolanje uporabnikov oz. vzdrževalnega osebja za uporabo in vzdrževanje sistemov, - navodila za obratovanje in vzdrževanje, - vsi potrebni certifikati, izjave o skladnosti oz. potrdila ter - vsa druga pomožna dela in material, da se zagotovi funkcionalnost posamezne postavke popisa. | The following must also be included or taken into account in the uniform prices for individual items relating to equipment and individual systems: - delivery/transport, - the cost of all lifting machines and work baskets for access to work sites; - any costs incurred to the operators of utility infrastructure (GJI) in connection with the subject construction; - installation, including ancillary installation materials (bonding, sealing and fixing materials, anchors, support profiles, substructures, etc.) and manufacturer's instructions, - eliminating all system-to-wall and system-to-system collisions, - all necessary sealing work, - connection and set-up, including calibration if necessary, - commissioning, testing and measurements, including reports, - training users or maintenance staff in the use and maintenance of the systems, - operating and maintenance instructions, - any necessary certificates, declarations of conformity or attestations; and - all other ancillary works and materials to ensure the functionality of each inventory item.
0.1.20 | Vsi odri morajo biti upoštevani v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All scaffolding must be included in the uniform prices of the items listed, except where specifically mentioned.
0.1.21 | Vsi delovni in pomožni odri, lestve in ostala potrebna pomožna sredstva, kot tudi čiščenje vseh elementov po končanih delih, mora biti upoštevano v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All working and auxiliary scaffolding, ladders and other necessary ancillaries, as well as the cleaning of all elements after completion of the works, shall be included in the uniform prices of the items listed, except those specifically mentioned.
0.1.22 | Delavniško dokumentacijo za vse nosilne jeklene konstrukcije in podkonstrukcije izdela izvajalec, strošek izdelave delavniške dokumentacije se upošteva v ponujenih cenah in se ne obračuna posebej. | The cost of the shop drawings for all steelwork and substructures shall be included in the prices quoted and shall not be charged separately.
0.1.23 | V enotnih cenah postavk mora biti vključeno tudi vgrajevanje vseh instalacijskih razvodov v opaže armirano betonskih elementov in izdelava prehodov inštalacij ter dodatno izrezovanje utorov in prebojev v kamnite, zidane ali armirano-betonske stene, ponovno demontiranje in montiranje vseh vrst montažnih sten, vsa dodatna dela za zagotavljanje primernih križanj med posameznimi instalacijskimi vodi, izdelava vseh vrst ojačitev konstrukcij in podobna dela, ki zagotavljajo kakovostno vgradnjo vseh vrst instalacijskih vodov in niso posebej navedena v popisu GOI del. V ponudbi morajo biti upoštevana vsa drobna strojna in elektro instalacijska dela in transporti. | The installation of all installation ducts in the formwork of reinforced concrete elements and the construction of installation penetrations, as well as the additional cutting of grooves and penetrations in stone, masonry or reinforced concrete walls, the reassembly and reinstallation of all types of prefabricated walls, all additional work to ensure adequate crossings between individual installation ducts, the construction of all types of structural reinforcement and similar work to ensure the quality installation of all types of installation ducts and not specifically mentioned in the BoQ of the Construction, installation and finishing works (GOI) shall also be included in the uniform prices of the items. The tender shall take into account all minor mechanical and electrical installation work and transport.
0.1.24 | Vsi kovinski elementi in konstrukcije, ki bi lahko bili izpostavljeni atmosferskim in ostalim korozijskim vplivom, morajo biti ustrezno protikorozijsko zaščiteni. | All metallic elements and structures that could be exposed to atmospheric and other corrosive influences must be adequately protected against corrosion.
0.1.25 | Za vse večje jeklene dele se skladno s predpisi, izdelajo ustrezne ozemljitve, nevidno pritrjene in speljane na splošno ozemljitev objekta. | For all major steel parts, appropriate earth connections shall be made in accordance with the regulations, invisibly attached and connected to the general earth of the building.
0.1.26 | Za vse vidne elemente in serijske elemente je obvezna predhodna uskladitev obdelav, barv in materialov s projektantom na podlagi dostavljenih vzorcev v ustrezni velikosti. Obvezna je preveritev dejanskih mer na licu mesta in posledična prilagoditev elementov in njihove montaže. | For all visible elements and serial elements, it is mandatory to coordinate the finishes, colours and materials with the designer beforehand on the basis of the supplied samples in the appropriate size. It is mandatory to check the actual dimensions on site and to adjust the elements and their installation accordingly.
0.1.27 | Dimenzije obrtniških izdelkov in količine je potrebno pred naročanjem preveriti na objektu. Potrebna je uskladitev vseh elementov (kljuke, okovje, detajlne konstrukcije in obdelave, itd.) s projektantom, nadzornikom in investitorjem. Izvajalec je dolžan pred izdelavo predložiti projektantu v potrditev ustrezne delavniške načrte in detajle. | The dimensions of the workmanship and quantities must be checked on site before ordering. All elements (hooks, fittings, detailed construction and finishes, etc.) must be coordinated with the designer, the supervisor and the investor. The contractor is obliged to submit the relevant workshop plans and details to the designer for approval before manufacture.
0.1.28 | V posameznih postavkah popisa so navedeni proizvajalci in/ali tipi posameznih sistemov, materialov ali opreme, s čimer so zgolj natančno opredeljene zahtevane tehnične lastnosti. Izvajalec del lahko ponudi nadomesten sistem, material ali opremo drugega proizvajalca in tipa, pri čemer morajo biti tehnične lastnosti ponujenega sistema, materiala ali opreme enakovredne ali boljše od opredeljenih v popisu, dimenzijsko pa ne smejo presegati projektiranih dimenzij. Vse funkcijske in tehnične karakteristike nadomestnih sistemov, materialov ali opreme mora izvajalec dokazati z ustrezno dokumentacijo. Vse morebitne posledice zaradi spremembe sistemov, materialov ali opreme vključno z morebitnimi spremembami oz. dopolnitvami BIM modelov in projektne dokumentacije, stroškovno in časovno bremenijo izvajalca. | The individual items of the Inventory shall specify the manufacturers and/or types of the individual systems, materials or equipment, thereby merely specifying the required technical characteristics. The Contractor may offer a substitute system, material or equipment of a different manufacturer and type, provided that the technical characteristics of the offered system, material or equipment shall be equivalent to or better than those specified in the BoQ, and shall not exceed the design dimensions. All functional and technical characteristics of the substitute systems, materials or equipment shall be demonstrated by the Contractor with appropriate documentation. Any consequences resulting from changes to systems, materials or equipment, including any changes or additions to the BIM models and project documentation, shall be borne by the Contractor in terms of cost and time.
0.1.29 | Vsako zamenjavo, uporabo in končni izbor nadomestnih sistemov, materialov, proizvodov in opreme morajo obvezno in pravočasno (pred dobavo in vgradnjo) pisno potrditi projektant (vseh sodelujočih strok), nadzornik in investitor. | Any replacement, use and final selection of alternative systems, materials, products and equipment must be approved in writing by the designer (of all disciplines involved), the supervisor and the investor in a timely manner (prior to delivery and installation).
0.1.30 | Izvajalec mora v ponudbeno ceno vključiti tudi: - ves čas gradnje sprotno beleženje sprememb oz. odstopanj od PZI dokumentacije, vključno z izdelavo tekstualnega opisa sprememb, - pripravo podlog na nivoju PZI, ki so potrebne za posodobitev oz. uskladitev BIM modela z izvedenim stanjem (LOD 500) in izdelavo projektne dokumentacije izvedenih del (PID), - mesečno predajanje potrjenih sprememb opreme in materiala, ki vplivajo na BIM model, v formatu IFC, - vzdrževanje in uporabljanje pri izvedbi zadnje veljavne revizije PZI dokumentacije, vključno z dopolnitvami PZI načrtov, ki so nastali zaradi sprememb med gradnjo. | The contractor must also include in the tender price: - keeping a record of changes or deviations from the construction documentation (PZI) throughout construction, including a textual description of the changes, - preparation of the Detailed Design (PZI) level documents required to update or align the BIM model with the as-built condition (LOD 500) and the preparation of the as-built project documentation for the works (PID), - monthly submission of approved equipment and material changes affecting the BIM model in IFC format, - maintenance and use in the execution of the last valid revision of the construction documentation (PZI), including additions to the construction design documentation (PZI) resulting from changes during construction.

## 0.2_Uvod-DGNB
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | AKUSTIČNE CELICE | ACOUSTIC CELLS
0.2 | SPLOŠNI TEHNIČNI POGOJI ZA PODROČJE DGNB CERTIFICIRANJA | GENERAL TECHNICAL CONDITIONS FOR DGNB CERTIFICATION
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic entity with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
| Splošni pogoji za področje DGNB certificiranja predstavljajo dopolnilo splošnim tehničnim pogojem in ne odpravljajo drugih obveznosti in odgovornosti, ki jih ima izvajalec v skladu s predpisi in pogodbo. | The General Conditions for DGNB Certification are complementary to the General Technical Conditions and do not exclude other obligations and responsibilities that the Contractor has under the Regulations and the Contract.
0.2.1 | Izvajalec mora v svojih ponudbah upoštevati, da se bo objekt certificiral v skladu z zahtevami DGNB sistema certificiranja trajnostne gradnje, ter pravočasno (vsaj 60 dni pred vgradnjo posameznega produkta) dostaviti vso ustrezno dokumentacijo za vse v ponudbi zajete materiale, elemente in opremo. Zahtevana je uporaba materialov, elementov ali opreme, ki so okolju in ljudem prijazni, energetsko učinkoviti in obenem ustrezajo zahtevam DGNB sistema. Zahtevan nivo certifikata je: ZLATI CERTIFIKAT | The Contractor shall take into account in its tenders that the building will be certified in accordance with the requirements of the DGNB Sustainable Building Certification Scheme and shall deliver all relevant documentation for all materials, elements and equipment included in the tender in a timely manner (at least 60 days before the installation of each product). The use of materials, elements or equipment that are environmentally and human friendly, energy efficient and at the same time meet the requirements of the DGNB system is required. The required level of certification is: GOLD CERTIFICATE
0.2.2 | Podrobnejši opis DGNB sistema in navodila za posamezne kriterije so dostopna v dokumentu"DGNB Criteria Set New Construction Buildings, Version 2020 International", ki je na voljo na DGNB spletni strani https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria | A more detailed description of the DGNB system and guidance on the individual criteria is available in the document "DGNB Criteria Set New Construction Buildings, Version 2020 International", available on the DGNB website https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria
0.2.3 | Izvajalec mora v svojih ponudbah upoštevati, da je potrebno skladno z določili DGNB certifikacijskega sistema, pravočasno (pred pričetkom gradnje) dostaviti vso ustrezno dokumentacijo, za vse v ponudbi zajete materiale, elemente in opremo (tehnični list, varnostni list, izjava o lastnostih, tehnična navodila za ravnanje, servisiranje, vzdrževanje,...) v slovenskem jeziku. Vgradnja kakršnihkoli materialov, elementov ali opreme, se izvede zgolj na podlagi predhodne preveritve posredovane dokumentacije in obenem potrditve s strani nadzornika. | The Contractor must take into account in its tenders that, in accordance with the provisions of the DGNB certification system, all relevant documentation for all materials, elements and equipment included in the tender (technical data sheet, safety data sheet, declaration of properties, technical instructions for handling, servicing, maintenance,...) must be delivered on time (prior to the start of construction) in the Slovene language (in accordance with the provisions of the DGNB certification system). The installation of any materials, elements or equipment shall be subject to prior checking of the submitted documentation and, at the same time, to the approval of the Supervisor.
0.2.4 | Izbrani materiali, elementi, naprave, sistemi in oprema morajo prispevati k večji trajnosti stavbe v smeri zagotavljanja energetske učinkovitosti, ekonomičnega in enostavnega vzdrževanja ter čiščenja, dolge življenjske dobe, uporabe okolju prijaznih materialov ipd. | The materials, elements, appliances, systems and equipment chosen must contribute to the sustainability of the building in terms of energy efficiency, economic and easy maintenance and cleaning, long lifetime, use of environmentally friendly materials, etc.
0.2.5 | Predloženi dokumenti za vse uporabljene materiale, elemente in opremo morajo izpolnjevati zahteve najmanj kakovostne stopnje QS3 (zaželeno QS4), iz dokumenta: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001) | The documents submitted for all materials, components and equipment used shall meet the requirements of at least quality level QS3 (preferably QS4) of the document DGNB Quality Grades for Materials, Components and Equipment (JULFS--7X9001)
0.2.6 | V kolikor izbrani materiali oz. elementi, navedeni v posameznih postavkah, ne ustrezajo vsaj kakovostni stopnji QS3 iz seznama: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), je izvajalec dolžan na to opozoriti projektanta, nadzor in investitorja ter podati predlog ustreznega materiala oz. elementa. | If the selected materials or elements listed in the individual items do not meet at least quality level QS3 of the list of DGNB quality classes for materials, elements and equipment (JULFS--7X9001), the Contractor shall draw this to the attention of the Designer, the Supervisor and the Investor, and shall make a proposal for a suitable material or element.
0.2.7 | Izvajalec lahko v svoji ponudbi predlaga alternativne produkte in rešitve glede na predvidene s projektom, pod pogojem, da le-te prav tako izpolnjujejo vse navedene zahteve. Pri morebitnih predlaganih alternativnih produktih oz. rešitvah je potrebno upoštevati najmanj enake ali boljše lastnosti v smislu življenjske dobe, obstojnosti, ter enostavnosti in stroška čiščenja ter vzdrževanja v primerjavi s projektom predpisanimi rešitvami. Za alternativne rešitve izvajalec pridobi soglasje projektanta, nadzornika in investitorja pred pričetkom gradnje. | The Contractor may propose alternative products and solutions to those envisaged by the project in its tender, provided that they also meet all the requirements set out above. Any alternative products or solutions proposed shall have at least the same or better characteristics in terms of service life, durability, and ease and cost of cleaning and maintenance compared to the solutions envisaged by the project. For alternative solutions, the contractor shall obtain the agreement of the designer, the supervisor and the investor before starting construction.
0.2.8 | Izvajalec med gradnjo dnevno beleži vsa eventualna odstopanja od PZI projektne dokumentacije ter podatke pravočasno posreduje naročniku, nadzoru in projektantu. Potrjene spremembe vnese v podlage za izdelavo PID in posodobitev BIM modelov. | During construction, the Contractor shall record on a daily basis any deviations from the Detailed Design documentation (PZI) and shall provide the information to the Client, Supervision and the Designer in a timely manner. Confirmed changes shall be entered into the basis for the As-built documentation (PID) and BIM model updates.
0.2.9 | Izvajalec med gradnjo sproti izpolnjuje Seznam vseh konstrukcijskih sestav s pripadajočimi vgrajenimi gradbenimi materiali in dokumentira naslednje podatke o vgrajenih materialih (v slovenskem jeziku): - Varnostni list - Tehnični list - Izjavo o lastnostih (če je relevantno) - Izkazovanje morebiti obstoječega okoljskega certifikata (Tip I - okoljski znak ali Tip III - okoljska produktna deklaracija /EPD) - Izjavo proizvajalca ali dobavitelja, da produkt ustreza zahtevam ENV1.2 - Tehnična navodila za ravnanje, servisiranje, vzdrževanje oziroma ostale, z zakonom predpisane dokumente in dokumentacijo. | During construction, the Contractor shall keep a List of all structural assemblies with their associated construction materials and document the following information on the materials installed (in Slovene language): - Safety Data Sheet - Technical Data Sheet - Declaration of performance (if applicable) - Demonstration of any existing environmental certification (Type I - Ecolabel or Type III - Environmental Product Declaration /EPD) - A declaration by the manufacturer or supplier that the product complies with the requirements of ENV1.2 - Technical instructions for handling, servicing, maintenance or other documents and documentation required by law.
0.2.10 | Za vse vgrajene bistvene tehnične sisteme mora izvajalec zagotoviti obstoj pooblaščenega servisa, ki deluje na območju Republike Slovenije, da ima investitor možnost skleniti ustrezno pogodbo o vzdrževanju. Med bistvene tehnične sisteme sodijo npr.: sistemi ogrevanja in hlajenja, priprava tehnoloških medijev, prezračevanje in klimatizacija, sistemi detekcije in gašenja požara, sistemi tehničnega varovanja, BMS in CNS sistemi upravljanja stavbe, razsvetljava, komunikacijski in WI-FI sistemi,... | For all installed essential technical systems, the contractor must ensure the existence of an authorised service centre operating in the territory of the Republic of Slovenia, so that the investor has the possibility of concluding an appropriate maintenance contract. The essential technical systems include, for example: heating and cooling systems, technological media preparation, ventilation and air conditioning, fire detection and extinguishing systems, technical security systems, BMS and CNS building management systems, lighting, communication and WI-FI systems,...
0.2.11 | Zaželeno je, da imajo uporabljeni elementi in materiali okoljsko oznako Tip I. (kot npr. ENCODE, BLUE ANGEL, ipd...). | It is preferable that the elements and materials used have a Type I environmental label (such as ENCODE, BLUE ANGEL, etc...).
0.2.12 | Izvajalec bo za elemente iz lesa moral dokazovati izvor z navedbo izvorne države in tipa lesa, FSC / PEFC certifikat z dodatnim pripadajočim potrdilom Chain of custody-trgovski certifikat dobavitelja - ta se dokazuje z dobavnicami, računi ali enakovredno. Za izdelke iz naravnega kamna iz EU držav je potrebna deklaracija, da je izvor in procesiranje teh izdelkov v celoti v EU državah. Za izdelke iz naravnega kamna, ki prihajajo iz držav izven EU, je potrebno predložiti dokazilo o izpolnjevanju ILO konvencije 182, ki vključuje neodvisna inšpekcijska poročila. | For wood elements, the contractor will be required to provide proof of origin, indicating the country of origin and the type of wood, FSC/PEFC certification with an additional Chain of Custody certificate - the supplier's trade certificate - this shall be evidenced by delivery notes, invoices or equivalent. For natural stone products from EU countries, a declaration that the sourcing and processing of these products is entirely in EU countries is required. For natural stone products from non-EU countries, proof of compliance with ILO Convention 182, including independent inspection reports, is required.
0.2.13 | Izobraževanje udeležencev pri gradnji Izvajalec je dolžan vse udeležence pri gradnji podrobneje seznaniti tudi z relevantnimi koncepti, študijami, elaborati, ki opredelujejo trajnostni način gradnje za naslednja področja: - zaščita pred hrupom (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)) - zaščita pred prašenjem - zaščita tal in podzemne vode (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)), Analiza tveganja za onesnaženje vodnega telesa podzemne vode št. 0346-023/2023, maj 2023 (Geološko projektiranje d.o.o.)) - ravnanje z gradbenimi odpadki (Načrt gospodarjenja z gradbenimi odpadki) Izobraževanja se izvajajo skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.1 1.2, 2.2, 3.2 in 4.2 Training for the parties implementing the construction work | Training of construction participants The contractor is also obliged to inform all construction participants in detail about relevant concepts, studies, elaborations defining sustainable construction methods for the following areas: - noise protection (Environmental Impact Assessment Report No 100123-11523, dated 11.5.2023, supplemented on 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.)) - dust protection - protection of soil and groundwater (Environmental Impact Assessment Report No. 100123-11523, dated 11.5.2023, supplemented 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.), Risk analysis for contamination of the groundwater No. 0346-023/2023, May 2023 (Geološko projektiranje d.o.o.)) - construction waste management (Construction Waste Management Plan) The training shall be carried out in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.1 1.2, 2.2, 3.2 and 4.2 Training for the parties implementing the construction work
0.2.14 | Navodila za obratovanje in vzdrževanje objekta Izvajalec pripravi Navodila za obratovanje in vzdrževanje objekta skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilih: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual | Instructions for the operation and maintenance of the facility The Contractor shall prepare the Operation and Maintenance Instructions for the Facility in accordance with the applicable Slovenian legislation and the DGNB System Instructions specified in the Criteria: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual
0.2.15 | Meritve kontrole kakovosti gradnje Izvajalec mora upoštevati, da se bodo po koncu gradnje izvedle naslednje meritve: - meritve zrakotesnosti - meritve s termokamero (termografija) - meritve akustike - meritve zvočne zaščite ovoja stavbe - meritve zvočne zaščite ločilnih elementov med posameznimi prostori različnih namembnosti - meritve udarnega zvoka - meritve vlažnosti vgrajenih elementov, pred vgradnjo finalnih tlakov - test odvoda dima in toplote Meritve morajo opraviti ustrezno usposobljeni preskusni organi ali strokovnjaki ter rezultate oceniti in primerjati z zahtevami. Obseg opravljenih meritev mora biti sorazmeren z velikostjo zgradbe in mora ustrezno odražati cilj preverjanja kakovosti zgradbe. Smiselno je, da izvajalec del tekom gradnje za sprotno kontrolo kakovosti vgrajenih materialov, elementov in opreme, sam izvaja meritve. Končne meritve (ob primopredaji) izvede tretja oseba kot neodvisna potrditev doseganja zahtev. Meritve se izvajajo skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 2. Quality control measurements | Construction quality control measurements The contractor must take into account that the following measurements will be carried out after completion of the construction: - airtightness measurements - thermal camera measurements (thermography) - acoustics measurements - measurements of the sound insulation of the building envelope - measurements of the sound insulation of the separating elements between different rooms of different uses - impact sound measurements - moisture measurements of the installed elements, prior to the installation of the final flooring - smoke and heat extraction test The measurements shall be carried out by suitably qualified test bodies or experts and the results evaluated and compared with the requirements. The extent of the measurements carried out shall be proportionate to the size of the building and shall adequately reflect the objective of the building quality verification. It is reasonable for the contractor to carry out his own measurements during construction to check the quality of the materials, elements and equipment installed. Final measurements (at handover) are carried out by a third party as an independent confirmation of compliance with the requirements. The measurements shall be carried out in accordance with the applicable Slovenian legislation and the DGNB system instructions specified in the benchmark: PRO 2.2 2. Quality control measurements
0.2.16 | Zagotavljanje kakovosti za uporabljene gradbene proizvode Izvajalec mora zagotavljati izvajanje primerjav med definiranim in dejansko uporabljenim materialom, elementom ali opremo skladno seznamom: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), vključno z dokazno dokumentacijo ugotovitev primerjav ter skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 3.1 Quality assurance for the used construction products | Quality assurance for the construction products used The Contractor shall ensure that comparisons are made between the defined and the actual material, element or equipment used in accordance with the list: DGNB Quality Grades of Installed Materials, Elements and Equipment (JULFS--7X9001), including supporting documentation of the findings of the comparisons, and in accordance with the DGNB system instructions defined in the Criterion: PRO 2.2 3.1 Quality assurance for the used construction products
0.2.17 | Zaščita pred vlago Izvajalec predloži dokumentacijo, ki dokazuje, da je bil izveden program prezračevanja, prilagojen stavbi, s čimer se zagotovi pogoje, da so vgrajeni gradbeni elementi ustrezno suhi, skladno z navodili DGNB opredeljenimi v merilu: PRO 2.2 4.1 Mould prevention | Protection against moisture The Contractor shall provide documentation demonstrating that a building-specific ventilation programme has been implemented to ensure that the building elements installed are adequately dry, in accordance with the DGNB guidelines specified in the criteria: PRO 2.2 4.1 Mould prevention
0.2.18 | Preizkusi delovanja sistemov Izvajalec sodeluje pri izvedbi predhodnega in končnega preizkusa delovanja vseh bistvenih tehničnih komponent stavbe in pripravi ustrezne dokazne dokumentacije ter pri usposabljanju vzdrževalcev/upravljalcev stavbe, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators | System performance tests The Contractor shall be involved in the performance of the preliminary and final performance tests of all essential technical components of the building and the preparation of the relevant supporting documentation, as well as in the training of the maintenance/management staff of the building, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators
0.2.19 | Poročilo o zagonu objekta Izvajalec sodeluje pri pripravi končnega poročila o zagonu objekta, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 5.1 Creation of a detailed final report | Commissioning report The Contractor shall be involved in the preparation of the final commissioning report, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 5.1 Creation of a detailed final report
0.2.20 | Koncept celovitega delovanja sistemov v stavbi Izvajalec sodeluje pri procesu implementiranja stalnega nadzora in nastavitev delovanja stavbe ter usposabljanju vzdrževalcev/upravljalcev stavbe. Navedeno se izvede v skladu z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 6.1 Creation and handover of an integral operating concept | The concept of integrated building systems The contractor is involved in the process of implementing the building's continuous monitoring and settings and training the building's maintenance/management staff. This shall be done in accordance with the DGNB system instructions defined in the benchmark: PRO 2.3 6.1 Creation and handover of an integral operating concept
0.2.21 | Prilagoditev nastavitev sistemov po začetni fazi uporabe objekta Izvajalec sodeluje pri ponovnem pregledu delovanja vseh bistvenih tehničnih sistemov ter eventualni ponovni prilagoditvi teh sistemov s strani strokovnjaka oz. (neodvisne) tretje osebe. Postopek se izvede po približno 10–14 mesecih po zaključku gradnje, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 7.1 Readjustment of the system following initial operating phase | Adjusting system settings after the initial phase of use of the building The Contractor shall be involved in the re-examination of the functioning of all essential technical systems and the possible re-adjustment of these systems by an expert or (independent) third party. The procedure shall be carried out approximately 10-14 months after completion of construction, in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.3 7.1 Readjustment of the system following initial operating phase

## 1.6.2.0_Rekapitulacija
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | AKUSTIČNE CELICE | ACOUSTIC CELLS
| REKAPITULACIJA STROŠKOV GRADBENO OBRTNIŠKIH DEL | COST SUMMARY OF CONSTRUCTION AND CRAFT WORKS
| 1 NAČRT S PODROČJA ARHITEKTURE | 1 DOCUMENTATION IN THE FIELD OF ARCHITECTURE
| 1/6 Projektantski popis gradbeno obrtniških del | 1/6 Bill of Quantities of Construction and Craft Works
1.6.2 | GRADBENO OBRTNIŠKA DELA | CONSTRUCTION AND CRAFT WORKS
1.6.2.1 | GRADBENA DELA | CONSTRUCTION WORKS | 0
0% | NEPREDVIDENA DELA | UNFORSEEN WORKS | 0
1.6.2.2 | ZAKLJUČNA OBRTNIŠKA DELA | CRAFT WORKS | 0
0% | NEPREDVIDENA DELA | UNFORSEEN WORKS | 0
| SKUPAJ GRADBENO OBRTNIŠKA DELA | TOTAL CONSTRUCTION AND CRAFT WORKS | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT

## 1.6.2.1.0_Rekapitulacija_G_del
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | AKUSTIČNE CELICE | ACOUSTIC CELLS
| REKAPITULACIJA STROŠKOV GRADBENIH DEL | COST SUMMARY OF CONSTRUCTION WORKS
| 1 NAČRT S PODROČJA ARHITEKTURE | 1 DOCUMENTATION IN THE FIELD OF ARCHITECTURE
| 1/6 Projektantski popis gradbeno obrtniških del | 1/6 Bill of Quantities of Construction and Craft Works
1.6.2.1 | GRADBENA DELA | CONSTRUCTION WORKS
1.6.2.1.1 | BETONSKA DELA | CONCRETE WORKS | 0
1.6.2.1.2 | ZIDARSKA DELA | MASONRY WORKS | 0
1.6.2.1.3 | TESARSKA DELA | TESAR WORKS | 0
1.6.2.1.4 | PLAVAJOČE PLOŠČE | FLOATING PANELS | 0
0
0 | NEPREDVIDENA DELA | UNFORSEEN WORKS | 0
| SKUPAJ GRADBENA DELA | TOTAL CONSTRUCTION WORKS | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT

## 1.6.2.1.1_Betonska_dela
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | AKUSTIČNE CELICE | ACOUSTIC CELLS
1.6.2.1 | GRADBENA DELA | CONSTRUCTION WORKS
1.6.2.1.1 | BETONSKA DELA | CONCRETE WORKS |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
1.1 | BETONSKA DELA | CONCRETE WORKS
| OPOMBA: Pri izdelavi ponudbe upoštevati pripombe, iz poglavja 0.1 UVOD Pri izdelavi popisa upoštevati pripombe, iz poglavja 0.2 UVOD - DGNB in dokument: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme. | NOTE: Take into account the comments made in section 0.1 INTRODUCTION when preparing the offer In the preparation of the inventory, take into account the comments made in Section 0.2 INTRODUCTION - DGNB and the document DGNB Quality Grades of Installed Materials, Elements and Equipment.
| • Vse mere preveriti na lokaciji vgradnje in uskladiti z arhitekturnimi risbami. • Pri izvedbi je potrebno upoštevati načrte, na katerih so prikazane trase inštalacijskih vodov ter pred vgradnjo upoštevati vse elemente, ki so zajeti v načrtu s področja strojništva. • Pri samem vgrajevanju betona je potrebno upoštevati tudi vse elemente masivnih vrat in elementov, ki niso del tega popisa, glej tloris pritličja. • Pred izvedbo mora izvajalec izdelati na svoje stroške: Projekt izvajanja betonskih konstrukcij, ki ga pripravi specializiran tehnolog za beton. V Projektu izvajanja betonskih konstrukcij je potrebno predvideti vse potrebne dodatke, način izvedbe in način vzdrževanja. • Med izvedbo gradbenih posegov mora biti zagotovljen strokovni nadzor, ki bo zagotavljal skladnost gradnje s pogoji iz gradbenega dovoljenja ter kvaliteto izvedenih del v skladu z gradbenimi predpisi. • Za vgradnjo dilatacijskih elementov, pokrovov jaškov in kanalet upoštevati navodila dobavitelja. • V primeru nejasnosti, spremenjenih pogojev ali odstopanja od projekta se je potrebno posvetovati s projektantom. | - All dimensions to be verified at the installation site and coordinated with the architectural drawings. - The plans showing the routes of the installation lines must be followed and all the elements covered by the mechanical engineering plan must be taken into account before installation. - The concrete itself must also take into account all the elements of the solid doors and elements not included in this inventory, see ground floor plan. - Prior to execution, the Contractor shall draw up, at his own expense, a Concrete Execution Project prepared by a specialist concrete technologist. The Concrete Execution Project shall provide for all necessary additions, the method of execution and the method of maintenance. - During the construction works, professional supervision must be provided to ensure that the construction complies with the conditions of the building permit and that the quality of the works is in accordance with the building regulations. - Follow the supplier's instructions for the installation of expansion joints, manhole covers and ducts. - In case of any ambiguity, changed conditions or deviation from the design, the designer should be consulted.
| Splošna opomba za vse betonske konstrukcije: ~ vsi vgrajeni betoni morajo izpolnjevati zahteve SIST EN 206, SIST EN 1026 in SIST EN 1992-1-1; ~ za vse betonske konstrukcije velja zahteva za 2. izvedbeni razred in 1. tolerančni razred po SIST EN 13670 in nacionalnem dodatku, kar je potrebno upoštevati pri pripravi in izvajanju programa kontrole kakovosti in projekta betona; ~ na proste robove vidnih površin se v opaž vgradi trikotne letve; ~ za vse vidne površine brez posebnih arhitekturnih oz. drugih zahtev in za nevidne površine veljajo zahteve za obdelavo površin po SIST EN 13670 in nacionalnem dodatku, kar je potrebno upoštevati pri izbiri opažev: - vidne površine • opažene površine enostavna VB2 • neopažene površine osnovna - nevidne površine: • opažene: enostavna/VB0 • neopažene: enostavna ~ za izvedbo zaščitnih slojev glej armaturni načrt. | General note for all concrete structures: ~ All concrete installed shall comply with the requirements of SIST EN 206, SIST EN 1026 and SIST EN 1992-1-1; ~ all concrete structures are subject to the requirement for Performance Class 2 and Tolerance Class 1 in accordance with SIST EN 13670 and the National Supplement, which must be taken into account in the preparation and implementation of the quality control programme and the concrete design; ~ triangular battens shall be installed in the formwork at the free edges of the visible surfaces; ~ all visible surfaces without special architectural or other requirements and invisible surfaces are subject to the surface treatment requirements of SIST EN 13670 and the National Supplement, which must be taken into account when selecting the formwork: - visible surfaces - observed surfaces easy VB2 - unnoticed areas basic - invisible surfaces: - sightings: easy/VB0 - undetected: easy ~ see reinforcement plan for the design of the protective layers.
| Opomba: Kjer je finalni tlak epoksi, je zahtevana ravnost tal po DIN 18202, tabela 3, za skupino 4. Priprava površine za nanos epoksidnega tlaka. Zahteve upoštevati v cenah. | Note: Where the final flooring is epoxy, the floor flatness is required according to DIN 18202, table 3, for group 4. Surface preparation for application of epoxy flooring. Requirements to be taken into account in the pricing.
| Pri betonskih estrihih in tlakih, je potrebno v ceni upoštevati tudi naklone za odvodnjavanje - glej v načrtih arhitekture. | For concrete screeds and floors, drainage slopes must also be taken into account in the price - see architectural plans.
| Vsi delovni odri morajo biti upoštevani v cenah na enoto. | All working scaffolds must be included in the unit prices.
| Vsi delovni stiki morajo biti premazani z osnovnim premazom/emulzijo za boljšo vezavo starega in novega betona. Tesnenje delovnih stikov se izvede s tesnilnim trakom, zajeto v poglavju dilatacij in delovnih stikov. Upoštevati v cenah na enoto ter vgraditi po navodilih proizvajalca. | All working joints shall be coated with a primer/emulsion to improve bonding of old and new concrete. Sealing of working joints shall be carried out with sealing tape, covered in the section on expansion joints and working joints. To be taken into account in unit prices and installed according to the manufacturer's instructions.
| Dodatne zahteve - DGNB | Additional requirements - DGNB
| Zaščita pred vlago Predloži se dokumentacija, ki dokazuje, da je bil izveden program prezračevanja, prilagojen stavbi, s čimer se zagotovi, da so vgrajeni gradbeni elementi ustrezno suhi, skladno z navodili DGNB. | Protection against moisture Documentation shall be provided to demonstrate that a ventilation programme adapted to the building has been implemented to ensure that the building elements installed are adequately dry, in accordance with the DGNB guidelines.
| SPLOŠNA DOLOČILA | GENERAL PROVISIONS
1. | Za vse nejasnosti ali variantne rešitve se je obvezno posvetovati s projektantom. | For any ambiguities or alternative solutions, the designer must be consulted.
2. | Vsa dela morajo biti izvršena po določilih veljavnih normativov in v soglasju s tehničnimi predpisi za izvajanje tovrstnih del. | All work must be carried out in accordance with the applicable norms and in conformity with the technical regulations for the execution of this type of work.
3. | Storitve kooperanta obsegajo (če ni z medsebojno pogodbo drugače določeno): | The services of the Cooperator include (unless otherwise specified in a mutual agreement):
| a. snemanje vseh potrebnih izmer na objektu pred pričetkom izvajanja del, | a. recording all necessary measurements on the site before the works start,
| b. pregled in čiščenje podloge, | b. inspection and cleaning of the lining,
| c. nanos izravnalne mase, kjer je to zahtevano po opisu posamezne postavke, | c. application of levelling compound where required by the item description,
| d. vsa dela na objektu vključno z vsemi dajatvami, | d. all works on the building, including all charges,
| e. dobava osnovnega in pomožnega materiala, | e. the supply of basic and ancillary materials,
| f. prevoz materiala in orodja na objekt z vsem potrebnim nakladanjem, ekspeditom, razkladanjem in notranjim transportom do mesta vgrajevanja ter polaganje po opisu posamezne postavke, | f. transport of materials and tools to the site with all necessary loading, forwarding, unloading and internal transport to the installation site and installation as described in each item,
| g. popravila zidov oz. oblog sten, poškodovanih ob izvajanju del ter | g. repairs to walls or wall cladding damaged during the works; and
| h. odstranjevanje preostalega materiala, odnos in odvoz iz gradbišča, končno čiščenje in zavarovanje izvedenih del do predaje in podobno. | h. removal of residual materials, take-off and removal from the site, final cleaning and securing of the works until handover, etc.
4. | Enotne cene morajo vsebovati: | The uniform prices must include:
| a. vsa potrebna dokumentacija za začetek del, | a. all necessary documentation for the start of the works,
| b. vsa potrebna pripravljalna in pospravljalna dela, | b. all necessary preparatory and clean-up work,
| c. pregled in čiščenje podloge, nanos izravnalne mase, kjer je to potrebno, | c. inspection and cleaning of the substrate, application of levelling compound where necessary,
| d. snemanje potrebnih izmer na gradbišču in po načrtih, | d. recording the necessary measurements on site and as planned,
| e. prenos in obeleževanje višinskih točk na objektu, | e. the transfer and marking of height points on the building,
| f. po potrebi izdelava vzorca in vgradnja le-tega na objektu, | f. if necessary, the production of a sample and its installation on site,
| g. ves potrebni material: glavni, pomožni, pritrdilni in vezni material, | g. all necessary materials: main, auxiliary, fixing and binding materials,
| h. vse potrebne transporte in prenose, | h. all necessary transports and transfers,
| i. ustrezno začasno skladiščenje na delovišču, | i. adequate temporary storage on the worksite,
| j. vsa potrebna pomožna sredstva za montažo in demontažo na objektu, | j. all necessary means of assembly and dismantling on site,
| k. uporabo vse potrebne mehanizacije ali drugih delovnih sredstev z vsemi stroški povezanimi s tem, | k. the use of any necessary machinery or other means of work, with all associated costs,
| l. usklajevanje z osnovnim načrtom in posvetovanje s projektantom, | l. coordination with the basic plan and consultation with the designer,
| m. vso potrebno delo do končnega izdelka, | m. all the work needed to get to the finished product,
| n. vso potrebno zunanje (tehnolog, laboratorij) in notranje kontrole kakovosti, | n. all necessary external (technologist, laboratory) and internal quality control,
| o. vsa potrebna dokazovanja kakovosti materiala, pravilnega načina izvedbe in izvedenih del (certifikati uporabljenih materialov, meritve tlačne trdnosti, poročila itd.), | o. all necessary evidence of the quality of the material, the correct method of execution and the work carried out (certificates of materials used, compressive strength measurements, reports, etc.),
| p. terminsko usklajevanje del z ostalimi izvajalci na objektu, | p. coordinating the timing of works with other contractors on site,
| r. vse potrebne ukrepe za doseganje zahtevane kakovosti in rokov iz potrjenega terminskega plana izvajalca (na primer: Pred pričetkom del na akustičnih celicah mora izvajalec organizirati obvezno izobraževanje delavcev, njihovih vodij in koordinatorjev, ki bodo ta dela opravljali.), | r. all the necessary measures to achieve the required quality and the deadlines set out in the contractor's approved schedule (for example: before starting work on the acoustic cells, the contractor must organise mandatory training for the workers, their supervisors and the coordinators who will carry out the work),
| s. popravilo morebitne povzročene škode ostalim izvajalcem na gradbišču, | s. repair any damage caused to other contractors on site,
| š. čiščenje prostorov, nakladanje in odvoz odpadnega materiala na stalno deponijo, | cleaning the premises, loading and removal of waste materials to a permanent landfill,
| t. plačilo komunalnega prispevka za stalno deponijo odpadnega materiala, | t. payment of the municipal contribution for the permanent landfill of waste materials,
| u. vsi ukrepi za zaščito delavcev na gradbišču, skladno z veljavnimi predpisi s področja varnosti in zdravja pri delu, | u. all measures to protect workers on the construction site, in accordance with the applicable occupational safety and health regulations,
| v. v enotnih cenah morajo biti vključeni stroški na stalni deponiji. Izvajalec je dolžan predati vse evidenčne liste o oddaji odpadnega materiala v stalno deponijo, | v. the unit prices shall include the costs at the permanent landfill. The Contractor shall be obliged to hand over all record sheets of the delivery of the waste material to the permanent landfill,
| z. v enotni ceni morajo biti tudi zajeti stroški zaščite dostopnih koridorjev v notranjosti objekta, do prostorov, kjer se izvajajo dela. | z. the unit price must also include the cost of protecting access corridors inside the building to the areas where the work is being carried out.
5. | V primeru da posamezne postavke v popisu ne zajemajo celotnega opisa potrebnega za funkcionalno dokončanje dela, mora ponudnik izvedbo le tega vključiti v ceno na enoto! | In the event that individual items in the inventory do not cover the full description necessary for the functional completion of the work, the tenderer must include this in the unit price!
6. | Vsa dela morajo biti izvršena tako, da je zagotovljena funkcionalnost, stabilnost, varnost, natančnost in življenjska doba posameznih elementov. | All work must be carried out in such a way as to ensure the functionality, stability, safety, precision and service life of the individual components.
| Na vseh betonskih površinah, ki so izvedene v kvaliteti vidnega betona, se luknje od opaža zapolnijo s sanacijsko malto v barvi betona samo v območju luknje - pazljiva obdelava. Izvajalec izdela poskusni vzorec zapolnitve, ki ga potrdi arhitekt. Navedena popravila in popravila ev. nepravilnosti v betonski površini (stiki med opažnimi ploščami, naravnine, gnezda, vidna armatura) morajo biti cenovno upoštevana v ceni opažev. | On all concrete surfaces executed in visible concrete quality, the holes from the formwork shall be filled with remedial mortar in the colour of the concrete only in the area of the hole - careful treatment. The Contractor shall make a trial sample of the filling, which shall be approved by the Architect. The above repairs and repairs of any irregularities in the concrete surface (joints between the formwork slabs, natural joints, nests, visible reinforcement) shall be taken into account in the price of the formwork.
1.1.1 | Dobava, rezanje, krivljenje, polaganje in vezanje rebraste armature B500 B, lastnosti v skladu s SIST EN 10080; 2005. Srednje komplicirana armatura. | Supply, cutting, bending, laying and bonding of ribbed reinforcement B500 B, properties in accordance with SIST EN 10080; 2005. Medium-complex reinforcement. | kg | 70560 |  | 0
1.1.2 | Dobava in vgrajevanje betona v armirane konstrukcije različnih presekov; z vsemi pomožnimi deli in prenosi do mesta vgraditve; AB vertikalne vezi | Supply and installation of concrete in reinforced concrete structures of various cross-sections; with all ancillary works and transfers to the installation site; AB vertical ties
a. | ~ beton C30/37, XC3, Cl0,2, Dmax16 | ~ concrete C30/37, XC3, Cl0.2, Dmax16
a1. | • preseka do 0,04 m3/m1 | - cross-section up to 0,04 m3/m1 | m3 | 50 |  | 0
a2. | • preseka nad 0,04 do 0,08 m3/m1 | - cross-sectional area over 0,04 to 0,08 m3/m1 | m3 | 12 |  | 0
a3. | • preseka nad 0,08 do 0,12 m3/m1 | - cross-sectional area over 0,08 to 0,12 m3/m1 | m3 | 8 |  | 0
a4. | • preseka nad 0,12 do 0,20 m3/m1 | - cross-sectional area over 0,12 to 0,20 m3/m1 | m3 | 4 |  | 0
a5. | • preseka nad 0,20 do 0,30 m3/m1 | - cross-sectional area over 0,20 to 0,30 m3/m1 | m3 | 2 |  | 0
1.1.3 | Dobava in vgrajevanje betona v armirane konstrukcije različnih presekov; z vsemi pomožnimi deli in prenosi do mesta vgraditve; AB horizontalne vezi | Supply and installation of concrete in reinforced concrete structures of various cross-sections; with all ancillary works and transfers to the installation site; AB horizontal ties
a. | ~ beton C30/37, XC3, Cl0,2, Dmax16 | ~ concrete C30/37, XC3, Cl0.2, Dmax16
a1. | • preseka do 0,04 m3/m1 | - cross-section up to 0,04 m3/m1 | m3 | 29 |  | 0
a2. | • preseka nad 0,04 do 0,08 m3/m1 | - cross-sectional area over 0,04 to 0,08 m3/m1 | m3 | 12 |  | 0
a3. | • preseka nad 0,08 do 0,12 m3/m1 | - cross-sectional area over 0,08 to 0,12 m3/m1 | m3 | 6 |  | 0
1.1.4 | Dobava in vgrajevanje betona v armirane konstrukcije različnih presekov; z vsemi pomožnimi deli in prenosi do mesta vgraditve; AB stene | Supply and installation of concrete in reinforced concrete structures of various cross-sections; with all ancillary works and transfers to the installation site; AB walls
a. | ~ beton C30/37, XC3, Cl0,2, Dmax16 | ~ concrete C30/37, XC3, Cl0.2, Dmax16
a1. | • preseka nad 0,12 do 0,20 m3/m2 | - cross-sectional area over 0,12 to 0,20 m3/m2
a1.1. | - višine do 3,00 m | - heights up to 3,00 m | m3 | 128 |  | 0
a1.2. | - višine nad 3,00 do 6,00 m | - heights above 3,00 m to 6,00 m | m3 | 25 |  | 0
a2. | • preseka nad 0,20 do 0,30 m3/m2 | - cross-sectional area over 0,20 to 0,30 m3/m2
a2.1. | - višine do 3,00 m | - heights up to 3,00 m | m3 | 10.5 |  | 0
1.1.5 | Dobava in vgrajevanje betona v armirane konstrukcije različnih presekov; z vsemi pomožnimi deli in prenosi do mesta vgraditve; AB plošče - stropne | Supply and installation of concrete in reinforced concrete structures of various cross-sections; with all ancillary works and transfers to the site of installation; AB slabs - ceiling slabs
a. | ~ beton C30/37, XC3, Cl0,2, Dmax16 | ~ concrete C30/37, XC3, Cl0.2, Dmax16
a1. | • preseka nad 0,12 do 0,20 m3/m2 | - cross-sectional area over 0,12 to 0,20 m3/m2 | m3 | 1 |  | 0
a2. | • preseka nad 0,12 do 0,20 m3/m2 | - cross-sectional area over 0,12 to 0,20 m3/m2 | m3 | 86 |  | 0
1.1.6 | Dobava in vgrajevanje betona v vertikalne vezi in preklade nad vrati; beton C30/37, XC3, CI0,2, Dmax16 - akustične celice | Supply and installation of concrete in vertical ties and lintels above doors; concrete C30/37, XC3, CI0,2, Dmax16 - acoustic cells
a. | ~ preseka do 0,08 m3/m1. | ~ cross-section up to 0,08 m3/m1. | m3 | 7 |  | 0
b. | ~ montaža in demontaža opaža, z višino podpiranja h = 3,00 m | ~ installation and dismantling of formwork, with support height h = 3.00 m | m2 | 94 |  | 0
c. | ~ izdelava, dobava in vgrajevanje armature do fi 12 mm | ~ manufacture, supply and installation of fittings up to 12 mm fi | kg | 950 |  | 0
1.1.7 | AB vezi ob vratnih odprtinah; AB konstrukcija prereza 0,04 do 0,08 m3/m1 - akustične celice | AB ties at door openings; AB construction cross-section 0,04 to 0,08 m3/m1 - acoustic cells
a. | ~ dobava in vgrajevanje betona C25/30, Dmax16 | ~ supply and installation of concrete C25/30, Dmax16 | m3 | 7 |  | 0
b. | ~ montaža in demontaža opaža | ~ installation and dismantling of formwork | m2 | 106 |  | 0
| BETONSKA DELA | CONCRETE WORKS |  |  |  | 0

## 1.6.2.1.2_Zidarska_dela
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | AKUSTIČNE CELICE | ACOUSTIC CELLS
1.6.2.1 | GRADBENA DELA | CONSTRUCTION WORKS
1.6.2.1.2 | ZIDARSKA DELA | MASONRY WORKS |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
1.2 | ZIDARSKA DELA | MASONRY WORKS
| OPOMBA: Pri izdelavi ponudbe upoštevati pripombe, iz poglavja 0.1 UVOD Pri izdelavi popisa upoštevati pripombe, iz poglavja 0.2 UVOD - DGNB in dokument: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme. | NOTE: Take into account the comments made in section 0.1 INTRODUCTION when preparing the offer In the preparation of the inventory, take into account the comments made in Section 0.2 INTRODUCTION - DGNB and the document DGNB Quality Grades of Installed Materials, Elements and Equipment.
| Zidarska dela se morajo izvajati po določilih veljavnih tehničnih predpisov in normativov. | The masonry work shall be carried out in accordance with the provisions of the applicable technical regulations and standards.
| Zidanje mora biti čisto, s pravilno vezavo opeke. Stiki morajo biti dobro zaliti z malto, vrste popolnoma vodoravne, malta pa ne sme biti v debelejšem sloju kot 15 mm. Vse površine morajo biti popolnoma ravne in navpične, odvečna malta iz stikov se mora odstraniti, dokler je še sveža. | The brickwork must be clean, with the bricks properly bonded. The joints must be well flooded with mortar, the courses must be perfectly horizontal and the mortar must not be more than 15 mm thick. All surfaces must be perfectly flat and vertical, and excess mortar from the joints must be removed while it is still fresh.
| Vgrajeni material za ta dela mora po kvaliteti ustrezati določilom veljavnih tehničnih predpisov. | The materials incorporated in these works must meet the quality requirements of the applicable technical regulations.
| Vgrajeni materjali za zidarska dela morajo po kvaliteti ustrezati določilom veljavnih tehničnih predpisov: 5.1. malta za grobi in fini omet: SIST EN 998-1 5.2. malta za zidanje: SIST EN 998-2 5.3. zidarski cement: SIST EN 413-1 5.4. gradbeno apno: SIST EN 459-1 5.4. opečni zidaki: SIST EN 771-1 | The quality of the materials used for the masonry work shall comply with the provisions of the applicable technical regulations: 5.1. mortar for coarse and fine plaster: SIST EN 998-1 5.2. mortar for masonry: SIST EN 998-2 5.3. masonry cement: SIST EN 413-1 5.4. building lime: SIST EN 459-1 5.4. brickwork: SIST EN 771-1
| Standardi za zidarska dela vsebujejo poleg izdelave, opisane v posamezni postavki, še vsa potrebna pomožna dela in sicer: | In addition to the workmanship described under each heading, the standards for masonry work include all the necessary ancillary work, namely:
| a. dela in ukrepe po določilih veljavnih predpisov varstva pri delu, | a. works and measures under the provisions of the applicable occupational safety regulations,
| b. prenos vode za močenje opeke in zidov, premeščanje maltark in občasno mešanje malte, dodajanje materiala in orodja, | b. transferring water for wetting bricks and walls, moving mortars and occasionally mixing mortar, adding materials and tools,
| c. postavitev, premeščanje in odstranitev premičnih odrov višine do 2,00 m, | c. erection, relocation and removal of mobile scaffolding up to 2.00 m in height,
| d. prenos in obeleževanje višinskih točk na objektu in | d. the transfer and marking of height points on the installation; and
| e. čiščenje prostorov, izdelkov in delovnih priprav med delom in po končanem delu. | e. cleaning the premises, products and work preparations during and after work.
| OMETI: | OMETI:
| Standardni za izvedbo ometov vsebujejo poleg opisa, opisane v posamezni potavki še vsa pomožna dela in ukrepe kot sledi: - dela in ukrepe po določilih veljavnih predpisov varstva pri delu, - vsa potrebna merjenja z določanjem točk smeri, višin in ravnin, nameščanje in zaščito oznak, vodil in podobno, - potrebno čiščenje reg in podlog ter vlaženje podlog pred pričetkom del, - izdelava vodil (faž), zaključkov in špalet, - zaščito izdelkov pred mrazom, vročino, vetrom in fizičnim poškodbam, - krpanje poškodovanih podlog, - obračun se vrši v merskih enotah navedenih v posamezni postavki. | In addition to the description given in the individual pot, the standard for the execution of renderings shall include all ancillary works and measures as follows: - work and measures under the applicable occupational health and safety rules, - all necessary measurements by setting points of direction, heights and planes, installing and protecting markings, guides, etc, - cleaning of the racks and subfloors and moistening of the subfloors before starting work, - the manufacture of guides (fascias), finials and spars, - protect products from cold, heat, wind and physical damage, - patching damaged linings, - accounting is in the units of measurement indicated in each item.
| VZIDAVE | IMAGES
| Vse vzidave in zidarske obdelave morajo biti izvršene v skladu s projektno dokumentacijo ali po zahtevah v drugi dokumentaciji. | All erection and masonry work shall be carried out in accordance with the project documentation or as required in other documentation.
| Materjal za vgrajevanje elementov, kot za zidarsko obdelavo mora po kvaliteti ustrezati določilom veljavnih predpisov . | The material used for the installation of the elements, as well as for the masonry work, must meet the quality requirements of the applicable regulations.
| Standardi za vzidave in zidarske obdelave zajemajo poleg del, opisanih v posamezni postavki, še: - merjenje in označevanje lege vzidave elementa, - dolbljenje oz. drug način priprave ležišča pred zalivanjem, - nameščanje, sidranje, opiranje, podpiranje in vezanje elementa za vzidavo. Dobava elementov načeloma ni upoštevana pri vzidavi temveč v obrtniških delih; upoštevati jo je treba samo, če je to v posamezni postavki za vzidave posebej navedeno. | In addition to the work described under each heading, the standards for masonry and masonry workmanship cover: - measuring and marking the position of the element, - dolbing or other preparation of the bed before watering, - installing, anchoring, supporting, bracing and tying the element to be erected. The supply of elements is in principle not included in the erection but in the workmanship; it should only be taken into account if specifically mentioned in the individual item for erections.
| IZOLACIJE | INSULATIONS
| Kot izolacije se smatra vse vrste hidroizolacij temeljev, tlakov, zidov in stropov. Kvaliteta dela in vgrajeni materjali morajo ustrezati določilom veljavnih tehničnih predpisov, normativov in standardov. Standardi za izolacijska dela vsebujejo poleg izdelave, opisane v posamezni postavki, še: - vsa dela in ukrepe po določilih veljavnih predpisov varstva pri delu; - pripravo izolacijskega materjala s prenosom do mesta vgraditve; - napravo izolacij po opisu in tehničnih pogojih proizvajalca. | Insulation is defined as all types of waterproofing of foundations, floors, walls and ceilings. The quality of the work and the materials used must comply with the provisions of the applicable technical regulations, norms and standards. In addition to the workmanship described in each item, the standards for insulation work include: - all work and measures under the applicable occupational health and safety regulations; - preparation of the insulation material by transfer to the installation site; - the installation of the insulations according to the manufacturer's description and specifications.
| SPLOŠNA DOLOČILA | GENERAL PROVISIONS
1. | Za vse nejasnosti ali variantne rešitve se je obvezno posvetovati s projektantom. | For any ambiguities or alternative solutions, the designer must be consulted.
2. | Vsa dela morajo biti izvršena po določilih veljavnih normativov in v soglasju s tehničnimi predpisi za izvajanje tovrstnih del. | All work must be carried out in accordance with the applicable norms and in conformity with the technical regulations for the execution of this type of work.
3. | Storitve kooperanta obsegajo (če ni z medsebojno pogodbo drugače določeno): | The services of the Cooperator include (unless otherwise specified in a mutual agreement):
| a. snemanje vseh potrebnih izmer na objektu pred pričetkom izvajanja del, | a. recording all necessary measurements on the site before the works start,
| b. pregled in čiščenje podloge, | b. inspection and cleaning of the lining,
| c. nanos izravnalne mase, kjer je to zahtevano po opisu posamezne postavke, | c. application of levelling compound where required by the item description,
| d. vsa dela na objektu vključno z vsemi dajatvami, | d. all works on the building, including all charges,
| e. dobava osnovnega in pomožnega materiala, | e. the supply of basic and ancillary materials,
| f. prevoz materiala in orodja na objekt z vsem potrebnim nakladanjem, ekspeditom, razkladanjem in notranjim transportom do mesta vgrajevanja ter polaganje po opisu posamezne postavke, | f. transport of materials and tools to the site with all necessary loading, forwarding, unloading and internal transport to the installation site and installation as described in each item,
| g. popravila zidov oz. oblog sten, poškodovanih ob izvajanju del ter | g. repairs to walls or wall cladding damaged during the works; and
| h. odstranjevanje preostalega materiala, odnos in odvoz iz gradbišča, končno čiščenje in zavarovanje izvedenih del do predaje in podobno. | h. removal of residual materials, take-off and removal from the site, final cleaning and securing of the works until handover, etc.
4. | Enotne cene morajo vsebovati: | The uniform prices must include:
| a. vsa potrebna dokumentacija za začetek del, | a. all necessary documentation for the start of the works,
| b. vsa potrebna pripravljalna in pospravljalna dela, | b. all necessary preparatory and clean-up work,
| c. pregled in čiščenje podloge, nanos izravnalne mase, kjer je to potrebno, | c. inspection and cleaning of the substrate, application of levelling compound where necessary,
| d. snemanje potrebnih izmer na gradbišču in po načrtih, | d. recording the necessary measurements on site and as planned,
| e. prenos in obeleževanje višinskih točk na objektu, | e. the transfer and marking of height points on the building,
| f. po potrebi izdelava vzorca in vgradnja le-tega na objektu, | f. if necessary, the production of a sample and its installation on site,
| g. ves potrebni material: glavni, pomožni, pritrdilni in vezni material, | g. all necessary materials: main, auxiliary, fixing and binding materials,
| h. vse potrebne transporte in prenose, | h. all necessary transports and transfers,
| i. ustrezno začasno skladiščenje na delovišču, | i. adequate temporary storage on the worksite,
| j. vsa potrebna pomožna sredstva za montažo in demontažo na objektu, | j. all necessary means of assembly and dismantling on site,
| k. uporabo vse potrebne mehanizacije ali drugih delovnih sredstev z vsemi stroški povezanimi s tem, | k. the use of any necessary machinery or other means of work, with all associated costs,
| l. usklajevanje z osnovnim načrtom in posvetovanje s projektantom, | l. coordination with the basic plan and consultation with the designer,
| m. vso potrebno delo do končnega izdelka, | m. all the work needed to get to the finished product,
| n. vso potrebno zunanje (tehnolog, laboratorij) in notranje kontrole kakovosti, | n. all necessary external (technologist, laboratory) and internal quality controls,
| o. vsa potrebna dokazovanja kakovosti materiala, pravilnega načina izvedbe in izvedenih del (certifikati uporabljenih materialov, meritve tlačne trdnosti, poročila itd.), | o. all necessary evidence of the quality of the material, the correct method of execution and the work carried out (certificates of materials used, compressive strength measurements, reports, etc.),
| p. terminsko usklajevanje del z ostalimi izvajalci na objektu, | p. coordinating the timing of works with other contractors on site,
| r. vse potrebne ukrepe za doseganje zahtevane kakovosti in rokov iz potrjenega terminskega plana izvajalca, | r. all necessary measures to achieve the required quality and the deadlines set out in the Contractor's approved schedule,
| s. popravilo morebitne povzročene škode ostalim izvajalcem na gradbišču, | s. repair any damage caused to other contractors on site,
| š. čiščenje prostorov, nakladanje in odvoz odpadnega materiala na stalno deponijo, | cleaning the premises, loading and removal of waste materials to a permanent landfill,
| t. plačilo komunalnega prispevka za stalno deponijo odpadnega materiala, | t. payment of the municipal contribution for the permanent landfill of waste materials,
| u. vsi ukrepi za zaščito delavcev na gradbišču, skladno z veljavnimi predpisi s področja varnosti in zdravja pri delu, | u. all measures to protect workers on the construction site, in accordance with the applicable occupational safety and health regulations,
| v. v enotnih cenah morajo biti vključeni stroški na stalni deponiji. Izvajalec je dolžan predati vse evidenčne liste o oddaji odpadnega materiala v stalno deponijo, | v. the unit prices shall include the costs at the permanent landfill. The Contractor shall be obliged to hand over all record sheets of the delivery of the waste material to the permanent landfill,
| z. v enotni ceni morajo biti tudi zajeti stroški zaščite dostopnih koridorjev v notranjosti objekta, do prostorov, kjer se izvajajo dela. | z. the unit price must also include the cost of protecting access corridors inside the building to the areas where the work is being carried out.
5. | V primeru da posamezne postavke v popisu ne zajemajo celotnega opisa potrebnega za funkcionalno dokončanje dela, mora ponudnik izvedbo le tega vključiti v ceno na enoto! | In the event that individual items in the inventory do not cover the full description necessary for the functional completion of the work, the tenderer must include this in the unit price!
6. | Vsa dela morajo biti izvršena tako, da je zagotovljena funkcionalnost, stabilnost, varnost, natančnost in življenjska doba posameznih elementov. | All work must be carried out in such a way as to ensure the functionality, stability, safety, precision and service life of the individual components.
| Na vseh betonskih površinah, ki so izvedene v kvaliteti vidnega betona, se luknje od opaža zapolnijo s sanacijsko malto v barvi betona samo v območju luknje - pazljiva obdelava. Izvajalec izdela poskusni vzorec zapolnitve, ki ga potrdi arhitekt. Navedena popravila in popravila ev. nepravilnosti v betonski površini (stiki med opažnimi ploščami, naravnine, gnezda, vidna armatura) morajo biti cenovno upoštevana v ceni opažev. | On all concrete surfaces executed in visible concrete quality, the holes from the formwork shall be filled with remedial mortar in the colour of the concrete only in the area of the hole - careful treatment. The Contractor shall make a trial sample of the filling, which shall be approved by the Architect. The above repairs and repairs of any irregularities in the concrete surface (joints between the formwork slabs, natural joints, nests, visible reinforcement) shall be taken into account in the price of the formwork.
| Pri prehodih iz vertikalne v horizontalno hidroizolacijo v ceni upoštevati tudi trikotna polnila, material in montažo, izvedba po navodilih proizvajalca izbrane hidroizolacije. Prav tako morajo biti upoštevani v cenah na enoto vsi preklopi hidroizolacij, geotkstila, čepaste folije itd., skladno z navodili izbranega proizvajalca. | For transitions from vertical to horizontal waterproofing, the price shall also take into account triangular fillers, material and installation, to be carried out according to the instructions of the manufacturer of the chosen waterproofing. All overlaps of waterproofing, geotextiles, sheeting, etc. shall also be included in the unit prices in accordance with the instructions of the selected manufacturer.
| Opomba: v enotnih cenah mora izvajalec zajeti vse pomožne odre za dela na višini: pritličje h = do 5,20 m; nadstropja h = do 4,25 m vključno z montažo in demontažo. | Note: the Contractor shall include in the uniform prices all ancillary scaffolding for work at height: ground floor h = up to 5,20 m; storeys h = up to 4,25 m including erection and dismantling.
| Popis vezan na »školjke« oz. »akustične celice«: Podrobni opis poteka izvedbe akustičnih celic je podan v dokumentu: Tehnični opis in statični izračun akustičnih celic št. JULFS--7G1203. Pred pričetkom del na akustičnih celicah mora izvajalec organizirati obvezno izobraževanje delavcev, njihovih vodij in koordinatorjev, ki bodo ta dela opravljali. Izobraževanje mora dogovoriti in naročiti s projektantskim nadzorom ter predstavniki dobavitelja akustičnih elementov. | Inventory related to "shells" or "acoustic cells": a detailed description of the implementation of the acoustic cells is given in the document: Technical description and static calculation of acoustic cells No JULFS--7G1203. Before starting work on the acoustic cells, the contractor shall organise compulsory training for the workers, their supervisors and the coordinators who will carry out the work. The training shall be agreed and ordered with the design supervision and the representatives of the supplier of the acoustic elements.
1.2.1 | Dobava in zidanje zidov z opažnimi betonskimi zidaki debeline 10 cm, polnjenih z betonom. V ceni zajeti tudi dobova in vgrajevanje betona C25/30 Dmax16 | Supply and erection of 10 cm thick concrete formwork walls, filled with concrete. Price includes supply and installation of C25/30 Dmax16 concrete | m3 | 3.15 |  | 0
1.2.2 | Dobava in zidanje zidov z opažnimi betonskimi zidaki debeline 20 cm, polnjenih z betonom. V ceni zajeti tudi dobova in vgrajevanje betona C25/30 Dmax16 | Supply and erection of walls with 20 cm thick concrete formwork blocks filled with concrete. Price includes supply and installation of concrete C25/30 Dmax16 | m3 | 1030.05 |  | 0
1.2.3 | Dobava in zidanje zidov z opažnimi betonskimi zidaki debeline 30 cm, polnjenih z betonom. V ceni zajeti tudi dobova in vgrajevanje betona C25/30 Dmax16 | Supply and erection of 30 cm thick concrete formwork walls, filled with concrete. The price also includes the supply and installation of C25/30 Dmax16 concrete | m3 | 69.3 |  | 0
1.2.4 | Dobava in vgradnja mineralne kamene volne gostote 30 kg/m3, debeline 10 cm, lepljene na AB stene - zračni prostor med zidovi iz betonskih blokov. Zračni prostor med zidano steno in AB stebri mora biti v celoti zapolnjen z mineralno volno, brez zračnih rež. Sestava NZ-01.7 in NZ-01.7a, NZ-06.1 in NZ-06.2. | Supply and installation of mineral stone wool with a density of 30 kg/m3, 10 cm thick, bonded to AB walls - air space between concrete block walls. The air space between the masonry wall and the AB columns shall be completely filled with mineral stone wool, without air gaps. Composition NZ-01.7 and NZ-01.7a, NZ-06.1 and NZ-06.2. | m2 | 1859.55 |  | 0
1.2.5 | Dobava in vgradnja mineralne kamene volne gostote 30 kg/m3, debeline 20 cm, lepljene na AB stene - zračni prostor med zidovi iz betonskih blokov. Zračni prostor med zidano steno in AB stebri mora biti v celoti zapolnjen z mineralno volno, brez zračnih rež. Sestava NZ-07. | Supply and installation of mineral stone wool, density 30 kg/m3, thickness 20 cm, bonded to AB walls - air space between concrete block walls. The air space between the masonry wall and the AB columns must be completely filled with mineral stone wool, without air gaps. Composition NZ-07. | m2 | 118.65 |  | 0
1.2.6 | Dobava in izdelava notranjega apneno cementnega strojnega ometa, fino zariban kot npr. Baumit MPI 25 ali enakovredno. Omet debeline 2 cm. V enotni ceni upoštevati dobavo in rabiciranje stikov zidanih sten z AB vezmi in prekladami z rabitz mrežo, pasovi širine 50 cm. | Supply and manufacture of internal lime-cement plaster, finely grooved, e.g. Baumit MPI 25 or equivalent. 2 cm thick plaster. Include in the uniform price the supply and rabbeting of the joints of the masonry walls with AB ties and lintels with rabbit netting, 50 cm wide strips.
a. | ~ omet | ~ plaster | m2 | 15949.5 |  | 0
b. | ~ rabiciranje stikov zidanih sten z AB vezmi - vertikalno | ~ Rhabrication of masonry wall joints with AB ties - vertical
| - višina vezi do 3 m | - height of ties up to 3 m | m2 | 4486.65 |  | 0
| - višina vezi 3 do 6 m | - tie height 3 to 6 m | m2 | 3111.15 |  | 0
1.2.7 | Oznaka sestave: NT-06 Medetažna plošča proti garaži - "školjka" laboratoriji (cona hrupa A in B, vibracijska cona VIB1) | Composition code: NT-06 Mezzanine slab facing the garage - "shell" laboratories (noise zones A and B, vibration zone VIB1)
a. | Podlaga: ~ mikroarmirani betonski estrih s fibriliranimi polipropilenskimi vlakni (2000 kg/m3), debeline 14,5 cm | Basis: ~ micro-reinforced concrete screed with fibrillated polypropylene fibres (2000 kg/m3), thickness 14,5 cm | m2 | 1627.5 |  | 0
1.2.8 | Oznaka sestave: NT-06a Medetažna plošča proti garaži - "školjka" bazenček v labu LVTS (cona hrupa A in B, vibracijska cona VIB1) | Composition code: NT-06a Mezzanine slab facing the garage - "shell" pool in favour of LVTS (noise zone A and B, vibration zone VIB1)
a. | Podlaga: ~ mikroarmirani betonski estrih s fibriliranimi polipropilenskimi vlakni (2000 kg/m3), debeline 14,5 cm | Basis: ~ micro-reinforced concrete screed with fibrillated polypropylene fibres (2000 kg/m3), thickness 14,5 cm | m2 | 29.4 |  | 0
1.2.9 | Oznaka sestave: NT-06b Medetažna plošča proti garaži - "školjka" prostori labov LAVAR in LATOP (cona hrupa A in B, vibracijska cona VIB1) | Composition code: NT-06b Mezzanine slab against the garage - "shell" LAVAR and LATOP lab spaces (noise zone A and B, vibration zone VIB1)
a. | Podlaga: ~ mikroarmirani betonski estrih s fibriliranimi polipropilenskimi vlakni (2000 kg/m3), debeline 14 cm | Basis: ~ micro-reinforced concrete screed with fibrillated polypropylene fibres (2000 kg/m3), 14 cm thick | m2 | 194.25 |  | 0
1.2.10 | Oznaka sestave: NT-06c Medetažna plošča proti garaži - "školjka" prostor laba TINT - Zobniki FZG (cona hrupa A in B, vibracijska cona VIB1) | Composition code: NT-06c Mezzanine slab towards the garage - "clamshell" area of the TINT - FZG gears (noise zone A and B, vibration zone VIB1)
a. | Zvočna izolacija pod sekundarno betonsko ploščo: ~ zvočno izolacijski material določen na podlagi obtežbe na talno ploščo, da bo lastna frekvenca sistema pod 10 Hz (kot npr. Getzner Sylomer SR ali enakovredno), predvidene debeline 5 cm Opomba: točen tip materiala in njegova debelina se določi na podlagi izračuna proizvajalca. | Sound insulation under the secondary concrete slab: ~ soundproofing material specified on the basis of the load on the floor slab to keep the natural frequency of the system below 10 Hz (such as Getzner Sylomer SR or equivalent), intended thickness 5 cm Note: the exact material type and thickness is determined by the manufacturer's calculation. | m2 | 21 |  | 0
1.2.11 | Oznaka sestave: NT-20 Tla odmevnice (N1) | Composition code: NT-20 Echo chamber floor (N1)
a. | Podlaga: ~ mikroarmiran betonski estrih C20/25, fino zaglajen, s fibriliranimi PP vlakni (0,95 kg/m3) (kot npr. Fibrils F120 ali enakovredno) | Basis: ~ micro-reinforced concrete screed C20/25, finely smoothed, with fibrillated PP fibres (0,95 kg/m3) (such as Fibrils F120 or equivalent) | m2 | 12.6 |  | 0
b. | Zvočna izolacija pod sekundarno betonsko ploščo: ~ zvočno izolacijski material določen na podlagi obtežbe na talno ploščo, da bo lastna frekvenca sistema pod 10 Hz (kot npr. Getzner Sylomer SR ali enakovredno), predvidene debeline 10 cm Opomba: točen tip materiala in njegova debelina se določi na podlagi izračuna proizvajalca. | Sound insulation under the secondary concrete slab: ~ soundproofing material specified on the basis of the load on the floor slab to keep the natural frequency of the system below 10 Hz (such as Getzner Sylomer SR or equivalent), intended thickness 10 cm Note: the exact material type and thickness is determined by the manufacturer's calculation. | m2 | 12.6 |  | 0
1.2.12 | Oznaka sestave: NT-21 Tla pod gluho sobo (N1) | Composition code: NT-21 Floor under the deaf room (N1)
a. | Zvočna izolacija pod sekundarno betonsko ploščo: ~ zvočno izolacijski material določen na podlagi obtežbe na talno ploščo, da bo lastna frekvenca sistema pod 10 Hz (kot npr. Getzner Sylomer SR ali enakovredno), predvidene debeline 10 cm Opomba: točen tip materiala in njegova debelina se določi na podlagi izračuna proizvajalca. | Sound insulation under the secondary concrete slab: ~ soundproofing material specified on the basis of the load on the floor slab to keep the natural frequency of the system below 10 Hz (such as Getzner Sylomer SR or equivalent), intended thickness 10 cm Note: the exact material type and thickness is determined by the manufacturer's calculation. | m2 | 14.7 |  | 0
1.2.13 | Oznaka sestave: STR-02 Montažni strop nad prostori z akustičnimi zahtevami - "školjka" (cona hrupa A in B) | Composition code: STR-02 Prefabricated ceiling over rooms with acoustic requirements - "shell" (noise zones A and B)
a. | Zvočna izolacija: ~ med lesenimi morali vstavljena kamena volna d = 15 cm, gostote min. 30 kg/m3 | Sound insulation: ~ stone wool d = 15 cm, density min. 30 kg/m3 inserted between the timber | m2 | 1508.85 |  | 0
b. | Absorpcijska obloga: ~ termo in zvočno izolacijska plošče s sredico iz kamene volne in plasti mineralizirane lesne volne (kot npr. Fragmat Drvoterm DTO3 A2 ali enakovredno), debeline 10 cm, vijačene in lepljene na oblogo/konstrukcijo stropa | Absorption liner: ~ thermal and acoustic insulation panels with a stone wool core and a layer of mineralised wood wool (such as Fragmat Drvoterm DTO3 A2 or equivalent), 10 cm thick, screwed and glued to the ceiling lining/structure | m2 | 1508.85 |  | 0
1.2.14 | Oznaka sestave: STR-03 Strop prostora z akustičnimi zahtevami - "školjka" (Zobniki - TINT) (P1) | Composition code: STR-03 Ceiling of a room with acoustic requirements - "shell" (Gears - TINT) (P1)
a. | Zvočna izolacija: ~ mineralna volna gostote min. 30 kg/m3 na AB plošči, debeline 15 cm | Sound insulation: ~ mineral wool with a density of min. 30 kg/m3 on an AB slab, 15 cm thick | m2 | 21 |  | 0
b. | Absorpcijska obloga: ~ termo in zvočno izolacijska plošče s sredico iz kamene volne in plasti mineralizirane lesne volne (kot npr. Fragmat Drvoterm DTO3 A2 ali enakovredno), debeline 10 cm, vijačene in lepljene na oblogo/konstrukcijo stropa | Absorption liner: ~ thermal and acoustic insulation panels with a stone wool core and a layer of mineralised wood wool (such as Fragmat Drvoterm DTO3 A2 or equivalent), 10 cm thick, screwed and glued to the ceiling lining/structure | m2 | 21 |  | 0
1.2.15 | Oznaka sestave: STR-09 Strop odmevnice - AB školjka (N1) | Composition code: STR-09 Reflection ceiling - AB shell (N1)
a. | Zvočna izolacija: ~ mineralna volna gostote min. 30 kg/m3 na AB plošči, debeline 15 cm | Sound insulation: ~ mineral wool with a density of min. 30 kg/m3 on an AB slab, 15 cm thick | m2 | 12.6 |  | 0
1.2.16 | Oznaka sestave: STR-11 Strop nad gluho sobo (N1) | Composition code: STR-11 Ceiling above deaf room (N1)
a. | Zvočna izolacija: ~ mineralna volna gostote min. 30 kg/m3 na AB plošči, debeline 15 cm | Sound insulation: ~ mineral wool with a density of min. 30 kg/m3 on an AB slab, 15 cm thick | m2 | 14.7 |  | 0
b. | Obloga stropa: ~ predmet naročnika | Ceiling cladding: ~ the subject of the client
| ZIDARSKA DELA | MASONRY WORKS |  |  |  | 0

## 1.6.2.1.3_Tesarska_dela
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | AKUSTIČNE CELICE | ACOUSTIC CELLS
1.6.2.1 | GRADBENA DELA | CONSTRUCTION WORKS
1.6.2.1.3 | TESARSKA DELA | TESAR WORKS |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
1.3 | TESARSKA DELA | TESAR WORKS
| OPOMBA: Pri izdelavi ponudbe upoštevati pripombe, iz poglavja 0.1 UVOD Pri izdelavi popisa upoštevati pripombe, iz poglavja 0.2 UVOD - DGNB in dokument: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme. | NOTE: Take into account the comments made in section 0.1 INTRODUCTION when preparing the offer In the preparation of the inventory, take into account the comments made in Section 0.2 INTRODUCTION - DGNB and the document DGNB Quality Grades of Materials, Elements and Equipment.
| Pri izbiri opažev je potrebno za vse površine upoštevati zahteve za obdelavo površin po SIST EN 13670 in nacionalnem dodatku, razen za posebne arhitekturne oz. druge zahteve. Upoštevati je potrebno tudi pripombe poglavja Betonska dela. | When selecting formwork, the requirements for surface treatment according to SIST EN 13670 and the National Supplement shall be observed for all surfaces, except for special architectural or other requirements. The comments in the Concrete Works chapter shall also be observed.
| V cenah vidnih opažev morajo biti zajete tudi trikotne letve za posnete robove. Izvajalec mora odvažati vse odpadke, ki nastajajo pri izvedbi. Odvoz v pooblaščeno deponijo, kar je opotrebo upoštevati v cenah na enoto. | The prices for visible formwork shall also include triangular mouldings for chamfered edges. The Contractor shall take away all waste generated during the execution of the works. The waste shall be taken to an authorised landfill site, which shall be taken into account in the unit prices.
| Vsi delovni odri morajo biti upoštevani v cenah na enoto, razen tistih, ki so posebej navedeni v popisu. | All working platforms must be included in the unit prices, except those specifically mentioned in the inventory.
| Na vseh betonskih površinah, ki so izvedene v kvaliteti vidnega betona, se luknje od opaža zapolnijo s sanacijsko malto v barvi betona samo v območju luknje - pazljiva obdelava. Izvajalec izdela poskusni vzorec zapolnitve, ki ga potrdi arhitekt. Navedena popravila in popravila ev. nepravilnosti v betonski površini (stiki med opažnimi ploščami, naravnine, gnezda, vidna armatura) morajo biti cenovno upoštevana v ceni opažev. | On all concrete surfaces executed in visible concrete quality, the holes from the formwork shall be filled with remedial mortar in the colour of the concrete only in the area of the hole - careful treatment. The Contractor shall make a trial sample of the filling, which shall be approved by the Architect. The above repairs and repairs of any irregularities in the concrete surface (joints between formwork slabs, natural joints, nests, visible reinforcement) shall be taken into account in the price of the formwork.
| SPLOŠNA DOLOČILA | GENERAL PROVISIONS
1. | Za vse nejasnosti ali variantne rešitve se je obvezno posvetovati s projektantom. | For any ambiguities or alternative solutions, the designer must be consulted.
2. | Vsa dela morajo biti izvršena po določilih veljavnih normativov in v soglasju s tehničnimi predpisi za izvajanje tovrstnih del. | All work must be carried out in accordance with the applicable norms and in conformity with the technical regulations for the execution of this type of work.
3. | Storitve kooperanta obsegajo (če ni z medsebojno pogodbo drugače določeno): | The services of the Cooperator include (unless otherwise specified in a mutual agreement):
| a. snemanje vseh potrebnih izmer na objektu pred pričetkom izvajanja del, | a. recording all necessary measurements on the site before the works start,
| b. pregled in čiščenje podloge, | b. inspection and cleaning of the lining,
| c. nanos izravnalne mase, kjer je to zahtevano po opisu posamezne postavke, | c. application of levelling compound where required by the item description,
| d. vsa dela na objektu vključno z vsemi dajatvami, | d. all works on the building, including all charges,
| e. dobava osnovnega in pomožnega materiala, | e. the supply of basic and ancillary materials,
| f. prevoz materiala in orodja na objekt z vsem potrebnim nakladanjem, ekspeditom, razkladanjem in notranjim transportom do mesta vgrajevanja ter polaganje po opisu posamezne postavke, | f. transport of materials and tools to the site with all necessary loading, forwarding, unloading and internal transport to the installation site and installation as described in each item,
| g. popravila zidov oz. oblog sten, poškodovanih ob izvajanju del ter | g. repairs to walls or wall cladding damaged during the works; and
| h. odstranjevanje preostalega materiala, odnos in odvoz iz gradbišča, končno čiščenje in zavarovanje izvedenih del do predaje in podobno. | h. removal of residual materials, take-off and removal from the site, final cleaning and securing of the works until handover, etc.
4. | Enotne cene morajo vsebovati: | The uniform prices must include:
| a. vsa potrebna dokumentacija za začetek del, | a. all necessary documentation for the start of the works,
| b. vsa potrebna pripravljalna in pospravljalna dela, | b. all necessary preparatory and clean-up work,
| c. pregled in čiščenje podloge, nanos izravnalne mase, kjer je to potrebno, | c. inspection and cleaning of the substrate, application of levelling compound where necessary,
| d. snemanje potrebnih izmer na gradbišču in po načrtih, | d. recording the necessary measurements on site and as planned,
| e. prenos in obeleževanje višinskih točk na objektu, | e. the transfer and marking of height points on the building,
| f. po potrebi izdelava vzorca in vgradnja le-tega na objektu, | f. if necessary, the production of a sample and its installation on site,
| g. ves potrebni material: glavni, pomožni, pritrdilni in vezni material, | g. all necessary materials: main, auxiliary, fixing and binding materials,
| h. vse potrebne transporte in prenose, | h. all necessary transports and transfers,
| i. ustrezno začasno skladiščenje na delovišču, | i. adequate temporary storage on the worksite,
| j. vsa potrebna pomožna sredstva za montažo in demontažo na objektu, | j. all necessary means of assembly and dismantling on site,
| k. uporabo vse potrebne mehanizacije ali drugih delovnih sredstev z vsemi stroški povezanimi s tem, | k. the use of any necessary machinery or other means of work, with all associated costs,
| l. usklajevanje z osnovnim načrtom in posvetovanje s projektantom, | l. coordination with the basic plan and consultation with the designer,
| m. vso potrebno delo do končnega izdelka, | m. all the work needed to get to the finished product,
| n. vso potrebno zunanje (tehnolog, laboratorij) in notranje kontrole kakovosti, | n. all necessary external (technologist, laboratory) and internal quality control,
| o. vsa potrebna dokazovanja kakovosti materiala, pravilnega načina izvedbe in izvedenih del (certifikati uporabljenih materialov, meritve tlačne trdnosti, poročila itd.), | o. all necessary evidence of the quality of the material, the correct method of execution and the work carried out (certificates of materials used, compressive strength measurements, reports, etc.),
| p. terminsko usklajevanje del z ostalimi izvajalci na objektu, | p. coordinating the timing of works with other contractors on site,
| r. vse potrebne ukrepe za doseganje zahtevane kakovosti in rokov iz potrjenega terminskega plana izvajalca (na primer: Pred pričetkom del na akustičnih celicah mora izvajalec organizirati obvezno izobraževanje delavcev, njihovih vodij in koordinatorjev, ki bodo ta dela opravljali.), | r. all the necessary measures to achieve the required quality and the deadlines set out in the contractor's approved schedule (for example: before starting work on the acoustic cells, the contractor must organise mandatory training for the workers, their supervisors and the coordinators who will carry out the work),
| s. popravilo morebitne povzročene škode ostalim izvajalcem na gradbišču, | s. repair any damage caused to other contractors on site,
| š. čiščenje prostorov, nakladanje in odvoz odpadnega materiala na stalno deponijo, | cleaning the premises, loading and removal of waste materials to a permanent landfill,
| t. plačilo komunalnega prispevka za stalno deponijo odpadnega materiala, | t. payment of the municipal contribution for the permanent landfill of waste materials,
| u. vsi ukrepi za zaščito delavcev na gradbišču, skladno z veljavnimi predpisi s področja varnosti in zdravja pri delu, | u. all measures to protect workers on the construction site, in accordance with the applicable occupational safety and health regulations,
| v. v enotnih cenah morajo biti vključeni stroški na stalni deponiji. Izvajalec je dolžan predati vse evidenčne liste o oddaji odpadnega materiala v stalno deponijo, | v. the unit prices shall include the costs at the permanent landfill. The Contractor shall be obliged to hand over all records of the delivery of waste material to the permanent landfill,
| z. v enotni ceni morajo biti tudi zajeti stroški zaščite dostopnih koridorjev v notranjosti objekta, do prostorov, kjer se izvajajo dela. | z. the unit price must also include the cost of protecting access corridors inside the building to the areas where the work is being carried out.
5. | V primeru da posamezne postavke v popisu ne zajemajo celotnega opisa potrebnega za funkcionalno dokončanje dela, mora ponudnik izvedbo le tega vključiti v ceno na enoto! | In the event that individual items in the inventory do not cover the full description necessary for the functional completion of the work, the tenderer must include this in the unit price!
6. | Vsa dela morajo biti izvršena tako, da je zagotovljena funkcionalnost, stabilnost, varnost, natančnost in življenjska doba posameznih elementov. | All work must be carried out in such a way as to ensure the functionality, stability, safety, precision and service life of the individual components.
1.3.1 | Izdelava, dobava, montaža in demontaža opaža horizontalnih vezi in preklad širine 20 in 30 cm. | Manufacture, supply, installation and dismantling of horizontal ties and lintels of 20 and 30 cm width. | m2 | 1355 |  | 0
1.3.2 | Izdelava, dobava, montaža in demontaža opaža vertikalnih vezi. | Fabrication, supply, installation and dismantling of vertical tie formwork.
a. | ~ opaž vezi višine do 3 m | ~ formwork ties up to 3 m high | m2 | 855 |  | 0
b. | ~ opaž vezi višine 3 do 6 m | ~ 3 to 6 m high formwork ties | m2 | 595 |  | 0
1.3.3 | Izdelava, dobava, montaža in demontaža opaža AB plošč skupaj z opažem robov. | Fabrication, supply, installation and dismantling of AB panel formwork including edge formwork.
a. | ~ višina podpiranja do 3 m | ~ support height up to 3 m | m2 | 23 |  | 0
b. | ~ višina podpiranja 3 do 6 m | ~ support height 3 to 6 m | m2 | 470 |  | 0
c. | ~ plošča v naklonu (višina 3 do 6 m) | ~ inclined slab (height 3 to 6 m) | m2 | 20 |  | 0
1.3.4 | Izdelava, dobava, montaža in demontaža opaža AB sten. ~ dvostranski opaž ~ del opaža med konstrukcijama ak. celice in stavbe fakultete se šteje kot izgubljeni opaž | Fabrication, supply, installation and dismantling of AB wall formwork. ~ double-sided formwork ~ part of the formwork between the structures of the battery cell and the faculty building is considered as lost formwork
a. | ~ opaž višine do 3 m | ~ formwork up to 3 m high
a1. | - enostranski opaž | - single-sided formwork | m2 | 630 |  | 0
a2. | - izgubljeni opaž | - lost formwork | m2 | 630 |  | 0
b. | ~ opaž višine 3 do 6 m | ~ 3 to 6 m high formwork
b1. | - enostranski opaž | - single-sided formwork | m2 | 130 |  | 0
b2. | - izgubljeni opaž | - lost formwork | m2 | 130 |  | 0
1.3.5 | Izdelava, dobava in montaža podkonstrukcije stropa akustičnih celic iz lepljenega lameliranega lesa (GL24h) s porabo lesa do 0,03 m3/m2. ~ lameliran les GL24h skladno s SIST EN 1996-1-1, ~ leseni deli so zaščiteni s premazi proti lesnim škodljivcem, ~ leseni morali se lepijo na jekleno podkonstrukcijo na razmaku 62,5 cm, ~ leseni morali 10x10. | Fabrication, supply and installation of the substructure of the acoustic cell ceiling made of glued laminated timber (GL24h) with a timber consumption of up to 0.03 m3/m2. ~ laminated wood GL24h according to SIST EN 1996-1-1, ~ the wooden parts are protected with wood-pest coatings, ~ the wooden posts are glued to the steel substructure at 62,5 cm centres, ~ wooden moral 10x10. | m2 | 1437 |  | 0
| TESARSKA DELA | TESAR WORKS |  |  |  | 0

## 1.6.2.1.4_Plavajoče_plošče
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | AKUSTIČNE CELICE | ACOUSTIC CELLS
1.6.2.1 | GRADBENA DELA | CONSTRUCTION WORKS
1.6.2.1.4 | PLAVAJOČE PLOŠČE | FLOATING PANELS |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
1.4 | PLAVAJOČE PLOŠČE | FLOATING PANELS
| OPOMBA: Pri izdelavi ponudbe upoštevati pripombe, iz poglavja 0.1 UVOD Pri izdelavi popisa upoštevati pripombe, iz poglavja 0.2 UVOD - DGNB in dokument: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme. | NOTE: Take into account the comments made in section 0.1 INTRODUCTION when preparing the offer In the preparation of the inventory, take into account the comments made in Section 0.2 INTRODUCTION - DGNB and the document DGNB Quality Grades of Installed Materials, Elements and Equipment.
| Pri izbiri opažev je potrebno za vse površine upoštevati zahteve za obdelavo površin po SIST EN 13670 in nacionalnem dodatku, razen za posebne arhitekturne oz. druge zahteve. Upoštevati je potrebno tudi pripombe poglavja Betonska dela. | When selecting formwork, the requirements for surface treatment according to SIST EN 13670 and the National Supplement shall be observed for all surfaces, except for special architectural or other requirements. The comments in the Concrete Works chapter shall also be observed.
| V cenah vidnih opažev morajo biti zajete tudi trikotne letve za posnete robove. Izvajalec mora odvažati vse odpadke, ki nastajajo pri izvedbi. Odvoz v pooblaščeno deponijo, kar je opotrebo upoštevati v cenah na enoto. | The prices for visible formwork shall also include triangular mouldings for chamfered edges. The Contractor shall take away all waste generated during the execution of the works. The waste shall be taken to an authorised landfill site, which shall be taken into account in the unit prices.
| Vsi delovni odri morajo biti upoštevani v cenah na enoto, razen tistih, ki so posebej navedeni v popisu. | All working platforms must be included in the unit prices, except those specifically mentioned in the inventory.
| Na vseh betonskih površinah, ki so izvedene v kvaliteti vidnega betona, se luknje od opaža zapolnijo s sanacijsko malto v barvi betona samo v območju luknje - pazljiva obdelava. Izvajalec izdela poskusni vzorec zapolnitve, ki ga potrdi arhitekt. Navedena popravila in popravila ev. nepravilnosti v betonski površini (stiki med opažnimi ploščami, naravnine, gnezda, vidna armatura) morajo biti cenovno upoštevana v ceni opažev. | On all concrete surfaces executed in visible concrete quality, the holes from the formwork shall be filled with remedial mortar in the colour of the concrete only in the area of the hole - careful treatment. The Contractor shall make a trial sample of the filling, which shall be approved by the Architect. The above repairs and repairs of any irregularities in the concrete surface (joints between the formwork slabs, natural joints, nests, visible reinforcement) shall be taken into account in the price of the formwork.
| SPLOŠNA DOLOČILA | GENERAL PROVISIONS
1. | Za vse nejasnosti ali variantne rešitve se je obvezno posvetovati s projektantom. | For any ambiguities or alternative solutions, the designer must be consulted.
2. | Vsa dela morajo biti izvršena po določilih veljavnih normativov in v soglasju s tehničnimi predpisi za izvajanje tovrstnih del. | All work must be carried out in accordance with the applicable norms and in conformity with the technical regulations for the execution of this type of work.
3. | Storitve kooperanta obsegajo (če ni z medsebojno pogodbo drugače določeno): | The services of the Cooperator include (unless otherwise specified in a mutual agreement):
| a. snemanje vseh potrebnih izmer na objektu pred pričetkom izvajanja del, | a. recording all necessary measurements on the site before the works start,
| b. pregled in čiščenje podloge, | b. inspection and cleaning of the lining,
| c. nanos izravnalne mase, kjer je to zahtevano po opisu posamezne postavke, | c. application of levelling compound where required by the item description,
| d. vsa dela na objektu vključno z vsemi dajatvami, | d. all works on the building, including all charges,
| e. dobava osnovnega in pomožnega materiala, | e. the supply of basic and ancillary materials,
| f. prevoz materiala in orodja na objekt z vsem potrebnim nakladanjem, ekspeditom, razkladanjem in notranjim transportom do mesta vgrajevanja ter polaganje po opisu posamezne postavke, | f. transport of materials and tools to the site with all necessary loading, forwarding, unloading and internal transport to the installation site and installation as described in each item,
| g. popravila zidov oz. oblog sten, poškodovanih ob izvajanju del ter | g. repairs to walls or wall cladding damaged during the works; and
| h. odstranjevanje preostalega materiala, odnos in odvoz iz gradbišča, končno čiščenje in zavarovanje izvedenih del do predaje in podobno. | h. removal of residual materials, take-off and removal from the site, final cleaning and securing of the works until handover, etc.
4. | Enotne cene morajo vsebovati: | The uniform prices must include:
| a. vsa potrebna dokumentacija za začetek del, | a. all necessary documentation for the start of the works,
| b. vsa potrebna pripravljalna in pospravljalna dela, | b. all necessary preparatory and clean-up work,
| c. pregled in čiščenje podloge, nanos izravnalne mase, kjer je to potrebno, | c. inspection and cleaning of the substrate, application of levelling compound where necessary,
| d. snemanje potrebnih izmer na gradbišču in po načrtih, | d. recording the necessary measurements on site and as planned,
| e. prenos in obeleževanje višinskih točk na objektu, | e. the transfer and marking of height points on the building,
| f. po potrebi izdelava vzorca in vgradnja le-tega na objektu, | f. if necessary, the production of a sample and its installation on site,
| g. ves potrebni material: glavni, pomožni, pritrdilni in vezni material, | g. all necessary materials: main, auxiliary, fixing and binding materials,
| h. vse potrebne transporte in prenose, | h. all necessary transports and transfers,
| i. ustrezno začasno skladiščenje na delovišču, | i. adequate temporary storage on the worksite,
| j. vsa potrebna pomožna sredstva za montažo in demontažo na objektu, | j. all necessary means of assembly and dismantling on site,
| k. uporabo vse potrebne mehanizacije ali drugih delovnih sredstev z vsemi stroški povezanimi s tem, | k. the use of any necessary machinery or other means of work, with all associated costs,
| l. usklajevanje z osnovnim načrtom in posvetovanje s projektantom, | l. coordination with the basic plan and consultation with the designer,
| m. vso potrebno delo do končnega izdelka, | m. all the work needed to get to the finished product,
| n. vso potrebno zunanje (tehnolog, laboratorij) in notranje kontrole kakovosti, | n. all necessary external (technologist, laboratory) and internal quality control,
| o. vsa potrebna dokazovanja kakovosti materiala, pravilnega načina izvedbe in izvedenih del (certifikati uporabljenih materialov, meritve tlačne trdnosti, poročila itd.), | o. all necessary evidence of the quality of the material, the correct method of execution and the work carried out (certificates of materials used, compressive strength measurements, reports, etc.),
| p. terminsko usklajevanje del z ostalimi izvajalci na objektu, | p. coordinating the timing of works with other contractors on site,
| r. vse potrebne ukrepe za doseganje zahtevane kakovosti in rokov iz potrjenega terminskega plana izvajalca (na primer: Pred pričetkom del na akustičnih celicah mora izvajalec organizirati obvezno izobraževanje delavcev, njihovih vodij in koordinatorjev, ki bodo ta dela opravljali.), | r. all the necessary measures to achieve the required quality and the deadlines set out in the Contractor's approved schedule (e.g. Before starting work on the acoustic cells, the Contractor must organise mandatory training for the workers, their supervisors and the coordinators who will carry out the work),
| s. popravilo morebitne povzročene škode ostalim izvajalcem na gradbišču, | s. repair any damage caused to other contractors on site,
| š. čiščenje prostorov, nakladanje in odvoz odpadnega materiala na stalno deponijo, | cleaning the premises, loading and removal of waste materials to a permanent landfill,
| t. plačilo komunalnega prispevka za stalno deponijo odpadnega materiala, | t. payment of the municipal contribution for the permanent landfill of waste materials,
| u. vsi ukrepi za zaščito delavcev na gradbišču, skladno z veljavnimi predpisi s področja varnosti in zdravja pri delu, | u. all measures to protect workers on the construction site, in accordance with the applicable occupational safety and health regulations,
| v. v enotnih cenah morajo biti vključeni stroški na stalni deponiji. Izvajalec je dolžan predati vse evidenčne liste o oddaji odpadnega materiala v stalno deponijo, | v. the unit prices shall include the costs at the permanent landfill. The Contractor shall be obliged to hand over all record sheets of the delivery of the waste material to the permanent landfill,
| z. v enotni ceni morajo biti tudi zajeti stroški zaščite dostopnih koridorjev v notranjosti objekta, do prostorov, kjer se izvajajo dela. | z. the unit price must also include the cost of protecting access corridors inside the building to the areas where the work is being carried out.
5. | V primeru da posamezne postavke v popisu ne zajemajo celotnega opisa potrebnega za funkcionalno dokončanje dela, mora ponudnik izvedbo le tega vključiti v ceno na enoto! | In the event that individual items in the inventory do not cover the full description necessary for the functional completion of the work, the tenderer must include this in the unit price!
6. | Vsa dela morajo biti izvršena tako, da je zagotovljena funkcionalnost, stabilnost, varnost, natančnost in življenjska doba posameznih elementov. | All work must be carried out in such a way as to ensure the functionality, stability, safety, precision and service life of the individual components.
| Pri izvajanju del je potrebno posvetiti posebno pozornost spoštovanju navodil, pravilnemu poteku del in uporabi pravilnih postopkov, da se izognemo možnosti poškodovanja gumijastih zvočnih blažilcev. | When carrying out works, special attention must be paid to following instructions, following the correct workflow and using the correct procedures to avoid the possibility of damaging the rubber sound absorbers.
1.4.1 | Dobava, razrez in polaganje PU elastomerne penaste gume (kot na primer Sylomer SR 1200 debeline 25 mm) v enem sloju po robu AB dvigajoče/plavajoče plošče. Razrez na trakove širine 25 cm, ki se položojo vertikalno ob AB vertikalne nosilne elemente na stikih s ploščami (označeno v projektu konstrukcije). Obračun po kvadretnem metru porabljenega materiala. | Supply, cutting and laying of PU elastomeric foam rubber (such as Sylomer SR 1200, 25 mm thick) in a single layer around the edge of the AB lifting/floating slab. Cutting into strips 25 cm wide to be laid vertically against the AB vertical support members at the interfaces with the slabs (indicated in the structural design). Charging per square metre of material used. | m2 | 160 |  | 0
1.4.2 | Dobava, rezanje, krivljenje, polaganje in vezanje rebraste armature B500 B, lastnosti v skladu s SIST EN 10080; 2005. Srednje komplicirana armatura. | Supply, cutting, bending, laying and bonding of ribbed reinforcement B500 B, properties in accordance with SIST EN 10080; 2005. Medium-complex reinforcement. | kg | 43000 |  | 0
1.4.3 | Dobava, razrez in polaganje kamene volne debeline 2,5 cm, v pasovih višine 25 cm po obodu dvigajočih/plavajočih plošč. Vsi stiki so tesno prilegajoči. Kamena volna mora imeti gostoto 100 kg/m3. Volna se ne položi na mestih, kjer je predvideno polaganje PU elastomerne penaste gume. | Supply, cutting and laying of 2,5 cm thick stone wool in 25 cm high strips around the perimeter of the lifting/floating slabs. All joints shall be tight fitting. The stone wool shall have a density of 100 kg/m3. The stone wool shall not be laid where PU elastomeric foam rubber is to be laid. | m2 | 2135 |  | 0
1.4.4 | Dobava in polaganje prozorne polietilenske folije debeline 0,15 mm neposredno na izravnano in očiščeno obstoječo konstrukcijsko AB ploščo s predpisanim prekrivanjem (min. 30 cm). Folija se položi pod antivibracijskimi dušilnimi elementi, ki podpirajo vso armaturo plošč in preko mineralne volne/PU elastomerne penaste gume. Vsi stiki folije morajo biti medsebojno neprekinjeno zalepljeni; vertikalni pasovi morajo biti ustrezno pritrjeni - beton pri zalivanju plavajoče plošče ne sme prehajati skozi to folijo in v nobenem primeru, po obodu ne sme tvoriti togega stika z objektom. Folija se pred betonažo ne sme poškodovati, da bo možen naknaden dvig plošče brez tveganja, da se pojavijo toge povezave med plavajočo ploščo in nosilno podlago. Pred betonažo je potrebno natančno pregledati stanje položene folije in sanirati morebitne poškodbe. Opomba: Pred polaganjem polietilenske folije se na konstrukcijsko AB ploščo točno zarišejo vse pozicije akustičnih blažilcev. | Dobava in polaganje prozorne polietilenske folije debeline 0,15 mm neposredno na izravnano in očiščeno obstoječo konstrukcijsko AB ploščo s predpisanim prekrivanjem (min. 30 cm). Folija se položi pod antivibracijskimi dušilnimi elementi, ki podpirajo vso armaturo plošč in preko mineralne volne/PU elastomerne penaste gume. Vsi stiki folije morajo biti medsebojno neprekinjeno zalepljeni; vertikalni pasovi morajo biti ustrezno pritrjeni - beton pri zalivanju plavajoče plošče ne sme prehajati skozi to folijo in v nobenem primeru, po obodu ne sme tvoriti togega stika z objektom. Folija se pred betonažo ne sme poškodovati, da bo možen naknaden dvig plošče brez tveganja, da se pojavijo toge povezave med plavajočo ploščo in nosilno podlago. Pred betonažo je potrebno natančno pregledati stanje položene folije in sanirati morebitne poškodbe. Note: Before laying the polyethylene sheeting, all positions of the acoustic absorbers shall be accurately plotted on the structural AB panel. | m2 | 2135 |  | 0
1.4.5 | Dobava in vgradnja akustičnih elementov (elastičnih stojk) za AB dvižne, plavajoče plošče. Nosilnost posameznega elementa mora biti v razponu od 800 do 2200 kg, pri čem mora sestavljena konstrukcija laboratorija zagotoviti lastno resonančno frekvenco pod 10 Hz za preprečitev prenosa udarnega zvoka hrupa v zraku in vibracij. Predviden končen dvig plošč je 50 mm, pri čem je potrebno vse upoštevati tudi stalne obtežbe, tudi tiste, ki bodo nastopile po aktiviranju vzmeti. Zaradi večje fleksibilnosti laboratorijev, kar je povezano z velikim razponom obremenitve na akustične elemente so izbrani elementi z vzmetjo in elastomernim materialom kot na primer AMC Mecanocaucho FZH2M 1953 + SYLOMER H200 + D. OPOMBA: Končno število, tip in postavitev (mikrolokacijo) določi dobavitelj akustičnih podložnih elementov na osnovi vhodnih podatkov podanih v načrtu JULFS--7G/07 (Akustične celice). | Supply and installation of acoustic elements (elastic stands) for the AB lifting, floating panels. The load capacity of each element must be in the range 800-2200 kg, with the composite structure of the laboratory ensuring an intrinsic resonance frequency below 10 Hz to prevent the transmission of airborne impact sound and vibration. The final lift of the panels is expected to be 50 mm, all of which must take into account the permanent loads, including those that will occur after the springs have been activated. To increase the flexibility of the laboratories, which is related to the large load range on the acoustic elements, elements with spring and elastomeric material are chosen, such as AMC Mecanocaucho FZH2M 1953 + SYLOMER H200 + D. NOTE: The final number, type and layout (micro-location) of acoustic lining elements shall be determined by the acoustic lining element supplier on the basis of the input data given in plan JULFS--7G/07 (Acoustic Cells). | kos | 4260 |  | 0
1.4.6 | Dobava in vgrajevanje betona C30/37, XC3, Cl0,2, Dmax16 v AB konstrukcije "dvižne plavajoče plošče", po sistemu dobavitelja antivibracijskih dušilnih elementov in nastavkov za različne debeline plošč. Debelina plošče je 20 cm s toleranco izravnave površine +/- 5 mm glede na predvideno koto, dilatirana in višinsko oblikovana skladno z arhitekturo akustično ločenih enot laboratorijev. OPOMBA: Pri izvedbi je potrebna velika natančnost in pazljivost, vsi postopki ter detajli se morajo uskladiti s tehnologijo izbranega dobavitelja akustičnih podložnih elementov (kot naprimer AMC Mecanocaucho, Mason, ipd.). | Supply and installation of concrete C30/37, XC3, Cl0,2, Dmax16 in AB structures of "riser floating slabs", according to the supplier's system of anti-vibration damping elements and adaptors for different slab thicknesses. The slab thickness shall be 20 cm with a tolerance of surface levelling of +/- 5 mm with respect to the intended angle, dilated and height-formed in accordance with the architecture of the acoustically separated units of the laboratories. NOTE: Great care and precision is required in the execution and all procedures and details must be in accordance with the technology of the chosen acoustic substrate supplier (such as AMC Mecanocaucho, Mason, etc.). | m3 | 410 |  | 0
1.4.7 | Izdelava opažnih in armaturnih risb plavajočih plošč z upoštevanjem števila in mikrolokacije akustičnih podložnih elementov ter potrebnih prebojev in drugih relevantnih vsebin ostalih načrtov PZI. OPOMBA: Izvedba navedenih del mora potekati pod nadzorom dobavitelja akustičnih podložnih elementov (kot naprimer AMC Mecanocaucho, Mason, ipd.). | Preparation of formwork and reinforcement drawings of the floating slabs, taking into account the number and micro-location of the acoustic substructure elements and the necessary penetrations and other relevant content of the other PZI plans. NOTE: The execution of the above works shall be carried out under the supervision of the supplier of the acoustic underlay (such as AMC Mecanocaucho, Mason, etc.). | kpl | 1 |  | 0
1.4.8 | Dvigovanje plavajočih plošč celic na predpisano višino po navodilih in z vodenjem predstavnika proizvajalca akustičnih podložnih elementov (kot naprimer AMC Mecanocaucho, Mason, ipd.). OPOMBA: Izvajalec mora priskrbeti 8 - 10 pomočnikov, ki bodo pozorno sodelovali pri aktiviranju antivibracijskih dušilnih elementov. | Raising the floating cell panels to the specified height as directed and guided by a representative of the acoustic substrate manufacturer (such as AMC Mecanocaucho, Mason, etc.). NOTE: The Contractor shall provide 8 - 10 assistants who will be closely involved in the activation of the anti-vibration dampers. | kpl | 1 |  | 0
1.4.9 | Izvedba kontrole morebitnih "togih stikov" po dvigu plavajočih plošč s pospeškometri in meritve doseganih protihrupnih in protivibracijskih parametrov vseh posameznih celic s strani dobavitelja akustičnih podložnih elementov (kot naprimer AMC Mecanocaucho, Mason, ipd.). | Checking for any "hard contacts" after the floating panels have been raised with accelerometers and measuring the achieved noise and anti-vibration parameters of all individual cells by the supplier of the acoustic substrate (such as AMC Mecanocaucho, Mason, etc.). | kpl | 1 |  | 0
| PLAVAJOČE PLOŠČE | FLOATING PANELS |  |  |  | 0

## 1.6.2.2.0_Rekapitulacija_ZO_del
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | AKUSTIČNE CELICE | ACOUSTIC CELLS
| REKAPITULACIJA STROŠKOV ZAKLJUČNIH OBRTNIŠKIH DEL | COST SUMMARY OF CRAFT WORKS
| 1 NAČRT S PODROČJA ARHITEKTURE | 1 DOCUMENTATION IN THE FIELD OF ARCHITECTURE
| 1/6 Projektantski popis gradbeno obrtniških del | 1/6 Bill of Quantities of Construction and Craft Works
1.6.2.2 | ZAKLJUČNA OBRTNIŠKA DELA | CRAFT WORKS
1.6.2.2.1 | KLJUČAVNIČARSKA DELA | LOCKSMITH WORK | 0
1.6.2.2.2 | SUHOMONTAŽNA DELA | DRYWALL WORKS | 0
1.6.2.2.3 | KERAMIČARSKA DELA | CERAMIC WORK | 0
1.6.2.2.4 | TLAKARSKA DELA | PRESS WORKS | 0
0
0 | NEPREDVIDENA DELA | UNFORSEEN WORKS | 0
| SKUPAJ ZAKLJUČNA OBRTNIŠKA DELA | TOTAL CRAFT WORKS | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT

## 1.6.2.2.1_KLjučavničarska_dela
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | AKUSTIČNE CELICE | ACOUSTIC CELLS
1.6.2.2 | ZAKLJUČNA OBRTNIŠKA DELA | CRAFT WORKS
1.6.2.2.1 | KLJUČAVNIČARSKA DELA | LOCKSMITH WORK |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
2.1 | KLJUČAVNIČARSKA DELA | LOCKSMITH WORK
| OPOMBA: Pri izdelavi ponudbe upoštevati pripombe, iz poglavja 0.1 UVOD Pri izdelavi popisa upoštevati pripombe, iz poglavja 0.2 UVOD - DGNB in dokument: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme. | NOTE: Take into account the comments made in section 0.1 INTRODUCTION when preparing the offer In the preparation of the inventory, take into account the comments made in Section 0.2 INTRODUCTION - DGNB and the document DGNB Quality Grades of Installed Materials, Elements and Equipment.
| SPLOŠNA DOLOČILA | GENERAL PROVISIONS
1. | Za vse nejasnosti ali variantne rešitve se je obvezno posvetovati s projektantom. | For any ambiguities or alternative solutions, the designer must be consulted.
2. | Vsa dela morajo biti izvršena po določilih veljavnih normativov in v soglasju s tehničnimi predpisi za izvajanje tovrstnih del. | All work must be carried out in accordance with the applicable norms and in conformity with the technical regulations for the execution of this type of work.
3. | Storitve kooperanta obsegajo (če ni z medsebojno pogodbo drugače določeno): | The services of the Cooperator include (unless otherwise specified in a mutual agreement):
| a. snemanje vseh potrebnih izmer na objektu pred pričetkom izvajanja del, | a. recording all necessary measurements on the site before the works start,
| b. pregled in čiščenje podloge, | b. inspection and cleaning of the lining,
| c. nanos izravnalne mase, kjer je to zahtevano po opisu posamezne postavke, | c. application of levelling compound where required by the item description,
| d. vsa dela na objektu vključno z vsemi dajatvami, | d. all works on the building, including all charges,
| e. dobava osnovnega in pomožnega materiala, | e. the supply of basic and ancillary materials,
| f. prevoz materiala in orodja na objekt z vsem potrebnim nakladanjem, ekspeditom, razkladanjem in notranjim transportom do mesta vgrajevanja ter polaganje po opisu posamezne postavke, | f. transport of materials and tools to the site with all necessary loading, forwarding, unloading and internal transport to the installation site and installation as described in each item,
| g. popravila zidov oz. oblog sten, poškodovanih ob izvajanju del ter | g. repairs to walls or wall cladding damaged during the works; and
| h. odstranjevanje preostalega materiala, odnos in odvoz iz gradbišča, končno čiščenje in zavarovanje izvedenih del do predaje in podobno. | h. removal of residual materials, take-off and removal from the site, final cleaning and securing of the works until handover, etc.
4. | Enotne cene morajo vsebovati: | The uniform prices must include:
| a. vsa potrebna dokumentacija za začetek del, | a. all necessary documentation for the start of the works,
| b. vsa potrebna pripravljalna in pospravljalna dela, | b. all necessary preparatory and clean-up work,
| c. pregled in čiščenje podloge, nanos izravnalne mase, kjer je to potrebno, | c. inspection and cleaning of the substrate, application of levelling compound where necessary,
| d. snemanje potrebnih izmer na gradbišču in po načrtih, | d. recording the necessary measurements on site and as planned,
| e. prenos in obeleževanje višinskih točk na objektu, | e. the transfer and marking of height points on the building,
| f. po potrebi izdelava vzorca in vgradnja le-tega na objektu, | f. if necessary, the production of a sample and its installation on site,
| g. ves potrebni material: glavni, pomožni, pritrdilni in vezni material, | g. all necessary materials: main, auxiliary, fixing and binding materials,
| h. vse potrebne transporte in prenose, | h. all necessary transports and transfers,
| i. ustrezno začasno skladiščenje na delovišču, | i. adequate temporary storage on the worksite,
| j. vsa potrebna pomožna sredstva za montažo in demontažo na objektu, | j. all necessary means of assembly and dismantling on site,
| k. uporabo vse potrebne mehanizacije ali drugih delovnih sredstev z vsemi stroški povezanimi s tem, | k. the use of any necessary machinery or other means of work, with all associated costs,
| l. usklajevanje z osnovnim načrtom in posvetovanje s projektantom, | l. coordination with the basic plan and consultation with the designer,
| m. vso potrebno delo do končnega izdelka, | m. all the work needed to get to the finished product,
| n. vso potrebno zunanje (tehnolog, laboratorij) in notranje kontrole kakovosti, | n. all necessary external (technologist, laboratory) and internal quality control,
| o. vsa potrebna dokazovanja kakovosti materiala, pravilnega načina izvedbe in izvedenih del (certifikati uporabljenih materialov, meritve tlačne trdnosti, poročila itd.), | o. all necessary evidence of the quality of the material, the correct method of execution and the work carried out (certificates of materials used, compressive strength measurements, reports, etc.),
| p. terminsko usklajevanje del z ostalimi izvajalci na objektu, | p. coordinating the timing of works with other contractors on site,
| r. vse potrebne ukrepe za doseganje zahtevane kakovosti in rokov iz potrjenega terminskega plana izvajalca, | r. all necessary measures to achieve the required quality and the deadlines set out in the Contractor's approved schedule,
| s. popravilo morebitne povzročene škode ostalim izvajalcem na gradbišču, | s. repair any damage caused to other contractors on site,
| š. čiščenje prostorov, nakladanje in odvoz odpadnega materiala na stalno deponijo, | cleaning the premises, loading and removal of waste materials to a permanent landfill,
| t. plačilo komunalnega prispevka za stalno deponijo odpadnega materiala, | t. payment of the municipal contribution for the permanent landfill of waste materials,
| u. vsi ukrepi za zaščito delavcev na gradbišču, skladno z veljavnimi predpisi s področja varnosti in zdravja pri delu, | u. all measures to protect workers on the construction site, in accordance with the applicable occupational safety and health regulations,
| v. v enotnih cenah morajo biti vključeni stroški na stalni deponiji. Izvajalec je dolžan predati vse evidenčne liste o oddaji odpadnega materiala v stalno deponijo, | v. the unit prices shall include the costs at the permanent landfill. The Contractor shall be obliged to hand over all record sheets of the delivery of the waste material to the permanent landfill,
| z. v enotni ceni morajo biti tudi zajeti stroški zaščite dostopnih koridorjev v notranjosti objekta, do prostorov, kjer se izvajajo dela. | z. the unit price must also include the cost of protecting access corridors inside the building to the areas where the work is being carried out.
5. | V primeru da posamezne postavke v popisu ne zajemajo celotnega opisa potrebnega za funkcionalno dokončanje dela, mora ponudnik izvedbo le tega vključiti v ceno na enoto! | In the event that individual items in the inventory do not cover the full description necessary for the functional completion of the work, the tenderer must include this in the unit price!
6. | Vsa dela morajo biti izvršena tako, da je zagotovljena funkcionalnost, stabilnost, varnost, natančnost in življenjska doba posameznih elementov. | All work must be carried out in such a way as to ensure the functionality, stability, safety, precision and service life of the individual components.
| Elementi jeklenih konstrukcij se izdelajo iz jekla kvalitete S355J2 v skladu s SIST EN 10025 in SIST EN 1993. Uporabljeno je konstrukcijsko jeklo S355 J2 v skladu s SIST EN 1993-1-1 in SIST EN 10025. Upoštevana je standardna kvaliteta zvarov po EN ISO 3834-3, vijaki so trdnostnega razreda 8.8, matice v skladu s SIST EN ISO 4032, podložke po SIST EN ISO 7089 in vijaki po SIST EN ISO 4017. Vijaki, matice in podložke morajo biti dobavljeni s serijsko izvedeno protikorozijsko zaščito. Vse jeklene elemente je potrebno izdelati v skladu z zahtevami za razred izvedbe EXC2 po SIST EN 1090-2 in v skladu z zahtevami za ugotavljanje skladnosti sestavnih delov konstrukcij po SIST EN 1090-1. | Elementi jeklenih konstrukcij se izdelajo iz jekla kvalitete S355J2 v skladu s SIST EN 10025 in SIST EN 1993. Uporabljeno je konstrukcijsko jeklo S355 J2 v skladu s SIST EN 1993-1-1 in SIST EN 10025. Upoštevana je standardna kvaliteta zvarov po EN ISO 3834-3, vijaki so trdnostnega razreda 8.8, matice v skladu s SIST EN ISO 4032, podložke po SIST EN ISO 7089 in vijaki po SIST EN ISO 4017. Vijaki, matice in podložke morajo biti dobavljeni s serijsko izvedeno protikorozijsko zaščito. Vse jeklene elemente je potrebno izdelati v skladu z zahtevami za razred izvedbe EXC2 po SIST EN 1090-2 in v skladu z zahtevami za ugotavljanje skladnosti sestavnih delov konstrukcij po SIST EN 1090-1.
| Kvaliteta jekla: S355 J2 Napetost tečenja fy za vročevaljana jekla: 355 MPa t ≤ 40 mm 335 MPa 40 < t ≤ 80 mm Napetost tečenja fy za škatlaste profile: 355 MPa t ≤ 40 mm 335 MPa 40 < t ≤ 80 mm Natezna trdnost fu za vročevaljana jekla: 510 MPa t ≤ 40 mm 470 MPa 40 < t ≤ 80 mm Natezna trdnost fu za škatlaste profile: 510 MPa t ≤ 40 mm 490 MPa 40 < t ≤ 80 mm Modul elastičnosti E: 210 GPa Strižni modul G: 81 GPa Specifična teža γ: 78,5 kN/m3 Poissonov količnik ν: 0,3 Koeficient toplotnega raztezanja αT: 12E-6 K | Steel grade: S355 J2 Yield stress fy for hot-worked steels: 355 MPa t ≤ 40 mm 335 MPa 40 < t ≤ 80 mm Creep stress fy for box profiles: 355 MPa t ≤ 40 mm 335 MPa 40 < t ≤ 80 mm Tensile strength fu for hot-worked steels: 510 MPa t ≤ 40 mm 470 MPa 40 < t ≤ 80 mm Tensile strength fu for box profiles: 510 MPa t ≤ 40 mm 490 MPa 40 < t ≤ 80 mm Modulus of elasticity E: 210 GPa Shear modulus G: 81 GPa Specific gravity γ: 78,5 kN/m3 Poisson's ratio ν: 0,3 Coefficient of thermal expansion αT: 12E-6 K
| Navadni konstrukcijski vijaki so kvalitete 8.8 v skladu s SIST EN 1993-1-8 in EN ISO 4017. Prednapeti konstrukcijski vijaki kvalitete 10.9 HV se izdelajo v skladu s SIST EN 1993-1-8 in SIST EN 14399-4. Sidrni vijaki (npr. Hilti) morajo biti skladni z veljavnimi standardi oziroma evropskimi ocenjevalnimi dokumenti (EAD). Vgrajeni morajo biti v skladu z navodili proizvajalca. | The common structural bolts shall be of quality 8.8 in accordance with SIST EN 1993-1-8 and EN ISO 4017. Pre-tensioned structural bolts of quality 10.9 HV shall be manufactured in accordance with SIST EN 1993-1-8 and SIST EN 14399-4. Anchor bolts (e.g. Hilti) shall comply with the applicable standards or European Assessment Documents (EAD). They shall be installed in accordance with the manufacturer's instructions.
| Projektne zahteve za navadne konstrukcijske vijake 8.8: Kvaliteta: 8.8 Napetost tečenja fyb: 640 Mpa Natezna trdnost fub: 800 Mpa Projektne zahteve za prednapete konstrukcijske vijake 10.9: Kvaliteta: 10.9 Napetost tečenja fyb: 900 Mpa Natezna trdnost fub: 1000 Mpa | Design requirements for ordinary structural bolts 8.8: Quality: 8.8 Yield stress fyb: 640 MPa Tensile strength fub: 800 MPa Design requirements for prestressed structural bolts 10.9: Quality: 10.9 Yield stress fyb: 900 MPa Tensile strength fub: 1000 MPa
| Vse jeklene konstrukcije so zaradi zahtevnosti uvrščene v izvedbeni razred EXC2 v skladu s SIST EN 1090-1 in SIST EN 1090-2 ter pripadajočim nacionalnim dodatkom. | Due to their complexity, all steel structures are classified in performance class EXC2 in accordance with SIST EN 1090-1 and SIST EN 1090-2 and the relevant national appendices.
| Antikorozijska zaščita: | Corrosion protection:
| Vsi jekleni elementi morajo biti antikorozijsko zaščiteni. AKZ je vroče cinkanje. Protikorozijska zaščita mora izpolnjevati zahteve SIST EN ISO 12944 (barvane konstrukcije) oziroma SIST EN ISO 1461 (vročecinkane konstrukcije). Zahteve za protikorozijsko zaščito: ~ kategorija izpostavljenosti okolja je C3 za notranje in C4 za zunanje konstrukcije in ~ stopnja trajnosti zaščite VH v skladu s SIST EN ISO 12944 oz. SIST EN ISO 1461. Izvajalec mora pripraviti in predati elaborat protikorozijske zaščite. | All steel elements shall be corrosion-protected. AKZ is hot-dip galvanising. Corrosion protection shall comply with the requirements of SIST EN ISO 12944 (painted structures) or SIST EN ISO 1461 (hot-dip galvanised structures). Requirements for corrosion protection: ~ the environmental exposure category is C3 for internal and C4 for external structures; and ~ degree of durability of VH protection in accordance with SIST EN ISO 12944 or SIST EN ISO 1461. The Contractor shall prepare and submit a corrosion protection study.
| Izvajalec premaza mora pri tehnologiji izvedbe dosledno upoštevati tehnična navodila proizvajalca o pripravi površin (vlaga, temperatura, čistost, hrapavost), čas pred naslednjim nanosom in čas sušenja po zadnjem nanosu, da se zagotovi zahtevana kvaliteta premaza in zadostna trdnost pred transportom. Poleg tega je izvajalec dolžan tekoče preverjati kvaliteto protikorozijskih sredstev in opreme za izvajanje del. Pred izvajanjem protikorozijske in požarne zaščite morajo biti privarjeni na konstrukcijo vsi s projektom predvideni elementi, katerih pritrditev je predvidena z varjenjem. Jeklenih delov konstrukcij, ki bodo vbetonirani v temelje, ni potrebno protikorozijsko zaščititi, pri čemer mora sistem zaščite segati vsaj 3 cm v beton. Izvajalec protikorozijske in požarne zaščite mora po zaključenem delu naročniku predati dokumentacijo o uporabljenih materialih, preizkusih in certifikatih. | The coating contractor shall strictly follow the manufacturer's technical instructions on surface preparation (moisture, temperature, cleanliness, roughness), time before the next application and drying time after the last application to ensure the required coating quality and sufficient strength before transport. In addition, the contractor is obliged to check the quality of the anti-corrosion agents and equipment used for the works on an ongoing basis. Before corrosion and fire protection is applied, all the elements foreseen by the design and whose fixing is to be by welding must be welded to the structure. The steel parts of the structures to be embedded in the foundations do not need to be corrosion-protected and the protection system must extend at least 3 cm into the concrete. Upon completion of the work, the corrosion and fire protection contractor shall provide the client with documentation of the materials used, tests and certificates.
| Dobavitelj mora po zaključku del predložiti naslednjo tehnično dokumentacijo: 1. delavniške dnevnike z vsemi popravki, spremembami in dopolnitvami delavniških načrtov oziroma odstopanji od projekta, kot tudi zvezo med izdelanimi elementi in certifikati o kakovosti materialov, 2. potrdila o kakovosti vgrajenega materiala (certifikati osnovnega, dodajnega in vijačnega materiala oz. poročila o preizkusih), 3. certifikate o usposobljenosti varilcev, 4. na zahtevo nadzornega organa predložiti varilne procedure (WPQR) ter navodila za varjenje posameznih tipov spojev (WPS), 5. certifikate oz. potrdila o kakovosti protikorozijskih premazov in cinkove žice ter dnevnike izvajanja protikorozijske zaščite, 6. zapisnike in poročila o vseh vmesnih kontrolah pri izdelavi konstrukcij. | The following technical documentation must be submitted by the Supplier on completion of the works: 1. the workmen's logs showing any corrections, alterations and amendments to the workmen's plans or deviations from the design, as well as the relationship between the elements manufactured and the certificates of quality of the materials, 2. certificates of the quality of the materials installed (certificates of the base material, filler material and screw material, or test reports), 3. certificates of competence for welders, 4. provide welding procedures (WPQR) and welding instructions for specific types of joints (WPS) at the request of the supervisory authority, 5. certificates or quality certificates for anti-corrosion coatings and zinc wire, and corrosion protection logs, 6. records and reports of all intermediate checks in the construction of the structures.
2.1.1 | Jeklene konstrukcije stropov "akustičnih celic": Kompletna izdelava, dobava in montaža jeklene konstrukcije stropov "akustičnih celic". Konstrukcija izdelana po detajlu statika. Izvajalec je dolžan izdelati vse potrebne delavniške načrte, ki jih pred izvedbo del potrdi odgovorni projektant / statik. Sidranje konstrukcije v AB konstrukcijo z nerjavečimi sidri. Vse mere mora izvajalec kontrolirati na mestu samem pred izdelavo in montažo. V enotni ceni mora izvajalec zajeti vsa pomožna dela, pomožne delovne odre za montažo nosilne konstrukcije in podobno, vse prenose in transporte vsega materiala do mesta vgrajevanja. | Steel structures for the ceilings of "acoustic cells": Complete fabrication, supply and erection of the steel structure of the "acoustic cell" ceilings. The structure to be fabricated according to the structural engineer's details. The contractor shall be obliged to draw up all the necessary shop drawings, which shall be approved by the responsible designer / structural engineer before the execution of the works. Anchoring of the structure to the AB structure with stainless anchors. All dimensions to be checked by the contractor on site prior to fabrication and erection. The contractor shall include in the lump sum price, all ancillary works, scaffolding for the erection of the support structure, etc., all transfers and transport of all material to the site of installation. 3.1.2. Anchoring of the structure to the AB structure with stainless anchors.
a. | ~ HEA180 | ~ HEA180 | kg | 51498 |  | 0
b. | ~ UPN120 | ~ UPN120 | kg | 11 |  | 0
c. | ~ UPN300 | ~ UPN300 | kg | 28304 |  | 0
| KLJUČAVNIČARSKA DELA | LOCKSMITH WORK |  |  |  | 0

## 1.6.2.2.2_Suhomontažna_dela
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | AKUSTIČNE CELICE | ACOUSTIC CELLS
1.6.2.2 | ZAKLJUČNA OBRTNIŠKA DELA | CRAFT WORKS
1.6.2.2.2 | SUHOMONTAŽNA DELA | DRYWALL WORKS |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
2.2 | SUHOMONTAŽNA DELA | DRYWALL WORKS
| OPOMBA: Pri izdelavi ponudbe upoštevati pripombe, iz poglavja 0.1 UVOD Pri izdelavi popisa upoštevati pripombe, iz poglavja 0.2 UVOD - DGNB in dokument: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme. | NOTE: Take into account the comments made in section 0.1 INTRODUCTION when preparing the offer In the preparation of the inventory, take into account the comments made in Section 0.2 INTRODUCTION - DGNB and the document DGNB Quality Grades of Installed Materials, Elements and Equipment.
| SPLOŠNA DOLOČILA | GENERAL PROVISIONS
1. | Za vse nejasnosti ali variantne rešitve se je obvezno posvetovati s projektantom. | For any ambiguities or alternative solutions, the designer must be consulted.
2. | Vsa dela morajo biti izvršena po določilih veljavnih normativov in v soglasju s tehničnimi predpisi za izvajanje tovrstnih del. | All work must be carried out in accordance with the applicable norms and in conformity with the technical regulations for the execution of this type of work.
3. | Storitve kooperanta obsegajo (če ni z medsebojno pogodbo drugače določeno): | The services of the Cooperator include (unless otherwise specified in a mutual agreement):
| a. snemanje vseh potrebnih izmer na objektu pred pričetkom izvajanja del, | a. recording all necessary measurements on the site before the works start,
| b. pregled in čiščenje podloge, | b. inspection and cleaning of the lining,
| c. nanos izravnalne mase, kjer je to zahtevano po opisu posamezne postavke, | c. application of levelling compound where required by the item description,
| d. vsa dela na objektu vključno z vsemi dajatvami, | d. all works on the building, including all charges,
| e. dobava osnovnega in pomožnega materiala, | e. the supply of basic and ancillary materials,
| f. prevoz materiala in orodja na objekt z vsem potrebnim nakladanjem, ekspeditom, razkladanjem in notranjim transportom do mesta vgrajevanja ter polaganje po opisu posamezne postavke, | f. transport of materials and tools to the site with all necessary loading, forwarding, unloading and internal transport to the installation site and installation as described in each item,
| g. popravila zidov oz. oblog sten, poškodovanih ob izvajanju del ter | g. repairs to walls or wall cladding damaged during the works; and
| h. odstranjevanje preostalega materiala, odnos in odvoz iz gradbišča, končno čiščenje in zavarovanje izvedenih del do predaje in podobno. | h. removal of residual materials, take-off and removal from the site, final cleaning and securing of the works until handover, etc.
4. | Enotne cene morajo vsebovati: | The uniform prices must include:
| a. vsa potrebna dokumentacija za začetek del, | a. all necessary documentation for the start of the works,
| b. vsa potrebna pripravljalna in pospravljalna dela, | b. all necessary preparatory and clean-up work,
| c. pregled in čiščenje podloge, nanos izravnalne mase, kjer je to potrebno, | c. inspection and cleaning of the substrate, application of levelling compound where necessary,
| d. snemanje potrebnih izmer na gradbišču in po načrtih, | d. recording the necessary measurements on site and as planned,
| e. prenos in obeleževanje višinskih točk na objektu, | e. the transfer and marking of height points on the building,
| f. po potrebi izdelava vzorca in vgradnja le-tega na objektu, | f. if necessary, the production of a sample and its installation on site,
| g. ves potrebni material: glavni, pomožni, pritrdilni in vezni material, | g. all necessary materials: main, auxiliary, fixing and binding materials,
| h. vse potrebne transporte in prenose, | h. all necessary transports and transfers,
| i. ustrezno začasno skladiščenje na delovišču, | i. adequate temporary storage on the worksite,
| j. vsa potrebna pomožna sredstva za montažo in demontažo na objektu, | j. all necessary means of assembly and dismantling on site,
| k. uporabo vse potrebne mehanizacije ali drugih delovnih sredstev z vsemi stroški povezanimi s tem, | k. the use of any necessary machinery or other means of work, with all associated costs,
| l. usklajevanje z osnovnim načrtom in posvetovanje s projektantom, | l. coordination with the basic plan and consultation with the designer,
| m. vso potrebno delo do končnega izdelka, | m. all the work needed to get to the finished product,
| n. vso potrebno zunanje (tehnolog, laboratorij) in notranje kontrole kakovosti, | n. all necessary external (technologist, laboratory) and internal quality control,
| o. vsa potrebna dokazovanja kakovosti materiala, pravilnega načina izvedbe in izvedenih del (certifikati uporabljenih materialov, meritve tlačne trdnosti, poročila itd.), | o. all necessary evidence of the quality of the material, the correct method of execution and the work carried out (certificates of materials used, compressive strength measurements, reports, etc.),
| p. terminsko usklajevanje del z ostalimi izvajalci na objektu, | p. coordinating the timing of works with other contractors on site,
| r. vse potrebne ukrepe za doseganje zahtevane kakovosti in rokov iz potrjenega terminskega plana izvajalca (na primer: Pred pričetkom del na akustičnih celicah mora izvajalec organizirati obvezno izobraževanje delavcev, njihovih vodij in koordinatorjev, ki bodo ta dela opravljali.), | r. all the necessary measures to achieve the required quality and the deadlines set out in the contractor's approved schedule (for example: before starting work on the acoustic cells, the contractor must organise mandatory training for the workers, their supervisors and the coordinators who will carry out the work),
| s. popravilo morebitne povzročene škode ostalim izvajalcem na gradbišču, | s. repair any damage caused to other contractors on site,
| š. čiščenje prostorov, nakladanje in odvoz odpadnega materiala na stalno deponijo, | cleaning the premises, loading and removal of waste materials to a permanent landfill,
| t. plačilo komunalnega prispevka za stalno deponijo odpadnega materiala, | t. payment of the municipal contribution for the permanent landfill of waste materials,
| u. vsi ukrepi za zaščito delavcev na gradbišču, skladno z veljavnimi predpisi s področja varnosti in zdravja pri delu, | u. all measures to protect workers on the construction site, in accordance with the applicable occupational safety and health regulations,
| v. v enotnih cenah morajo biti vključeni stroški na stalni deponiji. Izvajalec je dolžan predati vse evidenčne liste o oddaji odpadnega materiala v stalno deponijo, | v. the unit prices shall include the costs at the permanent landfill. The Contractor shall be obliged to hand over all records of the delivery of waste material to the permanent landfill,
| z. v enotni ceni morajo biti tudi zajeti stroški zaščite dostopnih koridorjev v notranjosti objekta, do prostorov, kjer se izvajajo dela. | z. the unit price must also include the cost of protecting access corridors inside the building to the areas where the work is being carried out.
5. | V primeru da posamezne postavke v popisu ne zajemajo celotnega opisa potrebnega za funkcionalno dokončanje dela, mora ponudnik izvedbo le tega vključiti v ceno na enoto! | In the event that individual items in the inventory do not cover the full description necessary for the functional completion of the work, the tenderer must include this in the unit price!
6. | Vsa dela morajo biti izvršena tako, da je zagotovljena funkcionalnost, stabilnost, varnost, natančnost in življenjska doba posameznih elementov. | All work must be carried out in such a way as to ensure the functionality, stability, safety, precision and service life of the individual components.
2.2.1 | Oznaka sestave: STR-02 Montažni strop nad prostori z akustičnimi zahtevami - "školjka" (cona hrupa A in B). Na lesene morale od spodaj privijačen dobro tesnjen sendvič strop d = 132 mm v sestavi od zgoraj navzdol: ~ cementno-iverna plošča d = 18 mm (kot npr. Betonyp) ~ bukova vezana plošča d = 25 mm ~ mavčno kartonska plošča d = 15 mm ~ mavčno kartonska plošča d = 15 mm ~ mavčno kartonska plošča d = 15 mm ~ OSB plošča d = 22 mm ~ OSB plošča d = 22 mm | Composition code: STR-02 Prefabricated ceiling over rooms with acoustic requirements - "shell" (noise zones A and B). A well-sealed sandwich ceiling d = 132 mm screwed from top to bottom to the timber mortared walls: ~ cement-river board d = 18 mm (such as Betonyp) ~ beech plywood d = 25 mm ~ plasterboard d = 15 mm ~ plasterboard d = 15 mm ~ plasterboard d = 15 mm ~ OSB board d = 22 mm ~ OSB board d = 22 mm | m2 | 1437 |  | 0
2.2.2 | NZ-07 obodna stena školjke - obloga AB stene znotraj laboratorijev v coni hrupa A in B | NZ-07 shell perimeter wall - AB wall lining inside laboratories in noise zones A and B
| kompletna izvedba v sestavi: | complete in assembly:
a. | obloga d = 8,80 cm; od ±0.00 do +2.60 m: (bandažirana, v kvaliteti K2) vlagoodporna mavčno-kartonska plošča d = 12,5 mm, ojačitvena OSB plošča d = 18 mm, alu tipska podkonstrukcija s CW 50 profili z vstavljeno kameno volno gostote min. 30 kg/m3 , odmik od naslednjega sloja 7 mm | cladding d = 8.80 cm; from ±0.00 to +2.60 m: (bandaged, quality K2) moisture-proof plasterboard d = 12.5 mm, reinforcing OSB d = 18 mm, aluminium type substructure with CW 50 profiles with embedded stone wool density of min. 30 kg/m3 , distance from the next layer 7 mm
b. | obloga: od +2,60 m do stropa: perforirana akustična plošča d = 12,5 mm z zamaknjeno okroglo perforacijo 8/12/50 R in z belo akustično tkanino (kot npr. Kanuf Cleaneo Akustik ali enakovredno), alu tipska podkonstrukcija s CW 75 profilov z vstavljeno kameno volno gostote min. 30 kg/m3 | cladding: from +2,60 m to ceiling: perforated acoustic panel d = 12,5 mm with offset round perforation 8/12/50 R and with white acoustic fabric (such as Kanuf Cleaneo Akustik or equivalent), aluminium type substructure with CW 75 profiles with embedded stone wool density of min. 30 kg/m3
| pritličje | ground floor | m2 | 112.84 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
2.2.3 | NZ-06.1 obodna stena školjke - cona hrupa A in B, vibracijska cona VIB1 (stene, ki mejijo na hodnike) | NZ-06.1 shell perimeter wall - noise zones A and B, vibration zone VIB1 (walls adjacent to corridors)
| kompletna izvedba v sestavi: | complete in assembly:
| Rw' ≥ 52 dB (velja za celo sestavo, po celotni višini) - glej elaborat akustike | Rw' ≥ 52 dB (applies to the whole structure, at full height) - see acoustics study
a. | absorpcojska obloga d = 8,80 cm; od ±0.00 do +2.60 m: (bandažirana, v kvaliteti K2) vlagoodporna mavčno-kartonska plošča d = 12,5 mm, ojačitvena OSB plošča d = 18 mm, alu tipska podkonstrukcija s CW 50 profili z vstavljeno kameno volno gostote min. 30 kg/m3, odmik od naslednjega sloja 7 mm | absorption layer d = 8.80 cm; from ±0.00 to +2.60 m: (bandaged, K2 quality) moisture-resistant plasterboard d = 12.5 mm, reinforcing OSB d = 18 mm, aluminium type substructure with CW 50 profiles with embedded stone wool with a density of min. 30 kg/m3, distance from the next layer 7 mm
| pritličje | ground floor | m2 | 176.54 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
| nad višino vrat do spuščenega stropa hodnika | above the door height up to the lowered ceiling of the corridor
b. | absorpcojska obloga d = 8,80 cm; od ±0.00 do +2.60 m: (bandažirana, v kvaliteti K2) vlagoodporna mavčno-kartonska plošča d = 12,5 mm, ojačitvena OSB plošča d = 18 mm, alu tipska podkonstrukcija s CW 50 profili z vstavljeno kameno volno gostote min. 30 kg/m3, odmik od naslednjega sloja 7 mm | absorption layer d = 8.80 cm; from ±0.00 to +2.60 m: (bandaged, K2 quality) moisture-resistant plasterboard d = 12.5 mm, reinforcing OSB d = 18 mm, aluminium type substructure with CW 50 profiles with embedded stone wool with a density of min. 30 kg/m3, distance from the next layer 7 mm
| AB stena - že zajeto | AB wall - already covered
| pritličje | ground floor | m2 | 176.54 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
c. | zračni prostor d = 10,00 cm: mineralna kamena volna gostote min. 30 kg/m3 | air space d = 10,00 cm: mineral stone wool with a density of at least 30 kg/m3
d. | obloga: mavčno-kartonska obloga Dvoslojna obloga z mavčno kartonskimi ploščami, d = 2 x 12,5 mm | cladding: plasterboard Double-layer plasterboard cladding, d = 2 x 12,5 mm
e. | podkonstrukcija d = 7,50 cm: Kovinska tipska enojna podkonstrukcija, izvedena po navodilu proizvajalca predelnih zidov (kot npr. Knauf W112 ali enakovredno). Medprostor je v celoti zapolnjen z mineralno volno. | substructure d = 7,50 cm: Metal type single substructure, made according to the instructions of the partition wall manufacturer (such as Knauf W112 or equivalent). The space between the two walls is completely filled with mineral wool.
f. | obloga: mavčno-kartonska obloga Dvoslojna obloga z mavčno kartonskimi ploščami, d = 2 x 12,5 mm | cladding: plasterboard Double-layer plasterboard cladding, d = 2 x 12,5 mm
g. | akustična obloga d = 1,50 cm: akustične plošče iz lesne volne (kot npr. Heradesign Superfine ali enakovredno) | acoustic lining d = 1,50 cm: acoustic wood wool panels (such as Heradesign Superfine or equivalent)
h. | zračni prostor d = 10,00 cm | air space d = 10,00 cm
| pritličje | ground floor | m2 | 101.85 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
| nad višino spuščenega stropa hodnika do montažnega stropa školjke | above the height of the lowered ceiling of the corridor up to the prefabricated ceiling of the shell
i. | obloga d = 8,80 cm: od ±0.00 do +2.60 m: (bandažirana, v kvaliteti K2) vlagoodporna mavčno-kartonska plošča d = 12,5 mm, ojačitvena OSB plošča d = 18 mm, alu tipska podkonstrukcija s CW 50 profili z vstavljeno kameno volno gostote min. 30 kg/m3, odmik od naslednjega sloja 7 mm | cladding d = 8.80 cm: from ±0.00 to +2.60 m: (bandaged, quality K2) moisture-proof plasterboard d = 12.5 mm, reinforcing OSB d = 18 mm, aluminium type substructure with CW 50 profiles with embedded stone wool density of min. 30 kg/m3, distance from the next layer 7 mm
| AB stena - že zajeto | AB wall - already covered
j. | zračni prostor d = 10,00 cm: mineralna kamena volna gostote min. 30 kg/m3 | air space d = 10,00 cm: mineral stone wool with a density of at least 30 kg/m3
k. | obloga: mavčno-kartonska obloga Dvoslojna obloga z mavčno kartonskimi ploščami, d = 2 x 12,5 mm | cladding: plasterboard Double-layer plasterboard cladding, d = 2 x 12,5 mm
l. | podkonstrukcija d = 7,50 cm: Kovinska tipska enojna podkonstrukcija, izvedena po navodilu proizvajalca predelnih zidov (kot npr. Knauf W112 ali enakovredno). Medprostor je v celoti zapolnjen z mineralno volno . | substructure d = 7,50 cm: Metal type single substructure, made according to the instructions of the partition wall manufacturer (such as Knauf W112 or equivalent). The space between the two walls is completely filled with mineral wool.
m. | obloga: mavčno-kartonska obloga Dvoslojna obloga z mavčno kartonskimi ploščami, d = 2 x 12,5mm | cladding: plasterboard Double-layer cladding with plasterboard, d = 2 x 12,5mm
n. | absorpcijska obloga d = 7,50 cm: obloga iz mineralne volne gostote min. 30 kg/m3 d = 5 cm + akustične plošče iz lesne volne d = 2,5 cm (kot npr. Heradesign Superfine ali enakovredno), skupaj pritrjeno s tipskimi profili v oblogo, barvano v antracit sivo barvo | absorption lining d = 7,50 cm: mineral wool lining with a density of at least 30 kg/m3 d = 5 cm + acoustic wood wool panels d = 2,5 cm (such as Heradesign Superfine or equivalent), fixed together with type profiles in the lining, painted anthracite grey
| pritličje | ground floor | m2 | 78 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
| nad montažnim stropom školjke | above the prefabricated ceiling of the shell
o. | obloga: mavčno-kartonska obloga Dvoslojna obloga z mavčno kartonskimi ploščami, d = 2 x 12,5 mm | cladding: plasterboard Double-layer plasterboard cladding, d = 2 x 12,5 mm
p. | podkonstrukcija d = 7,50 cm: Kovinska tipska enojna podkonstrukcija, izvedena po navodilu proizvajalca predelnih zidov (kot npr. Knauf W112 ali enakovredno). Medprostor je v celoti zapolnjen z mineralno volno. | substructure d = 7,50 cm: Metal type single substructure, made according to the instructions of the partition wall manufacturer (such as Knauf W112 or equivalent). The space between the two walls is completely filled with mineral wool.
r. | obloga: mavčno-kartonska obloga Dvoslojna obloga z mavčno kartonskimi ploščami, d = 2 x 12,5 mm | cladding: plasterboard Double-layer plasterboard cladding, d = 2 x 12,5 mm
s. | absorpcijska obloga d = 7,50 cm: obloga iz mineralne volne gostote min. 30 kg/m3 d = 5 cm + akustične plošče iz lesne volne d = 2,5 cm (kot npr. Heradesign Superfine ali enakovredno), skupaj pritrjeno s tipskimi profili v oblogo, barvano v antracit sivo barvo | absorption lining d = 7,50 cm: mineral wool lining with a density of at least 30 kg/m3 d = 5 cm + acoustic wood wool panels d = 2,5 cm (such as Heradesign Superfine or equivalent), fixed together with type profiles in the lining, painted anthracite grey
| pritličje | ground floor | m2 | 55 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
2.2.4 | NZ-01.5 predelna mavčno-kartonska stena med laboratoriji znotraj iste školjke (cona hrupa A in B) | NZ-01.5 plasterboard partition between laboratories within the same shell (noise zones A and B)
| kompletna izvedba v sestavi: | complete in assembly:
| min. zvočna izolirnost:Rw' ≥ 52 dB | min. sound insulation:Rw' ≥ 52 dB
a. | akustična obloga*: d = 8,80 cm: od ±0.00 do +2.60 m: (bandažirana, v kvaliteti K2) vlagoodporna mavčno-kartonska plošča d = 12,5 mm, ojačitvena OSB plošča d = 18 mm, alu tipska podkonstrukcija s CW 50 profili z vstavljeno kameno volno gostote min. 30 kg/m3, odmik od naslednjega sloja 7 mm | acoustic lining*: d = 8.80 cm: from ±0.00 to +2.60 m: (bandaged, quality K2) moisture-proof plasterboard d = 12.5 mm, reinforcing OSB d = 18 mm, aluminium type substructure with CW 50 profiles with embedded stone wool density of min. 30 kg/m3, distance from the next layer 7 mm
| pritličje | ground floor | m2 | 138 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
b. | od +2.60 m do stropa: perforirana akustična plošča d = 12,5 mm z zamaknjeno okroglo perforacijo 8/12/50 R in z belo akustično tkanino (kot npr. Kanuf Cleaneo Akustik ali enakovredno), alu tipska podkonstrukcija s CW 75 profilov z vstavljeno kameno volno gostote min. 30 kg/m3 | from +2.60 m to ceiling: perforated acoustic panel d = 12.5 mm with offset round perforation 8/12/50 R and white acoustic fabric (such as Kanuf Cleaneo Akustik or equivalent), aluminium type substructure with CW 75 profiles with embedded stone wool density min. 30 kg/m3
| pritličje | ground floor | m2 | 138 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
c. | obloga:mavčno-kartonska obloga Dvoslojna obloga z mavčno kartonskimi ploščami, d = 2 x 15mm; d = 3cm | cladding:plasterboard Double-layer plasterboard cladding, d = 2 x 15mm; d = 3cm
d. | podkonstrukcija: Nosilna kovinska ali lesena podkonstrukcija - debelina skladna s statičnim izračunom! Medprostor med konstrukcijo je v celoti zapolnjen z mineralno volno gostote min. 30 kg/m3, d = 10cm | substructure: load-bearing metal or timber substructure - thickness in accordance with the static calculation! The space between the structures is completely filled with mineral wool with a density of at least 30 kg/m3, d = 10 cm
e. | zračni prostor: zračni prostor; d = 1 cm | air space: air space; d = 1 cm
f. | podkonstrukcija: Nosilna kovinska ali lesena podkonstrukcija - debelina skladna s statičnim izračunom! Medprostor med konstrukcijo je v celoti zapolnjen z mineralno volno gostote min. 30 kg/m3, d = 10 cm | substructure: load-bearing metal or timber substructure - thickness according to static calculation! The space between the structures shall be completely filled with mineral wool with a density of at least 30 kg/m3, d = 10 cm
g. | obloga: mavčno-kartonska obloga. Dvoslojna obloga z mavčno kartonskimi ploščami, d = 2 x 15 mm; d = 3,3 cm | cladding: plasterboard cladding. Double-layer plasterboard cladding, d = 2 x 15 mm; d = 3,3 cm
| pritličje | ground floor | m2 | 276 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
h. | akustična obloga*: d = 8,80 cm: od ±0.00 do +2.60 m: (bandažirana, v kvaliteti K2) vlagoodporna mavčno-kartonska plošča d = 12,5 mm, ojačitvena OSB plošča d = 18 mm, alu tipska podkonstrukcija s CW 50 profili z vstavljeno kameno volno gostote min. 30 kg/m3, odmik od naslednjega sloja 7 mm | acoustic lining*: d = 8.80 cm: from ±0.00 to +2.60 m: (bandaged, quality K2) moisture-proof plasterboard d = 12.5 mm, reinforcing OSB d = 18 mm, aluminium type substructure with CW 50 profiles with embedded stone wool density of min. 30 kg/m3, distance from the next layer 7 mm
| pritličje | ground floor | m2 | 138 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
i. | od tal do stropa - prostor P1 J4 105: perforirana akustična plošča d = 12,5 mm z zamaknjeno okroglo perforacijo 8/12/50 R in z belo akustično tkanino (kot npr. Kanuf Cleaneo Akustik ali enakovredno), alu tipska podkonstrukcija s CW 75 profilov z vstavljeno kameno volno gostote min. 30 kg/m3 | floor to ceiling - room P1 J4 105: perforated acoustic panel d = 12,5 mm with offset round perforation 8/12/50 R and with white acoustic fabric (such as Kanuf Cleaneo Akustik or equivalent), aluminium type substructure with CW 75 profiles with embedded stone wool density of min. 30 kg/m3
| pritličje | ground floor | m2 | 242 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
2.2.5 | NZ-01.5a požarno varna mavčno-kartonska stena med laboratoriji znotraj iste školjke (cona hrupa A in B); EI 60 | NZ-01.5a fire-safe plasterboard wall between laboratories within the same shell (noise zone A and B); EI 60
| kompletna izvedba v sestavi: | complete in assembly:
| min. zvočna izolirnost:Rw' ≥ 52 dB | min. sound insulation:Rw' ≥ 52 dB
a. | akustična obloga: d = 8,80 cm: od ±0.00 do +2.60 m: (bandažirana, v kvaliteti K2) vlagoodporna mavčno-kartonska plošča d = 12,5 mm, ojačitvena OSB plošča d = 18 mm, alu tipska podkonstrukcija s CW 50 profili z vstavljeno kameno volno gostote min. 30 kg/m3, odmik od naslednjega sloja 7 mm | acoustic lining: d = 8.80 cm: from ±0.00 to +2.60 m: (bandaged, quality K2) moisture-proof plasterboard d = 12.5 mm, reinforcing OSB d = 18 mm, aluminium type substructure with CW 50 profiles with embedded stone wool density min. 30 kg/m3, distance from the next layer 7 mm
| pritličje | ground floor | m2 | 15.99 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
b. | od +2.60 m do stropa: perforirana akustična plošča d = 12,5 mm z zamaknjeno okroglo perforacijo 8/12/50 R in z belo akustično tkanino (kot npr. Kanuf Cleaneo Akustik ali enakovredno), alu tipska podkonstrukcija s CW 75 profilov z vstavljeno kameno volno gostote min. 30 kg/m3 | from +2.60 m to ceiling: perforated acoustic panel d = 12.5 mm with offset round perforation 8/12/50 R and white acoustic fabric (such as Kanuf Cleaneo Akustik or equivalent), aluminium type substructure with CW 75 profiles with embedded stone wool density min. 30 kg/m3
| pritličje | ground floor | m2 | 15.99 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
c. | obloga: mavčno-kartonska obloga Dvoslojna obloga s požarnimi mavčno kartonskimi ploščami, d = 2 x 15 mm; d = 3 cm | cladding: plasterboard Double-layer cladding with fire-resistant plasterboard, d = 2 x 15 mm; d = 3 cm
d. | podkonstrukcija: Nosilna kovinska ali lesena podkonstrukcija - debelina skladna s statičnim izračunom! Medprostor med konstrukcijo je v celoti zapolnjen z mineralno volno gostote min. 30 kg/m3, d = 10cm | substructure: load-bearing metal or timber substructure - thickness according to static calculation! The space between the structures shall be completely filled with mineral wool with a density of at least 30 kg/m3, d = 10 cm
e. | zračni prostor d = 1,00 cm | air space d = 1,00 cm
f. | podkonstrukcija: mavčno-kartonska obloga Dvoslojna obloga s požarnimi mavčno kartonskimi ploščami, d = 2 x 15 mm; d = 10 cm | substructure: plasterboard Double-layer cladding with fire-resistant plasterboard, d = 2 x 15 mm; d = 10 cm
g. | obloga: mavčno-kartonska obloga Dvoslojna obloga s požarnimi mavčno kartonskimi ploščami, d = 2 x 15 mm; d = 3 cm | cladding: plasterboard Double-layer cladding with fire-resistant plasterboard, d = 2 x 15 mm; d = 3 cm
| pritličje | ground floor | m2 | 31.98 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
h. | akustična obloga: d = 8,80 cm: od ±0.00 do +2.60 m: (bandažirana, v kvaliteti K2) vlagoodporna mavčno-kartonska plošča d = 12,5 mm, ojačitvena OSB plošča d = 18 mm, alu tipska podkonstrukcija s CW 50 profili z vstavljeno kameno volno gostote min. 30 kg/m3, odmik od naslednjega sloja 7 mm | acoustic lining: d = 8.80 cm: from ±0.00 to +2.60 m: (bandaged, quality K2) moisture-proof plasterboard d = 12.5 mm, reinforcing OSB d = 18 mm, aluminium type substructure with CW 50 profiles with embedded stone wool density min. 30 kg/m3, distance from the next layer 7 mm
| pritličje | ground floor | m2 | 15.99 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
i. | od +2.60 m do stropa: perforirana akustična plošča d = 12,5 mm z zamaknjeno okroglo perforacijo 8/12/50 R in z belo akustično tkanino (kot npr. Kanuf Cleaneo Akustik ali enakovredno), alu tipska podkonstrukcija s CW 75 profilov z vstavljeno kameno volno gostote min. 30 kg/m3 | from +2.60 m to ceiling: perforated acoustic panel d = 12.5 mm with offset round perforation 8/12/50 R and white acoustic fabric (such as Kanuf Cleaneo Akustik or equivalent), aluminium type substructure with CW 75 profiles with embedded stone wool density min. 30 kg/m3
| pritličje | ground floor | m2 | 15.99 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
2.2.6 | NZ-01.5b predelna mavčno-kartonska obloga v laboratoriji znotraj iste školjke (Vibratorij LADISK) | NZ-01.5b plasterboard partition in the laboratory within the same shell (LADISK Vibrator)
| kompletna izvedba v sestavi: | complete in assembly:
a. | akustična obloga: d = 8,80 cm: perforirana akustična plošča d = 12,5 mm z zamaknjeno okroglo perforacijo 8/12/50 R in z belo akustično tkanino (kot npr. Kanuf Cleaneo Akustik ali enakovredno), alu tipska podkonstrukcija s CW 75 profilov z vstavljeno kameno volno gostote min. 30 kg/m3 | acoustic lining: d = 8,80 cm: perforated acoustic panel d = 12,5 mm with offset round perforation 8/12/50 R and with white acoustic fabric (such as Kanuf Cleaneo Akustik or equivalent), aluminium type substructure with CW 75 profiles with embedded stone wool density of min. 30 kg/m3
b. | obloga: mavčno-kartonska obloga Dvoslojna obloga s požarnimi mavčno kartonskimi ploščami, d = 2 x 15 mm; d = 3 cm | cladding: plasterboard Double-layer cladding with fire-resistant plasterboard, d = 2 x 15 mm; d = 3 cm
c. | podkonstrukcija d = 10,00 cm: Nosilna kovinska ali lesena podkonstrukcija - debelina skladna s statičnim izračunom! Medprostor med konstrukcijo je v celoti zapolnjen z mineralno volno gostote min. 30 kg/m3. | substructure d = 10.00 cm: Supporting metal or timber substructure - thickness according to static calculation! The space between the structures shall be completely filled with mineral wool of a minimum density of 30 kg/m3.
d. | zračni prostor d = 1,00 cm | air space d = 1,00 cm
e. | podkonstrukcija d = 10,00 cm: Nosilna kovinska ali lesena podkonstrukcija - debelina skladna s statičnim izračunom! Medprostor med konstrukcijo je v celoti zapolnjen z mineralno volno gostote min. 30 kg/m3. | substructure d = 10.00 cm: Supporting metal or timber substructure - thickness according to static calculation! The space between the structures shall be completely filled with mineral wool of a minimum density of 30 kg/m3.
f. | zračni prostor do zidane/ab stene: d = 30 cm; mineralna kamena volna gostote min. 30 kg/m3 | air space to the masonry/ab wall: d = 30 cm; mineral stone wool with a density of min. 30 kg/m3
| pritličje | ground floor | m2 | 15 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
g. | znotraj prostora P1 J4 105 - absorpcijska obloga od tal do stropa | inside room P1 J4 105 - floor to ceiling absorbent lining
| akustična obloga: d = 8,80 cm: perforirana akustična plošča d = 12,5 mm z zamaknjeno okroglo perforacijo 8/12/50 R in z belo akustično tkanino (kot npr. Kanuf Cleaneo Akustik ali enakovredno), alu tipska podkonstrukcija s CW 75 profilov z vstavljeno kameno volno gostote min. 30 kg/m3 | acoustic lining: d = 8,80 cm: perforated acoustic panel d = 12,5 mm with offset round perforation 8/12/50 R and with white acoustic fabric (such as Kanuf Cleaneo Akustik or equivalent), aluminium type substructure with CW 75 profiles with embedded stone wool density of min. 30 kg/m3
| pritličje | ground floor | m2 | 242 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
2.2.7 | NZ-09.1 stena med AB školjko in instalacijskim jaškom ali požarnim stopniščem - knauf obloga (P1); d = 13,00 cm | NZ-09.1 wall between AB shell and installation shaft or fire escape - knauf lining (P1); d = 13,00 cm
| kompletna izvedba v sestavi: | complete in assembly:
| zvočna izolativnost: Rw ≥ 38 dB | sound insulation performance: Rw ≥ 38 dB
a. | obloga: mavčno-kartonska obloga Dvoslojna obloga z mavčno kartonskimi ploščami, d = 2 x 12,5 mm | cladding: plasterboard Double-layer plasterboard cladding, d = 2 x 12,5 mm
b. | podkonstrukcija d = 10,00 cm: Kovinska tipska enojna podkonstrukcija, izvedena po navodilu proizvajalca predelnih zidov (kot npr. Knauf W112 ali enakovredno). Medprostor je v celoti zapolnjen z mineralno volno . | substructure d = 10.00 cm: Metal type single substructure, made according to the instructions of the partition wall manufacturer (such as Knauf W112 or equivalent). The space between the walls is completely filled with mineral wool.
c. | zračni prostor d = 2,00 cm | air space d = 2,00 cm
| pritličje | ground floor | m2 | 83 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
d. | akustična obloga d = 8,80 cm; od ±0.00 do +2.60 m: (bandažirana, v kvaliteti K2) vlagoodporna mavčno-kartonska plošča d = 12,5 mm, ojačitvena OSB plošča d = 18 mm, alu tipska podkonstrukcija s CW 50 profili z vstavljeno kameno volno gostote min. 30 kg/m3, odmik od naslednjega sloja 7 mm | acoustic lining d = 8.80 cm; from ±0.00 to +2.60 m: (bandaged, quality K2) moisture-proof plasterboard d = 12.5 mm, reinforcing OSB d = 18 mm, aluminium type substructure with CW 50 profiles with embedded stone wool density min. 30 kg/m3, distance from the next layer 7 mm
| pritličje: h = 2,60 m | ground floor: h = 2.60 m | m2 | 41 |  | 0
| I.ND + II.ND + III.ND: h = 2,60 m | I.ND + II.ND + III.ND: h = 2,60 m | m2 | 0 |  | 0
e. | od +2.60 m do stropa: perforirana akustična plošča d = 12,5 mm z zamaknjeno okroglo perforacijo 8/12/50 R in z belo akustično tkanino (kot npr. Kanuf Cleaneo Akustik ali enakovredno), alu tipska podkonstrukcija s CW 75 profilov z vstavljeno kameno volno gostote min. 30 kg/m3 | from +2.60 m to the ceiling: perforated acoustic panel d = 12.5 mm with offset round perforation 8/12/50 R and white acoustic fabric (such as Kanuf Cleaneo Akustik or equivalent), aluminium type substructure with CW 75 profiles with embedded stone wool density of min. 30 kg/m3
| pritličje: h = 2,60 m | ground floor: h = 2.60 m | m2 | 41 |  | 0
| I.ND + II.ND + III.ND: h = 1,65 m | I.ND + II.ND + III.ND: h = 1,65 m | m2 | 0 |  | 0
2.2.8 | NZ-01.10 predelna mavčno-kartonska stena med laboratoriji in servisi znotraj iste školjke (cona hrupa A in B) | NZ-01.10 plasterboard partition between laboratories and service areas within the same shell (noise zones A and B)
| kompletna izvedba v sestavi: | complete in assembly:
| min. zvočna izolirnost: Rw' ≥ 52 dB | min. sound insulation: Rw' ≥ 52 dB
a. | obloga: mavčno-kartonska obloga Dvojna obloga z vlagoodpornimi impregniranimi mavčno kartonskimi ploščami, d = 2 x 12,5mm; d = 2,5 cm | cladding: plasterboard Double skin with moisture-resistant impregnated plasterboard, d = 2 x 12.5mm; d = 2.5 cm
b. | podkonstrukcija: Kovinska tipska enojna podkonstrukcija, izvedena po navodilu proizvajalca predelnih zidov (kot npr.: Knauf W112 ali enakovredno) Medprostor je v celoti zapolnjen z mineralno volno; d = 7,5 cm | substructure: single metal substructure of the type specified by the partition wall manufacturer (e.g. Knauf W112 or equivalent) The space between the walls is completely filled with mineral wool; d = 7,5 cm
c. | obloga:mavčno-kartonska obloga Dvojna obloga z vlagoodpornimi impregniranimi mavčno kartonskimi ploščami, d = 2 x 12,5 mm; d = 2,5 cm | cladding:plasterboard Double skin with moisture-resistant impregnated plasterboard, d = 2 x 12,5 mm; d = 2,5 cm
| pritličje | ground floor | m2 | 146 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
d. | absorpcijska obloga d = 8,80 cm: od ±0.00 do +2.60 m: (bandažirana, v kvaliteti K2) vlagoodporna mavčno-kartonska plošča d = 12,5 mm, ojačitvena OSB plošča d = 18 mm, alu tipska podkonstrukcija s CW 50 profili z vstavljeno kameno volno gostote min. 30 kg/m3, odmik od naslednjega sloja 7 mm | absorption lining d = 8.80 cm: from ±0.00 to +2.60 m: (bandaged, quality K2) moisture-proof plasterboard d = 12.5 mm, reinforcing OSB d = 18 mm, aluminium type substructure with CW 50 profiles with embedded stone wool density of min. 30 kg/m3, distance from the next layer 7 mm
| pritličje | ground floor | m2 | 73 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
e. | od +2.60 m do stropa: perforirana akustična plošča d = 12,5 mm z zamaknjeno okroglo perforacijo 8/12/50 R in z belo akustično tkanino (kot npr. Kanuf Cleaneo Akustik ali enakovredno), alu tipska podkonstrukcija s CW 75 profilov z vstavljeno kameno volno gostote min. 30 kg/m3 | from +2.60 m to the ceiling: perforated acoustic panel d = 12.5 mm with offset round perforation 8/12/50 R and white acoustic fabric (such as Kanuf Cleaneo Akustik or equivalent), aluminium type substructure with CW 75 profiles with embedded stone wool density of min. 30 kg/m3
| pritličje | ground floor | m2 | 74 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
2.2.9 | NZ-06.2 obodna stena školjke - cona hrupa A in B, vibracijska cona VIB1 (stene, ki mejijo na laboratorije) | NZ-06.2 shell perimeter wall - noise zones A and B, vibration zone VIB1 (walls adjacent to laboratories)
| kompletna izvedba v sestavi: | complete in assembly:
| Rw' ≥ 52 dB (velja za celo sestavo, po celotni višini) - glej elaborat akustike | Rw' ≥ 52 dB (applies to the whole structure, at full height) - see acoustics study
a. | absorpcojska obloga d = 8,80 cm; od ±0.00 do +2.60 m: (bandažirana, v kvaliteti K2) vlagoodporna mavčno-kartonska plošča d = 12,5 mm, ojačitvena OSB plošča d = 18 mm, alu tipska podkonstrukcija s CW 50 profili z vstavljeno kameno volno gostote min. 30 kg/m3, odmik od naslednjega sloja 7 mm | absorption layer d = 8.80 cm; from ±0.00 to +2.60 m: (bandaged, K2 quality) moisture-resistant plasterboard d = 12.5 mm, reinforcing OSB d = 18 mm, aluminium type substructure with CW 50 profiles with embedded stone wool with a density of min. 30 kg/m3, distance from the next layer 7 mm
| pritličje | ground floor | m2 | 234 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
b. | absorpcojska obloga d = 8,80 cm; od ±0.00 do +2.60 m: (bandažirana, v kvaliteti K2) vlagoodporna mavčno-kartonska plošča d = 12,5 mm, ojačitvena OSB plošča d = 18 mm, alu tipska podkonstrukcija s CW 50 profili z vstavljeno kameno volno gostote min. 30 kg/m3, odmik od naslednjega sloja 7 mm | absorption layer d = 8.80 cm; from ±0.00 to +2.60 m: (bandaged, K2 quality) moisture-resistant plasterboard d = 12.5 mm, reinforcing OSB d = 18 mm, aluminium type substructure with CW 50 profiles with embedded stone wool with a density of min. 30 kg/m3, distance from the next layer 7 mm
| pritličje | ground floor | m2 | 234 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
2.2.10 | NZ-06.3 obodna stena školjke - cona hrupa A, vibracijska cona VIB1 (stena med labom in gluho sobo LADISK - P1) | NZ-06.3 shell perimeter wall - noise zone A, vibration zone VIB1 (wall between lab and deaf room LADISK - P1)
| kompletna izvedba v sestavi: | complete in assembly:
| Rw' ≥ 52 dB (velja za celo sestavo, po celotni višini) - glej elaborat akustike | Rw' ≥ 52 dB (applies to the whole structure, at full height) - see acoustics study
a. | absorpcojska obloga d = 8,80 cm; od ±0.00 do +2.60 m: (bandažirana, v kvaliteti K2) vlagoodporna mavčno-kartonska plošča d = 12,5 mm, ojačitvena OSB plošča d = 18 mm, alu tipska podkonstrukcija s CW 50 profili z vstavljeno kameno volno gostote min. 30 kg/m3, odmik od naslednjega sloja 7 mm | absorption layer d = 8.80 cm; from ±0.00 to +2.60 m: (bandaged, K2 quality) moisture-resistant plasterboard d = 12.5 mm, reinforcing OSB d = 18 mm, aluminium type substructure with CW 50 profiles with embedded stone wool with a density of min. 30 kg/m3, distance from the next layer 7 mm
| pritličje | ground floor | m2 | 26 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
b. | absorpcijska obloga: d = 12,5 mm; od +2.60 m do stropa: perforirana akustična plošča d = 12,5 mm z zamaknjeno okroglo perforacijo 8/12/50 R in z belo akustično tkanino (kot npr. Kanuf Cleaneo Akustik ali enakovredno), alu tipska podkonstrukcija s CW 75 profilov z vstavljeno kameno volno gostote min. 30 kg/m3 | absorption lining: d = 12,5 mm; from +2,60 m to ceiling: perforated acoustic panel d = 12,5 mm with offset round perforation 8/12/50 R and white acoustic fabric (such as Kanuf Cleaneo Akustik or equivalent), aluminium type substructure with CW 75 profiles with embedded stone wool density of min. 30 kg/m3
| pritličje | ground floor | m2 | 26 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
2.2.11 | NZ-06.4 obodna stena školjke - cona hrupa A, vibracijska cona VIB1 (stena med labom LADISK in avlo - P1); d = 12,50 cm | NZ-06.4 shell perimeter wall - noise zone A, vibration zone VIB1 (wall between LADISK lab and lobby - P1); d = 12,50 cm
| kompletna izvedba v sestavi: | complete in assembly:
| do višine spuščenega stropa | up to the height of the lowered ceiling
| Rw' ≥ 52 dB (velja za celo sestavo, po celotni višini) - glej elaborat akustike | Rw' ≥ 52 dB (applies to the whole structure, at full height) - see acoustics study
a. | absorpcijska obloga: d = 8,80 cm; od ±0.00 do +2.60 m: (bandažirana, v kvaliteti K2) vlagoodporna mavčno-kartonska plošča d = 12,5 mm, ojačitvena OSB plošča d = 18 mm, alu tipska podkonstrukcija s CW 50 profili z vstavljeno kameno volno gostote min. 30 kg/m3, odmik od naslednjega sloja 7 mm | absorption lining: d = 8.80 cm; ±0.00 to +2.60 m: (bandaged, K2 quality) moisture-proof plasterboard d = 12.5 mm, reinforcing OSB d = 18 mm, aluminium type substructure with CW 50 profiles with embedded stone wool density of min. 30 kg/m3, distance from the next layer 7 mm
| pritličje | ground floor | m2 | 21 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
b. | absorpcijska obloga d = 12,50 mm; od +2.60 m do stropa: perforirana akustična plošča d = 12,5 mm z zamaknjeno okroglo perforacijo 8/12/50 R in z belo akustično tkanino (kot npr. Kanuf Cleaneo Akustik ali enakovredno), alu tipska podkonstrukcija s CW 75 profilov z vstavljeno kameno volno gostote min. 30 kg/m3 | absorption lining d = 12,50 mm; from +2,60 m to ceiling: perforated acoustic panel d = 12,5 mm with offset round perforation 8/12/50 R and white acoustic fabric (such as Kanuf Cleaneo Akustik or equivalent), aluminium type substructure with CW 75 profiles with embedded stone wool density of min. 30 kg/m3
| pritličje | ground floor | m2 | 21 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
c. | zračni prostor d = 10,00 cm: mineralna kamena volna gostote min. 30 kg/m3 | air space d = 10,00 cm: mineral stone wool with a density of at least 30 kg/m3
d. | obloga: mavčno-kartonska obloga Dvoslojna obloga z mavčno kartonskimi ploščami, d = 2 x 12,5 mm | cladding: plasterboard Double-layer plasterboard cladding, d = 2 x 12,5 mm
e. | podkonstrukcija d = 7,50 cm: Kovinska tipska enojna podkonstrukcija, izvedena po navodilu proizvajalca predelnih zidov (kot npr. Knauf W112 ali enakovredno). Medprostor je v celoti zapolnjen z mineralno volno. | substructure d = 7,50 cm: Metal type single substructure, made according to the instructions of the partition wall manufacturer (such as Knauf W112 or equivalent). The space between the two walls is completely filled with mineral wool.
f. | obloga: mavčno-kartonska obloga Dvoslojna obloga z mavčno kartonskimi ploščami, d = 2 x 12,5 mm | cladding: plasterboard Double-layer plasterboard cladding, d = 2 x 12,5 mm
| pritličje | ground floor | m2 | 21 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
| nad višino spuščenega stropa: | above the height of the lowered ceiling:
g. | absorpcijska obloga: d = 8,80 cm; od ±0.00 do +2.60 m: (bandažirana, v kvaliteti K2) vlagoodporna mavčno-kartonska plošča d = 12,5 mm, ojačitvena OSB plošča d = 18 mm, alu tipska podkonstrukcija s CW 50 profili z vstavljeno kameno volno gostote min. 30 kg/m3, odmik od naslednjega sloja 7 mm | absorption lining: d = 8.80 cm; ±0.00 to +2.60 m: (bandaged, K2 quality) moisture-proof plasterboard d = 12.5 mm, reinforcing OSB d = 18 mm, aluminium type substructure with CW 50 profiles with embedded stone wool density of min. 30 kg/m3, distance from the next layer 7 mm
| pritličje | ground floor | m2 | 13 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
| AB stena že zajeto | AB wall already covered
h. | absorpcijska obloga d = 12,50 mm; od +2.60 m do stropa: perforirana akustična plošča d = 12,5 mm z zamaknjeno okroglo perforacijo 8/12/50 R in z belo akustično tkanino (kot npr. Kanuf Cleaneo Akustik ali enakovredno), alu tipska podkonstrukcija s CW 75 profilov z vstavljeno kameno volno gostote min. 30 kg/m3 | absorption lining d = 12,50 mm; from +2,60 m to ceiling: perforated acoustic panel d = 12,5 mm with offset round perforation 8/12/50 R and white acoustic fabric (such as Kanuf Cleaneo Akustik or equivalent), aluminium type substructure with CW 75 profiles with embedded stone wool density of min. 30 kg/m3
| pritličje | ground floor | m2 | 13 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
i. | zračni prostor d = 10,00 cm: mineralna kamena volna gostote min. 30 kg/m3: zračni prostor med zidano steno in knauf oblogo mora biti v celoti zapolnjen z mineralno volno, brez zračnih reg | air space d = 10,00 cm: mineral stone wool with a density of min. 30 kg/m3: the air space between the masonry wall and the knauf cladding must be completely filled with mineral stone wool, without air gaps
j. | obloga: mavčno-kartonska obloga Dvoslojna obloga z mavčno kartonskimi ploščami, d = 2 x 12,5 mm | cladding: plasterboard Double-layer plasterboard cladding, d = 2 x 12,5 mm
k. | podkonstrukcija d = 7,50 cm: Kovinska tipska enojna podkonstrukcija, izvedena po navodilu proizvajalca predelnih zidov (kot npr. Knauf W112 ali enakovredno). Medprostor je v celoti zapolnjen z mineralno volno. | substructure d = 7,50 cm: Metal type single substructure, made according to the instructions of the partition wall manufacturer (such as Knauf W112 or equivalent). The space between the two walls is completely filled with mineral wool.
l. | obloga: mavčno-kartonska obloga Dvoslojna obloga z mavčno kartonskimi ploščami, d = 2 x 12,5 mm | cladding: plasterboard Double-layer plasterboard cladding, d = 2 x 12,5 mm
m. | finalni sloj d = 6,00 cm; termo in zvočno izolacijska plošče s sredico iz kamene volne in plasti mineralizirane lesne volne (kot. npr. Fragmat Drvoterm DTO2 A2 ali enakovredno) lepljene / sidrane v podlago, barvano v antracit sivo barvo | final layer d = 6,00 cm; thermal and acoustic insulation panels with stone wool core and mineralised wood wool layers (such as Fragmat Drvoterm DTO2 A2 or equivalent) glued/anchored to the substrate, painted anthracite grey
| pritličje | ground floor | m2 | 4 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
2.2.12 | NZ-11.7b stena iz betonskih zidakov z akustično oblogo (znotraj laboratorijev, zvokolovov v coni hrupa A - P1) - obojestranska oblaga zidane stene | NZ-11.7b concrete block wall with acoustic lining (inside laboratories, sound enclosures in noise zone A - P1) - masonry wall cladding on both sides
| kompletna izvedba v sestavi: | complete in assembly:
a. | absorpcijska obloga d = 8,80 cm: od ±0.00 do +2.60 m: (bandažirana, v kvaliteti K2) vlagoodporna mavčno-kartonska plošča d = 12,5 mm, ojačitvena OSB plošča d = 18 mm, alu tipska podkonstrukcija s CW 50 profili z vstavljeno kameno volno gostote min. 30 kg/m3, odmik od naslednjega sloja 7 mm | absorption lining d = 8.80 cm: from ±0.00 to +2.60 m: (bandaged, quality K2) moisture-proof plasterboard d = 12.5 mm, reinforcing OSB d = 18 mm, aluminium type substructure with CW 50 profiles with embedded stone wool density of min. 30 kg/m3, distance from the next layer 7 mm
| pritličje | ground floor | m2 | 148 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
b. | absorpcijska obloga: od +2.60 m do stropa: perforirana akustična plošča d = 12,5 mm z zamaknjeno okroglo perforacijo 8/12/50 R in z belo akustično tkanino (kot npr. Kanuf Cleaneo Akustik ali enakovredno), alu tipska podkonstrukcija s CW 75 profilov z vstavljeno kameno volno gostote min. 30 kg/m3 | absorption covering: from +2.60 m to ceiling: perforated acoustic panel d = 12.5 mm with offset round perforation 8/12/50 R and white acoustic fabric (such as Kanuf Cleaneo Akustik or equivalent), aluminium type substructure with CW 75 profiles with embedded stone wool density of min. 30 kg/m3
| pritličje | ground floor | m2 | 148 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
| zidana stena - zajeto v zidarskih delih | masonry wall - included in masonry works
c. | absorpcijska obloga d = 8,80 cm: od ±0.00 do +2.60 m: (bandažirana, v kvaliteti K2) vlagoodporna mavčno-kartonska plošča d = 12,5 mm, ojačitvena OSB plošča d = 18 mm, alu tipska podkonstrukcija s CW 50 profili z vstavljeno kameno volno gostote min. 30 kg/m3, odmik od naslednjega sloja 7 mm | absorption lining d = 8.80 cm: from ±0.00 to +2.60 m: (bandaged, quality K2) moisture-proof plasterboard d = 12.5 mm, reinforcing OSB d = 18 mm, aluminium type substructure with CW 50 profiles with embedded stone wool density of min. 30 kg/m3, distance from the next layer 7 mm
| pritličje | ground floor | m2 | 148 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
d. | absorpcijska obloga: od +2.60 m do stropa: perforirana akustična plošča d = 12,5 mm z zamaknjeno okroglo perforacijo 8/12/50 R in z belo akustično tkanino (kot npr. Kanuf Cleaneo Akustik ali enakovredno), alu tipska podkonstrukcija s CW 75 profilov z vstavljeno kameno volno gostote min. 30 kg/m3 | absorption covering: from +2.60 m to ceiling: perforated acoustic panel d = 12.5 mm with offset round perforation 8/12/50 R and white acoustic fabric (such as Kanuf Cleaneo Akustik or equivalent), aluminium type substructure with CW 75 profiles with embedded stone wool density of min. 30 kg/m3
| pritličje | ground floor | m2 | 148 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
2.2.13 | NZ-08.3 stena med AB školjko TINT in laboratoriji | NZ-08.3 wall between AB shell TINT and laboratories
| kompletna izvedba v sestavi: | complete in assembly:
| zvočna izolativnost: Rw ≥ 38 dB | sound insulation performance: Rw ≥ 38 dB
a. | akustična obloga d = 8,80 cm: perforirana akustična plošča d = 12,5 mm z zamaknjeno okroglo perforacijo 8/12/50 R in z belo akustično tkanino (kot npr. Kanuf Cleaneo Akustik ali enakovredno), alu tipska podkonstrukcija s CW 75 profilov z vstavljeno kameno volno gostote min. 30 kg/m3 | acoustic lining d = 8,80 cm: perforated acoustic panel d = 12,5 mm with offset round perforation 8/12/50 R and with white acoustic fabric (such as Kanuf Cleaneo Akustik or equivalent), aluminium type substructure with CW 75 profiles with embedded stone wool density of min. 30 kg/m3
b. | zračni prostor d = 2,00 cm | air space d = 2,00 cm
c. | podkonstrukcija d = 10,00 cm: Kovinska tipska enojna podkonstrukcija, izvedena po navodilu proizvajalca predelnih zidov (kot npr. Knauf W112 ali enakovredno). Medprostor je v celoti zapolnjen z mineralno volno. | substructure d = 10,00 cm: Metal type single substructure, made according to the instructions of the partition wall manufacturer (such as Knauf W112 or equivalent). The space between the two walls is completely filled with mineral wool.
d. | obloga: mavčno-kartonska obloga Dvoslojna obloga z mavčno kartonskimi ploščami, d = 2 x 12,5 mm | cladding: plasterboard Double-layer plasterboard cladding, d = 2 x 12,5 mm
| pritličje | ground floor | m2 | 58 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
e. | akustična obloga d = 8,80 cm: od ±0.00 do +2.60 m: (bandažirana, v kvaliteti K2) vlagoodporna mavčno-kartonska plošča d = 12,5 mm, ojačitvena OSB plošča d = 18 mm, alu tipska podkonstrukcija s CW 50 profili z vstavljeno kameno volno gostote min. 30 kg/m3, odmik od naslednjega sloja 7 mm | acoustic lining d = 8.80 cm: from ±0.00 to +2.60 m: (bandaged, quality K2) moisture-proof plasterboard d = 12.5 mm, reinforcing OSB d = 18 mm, aluminium type substructure with CW 50 profiles with embedded stone wool density min. 30 kg/m3, distance from the next layer 7 mm
| pritličje | ground floor | m2 | 29 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
f. | akustična obloga: od +2.60 m do stropa: perforirana akustična plošča d = 12,5 mm z zamaknjeno okroglo perforacijo 8/12/50 R in z belo akustično tkanino (kot npr. Kanuf Cleaneo Akustik ali enakovredno), alu tipska podkonstrukcija s CW 75 profilov z vstavljeno kameno volno gostote min. 30 kg/m3 | acoustic lining: from +2.60 m to the ceiling: perforated acoustic panel d = 12.5 mm with offset round perforation 8/12/50 R and with white acoustic fabric (such as Kanuf Cleaneo Akustik or equivalent), aluminium type substructure with CW 75 profiles with embedded stone wool density of min. 30 kg/m3
| pritličje | ground floor | m2 | 29 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
2.2.14 | NZ-01.7 obloga AB stebra v školjkah v coni hrupa A in B (P1) | NZ-01.7 AB column lining in shells in noise zones A and B (P1)
| absorpcijska obloga* d = 8,80 cm: | absorbent liner* d = 8.80 cm:
| kompletna izvedba v sestavi: | complete in assembly:
| *OPOMBA: zračni prostor med zidano steno in AB stebrom mora biti v celoti zapolnjen z mineralno volno, brez zračnih reg. | *NOTE: The air space between the masonry wall and the AB column must be completely filled with mineral wool, without air gaps.
| min. zvočna izolirnost:Rw' ≥ 52 dB | min. sound insulation:Rw' ≥ 52 dB
a. | od ±0.00 do +2.60 m: (bandažirana, v kvaliteti K2) vlagoodporna mavčno-kartonska plošča d = 12,5 mm, ojačitvena OSB plošča d = 18 mm, alu tipska podkonstrukcija s CW 50 profili z vstavljeno kameno volno gostote min. 30 kg/m3, odmik od naslednjega sloja 7 mm | from ±0.00 to +2.60 m: (bandaged, quality K2) moisture-resistant plasterboard d = 12.5 mm, reinforcing OSB d = 18 mm, aluminium type substructure with CW 50 profiles with embedded stone wool density of min. 30 kg/m3, distance from the next layer 7 mm
b. | zračni prostor d = 10,00 cm: mineralna kamena volna gostote min. 30 kg/m3 | air space d = 10,00 cm: mineral stone wool with a density of at least 30 kg/m3
| pritličje | ground floor | m2 | 1160 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
c. | od +2.60 m do stropa: perforirana akustična plošča d = 12,5 mm z zamaknjeno okroglo perforacijo 8/12/50 R in z belo akustično tkanino (kot npr. Kanuf Cleaneo Akustik ali enakovredno), alu tipska podkonstrukcija s CW 75 profilov z vstavljeno kameno volno gostote min. 30 kg/m3 | from +2.60 m to ceiling: perforated acoustic panel d = 12.5 mm with offset round perforation 8/12/50 R and white acoustic fabric (such as Kanuf Cleaneo Akustik or equivalent), aluminium type substructure with CW 75 profiles with embedded stone wool density min. 30 kg/m3
d. | zračni prostor d = 10,00 cm: mineralna kamena volna gostote min. 30 kg/m3 | air space d = 10,00 cm: mineral stone wool with a density of at least 30 kg/m3
| pritličje | ground floor | m2 | 581 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
d. | dodatek za oblogo v prrostoru TINT (P1) - zobniki - perforirana obloga kot npr. Knauf Cleaneo Akustik od tal do stropa! | tINT (P1) cavity lining add-on - gears - perforated cladding such as Knauf Cleaneo Acoustic from floor to ceiling!
| pritličje | ground floor | m2 | 63 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
2.2.15 | NZ-01.7a obloga AB stebra ali stene v školjkah v coni hrupa A in B - brez absorpcijske obloge (P1) | NZ-01.7a AB column or wall cladding in shells in noise zones A and B - without absorber cladding (P1)
| kompletna izvedba v sestavi: | complete in assembly:
| min. zvočna izolirnost:Rw' ≥ 52 dB | min. sound insulation:Rw' ≥ 52 dB
a. | zračni prostor*: mineralna volna: d = 10,00 cm | air space*: mineral wool: d = 10.00 cm
b. | obloga; od tal do višine vrat: (bandažirana, v kvaliteti K2) mavčno-kartonska plošča d = 12,5 mm, ojačitvena OSB plošča d = 18 mm, alu tipska podkonstrukcija s CW 50 profili z vstavljeno kameno volno gostote min. 30 kg/m3, odmik od naslednjega sloja 7 mm - d = 10,00 cm | cladding; from the floor to the door height: (bandaged, quality K2) plasterboard d = 12.5 mm, reinforcing OSB d = 18 mm, aluminium type substructure with CW 50 profiles with embedded stone wool density of min. 30 kg/m3, distance from the next layer 7 mm - d = 10.00 cm
| pritličje | ground floor | m2 | 242.97 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
c. | zračni prostor: d = 10,00 cm: mineralna volna | air space: d = 10,00 cm: mineral wool
| pritličje | ground floor | m2 | 486 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
d. | obloga: od višine vrat do stropa: perforirana akustična plošča d = 12,5 mm z zamaknjeno okroglo perforacijo 8/12/50 R in z belo akustično tkanino (kot npr. Kanuf Cleaneo Akustik ali enakovredno), alu tipska podkonstrukcija s CW 75 profilov z vstavljeno kameno volno gostote min. 30 kg/m3 | cladding: from door height to ceiling: perforated acoustic panel d = 12,5 mm with offset round perforation 8/12/50 R and with white acoustic fabric (such as Kanuf Cleaneo Akustik or equivalent), aluminium type substructure with CW 75 profiles with embedded stone wool density of min. 30 kg/m3
| pritličje | ground floor | m2 | 242.97 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 0 |  | 0
2.2.16 | NZ-01.2a predelna mavčno-kartonska stena med predprostorom odmevnice in avlo (N1); d = 25,50 cm | NZ-01.2a plasterboard partition wall between the echo chamber anteroom and the lobby (N1); d = 25.50 cm
| kompletna izvedba v sestavi: | complete in assembly:
| min. zvočna izolirnost: Rw' ≥ 52 dB | min. sound insulation: Rw' ≥ 52 dB
a. | akustična obloga d = 8,80 cm: perforirana akustična plošča d = 12,5 mm z zamaknjeno okroglo perforacijo 8/12/50 R in z belo akustično tkanino (kot npr. Kanuf Cleaneo Akustik ali enakovredno), alu tipska podkonstrukcija s CW 75 profilov z vstavljeno kameno volno gostote min. 30 kg/m3 | acoustic lining d = 8,80 cm: perforated acoustic panel d = 12,5 mm with offset round perforation 8/12/50 R and with white acoustic fabric (such as Kanuf Cleaneo Akustik or equivalent), aluminium type substructure with CW 75 profiles with embedded stone wool density of min. 30 kg/m3
b. | obloga: mavčno-kartonska obloga Dvoslojna obloga z mavčno kartonskimi ploščami, d = 2 x 12,5 mm; d = 2,5 cm | cladding: plasterboard Double-layer plasterboard cladding, d = 2 x 12,5 mm; d = 2,5 cm
c. | podkonstrukcija: Kovinska tipska dvojna podkonstrukcija, izvedena po navodilu proizvajalca predelnih zidov (kot npr. Knauf W115 ali enakovredno). Medprostor je v celoti zapolnjen z mineralno volno. d = 20,5 cm | substructure: Metal type double substructure, made according to the instructions of the partition wall manufacturer (such as Knauf W115 or equivalent). The space between the walls is completely filled with mineral wool. d = 20,5 cm
d. | obloga: mavčno-kartonska obloga Dvoslojna obloga z mavčno kartonskimi ploščami, d = 2 x 12,5 mm; d = 2,5 cm | cladding: plasterboard Double-layer plasterboard cladding, d = 2 x 12,5 mm; d = 2,5 cm
| min. zvočna izolirnost: Rw' ≥ 52 dB | min. sound insulation: Rw' ≥ 52 dB
| pritličje | ground floor | m2 | 0 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 5 |  | 0
| nad višino spuščenega stropa avle | above the height of the lowered ceiling of the lobby
e. | akustična obloga d = 6,00 cm: termo in zvočno izolacijska plošče s sredico iz kamene volne in plasti mineralizirane lesne volne (kot npr. Fragmat Drvoterm DTO2 A2 ali enakovredno) lepljene / sidrane v podlago, barvano v antracit sivo barvo | acoustic lining d = 6,00 cm: thermal and acoustic insulation panels with stone wool core and mineralised wood wool layers (such as Fragmat Drvoterm DTO2 A2 or equivalent) glued/anchored to the substrate, painted anthracite grey
| pritličje | ground floor | m2 | 0 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 13 |  | 0
2.2.17 | NZ-01.2b predelna mavčno-kartonska stena med odmevnico ali gluho sobo in avlo (N1); d = 45,50 cm | NZ-01.2b plasterboard partition wall between echo or deaf room and lobby (N1); d = 45.50 cm
| kompletna izvedba v sestavi: | complete in assembly:
| zvočna izolativnost: Rw' ≥ 60 dB | sound insulation: Rw' ≥ 60 dB
a. | zračni prostor: mineralna kamena volna gostote min. 30 kg/m3; d = 20cm | air space: mineral stone wool with a density of min. 30 kg/m3; d = 20 cm
b. | obloga: mavčno-kartonska obloga Dvoslojna obloga z mavčno kartonskimi ploščami, d = 2 x 12,5 mm; d = 2,5 cm | cladding: plasterboard Double-layer plasterboard cladding, d = 2 x 12,5 mm; d = 2,5 cm
c. | podkonstrukcija: Kovinska tipska dvojna podkonstrukcija, izvedena po navodilu proizvajalca predelnih zidov (kot npr. Knauf W115 ali enakovredno). Medprostor je v celoti zapolnjen z mineralno volno. d = 20,5cm | substructure: Metal type double substructure, made according to the instructions of the partition wall manufacturer (such as Knauf W115 or equivalent). The space between the walls is completely filled with mineral wool. d = 20,5 cm
d. | obloga:mavčno-kartonska obloga Dvoslojna obloga z mavčno kartonskimi ploščami, d = 2 x 12,5 mm; d = 2,5 cm | cladding:plasterboard Double-layer plasterboard cladding, d = 2 x 12,5 mm; d = 2,5 cm
| pritličje | ground floor | m2 | 0 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 39 |  | 0
| nad višino spuščenega stropa avle | above the height of the lowered ceiling of the lobby
e. | akustična obloga d = 6,00 cm: termo in zvočno izolacijska plošče s sredico iz kamene volne in plasti mineralizirane lesne volne (kot npr. Fragmat Drvoterm DTO2 A2 ali enakovredno) lepljene / sidrane v podlago, barvano v antracit sivo barvo | acoustic lining d = 6,00 cm: thermal and acoustic insulation panels with stone wool core and mineralised wood wool layers (such as Fragmat Drvoterm DTO2 A2 or equivalent) glued/anchored to the substrate, painted anthracite grey
| pritličje | ground floor | m2 | 0 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 11 |  | 0
2.2.18 | NZ-01.8a predelna mavčno-kartonska stena med odmevnico ali gluho sobo in hodnikom (N1); d = 25,50 cm | NZ-01.8a plasterboard partition wall between echo or deaf room and corridor (N1); d = 25.50 cm
| kompletna izvedba v sestavi: | complete in assembly:
| zvočna izolativnost: Rw' ≥ 60 dB | sound insulation: Rw' ≥ 60 dB
a. | zračni prostor: mineralna kamena volna gostote min. 30 kg/m3; d = 50 cm | air space: mineral stone wool with a density of at least 30 kg/m3; d = 50 cm
b. | obloga:mavčno-kartonska obloga Dvoslojna obloga z mavčno kartonskimi ploščami, d = 2 x 12,5 mm; d = 2,5 cm | cladding:plasterboard Double-layer plasterboard cladding, d = 2 x 12,5 mm; d = 2,5 cm
c. | obloga:mavčno-kartonska obloga Dvoslojna obloga z mavčno kartonskimi ploščami, d = 2 x 12,5 mm; d = 2,5 cm | cladding:plasterboard Double-layer plasterboard cladding, d = 2 x 12,5 mm; d = 2,5 cm
| pritličje | ground floor | m2 | 0 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 56 |  | 0
| nad višino vrat: - do spuščenega stropa | above door height: - to the lowered ceiling
| MK stena iz točke a.b.c | MK wall referred to in point a.b.c
d. | akustična obloga: akustične plošče iz lesne volne (kot npr. Heradesign Superfine ali enakovredno); d = 1,5 cm | acoustic lining: acoustic wood wool panels (such as Heradesign Superfine or equivalent); d = 1,5 cm
| zračni prostor d = 0,5 cm | air space d = 0,5 cm
| perforirana kovinska mreža vpeta v pločevinaste omega in L profile, (kot npr. Atena Monolama R, perforirana, 1200 x 600 mm, 40 x 40 mm, rezano na mero na objektu ali enakovredno), prašno barvano po RAL, ki ga določi projektant, zajeto v ključavničarskih delih - dela uskladiti z izvajalcem ključavničarskih del | perforated metal mesh embedded in sheet metal omega and L profiles, (such as Atena Monolama R, perforated, 1200 x 600 mm, 40 x 40 mm, cut to size on site or equivalent), powder-coated to RAL to be specified by the designer, included in the locksmith's works - works to be coordinated with the locksmith's contractor
| pritličje | ground floor | m2 | 0 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 11 |  | 0
| nad višino spuščenega stropa | above the height of the lowered ceiling
| MK stena iz točke a.b.c | MK wall referred to in point a.b.c
e. | akustična obloga d = 6,00 cm: termo in zvočno izolacijska plošče s sredico iz kamene volne in plasti mineralizirane lesne volne (kot npr. Fragmat Drvoterm DTO2 A2 ali enakovredno) lepljene / sidrane v podlago, barvano v antracit sivo barvo | acoustic lining d = 6,00 cm: thermal and acoustic insulation panels with stone wool core and mineralised wood wool layers (such as Fragmat Drvoterm DTO2 A2 or equivalent) glued/anchored to the substrate, painted anthracite grey
| pritličje | ground floor | m2 | 0 |  | 0
| I.ND + II.ND + III.ND | I.ND + II.ND + III.ND | m2 | 34 |  | 0
2.2.19 | NZ-13.17 AB stena z akustično oblogo (gluha soba v LADISK - P1) - obloga | NZ-13.17 AB wall with acoustic lining (deaf room in LADISK - P1) - lining
| kompletna izvedba v sestavi: | complete in assembly:
a. | akustična obloga d = 8,80 cm: od ±0.00 do +2.60 m: (bandažirana, v kvaliteti K2) vlagoodporna mavčno-kartonska plošča d = 12,5 mm, ojačitvena OSB plošča d = 18 mm, alu tipska podkonstrukcija s CW 50 profili z vstavljeno kameno volno gostote min. 30 kg/m3, odmik od naslednjega sloja 7 mm | acoustic lining d = 8.80 cm: from ±0.00 to +2.60 m: (bandaged, quality K2) moisture-proof plasterboard d = 12.5 mm, reinforcing OSB d = 18 mm, aluminium type substructure with CW 50 profiles with embedded stone wool density min. 30 kg/m3, distance from the next layer 7 mm
| pritličje: h = 2,60 m | ground floor: h = 2.60 m | m2 | 17 |  | 0
| I.ND + II.ND + III.ND: h = 2,60 m | I.ND + II.ND + III.ND: h = 2,60 m | m2 | 0 |  | 0
b. | od +2.60 m do stropa: perforirana akustična plošča d = 12,5 mm z zamaknjeno okroglo perforacijo 8/12/50 R in z belo akustično tkanino (kot npr. Kanuf Cleaneo Akustik ali enakovredno), alu tipska podkonstrukcija s CW 75 profilov z vstavljeno kameno volno gostote min. 30 kg/m3 | from +2.60 m to ceiling: perforated acoustic panel d = 12.5 mm with offset round perforation 8/12/50 R and white acoustic fabric (such as Kanuf Cleaneo Akustik or equivalent), aluminium type substructure with CW 75 profiles with embedded stone wool density of min. 30 kg/m3
| AB stena - že zajeto | AB wall - already covered
| pritličje: h = 2,60 m | ground floor: h = 2.60 m | m2 | 17 |  | 0
| I.ND + II.ND + III.ND: h = 1,65 m | I.ND + II.ND + III.ND: h = 1,65 m | m2 | 0 |  | 0
| notranji sloji gluhe sobe: predmet uporabnika | the inner layers of a deaf room: the subject of the user
| SUHOMONTAŽNA DELA | DRYWALL WORKS |  |  |  | 0

## 1.6.2.2.3_Keramičarska_dela
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | AKUSTIČNE CELICE | ACOUSTIC CELLS
1.6.2.2 | ZAKLJUČNA OBRTNIŠKA DELA | CRAFT WORKS
1.6.2.2.3 | KERAMIČARSKA DELA | CERAMIC WORK |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
2.3 | KERAMIČARSKA DELA | CERAMIC WORK
| OPOMBA: Pri izdelavi ponudbe upoštevati pripombe, iz poglavja 0.1 UVOD Pri izdelavi popisa upoštevati pripombe, iz poglavja 0.2 UVOD - DGNB in dokument: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme. | NOTE: Take into account the comments made in section 0.1 INTRODUCTION when preparing the offer In the preparation of the inventory, take into account the comments made in Section 0.2 INTRODUCTION - DGNB and the document DGNB Quality Grades of Installed Materials, Elements and Equipment.
| SPLOŠNA DOLOČILA | GENERAL PROVISIONS
1. | Za vse nejasnosti ali variantne rešitve se je obvezno posvetovati s projektantom. | For any ambiguities or alternative solutions, the designer must be consulted.
2. | Vsa dela morajo biti izvršena po določilih veljavnih normativov in v soglasju s tehničnimi predpisi za izvajanje tovrstnih del. | All work must be carried out in accordance with the applicable norms and in conformity with the technical regulations for the execution of this type of work.
3. | Storitve kooperanta obsegajo (če ni z medsebojno pogodbo drugače določeno): | The services of the Cooperator include (unless otherwise specified in a mutual agreement):
| a. snemanje vseh potrebnih izmer na objektu pred pričetkom izvajanja del, | a. recording all necessary measurements on the site before the works start,
| b. pregled in čiščenje podloge, | b. inspection and cleaning of the lining,
| c. nanos izravnalne mase, kjer je to zahtevano po opisu posamezne postavke, | c. application of levelling compound where required by the item description,
| d. vsa dela na objektu vključno z vsemi dajatvami, | d. all works on the building, including all charges,
| e. dobava osnovnega in pomožnega materiala, | e. the supply of basic and ancillary materials,
| f. prevoz materiala in orodja na objekt z vsem potrebnim nakladanjem, ekspeditom, razkladanjem in notranjim transportom do mesta vgrajevanja ter polaganje po opisu posamezne postavke, | f. transport of materials and tools to the site with all necessary loading, forwarding, unloading and internal transport to the installation site and installation as described in each item,
| g. popravila zidov oz. oblog sten, poškodovanih ob izvajanju del ter | g. repairs to walls or wall cladding damaged during the works; and
| h. odstranjevanje preostalega materiala, odnos in odvoz iz gradbišča, končno čiščenje in zavarovanje izvedenih del do predaje in podobno. | h. removal of residual materials, take-off and removal from the site, final cleaning and securing of the works until handover, etc.
4. | Enotne cene morajo vsebovati: | The uniform prices must include:
| a. vsa potrebna dokumentacija za začetek del, | a. all necessary documentation for the start of the works,
| b. vsa potrebna pripravljalna in pospravljalna dela, | b. all necessary preparatory and clean-up work,
| c. pregled in čiščenje podloge, nanos izravnalne mase, kjer je to potrebno, | c. inspection and cleaning of the substrate, application of levelling compound where necessary,
| d. snemanje potrebnih izmer na gradbišču in po načrtih, | d. recording the necessary measurements on site and as planned,
| e. prenos in obeleževanje višinskih točk na objektu, | e. the transfer and marking of height points on the building,
| f. po potrebi izdelava vzorca in vgradnja le-tega na objektu, | f. if necessary, the production of a sample and its installation on site,
| g. ves potrebni material: glavni, pomožni, pritrdilni in vezni material, | g. all necessary materials: main, auxiliary, fixing and binding materials,
| h. vse potrebne transporte in prenose, | h. all necessary transports and transfers,
| i. ustrezno začasno skladiščenje na delovišču, | i. adequate temporary storage on the worksite,
| j. vsa potrebna pomožna sredstva za montažo in demontažo na objektu, | j. all necessary means of assembly and dismantling on site,
| k. uporabo vse potrebne mehanizacije ali drugih delovnih sredstev z vsemi stroški povezanimi s tem, | k. the use of any necessary machinery or other means of work, with all associated costs,
| l. usklajevanje z osnovnim načrtom in posvetovanje s projektantom, | l. coordination with the basic plan and consultation with the designer,
| m. vso potrebno delo do končnega izdelka, | m. all the work needed to get to the finished product,
| n. vso potrebno zunanje (tehnolog, laboratorij) in notranje kontrole kakovosti, | n. all necessary external (technologist, laboratory) and internal quality control,
| o. vsa potrebna dokazovanja kakovosti materiala, pravilnega načina izvedbe in izvedenih del (certifikati uporabljenih materialov, meritve tlačne trdnosti, poročila itd.), | o. all necessary evidence of the quality of the material, the correct method of execution and the work carried out (certificates of materials used, compressive strength measurements, reports, etc.),
| p. terminsko usklajevanje del z ostalimi izvajalci na objektu, | p. coordinating the timing of works with other contractors on site,
| r. vse potrebne ukrepe za doseganje zahtevane kakovosti in rokov iz potrjenega terminskega plana izvajalca, | r. all necessary measures to achieve the required quality and the deadlines set out in the Contractor's approved schedule,
| s. popravilo morebitne povzročene škode ostalim izvajalcem na gradbišču, | s. repair any damage caused to other contractors on site,
| š. čiščenje prostorov, nakladanje in odvoz odpadnega materiala na stalno deponijo, | cleaning the premises, loading and removal of waste materials to a permanent landfill,
| t. plačilo komunalnega prispevka za stalno deponijo odpadnega materiala, | t. payment of the municipal contribution for the permanent landfill of waste materials,
| u. vsi ukrepi za zaščito delavcev na gradbišču, skladno z veljavnimi predpisi s področja varnosti in zdravja pri delu, | u. all measures to protect workers on the construction site, in accordance with the applicable occupational safety and health regulations,
| v. v enotnih cenah morajo biti vključeni stroški na stalni deponiji. Izvajalec je dolžan predati vse evidenčne liste o oddaji odpadnega materiala v stalno deponijo, | v. the unit prices shall include the costs at the permanent landfill. The Contractor shall be obliged to hand over all records of the delivery of waste material to the permanent landfill,
| z. v enotni ceni morajo biti tudi zajeti stroški zaščite dostopnih koridorjev v notranjosti objekta, do prostorov, kjer se izvajajo dela. | z. the unit price must also include the cost of protecting access corridors inside the building to the areas where the work is being carried out.
5. | V primeru da posamezne postavke v popisu ne zajemajo celotnega opisa potrebnega za funkcionalno dokončanje dela, mora ponudnik izvedbo le tega vključiti v ceno na enoto! | In the event that individual items in the inventory do not cover the full description necessary for the functional completion of the work, the tenderer must include this in the unit price!
6. | Vsa dela morajo biti izvršena tako, da je zagotovljena funkcionalnost, stabilnost, varnost, natančnost in življenjska doba posameznih elementov. | All work must be carried out in such a way as to ensure the functionality, stability, safety, precision and service life of the individual components.
2.3.1 | Oznaka sestave: NT-20 Tla odmevnice (N1) | Composition code: NT-20 Echo chamber floor (N1)
a. | Zaključni tlak: ~ keramika večjih dimenzij, z zelo gladko površino, nameščena brez fug lepljena s cement-akrilnim lepilom 0,5 cm (kot npr. Florima B&W - White glossy, 60 x 60 cm, d = 9 mm) Opomba: pod keramiko upoštevati izravnalno maso. | Final pressure: ~ ceramics of large dimensions, with a very smooth surface, installed without grout, glued with cement-acrylic adhesive 0.5 cm (such as Florima B&W - White glossy, 60 x 60 cm, d = 9 mm) Note: under ceramics, take into account the levelling compound. | m2 | 12 |  | 0
2.3.2 | Oznaka sestave: STR-09 Strop odmevnice - AB školjka (N1) | Composition code: STR-09 Reflection ceiling - AB shell (N1)
a. | Obloga stropa: ~ keramika večjih dimenzij, z zelo gladko površino, nameščena brez fug lepljena s cement-akrilnim lepilom 0,5 cm (kot npr. Florima B&W - White glossy, 60 x 60 cm, d = 9 mm) | Ceiling cladding: ~ ceramics of large dimensions, with a very smooth surface, installed without grout, glued with cement-acrylic adhesive 0.5 cm (such as Florima B&W - White glossy, 60 x 60 cm, d = 9 mm) | m2 | 12 |  | 0
2.3.3 | Oznaka sestave NZ-01.2b Predelna mavčno-kartonska stena med odmevnico ali gluho sobo in avlo (N1) | Composition code NZ-01.2b Partition plasterboard wall between echo or deaf room and lobby (N1)
a. | Stenska obloga: ~ keramika večjih dimenzij, z zelo gladko površino, nameščena brez fug lepljena s cement-akrilnim lepilom 0,5 cm (kot npr. Florima B&W - White glossy, 60 x 60 cm, d = 9 mm); skupna debelina 1,4 cm. | Wall cladding: ~ ceramics of large dimensions, with a very smooth surface, installed without joints, glued with a cement-acrylic adhesive of 0,5 cm (such as Florima B&W - White glossy, 60 x 60 cm, d = 9 mm); total thickness 1,4 cm. | m2 | 45 |  | 0
| KERAMIČARSKA DELA | CERAMIC WORK |  |  |  | 0

## 1.6.2.2.4_Tlakarska_dela
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | AKUSTIČNE CELICE | ACOUSTIC CELLS
1.6.2.2 | ZAKLJUČNA OBRTNIŠKA DELA | CRAFT WORKS
1.6.2.2.4 | TLAKARSKA DELA | PRESS WORKS |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
2.4 | TLAKARSKA DELA | PRESS WORKS
| OPOMBA: Pri izdelavi ponudbe upoštevati pripombe, iz poglavja 0.1 UVOD Pri izdelavi popisa upoštevati pripombe, iz poglavja 0.2 UVOD - DGNB in dokument: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme. | NOTE: Take into account the comments made in section 0.1 INTRODUCTION when preparing the offer In the preparation of the inventory, take into account the comments made in Section 0.2 INTRODUCTION - DGNB and the document DGNB Quality Grades of Installed Materials, Elements and Equipment.
| SPLOŠNA DOLOČILA | GENERAL PROVISIONS
1. | Za vse nejasnosti ali variantne rešitve se je obvezno posvetovati s projektantom. | For any ambiguities or alternative solutions, the designer must be consulted.
2. | Vsa dela morajo biti izvršena po določilih veljavnih normativov in v soglasju s tehničnimi predpisi za izvajanje tovrstnih del. | All work must be carried out in accordance with the applicable norms and in conformity with the technical regulations for the execution of this type of work.
3. | Storitve kooperanta obsegajo (če ni z medsebojno pogodbo drugače določeno): | The services of the Cooperator include (unless otherwise specified in a mutual agreement):
| a. snemanje vseh potrebnih izmer na objektu pred pričetkom izvajanja del, | a. recording all necessary measurements on the site before the works start,
| b. pregled in čiščenje podloge, | b. inspection and cleaning of the lining,
| c. nanos izravnalne mase, kjer je to zahtevano po opisu posamezne postavke, | c. application of levelling compound where required by the item description,
| d. vsa dela na objektu vključno z vsemi dajatvami, | d. all works on the building, including all charges,
| e. dobava osnovnega in pomožnega materiala, | e. the supply of basic and ancillary materials,
| f. prevoz materiala in orodja na objekt z vsem potrebnim nakladanjem, ekspeditom, razkladanjem in notranjim transportom do mesta vgrajevanja ter polaganje po opisu posamezne postavke, | f. transport of materials and tools to the site with all necessary loading, forwarding, unloading and internal transport to the installation site and installation as described in each item,
| g. popravila zidov oz. oblog sten, poškodovanih ob izvajanju del ter | g. repairs to walls or wall cladding damaged during the works; and
| h. odstranjevanje preostalega materiala, odnos in odvoz iz gradbišča, končno čiščenje in zavarovanje izvedenih del do predaje in podobno. | h. removal of residual materials, take-off and removal from the site, final cleaning and securing of the works until handover, etc.
4. | Enotne cene morajo vsebovati: | The uniform prices must include:
| a. vsa potrebna dokumentacija za začetek del, | a. all necessary documentation for the start of the works,
| b. vsa potrebna pripravljalna in pospravljalna dela, | b. all necessary preparatory and clean-up work,
| c. pregled in čiščenje podloge, nanos izravnalne mase, kjer je to potrebno, | c. inspection and cleaning of the substrate, application of levelling compound where necessary,
| d. snemanje potrebnih izmer na gradbišču in po načrtih, | d. recording the necessary measurements on site and as planned,
| e. prenos in obeleževanje višinskih točk na objektu, | e. the transfer and marking of height points on the building,
| f. po potrebi izdelava vzorca in vgradnja le-tega na objektu, | f. if necessary, the production of a sample and its installation on site,
| g. ves potrebni material: glavni, pomožni, pritrdilni in vezni material, | g. all necessary materials: main, auxiliary, fixing and binding materials,
| h. vse potrebne transporte in prenose, | h. all necessary transports and transfers,
| i. ustrezno začasno skladiščenje na delovišču, | i. adequate temporary storage on the worksite,
| j. vsa potrebna pomožna sredstva za montažo in demontažo na objektu, | j. any necessary means of assembly and dismantling on site,
| k. uporabo vse potrebne mehanizacije ali drugih delovnih sredstev z vsemi stroški povezanimi s tem, | k. the use of any necessary machinery or other means of work, with all associated costs,
| l. usklajevanje z osnovnim načrtom in posvetovanje s projektantom, | l. coordination with the basic plan and consultation with the designer,
| m. vso potrebno delo do končnega izdelka, | m. all the work needed to get to the finished product,
| n. vso potrebno zunanje (tehnolog, laboratorij) in notranje kontrole kakovosti, | n. all necessary external (technologist, laboratory) and internal quality control,
| o. vsa potrebna dokazovanja kakovosti materiala, pravilnega načina izvedbe in izvedenih del (certifikati uporabljenih materialov, meritve tlačne trdnosti, poročila itd.), | o. all necessary evidence of the quality of the material, the correct method of execution and the work carried out (certificates of materials used, compressive strength measurements, reports, etc.),
| p. terminsko usklajevanje del z ostalimi izvajalci na objektu, | p. coordinating the timing of works with other contractors on site,
| r. vse potrebne ukrepe za doseganje zahtevane kakovosti in rokov iz potrjenega terminskega plana izvajalca, | r. all necessary measures to achieve the required quality and the deadlines set out in the Contractor's approved schedule,
| s. popravilo morebitne povzročene škode ostalim izvajalcem na gradbišču, | s. repair any damage caused to other contractors on site,
| š. čiščenje prostorov, nakladanje in odvoz odpadnega materiala na stalno deponijo, | cleaning the premises, loading and removal of waste materials to a permanent landfill,
| t. plačilo komunalnega prispevka za stalno deponijo odpadnega materiala, | t. payment of the municipal contribution for the permanent landfill of waste materials,
| u. vsi ukrepi za zaščito delavcev na gradbišču, skladno z veljavnimi predpisi s področja varnosti in zdravja pri delu, | u. all measures to protect workers on the construction site, in accordance with the applicable occupational safety and health regulations,
| v. v enotnih cenah morajo biti vključeni stroški na stalni deponiji. Izvajalec je dolžan predati vse evidenčne liste o oddaji odpadnega materiala v stalno deponijo, | v. the unit prices shall include the costs at the permanent landfill. The Contractor shall be obliged to hand over all records of the delivery of waste material to the permanent landfill,
| z. v enotni ceni morajo biti tudi zajeti stroški zaščite dostopnih koridorjev v notranjosti objekta, do prostorov, kjer se izvajajo dela. | z. the unit price must also include the cost of protecting access corridors inside the building to the areas where the work is being carried out.
5. | V primeru da posamezne postavke v popisu ne zajemajo celotnega opisa potrebnega za funkcionalno dokončanje dela, mora ponudnik izvedbo le tega vključiti v ceno na enoto! | In the event that individual items in the inventory do not cover the full description necessary for the functional completion of the work, the tenderer must include this in the unit price!
6. | Vsa dela morajo biti izvršena tako, da je zagotovljena funkcionalnost, stabilnost, varnost, natančnost in življenjska doba posameznih elementov. | All work must be carried out in such a way as to ensure the functionality, stability, safety, precision and service life of the individual components.
2.4.1 | Oznaka sestave: NT-06 Medetažna plošča proti garaži - "školjka" laboratoriji (cona hrupa A in B, vibracijska cona VIB1) | Composition code: NT-06 Mezzanine slab facing the garage - "shell" laboratories (noise zones A and B, vibration zone VIB1)
a. | Zaključni tlak: ~ samorazlivni epoksidni premaz, zdrsnosti R9, mat (kot npr. KLB KÖTZAL sistem C1 v sestavi: zaključni sloj - EP 202 + PU 805 R9 mat, izravnalno gladilni sloj EP 57, primer - EP 57, skupne debeline 2,0 mm ali enakovredno) barvo po RAL izbere projektant | Final pressure: ~ self-leveling epoxy coating, slip resistance R9, matt (e.g. KLB KÖTZAL System C1 in the following composition: finishing coat - EP 202 + PU 805 R9 matt, levelling smoothing coat EP 57, primer - EP 57, total thickness 2.0 mm or equivalent) RAL colour to be chosen by the designer | m2 | 1550 |  | 0
b. | Ločilni sloj: ~ polimer cementna izravnalna masa tlačne trdnosti C50 (kot npr. KBL EC 633 ali enakovredno) Opomba: pred nanosom obrusiti estrihe! | Separation layer: ~ polymer cementitious levelling compound of compressive strength C50 (such as KBL EC 633 or equivalent) Note: Wipe off screeds before application! | m2 | 1550 |  | 0
2.4.2 | Oznaka sestave: NT-06a Medetažna plošča proti garaži - "školjka" bazenček v labu LVTS (cona hrupa A in B, vibracijska cona VIB1) | Composition code: NT-06a Mezzanine slab facing the garage - "shell" pool in favour of LVTS (noise zone A and B, vibration zone VIB1)
a. | Zaključni tlak: ~ vodotesen, kemijsko odporen samorazlivni epoksidni premaz (kot npr. KLB KÖTZAL sistem B1 v sestavi: zaključni sloj - EP 282 WHG, izravnalno gladilni sloj EP 55, primer - EP 55, debeline 1,5 - 2,0 mm ali enakovredno) barvo po RAL izbere projektant | Final pressure: ~ waterproof, chemical-resistant, self-leveling epoxy coating (such as KLB KÖTZAL System B1 in the following composition: finishing layer - EP 282 WHG, levelling smoothing layer EP 55, example - EP 55, thickness 1.5 - 2.0 mm or equivalent) RAL colour to be chosen by the designer | m2 | 28 |  | 0
b. | Ločilni sloj: ~ polimer cementna izravnalna masa tlačne trdnosti C50 (kot npr. KBL EC 633 ali enakovredno) Opomba: pred nanosom obrusiti estrihe! | Separation layer: ~ polymer cementitious levelling compound of compressive strength C50 (such as KBL EC 633 or equivalent) Note: Wipe off screeds before application! | m2 | 28 |  | 0
2.4.3 | Oznaka sestave: NT-06b Medetažna plošča proti garaži - "školjka" prostori labov LAVAR in LATOP (cona hrupa A in B, vibracijska cona VIB1) | Composition code: NT-06b Mezzanine slab against the garage - "shell" LAVAR and LATOP lab spaces (noise zone A and B, vibration zone VIB1)
a. | Zaključni tlak: ~ poliuretanski beton (kot npr. KLB KÖTZAL Chemoresin PU-Beton sistem 4009, skupne debeline 8 - 10 mm ali enakovredno), barvo določi projektant | Final pressure: ~ polyurethane concrete (such as KLB KÖTZAL Chemoresin PU-Beton System 4009, total thickness 8 - 10 mm or equivalent), colour to be determined by the designer | m2 | 185 |  | 0
2.4.4 | Oznaka sestave: NT-06c Medetažna plošča proti garaži - "školjka" prostor laba TINT - Zobniki FZG (cona hrupa A in B, vibracijska cona VIB1) | Composition code: NT-06c Mezzanine slab towards the garage - "clamshell" area of the TINT - FZG gears (noise zone A and B, vibration zone VIB1)
a. | Zaključni tlak: ~ antistatična obloga iz naravnih mineralov in čistih polimerov (kot npr. Kährs Upofloor ZERO Enomer ali enakovredno), lepljen na podlago z ustreznim disperzijskim lepilom . Tla so predhodno izravnana z 1x nanosom izravnalne mase. | Final pressure: ~ antistatic covering made of natural minerals and pure polymers (such as Kährs Upofloor ZERO Enomer or equivalent), bonded to the substrate with a suitable dispersion adhesive. The floor is pre-leveled with 1 application of levelling compound. | m2 | 17 |  | 0
| TLAKARSKA DELA | PRESS WORKS |  |  |  | 0