## 0_Naslovnica
OPOZORILO! Vsi prevodi v angleščino so strojno izdelani in zgolj informativne narave. V primeru kakršnekoli nejasnosti ali dvoma izključno velja izvirno besedilo v slovenščini. WARNING! All translations into English have been produced by machine translation and are provided for informational purposes only. In the event of any ambiguity or uncertainty, the original Slovenian text shall prevail exclusively.
| / | / | [5 empty] | /
| Sprem./Rev.: | Opis spremembe/Description of Changes: | [5 empty] | Datum/Date: | Podpis/Signature:
| Investitor/Investor: |  |  |  |  | Gradnja/Facility
|  |  | Univerza v Ljubljani Kongresni trg 12 1000 Ljubljana, Slovenija |  |  | Fakulteta za strojništvo/Faculty of Mechanical Engineering
| Projektant/Design Engineer: |  |  |  |  | Del objekta/sistem/Building/System:
|  |  | IBE, svetovanje, projektiranje in inženiring Ljubljana, Slovenija |  |  | ZUANJA UREDITEV IN KOMUNALNI PRIKLJUČKI/ EXTERIOR OF THE BUILDING AND UT. CONNECTIONS
| Projektant/Design Engineer: |  |  |  |  | Vrsta načrta/Documentation:
2 NAČRT S PODROČJA GRADBENIŠTVA/ DOC. IN THE FIELD OF CIVIL ENGEENIRING
|  | Ime in priimek/Name and Surname: |  |  | Id. št./Id. No: | Vsebina risbe (dokumenta)/Document Title:
| Vodja proj./ Des. Manager: | Boštjan Vuga, univ. dipl. inž. arh., grad. dip. (AA) |  |  | ZAPS 0035 PA PPN | PROJEKTANTSKI POPIS GRADBENIH DEL, KOMUNALNI PRIKLJUČKI OBJEKTA/BOQ OF UTILITY CONNECTIONS
| Poobl. strok./ Cert. Profess.: | Jan Mak Bevcl, mag. inž. grad. |  |  | IZS G-4683
| Poobl. strok./ Cert. Profess.: |  |  |  |  | Št. proj./ Proj. No.: | 362-19 |  | Vrsta dokument./ Document. Type: | DZR
| Izdelal/ Creator: | Manja Bittner, inž. grad. |  |  |  | Klas. ozn./ Class. No.: | -- |  | Stran/ Page: | 1/*
| Datum/ Date: | maj/May 2026 |  | Merilo/ Scale: | / | Ident. ozn./ Id. No: | JULFS--6G1603P

## 0_Osebe
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | KOMUNALNI PRIKLJUČKI OBJEKTA | UTILITY CONNECTIONS
POOBLAŠČENI STROKOVNJAKI, ODGOVORNI ZA IZDELAVO PROJEKTANTSKEGA POPISA:
Id. št. ZAPS/IZS | Pooblaščeni strokovnjak | Strokovno področje
IZS G-4683 | Jan Mak Bevcl, mag. inž. grad. | gradbene konstrukcije, zunanja in komunalna ureditev
SODELAVCI PRI IZDELAVI PROJEKTANTSKEGA POPISA:
/ | Manja Bittner, inž. grad. | izdelava popisov
/ | Katja Čerkez Košir, univ. dipl.inž.grad. | zunanja in komunalna ureditev
CERTIFIED EXPERTS RESPONSIBLE FOR ELABORATING THE BILL OF QUANTITIES:
Id. No ZAPS/IZS | Certified Expert | Area of Expertise
IZS G-4683 | Jan Mak Bevcl, mag. inž. grad. | building structures, Paving and Utility Connections
COLABORATORS IN THE ELABORATING THE BILL OF QUANTITIES:
/ | Manja Bittner, inž. grad. | elaborating the Bill of Quantities
/ | Katja Čerkez Košir, univ. dipl.inž.grad. | Paving and Utility Connections

## 0.1_Uvod-STP
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | KOMUNALNI PRIKLJUČKI OBJEKTA | UTILITY CONNECTIONS
0.1 | SPLOŠNI TEHNIČNI POGOJI | GENERAL TECHNICAL CONDITIONS
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic operator with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
0.1.1 | Izvajalec se obveže, da bo upošteval veljavno zakonodajo, ki ureja graditev objektov v Republiki Sloveniji, vključno s povezanimi podzakonskimi akti, predpisi, tehničnimi smernicami, standardi, pravili stroke in dobro gradbeno prakso. Prav tako mora izvajalec upoštevati vse zahteve izdanega integralnega gradbenega dovoljenja in vsa dela izvesti skladno s projektno dokumentacijo ter ostalimi pogoji, objavljenimi v razpisni dokumentaciji. | The Contractor undertakes to comply with the applicable legislation governing the construction of buildings in the Republic of Slovenia, including related by-laws, regulations, technical guidelines, standards, professional rules and good construction practice. The Contractor shall also comply with all the requirements of the integral building permit issued and shall carry out all works in accordance with the project documentation and other conditions published in the tender documentation.
0.1.2 | Dela lahko izvaja samo izvajalec, ki je registriran za opravljanje gradbene dejavnosti in ima za tovrstna dela ustrezno zavarovanje za škodo, certifikate, tehnično izobražen kader, sredstva ter je usposobljen za samostojno pripravo in izvedbo del. | The work may only be carried out by a contractor who is registered to carry out construction work and who has the appropriate insurance for such work, certificates, technically trained staff, resources and is qualified to prepare and carry out the work independently.
0.1.3 | Izvajalec odgovarja za kakovost izvedbe vseh del. | The Contractor shall be responsible for the quality of the execution of all works.
0.1.4 | Izvajalec nosi vso odgovornost za nesreče in škodo, ki nastane na objektu ali v okolici zaradi njegovega dela. | The Contractor shall bear all liability for accidents and damage to the installation or the surrounding area caused by his work.
0.1.5 | Pred oddajo ponudbe se je izvajalec dolžan seznaniti z območjem predvidenim za gradnjo in temu prilagoditi vsa potrebna dela, kar mora biti zajeto v ponudbi. V neposredni bližini predvidene gradnje se nahajajo stavbe, v katerih potekajo izobraževalni in raziskovalni procesi. Zato bo izvajalec moral izvajati kontrolo hrupa in kontrolo vibracij. Dela, ki so hrupna in dela, ki povzročajo vibracije bo izvajalec moral preprečiti oziroma jih izvesti na način, da povzročajo minimalne vplive. Tehnologijo rušenja, pilotiranja in tehnologijo izvedbe ostalih del bo izvajalec moral prilagoditi tako, da bo vpliv minimalen. Izvajalec mora preprečiti in zmanjšati emisije delcev iz gradbišča na najmanjšo možno mero. | Before submitting a tender, the contractor is obliged to familiarise himself with the area to be constructed and to adapt any necessary works accordingly, which must be included in the tender. In the immediate vicinity of the proposed construction, there are buildings in which educational and research processes take place. The contractor will therefore be required to carry out noise and vibration control. Noise and vibration works will have to be avoided or carried out in such a way as to minimise the impact. Demolition, piling and other works will have to be adapted to minimise the impact. The contractor must avoid and minimise the emission of particulates emitted from the construction site as far as is reasonably practicable.
0.1.6 | Izvajalec je pred oddajo ponudbe dolžan pregledati projektno dokumentacijo in ostale pogoje, ki so del razpisne dokumentacije V primeru morebitnih napak in neskladij je izvajalec dolžan na to opozoriti naročnika pred oddajo ponudbe. | The Contractor is obliged to review the project documentation and other conditions forming part of the tender documentation before submitting the tender In case of any errors or inconsistencies, the Contractor is obliged to bring these to the attention of the Contracting Authority before submitting the tender.
0.1.7 | Pred oddajo ponudbe je izvajalec dolžan preveriti ustreznost popisov del in količin v teh popisih ter njihovo skladnost z ostalimi dokumenti projektne dokumentacije, ki so del razpisne dokumentacije. Prav tako je izvajalec dolžan preveriti vse detajle in sheme. Vse izmere je potrebno preveriti po posameznih projektih oz. načrtih, ki sestavljajo razpisno dokumentacijo. V primeru ugotovljenih neskladij je v času priprave ponudbe obvezan o tem obvestiti naročnika. | Before submitting a tender, the Contractor shall check the adequacy of the inventories of works and quantities in these Bills of Quantities and their conformity with the other documents of the project documentation forming part of the tender documentation. The Contractor shall also check all details and diagrams. All measurements shall be checked against the individual projects or plans forming part of the tender documentation. In the event of any discrepancies, the Contractor shall inform the Contracting Authority at the time of preparing the tender.
0.1.8 | Pred oddajo ponudbe je izvajalec dolžan v tem popisu preveriti zmnožke in seštevke ter prenose le-teh v rekapitulacijo. Izvajalec se s pripravo ponudbe obvezuje, da je prebral vse celice in elemente celotnega popisa, vključno z vsemi postavkami in splošnimi navodili ali določili in je preveril pravilnost preračuna ter s tem zagotavlja ponudbeno vrednost. | Before submitting a tender, the Contractor is required to check the products and totals in this Bill of Quantities (BoQ) and their transfer to the recapitulation. The Contractor undertakes, by preparing a tender, to have read all the cells and elements of the complete BoQ, including all headings and general instructions or provisions, and to have checked the correctness of the conversion, thereby guaranteeing the value of the tender.
0.1.9 | Dela bo izvajalec moral izvajati po predloženi projektni dokumentaciji, detajlih in z upoštevanjem navodil in potrditev projektanta, nadzornika in investitorja. Vso potrebno delavniško dokumentacijo zagotovi izvajalec del v okviru ponujene cene. | The Contractor shall carry out the works in accordance with the submitted design documents, details and subject to the instructions and approvals of the Designer, the Supervisor and the Investor. All necessary workshop documentation shall be provided by the Contractor within the scope of the price quoted.
0.1.10 | Pred izvedbo posameznih del je izvajalec dolžan pregledati projektno dokumentacijo za izvedbo gradnje (PZI) in elaborate. Na morebitne napake v dokumentaciji ali neskladja med posameznimi načrti ali deli načrtov (popisi del, tehnična poročila, lokacijski in tehnični prikazi) izvajalec opozori nadzornika in projektanta, in se z njima pravočasno uskladi. | The Contractor shall review the Detailed Design documentation (PZI) and the studies before carrying out the individual works. The Contractor shall draw the attention of the Supervisor and the Designer to any errors in the documentation or discrepancies between the individual designs or parts of designs (BoQ, technical reports, location and technical drawings) and shall coordinate with them in good time.
0.1.11 | Tehnični opisi, prikazi, detajli, sheme ter ostali dokumenti v PZI dokumentaciji predstavljajo dodaten opis popisnih postavk gradbeno obrtniških in inštalacijskih del ter jih je potrebno dosledno upoštevati skupaj s popisom del. | The technical descriptions, illustrations, details, diagrams and other documents in the Detailed Design documentation (PZI) are additional descriptions of the BoQ inventory items of the building, construction and installation works and must be strictly followed together with the BoQ.
0.1.12 | Specifikacije in zahteve, navedene v popisu, se ne smejo upoštevati kot edine zahteve. Izvajalec je dolžan v ceni zajeti in dobaviti vse elemente opreme ter opraviti dela in storitve, ki niso eksplicitno navedeni, a so bistvenega pomena za funkcionalnost, skladnost s predpisi ter kontinuirano, zanesljivo in varno obratovanje opreme. | The specifications and requirements set out in the BoQ shall not be taken as the only requirements. The Contractor shall be obliged to include in the price and supply all items of equipment and to carry out works and services which are not expressly mentioned but which are essential for the functionality, regulatory compliance and continuous, reliable and safe operation of the equipment.
0.1.13 | Vsa dela morajo biti izvedena kvalitetno in iz materialov z zahtevanimi lastnostmi, izvedena skladno z veljavno zakonodajo in z upoštevanjem navodil za vgradnjo za izbrane materiale in opremo, s predložitvijo predpisanih izjav o lastnostih in/ali certifikatov. Vsi gradbeni proizvodi (GP) morajo biti označeni s CE oznako. | All work shall be of good quality and be executed with materials of the required characteristics, in accordance with the applicable legislation and in compliance with the installation instructions for the materials and equipment selected, and shall be accompanied by the prescribed declarations of performance and/or certificates. All construction products (GP) shall bear the CE marking.
0.1.14 | Za vsako opisano delo v popisu je potrebno upoštevati celotno potrebno delo, ves osnovni in pomožni material, prevoz materiala in orodja na objekt, notranje transporte, delovne in pomožne odre, zaključno čiščenje in odstranitev odpadkov po dovršenem delu. | For each work described in the inventory, the total work required, all basic and ancillary materials, the transport of materials and tools to the site, internal transports, working and ancillary scaffolding, final cleaning and the disposal of waste after the work has been completed must be taken into account.
0.1.15 | Vsa delovna sredstva, organizacija in koordinacija del, pripravljalna, spremljajoča in zaključna dela, potrebni montažni in tesnilni materiali ter podkonstrukcije so sestavni del posameznih postavk. | All labour, organisation and coordination of the works, preparatory, accompanying and finishing works, necessary prefabrication and sealing materials and substructures are part of the individual items.
0.1.16 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - načrt organizacije gradbišča s podrobnim terminskim planom in izvedba vseh pripravljalnih del, postavitev, organizacija, zaščita in prijava gradbišča, gradbiščnih objektov, ureditev začasnih deponij, tekoče vzdrževanje, skupaj s plačilom splošnih stroškov pristojbin in davkov upravnih organov, pridobivanju raznih dovoljenj in soglasij za izvedbo, ograditev gradbišča in postavitev gradbene table in prometne signalizacije, zagotavljanje ustrezne varnosti na gradbišču, tekoče vzdrževanje in končna odstranitev gradbišča; - zagotovitev potrebnih začasnih površin za transportne poti in gradnjo izven območja gradbišča s plačilom stroškov za sanacijo in vzpostavitev okoliških zemljišč in objektov v prvotno stanje (soglasja, odškodnine, itd.); - začasni odvoz, deponiranje in vračanje izkopanega materiala, ki ga ne bo možno deponirati na gradbišču; - odvoz in zagotovitev odstranjevanja odpadnega gradbenega materiala skladno z zakonodajo na področju ravnanja z odpadki (odvoz na urejene deponije s plačilom komunalnih prispevkov in taks itd.); - oteženi izkop v mokrem terenu, izkop v vodi, odvod meteorne vode iz gradbene jame in vode, ki se izceja iz bočnih strani izkopov; - ustrezno varovanje izkopa gradbene jame za objekt in ostalih manjših posameznih izkopov za izvedbo komunalne infrastrukture brez posegov na sosednja zemljišča; - ustrezno varovanje obstoječih objektov, infrastrukture in okolice v času gradnje ter dokumentiranje vseh morebitnih škodnih dogodkov; - pripravljalna, spremljajoča in zaključna dela (zakoličbe, zagotovitev potrebnih komunalnih priključkov za potrebe izvajanja gradnje, izvedba začasnih inštalacij, označevanje podzemnih vodov, postavljanje in vzdrževanje zakoličbenih profilov, izvedba in označevanje novih in starih križanj ter morebitna zaščita križanj komunalnih vodov, geodetski posnetki in izdajanje vmesnih posnetkov izvedene infrastrukture naročniku, izdelava zbirnih kart, itd.), v kolikor ni to drugače določeno; - pridobivanje soglasij in izvedba morebitnih zapor na vseh cestah s plačilom stroškov, nadomestil in pristojbin; - zagotovitev oz. postavitev in končna odstranitev po zaključku gradnje začasnih skladišč in začasnega pisarniškega kontejnerskega objekta vključno z opremo za dve delovni mesti in za skupne operativne sestanke vel. ca. 40 m2 za potrebe naročnika, s tekočim vzdrževanjem in čiščenjem. | The following must also be included or taken into account in the uniform prices for individual items: - a construction site organisation plan with a detailed timetable and the execution of all preparatory works, the setting-up, organisation, protection and registration of the construction site, site facilities, the arrangement of temporary storage facilities, ongoing maintenance, including the payment of general costs of fees and taxes of the administrative authorities, the obtaining of various permits and consents for the execution, the fencing of the site and the erection of construction signs and traffic signals, the provision of adequate security on the site, ongoing maintenance and the final dismantling of the construction site; - provision of the necessary temporary areas for transport routes and off-site construction, with costs for restoration and reinstatement of surrounding land and buildings (consents, compensation, etc.); - temporary removal, storage and return of excavated material that cannot be stored on site; - removing and disposing of waste building materials in accordance with waste management legislation (removal to regulated landfill sites with payment of municipal fees and charges, etc.); - difficult excavation in wet ground, excavation in water, drainage of rainwater from the construction pit and water draining from the sides of excavations; - adequate protection of the excavation of the construction pit for the building and other small individual excavations for the implementation of the utility infrastructure without encroaching on neighbouring land; - adequate protection of existing facilities, infrastructure and the surrounding area during construction, and documentation of any damage incidents; - preparatory, accompanying and finishing works (stake-out, provision of the necessary utility connections for the needs of construction, execution of temporary installations, marking of underground lines, installation and maintenance of stake-out profiles, execution and marking of new and old crossings and possible protection of crossings of utility lines, geodetic surveys and issuing of intermediate images of the completed infrastructure to the client, production of summary maps, etc.), unless otherwise specified; - obtaining consents and implementing any road closures, with costs, compensation and fees; - provision or erection and final removal on completion of construction of temporary storage and temporary office container building including equipment for two workstations and for joint operational meetings of approx. 40 m2 for the needs of the client, with ongoing maintenance and cleaning.
0.1.17 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - izdelava montažne tehnične dokumentacije, detajlov izvedbe in vse druge potrebne delavniške dokumentacije (s področja arhitekture, gradbeništva, elektrotehnike, strojništva in zunanje ter krajinske ureditve) ter pridobitev obvezne potrditve s strani projektanta, nadzornika in investitorja; - odprava vseh vrst inštalacijskih kolizij z izvajanjem potrebnih premikov inštalacij in njihovim usklajevanjem na mestu montaže, vse v obsegu, ki ne vpliva na projektirano rešitev ali tip inštalacij oz. opreme; - zagotavljanje kompletnosti elektro-instalacijskih sistemov s področja avtomatike za doseganje njihove popolne funkcionalnosti delovanja; - stroški za nadzor in koordinacijo izvedbe vseh elektro napeljav, ki so predmet končne instalacije proizvoda (senčila, vrata, okna,…); - izdelava montažnih skic in detajlov za izvedbo v dogovoru z vodjo gradnje in nadzornikom; - izdelava in predstavitev vzorcev v ustrezni velikosti za potrditev projektanta, nadzornika in investitorja; - zagotavljanje varnosti in zdravja pri delu, zlasti izvajanje vseh del, ki izhajajo in ukrepov, ki izhajajo iz določil veljavnih predpisov varstva pri delu in zahtev Varnostnega načrta;- stroški garancij, ki jih mora izvajalec predložiti naročniku. | The following must also be included or taken into account in the uniform prices for individual items: - preparation of prefabricated technical documentation, construction details and all other necessary workshop documentation (architectural, civil, electrical, mechanical, exterior and landscaping) and obtaining the mandatory approval of the designer, the supervisor and the investor; - elimination of all types of installation conflicts by carrying out the necessary relocation of installations and their coordination at the installation site, all to the extent that it does not affect the design solution or the type of installation or equipment; - ensuring the completeness of electrical installation systems in the automation sector to achieve their full operational functionality; - the cost of supervising and coordinating the installation of all the electrical installations that are the subject of the final installation of the product (blinds, doors, windows, etc.); - preparation of erection drawings and details for implementation in agreement with the construction manager and supervisor; - production and presentation of samples in appropriate sizes for the approval of the designer, the supervisor and the investor; - ensuring health and safety at work, in particular the implementation of all the works arising from and the measures resulting from the provisions of the applicable occupational safety regulations and the requirements of the Safety Plan; - the cost of the guarantees to be provided by the contractor to the client.
0.1.18 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - strošek vodje del glavnega izvajalca, ki bo izvajal tudi koordinacijo s podizvajalci in z drugimi izvajalci, ki jih bo izbral naročnik in bo opravljal delo vodje gradbišča; - koordinacija del z ostalimi izvajalci oz. podizvajalci del, projektantom, nadzornikom in investitorjem pri medsebojnem usklajevanju organizacije gradbišča in časovnega načrta del ter pri usklajevanju izdelave plana montaže, potrjenih s strani vseh udeležencev gradnje; - stroški koordinacije, sodelovanja in usklajevanja z dobavitelji tehnološke, laboratorijske, eksperimentalne in vse ostale pohištvene ter multimedijske opreme ter z vsemi ostalimi dobavitelji oz. podizvajalci na objektu; - stroški izdelave situacij; - stroški zavarovanja objekta v času izvedbe del in delavcev ter materiala na gradbišču v času izvajanja del, od začetka del do pridobitve uporabnega dovoljenja za objekt. Zavarovanje mora biti sklenjeno pri ustrezni zavarovalni družbi najmanj v višini pogodbene vrednosti ali v zakonsko predpisani vrednosti (v kolikor zavarovanje v višini pogodbene vrednosti presega zakonsko dovoljeno), za ves čas trajanja izvedbe del do uspešne primopredaje objekta; - preizkušanje kvalitete materiala, ki se vgrajuje in dokazovanje kvalitete s certifikati oz. tehničnimi soglasji; - izvedba vseh zahtevanih testov in preizkusov (npr. tlačni preizkusi, termografski pregledi, meritve elektromagnetnega sevanja, hrupa, itd.), poskusnega obratovanja celotnega objekta s poudarkom na vseh inštalacijah ter izvajanje predpisanega monitoringa v skladu s Poročilom o vplivih na okolje (pred gradnjo, med gradnjo in po končani gradnji); - izdelava izkaza požarne varnosti, vključno s sprotnim spremljanjem gradnje in izvajanjem požarnovarnostnih zahtev ter izdelava Požarnega reda z obveznimi prilogami; - izdelava Izkaza zaščite pred hrupom v stavbah; - izdelava Izkaza energijskih lastnosti stavbe in energetske izkaznice; - sodelovanje z izvajalci gradbenega in projektantskega nadzora in investitorjem za izvedbo tehničnega pregleda in priprava primopredaje, ki mora vsebovati vso zahtevano dokumentacijo, predvsem pa: izjave o skladnosti, požarni izkaz in ostale izkaze ter obvezne tabele, dokazilo o zanesljivosti objekta (DZO), certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo in vzdrževanje ter vse ostale dokumente v skladu s predpisi in pogodbenimi določili. | The following must also be included or taken into account in the uniform prices of the individual items: - the cost of a works manager for the main contractor, who will also coordinate with subcontractors and other contractors selected by the client and act as site manager; - coordination of the works with other contractors or subcontractors, the designer, the supervisor and the investor in coordinating the organisation of the construction site and the timetable for the works, and in coordinating the production of an installation plan approved by all the participants in the construction; - the costs of coordination, cooperation and coordination with suppliers of technological, laboratory, experimental and all other furniture and multimedia equipment, as well as with all other suppliers or subcontractors on the site; - the cost of drawing up situations; - the cost of insuring the building during the execution of the works and the workers and materials on site during the execution of the works, from the start of the works until the building has been licensed for occupation. The insurance must be taken out with a suitable insurance company for at least the contract value or the legal value (if the insurance for the contract value exceeds the legal value), for the entire duration of the works until the successful handover of the building; - testing the quality of the material to be installed and proving it with certificates or technical approvals; - carrying out all required tests and trials (e.g. pressure tests, thermographic inspections, electromagnetic radiation measurements, noise measurements, etc.), trial operation of the entire building, with emphasis on all installations, and carrying out the required monitoring in accordance with the Environmental Impact Assessment Report (before, during and after construction); - preparation of a fire safety statement, including ongoing monitoring of construction and implementation of fire safety requirements, and preparation of a Fire Safety Order with mandatory annexes; - preparation of a Noise Protection Statement for buildings; - preparation of the Building Energy Performance Report and Energy Performance Certificate; - cooperation with the construction and design supervision contractors and the investor to carry out the technical inspection and prepare the handover, which must include all the required documentation, in particular: declarations of conformity, fire and other statements and mandatory tables, proof of reliability of the building (DZO), certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use and maintenance, and all other documents in accordance with the regulations and the contractual provisions.
0.1.19 | V enotnih cenah posameznih postavk, ki se nanašajo na opremo in posamezne sisteme, mora biti zajeto oz. upoštevano tudi naslednje: - dobava oz. transport, - stroški za vse delovne stroje za dvigovanje bremen in delovne košare za dostope do delovišč; - morebitni stroški povzročeni upravljavcem GJI, ki bi nastali v zvezi s predmetno gradnjo; - montaža, vključno s pomožnim montažnim materialom (vezni, tesnilni in pritrdilni material, sidra, nosilni profili, podkonstrukcije in podobno) in navodili proizvajalca, - odprava vseh kolizij sistemov s stenami in med sistemi, - izvedba vseh potrebnih tesnjenj, - priključitev in nastavitve, vključno z morebitnim kalibriranjem, - zagon, testiranje in meritve, vključno s poročili, - šolanje uporabnikov oz. vzdrževalnega osebja za uporabo in vzdrževanje sistemov, - navodila za obratovanje in vzdrževanje, - vsi potrebni certifikati, izjave o skladnosti oz. potrdila ter - vsa druga pomožna dela in material, da se zagotovi funkcionalnost posamezne postavke popisa. | The following must also be included or taken into account in the uniform prices for individual items relating to equipment and individual systems: - delivery/transport, - the cost of all lifting machines and work baskets for access to work sites; - any costs incurred to the operators of utility infrastructure (GJI) in connection with the subject construction; - installation, including ancillary installation materials (bonding, sealing and fixing materials, anchors, support profiles, substructures, etc.) and manufacturer's instructions, - eliminating all system-to-wall and system-to-system collisions, - all necessary sealing work, - connection and set-up, including calibration if necessary, - commissioning, testing and measurements, including reports, - training users or maintenance staff in the use and maintenance of the systems, - operating and maintenance instructions, - any necessary certificates, declarations of conformity or attestations; and - all other ancillary works and materials to ensure the functionality of each inventory item.
0.1.20 | Vsi odri morajo biti upoštevani v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All scaffolding must be included in the uniform prices of the items listed, except where specifically mentioned.
0.1.21 | Vsi delovni in pomožni odri, lestve in ostala potrebna pomožna sredstva, kot tudi čiščenje vseh elementov po končanih delih, mora biti upoštevano v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All working and auxiliary scaffolding, ladders and other necessary ancillaries, as well as the cleaning of all elements after completion of the works, shall be included in the uniform prices of the items listed, except those specifically mentioned.
0.1.22 | Delavniško dokumentacijo za vse nosilne jeklene konstrukcije in podkonstrukcije izdela izvajalec, strošek izdelave delavniške dokumentacije se upošteva v ponujenih cenah in se ne obračuna posebej. | The cost of the shop drawings for all steelwork and substructures shall be included in the prices quoted and shall not be charged separately.
0.1.23 | V enotnih cenah postavk mora biti vključeno tudi vgrajevanje vseh instalacijskih razvodov v opaže armirano betonskih elementov in izdelava prehodov inštalacij ter dodatno izrezovanje utorov in prebojev v kamnite, zidane ali armirano-betonske stene, ponovno demontiranje in montiranje vseh vrst montažnih sten, vsa dodatna dela za zagotavljanje primernih križanj med posameznimi instalacijskimi vodi, izdelava vseh vrst ojačitev konstrukcij in podobna dela, ki zagotavljajo kakovostno vgradnjo vseh vrst instalacijskih vodov in niso posebej navedena v popisu GOI del. V ponudbi morajo biti upoštevana vsa drobna strojna in elektro instalacijska dela in transporti. | The installation of all installation ducts in the formwork of reinforced concrete elements and the construction of installation penetrations, as well as the additional cutting of grooves and penetrations in stone, masonry or reinforced concrete walls, the reassembly and reinstallation of all types of prefabricated walls, all additional work to ensure adequate crossings between individual installation ducts, the construction of all types of structural reinforcement and similar work to ensure the quality installation of all types of installation ducts and not specifically mentioned in the BoQ of the Construction, installation and finishing works (GOI) shall also be included in the uniform prices of the items. The tender shall take into account all minor mechanical and electrical installation work and transport.
0.1.24 | Vsi kovinski elementi in konstrukcije, ki bi lahko bili izpostavljeni atmosferskim in ostalim korozijskim vplivom, morajo biti ustrezno protikorozijsko zaščiteni. | All metallic elements and structures that could be exposed to atmospheric and other corrosive influences must be adequately protected against corrosion.
0.1.25 | Za vse večje jeklene dele se skladno s predpisi, izdelajo ustrezne ozemljitve, nevidno pritrjene in speljane na splošno ozemljitev objekta. | For all major steel parts, appropriate earth connections shall be made in accordance with the regulations, invisibly attached and connected to the general earth of the building.
0.1.26 | Za vse vidne elemente in serijske elemente je obvezna predhodna uskladitev obdelav, barv in materialov s projektantom na podlagi dostavljenih vzorcev v ustrezni velikosti. Obvezna je preveritev dejanskih mer na licu mesta in posledična prilagoditev elementov in njihove montaže. | For all visible elements and serial elements, it is mandatory to coordinate the finishes, colours and materials with the designer beforehand on the basis of the supplied samples in the appropriate size. It is mandatory to check the actual dimensions on site and to adjust the elements and their installation accordingly.
0.1.27 | Dimenzije obrtniških izdelkov in količine je potrebno pred naročanjem preveriti na objektu. Potrebna je uskladitev vseh elementov (kljuke, okovje, detajlne konstrukcije in obdelave, itd.) s projektantom, nadzornikom in investitorjem. Izvajalec je dolžan pred izdelavo predložiti projektantu v potrditev ustrezne delavniške načrte in detajle. | The dimensions of the workmanship and quantities must be checked on site before ordering. All elements (hooks, fittings, detailed construction and finishes, etc.) must be coordinated with the designer, the supervisor and the investor. The contractor is obliged to submit the relevant workshop plans and details to the designer for approval before manufacture.
0.1.28 | V posameznih postavkah popisa so navedeni proizvajalci in/ali tipi posameznih sistemov, materialov ali opreme, s čimer so zgolj natančno opredeljene zahtevane tehnične lastnosti. Izvajalec del lahko ponudi nadomesten sistem, material ali opremo drugega proizvajalca in tipa, pri čemer morajo biti tehnične lastnosti ponujenega sistema, materiala ali opreme enakovredne ali boljše od opredeljenih v popisu, dimenzijsko pa ne smejo presegati projektiranih dimenzij. Vse funkcijske in tehnične karakteristike nadomestnih sistemov, materialov ali opreme mora izvajalec dokazati z ustrezno dokumentacijo. Vse morebitne posledice zaradi spremembe sistemov, materialov ali opreme vključno z morebitnimi spremembami oz. dopolnitvami BIM modelov in projektne dokumentacije, stroškovno in časovno bremenijo izvajalca. | The individual items of the Inventory shall specify the manufacturers and/or types of the individual systems, materials or equipment, thereby merely specifying the required technical characteristics. The Contractor may offer a substitute system, material or equipment of a different manufacturer and type, provided that the technical characteristics of the offered system, material or equipment shall be equivalent to or better than those specified in the BoQ, and shall not exceed the design dimensions. All functional and technical characteristics of the substitute systems, materials or equipment shall be demonstrated by the Contractor with appropriate documentation. Any consequences resulting from changes to systems, materials or equipment, including any changes or additions to the BIM models and project documentation, shall be borne by the Contractor in terms of cost and time.
0.1.29 | Vsako zamenjavo, uporabo in končni izbor nadomestnih sistemov, materialov, proizvodov in opreme morajo obvezno in pravočasno (pred dobavo in vgradnjo) pisno potrditi projektant (vseh sodelujočih strok), nadzornik in investitor. | Any replacement, use and final selection of alternative systems, materials, products and equipment must be approved in writing by the designer (of all disciplines involved), the supervisor and the investor in a timely manner (prior to delivery and installation).
0.1.30 | Izvajalec mora v ponudbeno ceno vključiti tudi: - ves čas gradnje sprotno beleženje sprememb oz. odstopanj od PZI dokumentacije, vključno z izdelavo tekstualnega opisa sprememb, - pripravo podlog na nivoju PZI, ki so potrebne za posodobitev oz. uskladitev BIM modela z izvedenim stanjem (LOD 500) in izdelavo projektne dokumentacije izvedenih del (PID), - mesečno predajanje potrjenih sprememb opreme in materiala, ki vplivajo na BIM model, v formatu IFC, - vzdrževanje in uporabljanje pri izvedbi zadnje veljavne revizije PZI dokumentacije, vključno z dopolnitvami PZI načrtov, ki so nastali zaradi sprememb med gradnjo. | The contractor must also include in the tender price: - keeping a record of changes or deviations from the construction documentation (PZI) throughout construction, including a textual description of the changes, - preparation of the Detailed Design (PZI) level documents required to update or align the BIM model with the as-built condition (LOD 500) and the preparation of the as-built project documentation for the works (PID), - monthly submission of approved equipment and material changes affecting the BIM model in IFC format, - maintenance and use in the execution of the last valid revision of the construction documentation (PZI), including additions to the construction design documentation (PZI) resulting from changes during construction.

## 0.2_Uvod-DGNB
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | KOMUNALNI PRIKLJUČKI OBJEKTA | UTILITY CONNECTIONS
0.2 | SPLOŠNI TEHNIČNI POGOJI ZA PODROČJE DGNB CERTIFICIRANJA | GENERAL TECHNICAL CONDITIONS FOR DGNB CERTIFICATION
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic entity with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
| Splošni pogoji za področje DGNB certificiranja predstavljajo dopolnilo splošnim tehničnim pogojem in ne odpravljajo drugih obveznosti in odgovornosti, ki jih ima izvajalec v skladu s predpisi in pogodbo. | The General Conditions for DGNB Certification are complementary to the General Technical Conditions and do not exclude other obligations and responsibilities that the Contractor has under the Regulations and the Contract.
0.2.1 | Izvajalec mora v svojih ponudbah upoštevati, da se bo objekt certificiral v skladu z zahtevami DGNB sistema certificiranja trajnostne gradnje, ter pravočasno (vsaj 60 dni pred vgradnjo posameznega produkta) dostaviti vso ustrezno dokumentacijo za vse v ponudbi zajete materiale, elemente in opremo. Zahtevana je uporaba materialov, elementov ali opreme, ki so okolju in ljudem prijazni, energetsko učinkoviti in obenem ustrezajo zahtevam DGNB sistema. Zahtevan nivo certifikata je: ZLATI CERTIFIKAT | The Contractor shall take into account in its tenders that the building will be certified in accordance with the requirements of the DGNB Sustainable Building Certification Scheme and shall deliver all relevant documentation for all materials, elements and equipment included in the tender in a timely manner (at least 60 days before the installation of each product). The use of materials, elements or equipment that are environmentally and human friendly, energy efficient and at the same time meet the requirements of the DGNB system is required. The required level of certification is: GOLD CERTIFICATE
0.2.2 | Podrobnejši opis DGNB sistema in navodila za posamezne kriterije so dostopna v dokumentu"DGNB Criteria Set New Construction Buildings, Version 2020 International", ki je na voljo na DGNB spletni strani https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria | A more detailed description of the DGNB system and guidance on the individual criteria is available in the document "DGNB Criteria Set New Construction Buildings, Version 2020 International", available on the DGNB website https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria
0.2.3 | Izvajalec mora v svojih ponudbah upoštevati, da je potrebno skladno z določili DGNB certifikacijskega sistema, pravočasno (pred pričetkom gradnje) dostaviti vso ustrezno dokumentacijo, za vse v ponudbi zajete materiale, elemente in opremo (tehnični list, varnostni list, izjava o lastnostih, tehnična navodila za ravnanje, servisiranje, vzdrževanje,...) v slovenskem jeziku. Vgradnja kakršnihkoli materialov, elementov ali opreme, se izvede zgolj na podlagi predhodne preveritve posredovane dokumentacije in obenem potrditve s strani nadzornika. | The Contractor must take into account in its tenders that, in accordance with the provisions of the DGNB certification system, all relevant documentation for all materials, elements and equipment included in the tender (technical data sheet, safety data sheet, declaration of properties, technical instructions for handling, servicing, maintenance,...) must be delivered on time (prior to the start of construction) in the Slovene language (in accordance with the provisions of the DGNB certification system). The installation of any materials, elements or equipment shall be subject to prior checking of the submitted documentation and, at the same time, to the approval of the Supervisor.
0.2.4 | Izbrani materiali, elementi, naprave, sistemi in oprema morajo prispevati k večji trajnosti stavbe v smeri zagotavljanja energetske učinkovitosti, ekonomičnega in enostavnega vzdrževanja ter čiščenja, dolge življenjske dobe, uporabe okolju prijaznih materialov ipd. | The materials, elements, appliances, systems and equipment chosen must contribute to the sustainability of the building in terms of energy efficiency, economic and easy maintenance and cleaning, long lifetime, use of environmentally friendly materials, etc.
0.2.5 | Predloženi dokumenti za vse uporabljene materiale, elemente in opremo morajo izpolnjevati zahteve najmanj kakovostne stopnje QS3 (zaželeno QS4), iz dokumenta: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001) | The documents submitted for all materials, components and equipment used shall meet the requirements of at least quality level QS3 (preferably QS4) of the document DGNB Quality Grades for Materials, Components and Equipment (JULFS--7X9001)
0.2.6 | V kolikor izbrani materiali oz. elementi, navedeni v posameznih postavkah, ne ustrezajo vsaj kakovostni stopnji QS3 iz seznama: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), je izvajalec dolžan na to opozoriti projektanta, nadzor in investitorja ter podati predlog ustreznega materiala oz. elementa. | If the selected materials or elements listed in the individual items do not meet at least quality level QS3 of the list of DGNB quality classes for materials, elements and equipment (JULFS--7X9001), the Contractor shall draw this to the attention of the Designer, the Supervisor and the Investor, and shall make a proposal for a suitable material or element.
0.2.7 | Izvajalec lahko v svoji ponudbi predlaga alternativne produkte in rešitve glede na predvidene s projektom, pod pogojem, da le-te prav tako izpolnjujejo vse navedene zahteve. Pri morebitnih predlaganih alternativnih produktih oz. rešitvah je potrebno upoštevati najmanj enake ali boljše lastnosti v smislu življenjske dobe, obstojnosti, ter enostavnosti in stroška čiščenja ter vzdrževanja v primerjavi s projektom predpisanimi rešitvami. Za alternativne rešitve izvajalec pridobi soglasje projektanta, nadzornika in investitorja pred pričetkom gradnje. | The Contractor may propose alternative products and solutions to those envisaged by the project in its tender, provided that they also meet all the requirements set out above. Any alternative products or solutions proposed shall have at least the same or better characteristics in terms of service life, durability, and ease and cost of cleaning and maintenance compared to the solutions envisaged by the project. For alternative solutions, the contractor shall obtain the agreement of the designer, the supervisor and the investor before starting construction.
0.2.8 | Izvajalec med gradnjo dnevno beleži vsa eventualna odstopanja od PZI projektne dokumentacije ter podatke pravočasno posreduje naročniku, nadzoru in projektantu. Potrjene spremembe vnese v podlage za izdelavo PID in posodobitev BIM modelov. | During construction, the Contractor shall record on a daily basis any deviations from the Detailed Design documentation (PZI) and shall provide the information to the Client, Supervision and the Designer in a timely manner. Confirmed changes shall be entered into the basis for the As-built documentation (PID) and BIM model updates.
0.2.9 | Izvajalec med gradnjo sproti izpolnjuje Seznam vseh konstrukcijskih sestav s pripadajočimi vgrajenimi gradbenimi materiali in dokumentira naslednje podatke o vgrajenih materialih (v slovenskem jeziku): - Varnostni list - Tehnični list - Izjavo o lastnostih (če je relevantno) - Izkazovanje morebiti obstoječega okoljskega certifikata (Tip I - okoljski znak ali Tip III - okoljska produktna deklaracija /EPD) - Izjavo proizvajalca ali dobavitelja, da produkt ustreza zahtevam ENV1.2 - Tehnična navodila za ravnanje, servisiranje, vzdrževanje oziroma ostale, z zakonom predpisane dokumente in dokumentacijo. | During construction, the Contractor shall keep a List of all structural assemblies with their associated construction materials and document the following information on the materials installed (in Slovene language): - Safety Data Sheet - Technical Data Sheet - Declaration of performance (if applicable) - Demonstration of any existing environmental certification (Type I - Ecolabel or Type III - Environmental Product Declaration /EPD) - A declaration by the manufacturer or supplier that the product complies with the requirements of ENV1.2 - Technical instructions for handling, servicing, maintenance or other documents and documentation required by law.
0.2.10 | Za vse vgrajene bistvene tehnične sisteme mora izvajalec zagotoviti obstoj pooblaščenega servisa, ki deluje na območju Republike Slovenije, da ima investitor možnost skleniti ustrezno pogodbo o vzdrževanju. Med bistvene tehnične sisteme sodijo npr.: sistemi ogrevanja in hlajenja, priprava tehnoloških medijev, prezračevanje in klimatizacija, sistemi detekcije in gašenja požara, sistemi tehničnega varovanja, BMS in CNS sistemi upravljanja stavbe, razsvetljava, komunikacijski in WI-FI sistemi,... | For all installed essential technical systems, the contractor must ensure the existence of an authorised service centre operating in the territory of the Republic of Slovenia, so that the investor has the possibility of concluding an appropriate maintenance contract. The essential technical systems include, for example: heating and cooling systems, technological media preparation, ventilation and air conditioning, fire detection and extinguishing systems, technical security systems, BMS and CNS building management systems, lighting, communication and WI-FI systems,...
0.2.11 | Zaželeno je, da imajo uporabljeni elementi in materiali okoljsko oznako Tip I. (kot npr. ENCODE, BLUE ANGEL, ipd...). | It is preferable that the elements and materials used have a Type I environmental label (such as ENCODE, BLUE ANGEL, etc...).
0.2.12 | Izvajalec bo za elemente iz lesa moral dokazovati izvor z navedbo izvorne države in tipa lesa, FSC / PEFC certifikat z dodatnim pripadajočim potrdilom Chain of custody-trgovski certifikat dobavitelja - ta se dokazuje z dobavnicami, računi ali enakovredno. Za izdelke iz naravnega kamna iz EU držav je potrebna deklaracija, da je izvor in procesiranje teh izdelkov v celoti v EU državah. Za izdelke iz naravnega kamna, ki prihajajo iz držav izven EU, je potrebno predložiti dokazilo o izpolnjevanju ILO konvencije 182, ki vključuje neodvisna inšpekcijska poročila. | For wood elements, the contractor will be required to provide proof of origin, indicating the country of origin and the type of wood, FSC/PEFC certification with an additional Chain of Custody certificate - the supplier's trade certificate - this shall be evidenced by delivery notes, invoices or equivalent. For natural stone products from EU countries, a declaration that the sourcing and processing of these products is entirely in EU countries is required. For natural stone products from non-EU countries, proof of compliance with ILO Convention 182, including independent inspection reports, is required.
0.2.13 | Izobraževanje udeležencev pri gradnji Izvajalec je dolžan vse udeležence pri gradnji podrobneje seznaniti tudi z relevantnimi koncepti, študijami, elaborati, ki opredelujejo trajnostni način gradnje za naslednja področja: - zaščita pred hrupom (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)) - zaščita pred prašenjem - zaščita tal in podzemne vode (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)), Analiza tveganja za onesnaženje vodnega telesa podzemne vode št. 0346-023/2023, maj 2023 (Geološko projektiranje d.o.o.)) - ravnanje z gradbenimi odpadki (Načrt gospodarjenja z gradbenimi odpadki) Izobraževanja se izvajajo skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.1 1.2, 2.2, 3.2 in 4.2 Training for the parties implementing the construction work | Training of construction participants The contractor is also obliged to inform all construction participants in detail about relevant concepts, studies, elaborations defining sustainable construction methods for the following areas: - noise protection (Environmental Impact Assessment Report No 100123-11523, dated 11.5.2023, supplemented on 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.)) - dust protection - protection of soil and groundwater (Environmental Impact Assessment Report No. 100123-11523, dated 11.5.2023, supplemented 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.), Risk analysis for contamination of the groundwater No. 0346-023/2023, May 2023 (Geološko projektiranje d.o.o.)) - construction waste management (Construction Waste Management Plan) The training shall be carried out in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.1 1.2, 2.2, 3.2 and 4.2 Training for the parties implementing the construction work
0.2.14 | Navodila za obratovanje in vzdrževanje objekta Izvajalec pripravi Navodila za obratovanje in vzdrževanje objekta skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilih: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual | Instructions for the operation and maintenance of the facility The Contractor shall prepare the Operation and Maintenance Instructions for the Facility in accordance with the applicable Slovenian legislation and the DGNB System Instructions specified in the Criteria: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual
0.2.15 | Meritve kontrole kakovosti gradnje Izvajalec mora upoštevati, da se bodo po koncu gradnje izvedle naslednje meritve: - meritve zrakotesnosti - meritve s termokamero (termografija) - meritve akustike - meritve zvočne zaščite ovoja stavbe - meritve zvočne zaščite ločilnih elementov med posameznimi prostori različnih namembnosti - meritve udarnega zvoka - meritve vlažnosti vgrajenih elementov, pred vgradnjo finalnih tlakov - test odvoda dima in toplote Meritve morajo opraviti ustrezno usposobljeni preskusni organi ali strokovnjaki ter rezultate oceniti in primerjati z zahtevami. Obseg opravljenih meritev mora biti sorazmeren z velikostjo zgradbe in mora ustrezno odražati cilj preverjanja kakovosti zgradbe. Smiselno je, da izvajalec del tekom gradnje za sprotno kontrolo kakovosti vgrajenih materialov, elementov in opreme, sam izvaja meritve. Končne meritve (ob primopredaji) izvede tretja oseba kot neodvisna potrditev doseganja zahtev. Meritve se izvajajo skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 2. Quality control measurements | Construction quality control measurements The contractor must take into account that the following measurements will be carried out after completion of the construction: - airtightness measurements - thermal camera measurements (thermography) - acoustics measurements - measurements of the sound insulation of the building envelope - measurements of the sound insulation of the separating elements between different rooms of different uses - impact sound measurements - moisture measurements of the installed elements, prior to the installation of the final flooring - smoke and heat extraction test The measurements shall be carried out by suitably qualified test bodies or experts and the results evaluated and compared with the requirements. The extent of the measurements carried out shall be proportionate to the size of the building and shall adequately reflect the objective of the building quality verification. It is reasonable for the contractor to carry out his own measurements during construction to check the quality of the materials, elements and equipment installed. Final measurements (at handover) are carried out by a third party as an independent confirmation of compliance with the requirements. The measurements shall be carried out in accordance with the applicable Slovenian legislation and the DGNB system instructions specified in the benchmark: PRO 2.2 2. Quality control measurements
0.2.16 | Zagotavljanje kakovosti za uporabljene gradbene proizvode Izvajalec mora zagotavljati izvajanje primerjav med definiranim in dejansko uporabljenim materialom, elementom ali opremo skladno seznamom: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), vključno z dokazno dokumentacijo ugotovitev primerjav ter skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 3.1 Quality assurance for the used construction products | Quality assurance for the construction products used The Contractor shall ensure that comparisons are made between the defined and the actual material, element or equipment used in accordance with the list: DGNB Quality Grades of Installed Materials, Elements and Equipment (JULFS--7X9001), including supporting documentation of the findings of the comparisons, and in accordance with the DGNB system instructions defined in the Criterion: PRO 2.2 3.1 Quality assurance for the used construction products
0.2.17 | Zaščita pred vlago Izvajalec predloži dokumentacijo, ki dokazuje, da je bil izveden program prezračevanja, prilagojen stavbi, s čimer se zagotovi pogoje, da so vgrajeni gradbeni elementi ustrezno suhi, skladno z navodili DGNB opredeljenimi v merilu: PRO 2.2 4.1 Mould prevention | Protection against moisture The Contractor shall provide documentation demonstrating that a building-specific ventilation programme has been implemented to ensure that the building elements installed are adequately dry, in accordance with the DGNB guidelines specified in the criteria: PRO 2.2 4.1 Mould prevention
0.2.18 | Preizkusi delovanja sistemov Izvajalec sodeluje pri izvedbi predhodnega in končnega preizkusa delovanja vseh bistvenih tehničnih komponent stavbe in pripravi ustrezne dokazne dokumentacije ter pri usposabljanju vzdrževalcev/upravljalcev stavbe, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators | System performance tests The Contractor shall be involved in the performance of the preliminary and final performance tests of all essential technical components of the building and the preparation of the relevant supporting documentation, as well as in the training of the maintenance/management staff of the building, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators
0.2.19 | Poročilo o zagonu objekta Izvajalec sodeluje pri pripravi končnega poročila o zagonu objekta, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 5.1 Creation of a detailed final report | Commissioning report The Contractor shall be involved in the preparation of the final commissioning report, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 5.1 Creation of a detailed final report
0.2.20 | Koncept celovitega delovanja sistemov v stavbi Izvajalec sodeluje pri procesu implementiranja stalnega nadzora in nastavitev delovanja stavbe ter usposabljanju vzdrževalcev/upravljalcev stavbe. Navedeno se izvede v skladu z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 6.1 Creation and handover of an integral operating concept | The concept of integrated building systems The contractor is involved in the process of implementing the building's continuous monitoring and settings and training the building's maintenance/management staff. This shall be done in accordance with the DGNB system instructions defined in the benchmark: PRO 2.3 6.1 Creation and handover of an integral operating concept
0.2.21 | Prilagoditev nastavitev sistemov po začetni fazi uporabe objekta Izvajalec sodeluje pri ponovnem pregledu delovanja vseh bistvenih tehničnih sistemov ter eventualni ponovni prilagoditvi teh sistemov s strani strokovnjaka oz. (neodvisne) tretje osebe. Postopek se izvede po približno 10–14 mesecih po zaključku gradnje, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 7.1 Readjustment of the system following initial operating phase | Adjusting system settings after the initial phase of use of the building The Contractor shall be involved in the re-examination of the functioning of all essential technical systems and the possible re-adjustment of these systems by an expert or (independent) third party. The procedure shall be carried out approximately 10-14 months after completion of construction, in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.3 7.1 Readjustment of the system following initial operating phase

## 2.6.2.0_Rekapitulacija_G_del
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | KOMUNALNI PRIKLJUČKI OBJEKTA | UTILITY CONNECTIONS
| REKAPITULACIJA STROŠKOV GRADBENIH DEL | COST SUMMARY OF CONSTRUCTION WORKS
| 2 NAČRT S PODROČJA GRADBENIŠTVA | 2 DOCUMENTATION IN THE FIELD OF CIVIL ENGEENIRING
| 2/6 Zunanja ureditev in komunalni priključki objekta | 2/6 Grading, Paving and Utility Connections
2.6.2 | GRADBENA DELA | CONSTRUCTION WORKS
2.6.2.1 | FEKALNA KANALIZACIJA | FAECAL SEWERAGE | 0
2.6.2.2 | METEORNA KANALIZACIJA | METEORIC SEWERAGE | 0
2.6.2.3 | VODOVODNI PRIKLJUČEK | WATER CONNECTION | 0
2.6.2.4 | PLINSKI PRIKLJUČEK | GAS CONNECTION | 0
2.6.2.5 | KABELSKA KANALIZACIJA - SN | CABLE DUCT - SN | 0
2.6.2.6 | KABELSKA KANALIZACIJA - NN, TK IN RAZSVETLJAVA | CABLE DUCTING - LV, HV, HV AND LIGHTING | 0
0
0 | NEPREDVIDENA DELA | UNFORSEEN WORKS | 0
| SKUPAJ GRADBENA DELA | TOTAL CONSTRUCTION WORKS | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT

## 2.6.2.1_Fekalna_kanalizacija
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | KOMUNALNI PRIKLJUČKI OBJEKTA | UTILITY CONNECTIONS
2.6.2 | GRADBENA DELA | CONSTRUCTION WORKS
2.6.2.1 | FEKALNA KANALIZACIJA | FAECAL SEWERAGE |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
1 | FEKALNA KANALIZACIJA | FAECAL SEWERAGE
| OPOMBE: Pri izdelavi ponudbe upoštevati pripombe, iz poglavja 0.1 UVOD-STP Pri izdelavi ponudbe upoštevati pripombe, iz poglavja 0.2 UVOD - DGNB in dokument: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme. | NOTES: Take into account the comments made in section 0.1 INTRODUCTION-STP in the preparation of the offer When preparing the tender, take into account the comments made in Section 0.2 INTRODUCTION - DGNB and the document DGNB Quality Grades for Materials, Elements and Equipment.
| Pred pričetkom del je potrebno: ~ na licu mesta preveriti vse dimenzije navedene v načrtu in morebitna odstopanja prilagoditi dejanskemu stanju na terenu ~ vsa neskladja pravočasno / pred izvedbo uskladiti z vodjo projektiranja in ostalimi projektanti ~ vse izvedbe, materiale, obdelave in barve uskladiti s projektanti ~ pri vseh vidnih izvedbah je pred izvedbo potrebno delavniško uskladiti detajle ter jih predložiti projektantu v potrditev | Before starting work, it is necessary to: ~ on-site verification of all dimensions indicated in the plan and adjustment of any deviations to the actual situation on the ground ~ reconcile any discrepancies with the design manager and other designers in a timely manner / prior to implementation ~ all designs, materials, finishes and colours to be coordinated with the designers ~ all visible works shall be subject to workshop coordination of details and submitted to the designer for approval prior to implementation
| Osnova za izvedbo popisa za zemeljska dela je geodetski posnetek obstoječega stanja, načrti objektov, zunanje ureditve in načrti komunalne infra strukture, tehnično poročilo ter navodila in zahteve dobaviteljev za izvedbo in vgradnjo posameznih delov opreme. | The basis for the inventory for the earthworks is the existing geodetic survey, the building plans, the external layout plans and the utility infrastructure plans, the technical report and the suppliers' instructions and requirements for the design and installation of the individual pieces of equipment.
| Pri izvedbi vseh zemeljskih del mora biti prisoten geomehanski nadzor, ki preveri ustreznost predvidenih ukrepov, ustreznost homogenih tal, skladnost privzetih parametrov v PZI z dejanskim stanjem na terenu in geološko-geomehanskih raziskav iz Geološko-geotehničnega poročila (IRGO Consulting d.o.o., poročilo št. 3009776, januar 2021). | During the execution of all earthworks, geomechanical supervision must be present to verify the adequacy of the planned measures, the adequacy of the homogeneous soils, the compliance of the default parameters in the PIP with the actual situation on the ground and the geological-geomechanical investigations from the Geological-Geotechnical Report (IRGO Consulting d.o.o., Report No. 3009776, January 2021).
| V kolikor bi se v času izvajanja zemeljskih del izkazalo, da je dejansko stanje drugačno od predvidenega, geomehanik takoj obvesti projektanta in se pristopu k iskanju projektnih rešitev, ki ustrezajo dejanskemu stanju. Vsa odstopanja od PZI morata pred izvedbo pisno potrditi geomehanik in projektant. | Should the actual situation prove to be different from the intended situation during the execution of the earthworks, the geomechanic shall immediately inform the designer and the designer shall be approached to find design solutions that correspond to the actual situation. Any deviations from the PIP shall be confirmed in writing by the geomechanic and the designer prior to execution.
| Primernost izkopanega materiala za zasip ugotovi geomehanik na licu mesta. | The suitability of the excavated material for backfill shall be determined by the on-site geomechanist.
| Morebitne začasne deponije zemeljskega materiala in potrebne transporte v zvezi s tem je potrebno upoštevati v enotnih cenah. | Any temporary deposits of earth material and the necessary transport in this respect must be taken into account in the uniform prices.
| Izbrana mehanizacija mora omogočati upoštevanje varnostnih ukrepov. | The machinery chosen must be able to comply with safety precautions.
| Vsa izkopna dela in transporti izkopnih materialov se obračunajo po prostornini zemljine v raščenem stanju. Vsa nasipna dela se obračunajo po prostornini zemljine v vgrajenem stanju. Obračun količin se izvede po posnetih profilih pred in po nasipavanju. | All excavation work and transport of excavation materials shall be accounted for by the volume of soil in the loosened state. All embankment work shall be accounted for by the volume of soil in the as-built state. Quantities shall be accounted for on the basis of the recorded profiles before and after embankment.
| Utrjevanje z nabijanjem do predpisane zbitosti po projektu statike. | Curing by ramming to the specified compaction according to the structural design.
| Splošne opombe za betonske konstrukcije; ~ vsi vgrajeni betoni morajo izpolnjevati zahteve SIST EN 206-1, SIST EN 1026 in SIST EN 1992-1-1 ter NAC dodatki; ~ za vse betonske konstrukcije velja zahteva za 2. izvedbeni razred in 1. tolerančni razred po SIST EN 13670 in nacionalnem dodatku, kar je potrebno upoštevati pri pripravi in izvajanju programa kontrole kakovosti in projekta betona; ~ pred nadaljevanjem del morajo biti stiki očiščeni, navlaženi in premazani s sredstvom za povečanje sprijemnosti ~ debelino krovnega sloja je potrebno kontrolirati z merjenjem ~ na proste robove vidnih površin se v opaž vgradi trikotne letve; | General notes for concrete structures; ~ All concrete installed shall comply with the requirements of SIST EN 206-1, SIST EN 1026 and SIST EN 1992-1-1 and NAC Appendices; ~ all concrete structures are subject to the requirement for Performance Class 2 and Tolerance Class 1 in accordance with SIST EN 13670 and the National Supplement, which must be taken into account in the preparation and implementation of the quality control programme and the concrete design; ~ joints must be cleaned, moistened and coated with an adhesion promoter before work proceeds ~ the thickness of the deck layer must be controlled by measuring ~ triangular battens shall be installed in the formwork at the free edges of the visible surfaces;
| Splošne opombe za betonske konstrukcije; ~ za vse vidne površine brez posebnih arhitekturnih oz. drugih zahtev in za nevidne površine veljajo zahteve za obdelavo površin po SIST EN 13670 in nacionalnem dodatku, kar je potrebno upoštevati pri izbiri opažev: - vidne površine: • opažene vidne površine: enostavno – VB2, • neopažene vidne površine (tabela F4 v SIST EN 13670 in tabela N5 v nac, dodatku): enostavna - nevidne površine: • opažene nevidne površine: osnovna – VB0, • neopažene nevidne površine (tabela F4 v SIST EN 13670 in tabela N5 v nac. dodatku): osnovna ~ za izvedbo zaščitnih slojev glej armaturni načrt; | General notes for concrete structures; ~ all visible surfaces without special architectural or other requirements and invisible surfaces are subject to the surface treatment requirements of SIST EN 13670 and the National Supplement, which must be taken into account when selecting the formwork: - visible surfaces: - Visible surfaces observed: easy - VB2, - Unnoticed visible surfaces (Table F4 in SIST EN 13670 and Table N5 in the Appendix): simple - invisible surfaces: - observed invisible surfaces: basic - VB0, - Unnoticed invisible surfaces (Table F4 in SIST EN 13670 and Table N5 in the National Appendix): basic ~ see reinforcement plan for the design of the protective layers;
| Za ravnost in obdelavo površin poleg zahtev v projektni dokumentaciji upoštevati tudi zahteve izbranega dobavitelja zaščitnih premazov. | For the flatness and surface treatment, in addition to the requirements in the project documentation, the requirements of the chosen supplier of protective coatings shall also be observed.
| Izvajalec je dolžan na svoje stroške izdelati projekt izvajanja betonskih konstrukcij. | The Contractor shall be obliged to draw up, at his own expense, a project for the execution of the concrete structures.
| Pri izvedbi je potrebno upoštevati načrte, kjer so prikazane trase inštalacijskih vodov ter pred vgradnjo upoštevati vse elemente, ki so zajeti v elektro in strojnem načrtu. | The plans showing the routes of the installation lines must be followed and all the elements included in the electrical and mechanical plans must be taken into account before installation.
| Na armaturo je potrebno skladno z detajlom izbranega dobavitelja priključiti sistemske elemente za priključitev na ozemljitev - priključitev izvede izvajalec elektro del, pred betoniranjem. | System elements for connection to earth must be connected to the reinforcement in accordance with the details of the selected supplier - connection to be carried out by the electrical contractor prior to concreting.
| Vsi delovni stiki morajo biti premazani z osnovnim premazom/emulzijo za boljšo vezavo starih in novih konstrukcij/elementov. V ceni se upošteva izvedbo vseh delovnih stikov po navodilih proizvajalca. | All working joints shall be coated with a primer/emulsion for better bonding of old and new structures/elements. The price shall take into account the execution of all working joints according to the manufacturer's instructions.
| V primeru nejasnosti, spremenjenih pogojev ali odstopanja od projekta se je potrebno posvetovati s projektantom. | In case of any ambiguity, changed conditions or deviation from the design, the designer should be consulted.
| Med izvedbo gradbenih posegov mora biti zagotovljen strokovni nadzor, ki bo zagotavljal skladnost gradnje s pogoji iz gradbenega dovoljenja ter kvaliteto izvedenih del v skladu z gradbenimi predpisi. | During the construction works, professional supervision must be provided to ensure that the construction complies with the conditions of the building permit and that the quality of the works is in accordance with the building regulations.
| Upoštevati vse vertikalne in horizontalne transporte. | All vertical and horizontal transports must be taken into account.
| Potrebno je izvajati sprotno čiščenje. | Ongoing cleaning is necessary.
1.1 | Izkop jarka v zemljišču III.ktg. za komunalno infrastrukturo, z nakladanjem na kamion in odvozom na začasno deponijo, do ponovne vgradnje po izvedbi novih del. | Excavation of a trench in land III.ktg. for utility infrastructure, with loading onto a lorry and removal to a temporary landfill site, until re-installation after the new works have been carried out.
a. | ~strojni izkop (90%) | ~machine excavation (90%) | m3 | 865 |  | 0
b. | ~ročni izkop (10%) | ~hand excavation (10%) | m3 | 96 |  | 0
1.2 | Kompletna izvedba dvostranskega razpiranja jarka, globine od cca 2,50 do 3,50 m, kot npr. SISTEM SBH ali enakovredno, skupaj z vsemi potrebnimi deli in materialom. | Complete execution of a double-sided trench opening, approx. 2.50 to 3.50 m deep, as e.g. SBH SYSTEM or equivalent, including all necessary works and materials. | m2 | 63 |  | 0
1.3 | Planiranje in utrjevanje dna izkopa jarkov pred izvedbo komunalne infrastrukture, v predpisanem naklonu in do predpisane utrditve po projektu. | Plan and consolidate the bottom of the trench excavation prior to the implementation of the utility infrastructure, at the prescribed gradient and to the prescribed consolidation as per the design. | m2 | 126 |  | 0
1.4 | Zasip za komunalno infrastrukturo z izkopanim materialom deponiranim na začasni deponiji, komplet z nakladanjem in dovozom, raztiranjem in planiranjem ter utrjevanjem po plasteh od 20 do 30 cm s sprotnim komprimiranjem do predpisane utrditve po projektu. | Backfilling for utility infrastructure with excavated material deposited in a temporary landfill, complete with loading and access, grading and grading, and consolidation in layers of 20 to 30 cm with continuous compaction to the required consolidation as per design. | m3 | 848 |  | 0
1.5 | Odvoz izkopanega materiala na stalno deponijo, ki si jo priskrbi izvajalec, katero si izvajalec zagotovi sam ter plačilom taks na deponiji. | Removal of excavated material to a permanent landfill to be provided by the Contractor, which shall be provided by the Contractor, and payment of landfill charges. | m3 | 113 |  | 0
1.6 | Dobava in vgradnja PVC opozorilnega traku, položenega v zasip nad cevmi. | Supply and installation of PVC warning tape laid in the backfill above the pipes. | m | 131 |  | 0
1.7 | Kompletna izvedba križanj nove komunalne infrastrukture z obstoječimi komunalnimi vodi, skupaj z vsemi potrebnimi deli in materialom, skladno z upoštevanjem načina izvedbe in vseh pogojev po navodilih upravljalca komunalnega voda. | Complete execution of the crossings of the new utility infrastructure with the existing utility lines, including all necessary works and materials, in accordance with the method of execution and all conditions as specified by the utility line manager. | kpl | 3 |  | 0
1.8 | Dobava in polaganje polne PEHD cevi DN 125 za kanalizacijo, kompletno s fazonskimi kosi, spojnim in tesnilnim materialom, skupaj z izdelavo betonske podlage deb. 10 cm in polnim obbetoniranjem 20 cm nad temenom ter izvedbo preizkusa vodotesnosti po SIST EN 1610. ~ cevi po standardih skupine SIST EN 13476 ~ beton C16/20 X0 | Supply and installation of a DN 125 solid PEHD pipe for sewerage, complete with phase pieces, jointing and sealing material, including the construction of a 10 cm thick concrete base and full concreting 20 cm above the top and watertightness test according to SIST EN 1610. ~ pipes according to SIST EN 13476 group standards ~ concrete C16/20 X0 | m | 4 |  | 0
1.9 | Dobava in polaganje polne PEHD cevi DN 160 za kanalizacijo, kompletno s fazonskimi kosi, spojnim in tesnilnim materialom, skupaj z izdelavo betonske podlage deb. 10 cm in polnim obbetoniranjem 20 cm nad temenom ter izvedbo preizkusa vodotesnosti po SIST EN 1610. ~ cevi po standardih skupine SIST EN 13476 ~ beton C16/20 X0 | Supply and installation of full PEHD pipe DN 160 for sewerage, complete with bevel pieces, jointing and sealing material, including the construction of a concrete base 10 cm thick and full concreting 20 cm above the top, and watertightness test in accordance with SIST EN 1610. ~ pipes according to SIST EN 13476 group standards ~ concrete C16/20 X0 | m | 10 |  | 0
1.10 | Dobava in polaganje polne PEHD cevi DN 200 za kanalizacijo, kompletno s fazonskimi kosi, spojnim in tesnilnim materialom, skupaj z izdelavo betonske podlage deb. 10 cm in polnim obbetoniranjem 20 cm nad temenom ter izvedbo preizkusa vodotesnosti po SIST EN 1610. ~ cevi po standardih skupine SIST EN 13476 ~ beton C16/20 X0 | Supply and installation of full PEHD pipe DN 200 for sewerage, complete with bevel pieces, jointing and sealing material, together with the construction of a concrete base 10 cm thick and full concreting 20 cm above the top, and watertightness test in accordance with SIST EN 1610. ~ pipes according to SIST EN 13476 group standards ~ concrete C16/20 X0 | m | 9 |  | 0
1.11 | Dobava in polaganje polne PEHD cevi DN 250 za kanalizacijo, kompletno s fazonskimi kosi, spojnim in tesnilnim materialom, skupaj z izdelavo betonske podlage deb. 10 cm in polnim obbetoniranjem 20 cm nad temenom ter izvedbo preizkusa vodotesnosti po SIST EN 1610. ~ cevi po standardih skupine SIST EN 13476 ~ beton C16/20 X0 | Supply and installation of a DN 250 solid PEHD pipe for sewerage, complete with phase pieces, jointing and sealing material, including the construction of a 10 cm thick concrete base and full concreting 20 cm above the top and watertightness test according to SIST EN 1610. ~ pipes according to SIST EN 13476 group standards ~ concrete C16/20 X0 | m | 78 |  | 0
1.12 | Dobava in polaganje polne PEHD cevi DN 315 za kanalizacijo, kompletno s fazonskimi kosi, spojnim in tesnilnim materialom, skupaj z izdelavo betonske podlage deb. 10 cm in polnim obbetoniranjem 20 cm nad temenom ter izvedbo preizkusa vodotesnosti po SIST EN 1610. ~ cevi po standardih skupine SIST EN 13476 ~ beton C16/20 X0 | Supply and installation of full PEHD pipe DN 315 for sewerage, complete with bevel pieces, jointing and sealing material, together with the construction of a concrete base 10 cm thick and full concreting 20 cm above the top, and watertightness test in accordance with SIST EN 1610. ~ pipes according to SIST EN 13476 group standards ~ concrete C16/20 X0 | m | 30 |  | 0
1.13 | Kompletna izdelava revizijskih protivzgonskih jaškov z dvojnim dnom iz PE rebraste cevi, premera fi 1000 mm, globine od 2,00 do 3,00 m, z izdelavo dna, priključkov, armiranobetonskega razbremenilnega obroča in venca kot ležišče za LTŽ pokrov ter LTŽ pokrov fi 600 mm, nosilnosti B 125, kot npr. LIVAR art. 600, po SIST EN 124-2. Dobava in vgradnja razbremenilnega obroča in venca mora biti upoštevana v enotni ceni dobave in vgradnje LTŽ pokrova. Opomba: Betonski razbremenilni obroč in venec s pokrovom ne smejo biti temeljeni direktno na telo jaška, temveč na utrjeni zasip okrog jaška. Dilatacije med AB ploščo, vencem in PE jaškom morajo ustrezati zahtevam izbranega proizvajalca jaškov. | Complete construction of double-bottomed inspection shafts made of PE finned pipe, diameter fi 1000 mm, depth from 2.00 to 3.00 m, with construction of the bottom, connections, reinforced concrete relief ring and wreath as a bed for the LTŽ cover and the LTŽ cover fi 600 mm, load capacity B 125, such as LIVAR art. 600, according to SIST EN 124-2. The supply and installation of the relief ring and wreath must be included in the single price for the supply and installation of the LTŽ cover. Note: The concrete relief ring and the capped wreath shall not be founded directly on the manhole body, but on the hardened backfill around the manhole. The expansion between the AB slab, the wreath and the PE manhole shall comply with the requirements of the selected manhole manufacturer. | kos | 9 |  | 0
1.14 | Kompletna izvedba za cel kanalizacijski sistem: ~ geodetski posnetek osi, premera in višine temena cevi pred zasutjem, ~ geodetski posnetek pozicij in višin pokrovov, dna, vtokov ter iztokov na revizijskih jaških in ostalih elementih sistema pred zasutjem, ~ vnos tras v zbirno karto komunalnih vodov in v vzdolžni profil, ~ predaja naročniku v grafični in digitalni obliki kot podloga za izdelavo projekta izvedenih del (PID). | Complete implementation for the entire sewerage system: ~ a geodetic survey of the axis, diameter and elevation of the pipe before backfilling, ~ a geodetic survey of the positions and elevations of covers, bottoms, inlets and outlets at manholes and other system elements prior to backfilling, ~ entry of the routes in the summary map of the utility lines and in the longitudinal profile, ~ handed over to the client in graphic and digital form as a basis for the preparation of the detailed design (PID). | kpl | 1 |  | 0
1.15 | Razna pomoč pri gradbeno-obrtniških, elektro inštalaterskih in strojnih delih. ~ KV delavec | Miscellaneous assistance with building, electrical, plumbing and mechanical work. ~ KV worker | ur | 100 |  | 0
1.16 | Razna pomoč pri gradbeno-obrtniških, elektro inštalaterskih in strojnih delih. ~ PK delavec | Miscellaneous assistance with building, electrical, plumbing and mechanical work. ~ PK worker | ur | 100 |  | 0
| FEKALNA KANALIZACIJA | FAECAL SEWERAGE |  |  |  | 0

## 2.6.2.2_Meteorna_kanalizacija
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | KOMUNALNI PRIKLJUČKI OBJEKTA | UTILITY CONNECTIONS
2.6.2 | GRADBENA DELA | CONSTRUCTION WORKS
2.6.2.2 | METEORNA KANALIZACIJA | METEORIC SEWERAGE |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
2 | METEORNA KANALIZACIJA | METEORIC SEWERAGE
| OPOMBE: Pri izdelavi ponudbe upoštevati pripombe, iz poglavja 0.1 UVOD-STP Pri izdelavi ponudbe upoštevati pripombe, iz poglavja 0.2 UVOD - DGNB in dokument: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme. | NOTES: Take into account the comments made in section 0.1 INTRODUCTION-STP in the preparation of the offer When preparing the tender, take into account the comments made in Section 0.2 INTRODUCTION - DGNB and the document DGNB Quality Grades for Materials, Elements and Equipment.
| Pred pričetkom del je potrebno: ~ na licu mesta preveriti vse dimenzije navedene v načrtu in morebitna odstopanja prilagoditi dejanskemu stanju na terenu ~ vsa neskladja pravočasno / pred izvedbo uskladiti z vodjo projektiranja in ostalimi projektanti ~ vse izvedbe, materiale, obdelave in barve uskladiti s projektanti ~ pri vseh vidnih izvedbah je pred izvedbo potrebno delavniško uskladiti detajle ter jih predložiti projektantu v potrditev | Before starting work, it is necessary to: ~ on-site verification of all dimensions indicated in the plan and adjustment of any deviations to the actual situation on the ground ~ reconcile any discrepancies with the design manager and other designers in a timely manner / prior to implementation ~ all designs, materials, finishes and colours to be coordinated with the designers ~ all visible works shall be subject to workshop coordination of details and submitted to the designer for approval prior to implementation
| Osnova za izvedbo popisa za zemeljska dela je geodetski posnetek obstoječega stanja, načrti objektov, zunanje ureditve in načrti komunalne infra strukture, tehnično poročilo ter navodila in zahteve dobaviteljev za izvedbo in vgradnjo posameznih delov opreme. | The basis for the inventory for the earthworks is the existing geodetic survey, the building plans, the external layout and utility infrastructure plans, the technical report and the suppliers' instructions and requirements for the design and installation of the individual pieces of equipment.
| Pri izvedbi vseh zemeljskih del mora biti prisoten geomehanski nadzor, ki preveri ustreznost predvidenih ukrepov, ustreznost homogenih tal, skladnost privzetih parametrov v PZI z dejanskim stanjem na terenu in geološko-geomehanskih raziskav iz Geološko-geotehničnega poročila (IRGO Consulting d.o.o., poročilo št. 3009776, januar 2021). | During the execution of all earthworks, geomechanical supervision must be present to verify the adequacy of the planned measures, the adequacy of the homogeneous soils, the conformity of the default parameters in the PIP with the actual situation on the ground and the geological-geomechanical investigations from the Geological-Geotechnical Report (IRGO Consulting d.o.o., Report No. 3009776, January 2021).
| V kolikor bi se v času izvajanja zemeljskih del izkazalo, da je dejansko stanje drugačno od predvidenega, geomehanik takoj obvesti projektanta in se pristopu k iskanju projektnih rešitev, ki ustrezajo dejanskemu stanju. Vsa odstopanja od PZI morata pred izvedbo pisno potrditi geomehanik in projektant. | Should the actual situation prove to be different from the intended situation during the execution of the earthworks, the geomechanic shall immediately inform the designer and the designer shall be approached to find design solutions that correspond to the actual situation. Any deviations from the PIP shall be confirmed in writing by the geomechanic and the designer prior to execution.
| Primernost izkopanega materiala za zasip ugotovi geomehanik na licu mesta. | The suitability of the excavated material for backfill shall be determined by the on-site geomechanist.
| Morebitne začasne deponije zemeljskega materiala in potrebne transporte v zvezi s tem je potrebno upoštevati v enotnih cenah. | Any temporary deposits of earth material and the necessary transport in this respect must be taken into account in the uniform prices.
| Izbrana mehanizacija mora omogočati upoštevanje varnostnih ukrepov. | The machinery chosen must be able to comply with safety precautions.
| Vsa izkopna dela in transporti izkopnih materialov se obračunajo po prostornini zemljine v raščenem stanju. Vsa nasipna dela se obračunajo po prostornini zemljine v vgrajenem stanju. Obračun količin se izvede po posnetih profilih pred in po nasipavanju. | All excavation work and transport of excavation materials shall be accounted for by the volume of soil in the loosened state. All embankment work shall be accounted for by the volume of soil in the as-built state. Quantities shall be accounted for on the basis of the recorded profiles before and after embankment.
| Utrjevanje z nabijanjem do predpisane zbitosti po projektu statike. | Curing by ramming to the specified compaction according to the structural design.
| Splošne opombe za betonske konstrukcije; ~ vsi vgrajeni betoni morajo izpolnjevati zahteve SIST EN 206-1, SIST EN 1026 in SIST EN 1992-1-1 ter NAC dodatki; ~ za vse betonske konstrukcije velja zahteva za 2. izvedbeni razred in 1. tolerančni razred po SIST EN 13670 in nacionalnem dodatku, kar je potrebno upoštevati pri pripravi in izvajanju programa kontrole kakovosti in projekta betona; ~ pred nadaljevanjem del morajo biti stiki očiščeni, navlaženi in premazani s sredstvom za povečanje sprijemnosti ~ debelino krovnega sloja je potrebno kontrolirati z merjenjem ~ na proste robove vidnih površin se v opaž vgradi trikotne letve; | General notes for concrete structures; ~ All concrete installed shall comply with the requirements of SIST EN 206-1, SIST EN 1026 and SIST EN 1992-1-1 and NAC Appendices; ~ all concrete structures are subject to the requirement for Performance Class 2 and Tolerance Class 1 in accordance with SIST EN 13670 and the National Supplement, which must be taken into account in the preparation and implementation of the quality control programme and the concrete design; ~ joints must be cleaned, moistened and coated with an adhesion promoter before work proceeds ~ the thickness of the deck layer must be controlled by measuring ~ triangular battens shall be installed in the formwork at the free edges of the visible surfaces;
| Splošne opombe za betonske konstrukcije; ~ za vse vidne površine brez posebnih arhitekturnih oz. drugih zahtev in za nevidne površine veljajo zahteve za obdelavo površin po SIST EN 13670 in nacionalnem dodatku, kar je potrebno upoštevati pri izbiri opažev: - vidne površine: • opažene vidne površine: enostavno – VB2, • neopažene vidne površine (tabela F4 v SIST EN 13670 in tabela N5 v nac, dodatku): enostavna - nevidne površine: • opažene nevidne površine: osnovna – VB0, • neopažene nevidne površine (tabela F4 v SIST EN 13670 in tabela N5 v nac. dodatku): osnovna ~ za izvedbo zaščitnih slojev glej armaturni načrt; | General notes for concrete structures; ~ all visible surfaces without special architectural or other requirements and invisible surfaces are subject to the surface treatment requirements of SIST EN 13670 and the National Supplement, which must be taken into account when selecting the formwork: - visible surfaces: - Visible surfaces observed: easy - VB2, - Unnoticed visible surfaces (Table F4 in SIST EN 13670 and Table N5 in the Appendix): simple - invisible surfaces: - observed invisible surfaces: basic - VB0, - Unnoticed invisible surfaces (Table F4 in SIST EN 13670 and Table N5 in the National Appendix): basic ~ see reinforcement plan for the design of the protective layers;
| Za ravnost in obdelavo površin poleg zahtev v projektni dokumentaciji upoštevati tudi zahteve izbranega dobavitelja zaščitnih premazov. | For the flatness and surface treatment, in addition to the requirements in the project documentation, the requirements of the chosen supplier of protective coatings shall also be observed.
| Izvajalec je dolžan na svoje stroške izdelati projekt izvajanja betonskih konstrukcij. | The Contractor shall be obliged to draw up, at his own expense, a project for the execution of the concrete structures.
| Pri izvedbi je potrebno upoštevati načrte, kjer so prikazane trase inštalacijskih vodov ter pred vgradnjo upoštevati vse elemente, ki so zajeti v elektro in strojnem načrtu. | The plans showing the routes of the installation lines must be followed and all the elements included in the electrical and mechanical plans must be taken into account before installation.
| Na armaturo je potrebno skladno z detajlom izbranega dobavitelja priključiti sistemske elemente za priključitev na ozemljitev - priključitev izvede izvajalec elektro del, pred betoniranjem. | System elements for connection to earth must be connected to the reinforcement in accordance with the details of the selected supplier - connection to be carried out by the electrical contractor before concreting.
| Vsi delovni stiki morajo biti premazani z osnovnim premazom/emulzijo za boljšo vezavo starih in novih konstrukcij/elementov. V ceni se upošteva izvedbo vseh delovnih stikov po navodilih proizvajalca. | All working joints shall be coated with a primer/emulsion for better bonding of old and new structures/elements. The price shall take into account the execution of all working joints according to the manufacturer's instructions.
| V primeru nejasnosti, spremenjenih pogojev ali odstopanja od projekta se je potrebno posvetovati s projektantom. | In case of any ambiguity, changed conditions or deviation from the design, the designer should be consulted.
| Med izvedbo gradbenih posegov mora biti zagotovljen strokovni nadzor, ki bo zagotavljal skladnost gradnje s pogoji iz gradbenega dovoljenja ter kvaliteto izvedenih del v skladu z gradbenimi predpisi. | During the construction works, professional supervision must be provided to ensure that the construction complies with the conditions of the building permit and that the quality of the works is in accordance with the building regulations.
| Upoštevati vse vertikalne in horizontalne transporte. | All vertical and horizontal transports must be taken into account.
| Potrebno je izvajati sprotno čiščenje. | Ongoing cleaning is necessary.
2.1 | Izkop jarka v zemljišču III.ktg. za komunalno infrastrukturo, z nakladanjem na kamion in odvozom na začasno deponijo, do ponovne vgradnje po izvedbi novih del. | Excavation of a trench in land III.ktg. for utility infrastructure, with loading onto a lorry and removal to a temporary landfill site, until re-installation after the new works have been carried out.
a. | ~strojni izkop (90%) | ~machine excavation (90%) | m3 | 2000 |  | 0
b. | ~ročni izkop (10%) | ~hand excavation (10%) | m3 | 223 |  | 0
2.2 | Planiranje in utrjevanje dna izkopa jarkov pred izvedbo komunalne infrastrukture, v predpisanem naklonu in do predpisane utrditve po projektu. | Plan and consolidate the bottom of the trench excavation prior to the implementation of the utility infrastructure, at the prescribed gradient and to the prescribed consolidation as per the design. | m2 | 827 |  | 0
2.3 | Zasip za komunalno infrastrukturo z izkopanim materialom deponiranim na začasni deponiji, komplet z nakladanjem in dovozom, raztiranjem in planiranjem ter utrjevanjem po plasteh od 20 do 30 cm s sprotnim komprimiranjem do predpisane utrditve po projektu. | Backfilling for utility infrastructure with excavated material deposited in a temporary landfill, complete with loading and access, grading and grading, and consolidation in layers of 20 to 30 cm with continuous compaction to the required consolidation as per design. | m3 | 1760 |  | 0
2.4 | Odvoz izkopanega materiala na stalno deponijo, ki si jo priskrbi izvajalec, katero si izvajalec zagotovi sam ter plačilom taks na deponiji. | Removal of excavated material to a permanent landfill to be provided by the Contractor, which shall be provided by the Contractor, and payment of landfill charges. | m3 | 436 |  | 0
2.5 | Dobava in vgradnja PVC opozorilnega traku, položenega v zasip nad cevmi. | Supply and installation of PVC warning tape laid in the backfill above the pipes. | m | 812 |  | 0
2.6 | Kompletna izvedba križanj nove komunalne infrastrukture z obstoječimi komunalnimi vodi, skupaj z vsemi potrebnimi deli in materialom, skladno z upoštevanjem načina izvedbe in vseh pogojev po navodilih upravljalca komunalnega voda. | Complete execution of the crossings of the new utility infrastructure with the existing utility lines, including all necessary works and materials, in accordance with the method of execution and all conditions as specified by the utility line manager. | kpl | 17 |  | 0
2.7 | Dobava in polaganje polne PVC cevi DN 110 za kanalizacijo, kompletno s fazonskimi kosi, spojnim in tesnilnim materialom, skupaj z izdelavo betonske podlage deb. 10 cm in polnim obbetoniranjem 20 cm nad temenom ter izvedbo preizkusa vodotesnosti po SIST EN 1610. ~ cevi po standardih skupine SIST EN 13476 ~ beton C16/20 X0 | Supply and installation of full PVC pipe DN 110 for sewerage, complete with phase pieces, jointing and sealing material, including the construction of a concrete base 10 cm thick and full concreting 20 cm above the top, and watertightness test in accordance with SIST EN 1610. ~ pipes according to SIST EN 13476 group standards ~ concrete C16/20 X0 | m | 74 |  | 0
2.8 | Dobava in polaganje polne PVC cevi DN 160 za kanalizacijo, kompletno s fazonskimi kosi, spojnim in tesnilnim materialom, skupaj z izdelavo betonske podlage deb. 10 cm in polnim obbetoniranjem 20 cm nad temenom ter izvedbo preizkusa vodotesnosti po SIST EN 1610. ~ cevi po standardih skupine SIST EN 13476 ~ beton C16/20 X0 | Supply and installation of full PVC pipe DN 160 for sewerage, complete with bevel pieces, jointing and sealing material, including the construction of a concrete base 10 cm thick and full concreting 20 cm above the top, and watertightness test in accordance with SIST EN 1610. ~ pipes according to SIST EN 13476 group standards ~ concrete C16/20 X0 | m | 143 |  | 0
2.9 | Dobava in polaganje polne PVC cevi DN 200 za kanalizacijo, kompletno s fazonskimi kosi, spojnim in tesnilnim materialom, skupaj z izdelavo betonske podlage deb. 10 cm in polnim obbetoniranjem 20 cm nad temenom ter izvedbo preizkusa vodotesnosti po SIST EN 1610. ~ cevi po standardih skupine SIST EN 13476 ~ beton C16/20 X0 | Supply and installation of full PVC pipe DN 200 for sewerage, complete with bevel pieces, jointing and sealing material, including the construction of a concrete base 10 cm thick and full concreting 20 cm above the top, and watertightness test in accordance with SIST EN 1610. ~ pipes according to SIST EN 13476 group standards ~ concrete C16/20 X0 | m | 112 |  | 0
2.10 | Dobava in polaganje polne PVC cevi DN 250 za kanalizacijo, kompletno s fazonskimi kosi, spojnim in tesnilnim materialom, skupaj z izdelavo betonske podlage deb. 10 cm in polnim obbetoniranjem 20 cm nad temenom ter izvedbo preizkusa vodotesnosti po SIST EN 1610. ~ cevi po standardih skupine SIST EN 13476 ~ beton C16/20 X0 | Supply and installation of a DN 250 full PVC pipe for sewerage, complete with phase pieces, jointing and sealing material, including the construction of a concrete base 10 cm thick and full concreting 20 cm above the top and watertightness test in accordance with SIST EN 1610. ~ pipes according to SIST EN 13476 group standards ~ concrete C16/20 X0 | m | 65 |  | 0
2.11 | Dobava in polaganje polne PEHD cevi DN 80 za kanalizacijo, kompletno s fazonskimi kosi, spojnim in tesnilnim materialom, skupaj z izdelavo betonske podlage deb. 10 cm in polnim obbetoniranjem 20 cm nad temenom ter izvedbo preizkusa vodotesnosti po SIST EN 1610. ~ cevi po standardih skupine SIST EN 13476 ~ beton C16/20 X0 | Supply and installation of a DN 80 solid PEHD pipe for sewerage, complete with phase pieces, jointing and sealing material, including the construction of a concrete base 10 cm thick and full concreting 20 cm above the top and watertightness test in accordance with SIST EN 1610. ~ pipes according to SIST EN 13476 group standards ~ concrete C16/20 X0 | m | 3 |  | 0
2.12 | Dobava in polaganje polne PEHD cevi DN 90 za kanalizacijo, kompletno s fazonskimi kosi, spojnim in tesnilnim materialom, skupaj z izdelavo betonske podlage deb. 10 cm in polnim obbetoniranjem 20 cm nad temenom ter izvedbo preizkusa vodotesnosti po SIST EN 1610. ~ cevi po standardih skupine SIST EN 13476 ~ beton C16/20 X0 | Supply and installation of full PEHD pipe DN 90 for sewerage, complete with bevel pieces, jointing and sealing material, together with the construction of a concrete base 10 cm thick and full concreting 20 cm above the top, and watertightness test in accordance with SIST EN 1610. ~ pipes according to SIST EN 13476 group standards ~ concrete C16/20 X0 | m | 19 |  | 0
2.13 | Dobava in polaganje polne PEHD cevi DN 110 za kanalizacijo, kompletno s fazonskimi kosi, spojnim in tesnilnim materialom, skupaj z izdelavo betonske podlage deb. 10 cm in polnim obbetoniranjem 20 cm nad temenom ter izvedbo preizkusa vodotesnosti po SIST EN 1610. ~ cevi po standardih skupine SIST EN 13476 ~ beton C16/20 X0 | Supply and installation of a DN 110 solid PEHD pipe for sewerage, complete with phase pieces, jointing and sealing material, including the construction of a concrete base 10 cm thick and full concreting 20 cm above the top and watertightness test in accordance with SIST EN 1610. ~ pipes according to SIST EN 13476 group standards ~ concrete C16/20 X0 | m | 136 |  | 0
2.14 | Dobava in polaganje polne PEHD cevi DN 160 za kanalizacijo, kompletno s fazonskimi kosi, spojnim in tesnilnim materialom, skupaj z izdelavo betonske podlage deb. 10 cm in polnim obbetoniranjem 20 cm nad temenom ter izvedbo preizkusa vodotesnosti po SIST EN 1610. ~ cevi po standardih skupine SIST EN 13476 ~ beton C16/20 X0 | Supply and installation of full PEHD pipe DN 160 for sewerage, complete with bevel pieces, jointing and sealing material, including the construction of a concrete base 10 cm thick and full concreting 20 cm above the top, and watertightness test in accordance with SIST EN 1610. ~ pipes according to SIST EN 13476 group standards ~ concrete C16/20 X0 | m | 47 |  | 0
2.15 | Dobava in polaganje polne PEHD cevi DN 250 za kanalizacijo, kompletno s fazonskimi kosi, spojnim in tesnilnim materialom, skupaj z izdelavo betonske podlage deb. 10 cm in polnim obbetoniranjem 20 cm nad temenom ter izvedbo preizkusa vodotesnosti po SIST EN 1610. ~ cevi po standardih skupine SIST EN 13476 ~ beton C16/20 X0 | Supply and installation of a DN 250 solid PEHD pipe for sewerage, complete with phase pieces, jointing and sealing material, including the construction of a concrete base 10 cm thick and full concreting 20 cm above the top and watertightness test in accordance with SIST EN 1610. ~ pipes according to SIST EN 13476 group standards ~ concrete C16/20 X0 | m | 15 |  | 0
2.16 | Dobava in polaganje polne PEHD cevi DN 315 za kanalizacijo, kompletno s fazonskimi kosi, spojnim in tesnilnim materialom, skupaj z izdelavo betonske podlage deb. 10 cm in polnim obbetoniranjem 20 cm nad temenom ter izvedbo preizkusa vodotesnosti po SIST EN 1610. ~ cevi po standardih skupine SIST EN 13476 ~ beton C16/20 X0 | Supply and installation of full PEHD pipe DN 315 for sewerage, complete with bevel pieces, jointing and sealing material, together with the construction of a concrete base 10 cm thick and full concreting 20 cm above the top, and watertightness test in accordance with SIST EN 1610. ~ pipes according to SIST EN 13476 group standards ~ concrete C16/20 X0 | m | 9 |  | 0
2.17 | Dobava in polaganje polne PEHD cevi DN 400 za kanalizacijo, kompletno s fazonskimi kosi, spojnim in tesnilnim materialom, skupaj z izdelavo betonske podlage deb. 10 cm in polnim obbetoniranjem 20 cm nad temenom ter izvedbo preizkusa vodotesnosti po SIST EN 1610. ~ cevi po standardih skupine SIST EN 13476 ~ beton C16/20 X0 | Supply and installation of full PEHD pipe DN 400 for sewerage, complete with bevel pieces, jointing and sealing material, together with the construction of a concrete base 10 cm thick and full concreting 20 cm above the top, and watertightness test in accordance with SIST EN 1610. ~ pipes according to SIST EN 13476 group standards ~ concrete C16/20 X0 | m | 23 |  | 0
2.18 | Dobava in polaganje polne predizolirane PEHD cevi iz trde poliuretanske pene, DN 50 za kanalizacijo, kompletno s fazonskimi kosi, spojnim in tesnilnim materialom, skupaj z izdelavo betonske podlage deb. 10 cm in polnim obbetoniranjem 20 cm nad temenom ter izvedbo preizkusa vodotesnosti po SIST EN 1610. ~ zunanji plašč je iz polietilena visoke gostote - trda poliuretanska pena, kot npr. PURLEN ali enakovredno ~ cevi po standardih skupine SIST EN 13476 ~ beton C16/20 X0 | Supply and installation of a full preinsulated PEHD pipe made of rigid polyurethane foam, DN 50 for sewerage, complete with phase pieces, jointing and sealing material, together with the construction of a concrete base 10 cm thick and full concreting 20 cm above the top, and watertightness test in accordance with SIST EN 1610. ~ outer jacket made of high density polyethylene - rigid polyurethane foam, such as PURLEN or equivalent ~ pipes according to SIST EN 13476 group standards ~ concrete C16/20 X0 | m | 4 |  | 0
2.19 | Dobava in polaganje polne predizolirane PEHD cevi iz trde poliuretanske pene, DN 90 za kanalizacijo, kompletno s fazonskimi kosi, spojnim in tesnilnim materialom, skupaj z izdelavo betonske podlage deb. 10 cm in polnim obbetoniranjem 20 cm nad temenom ter izvedbo preizkusa vodotesnosti po SIST EN 1610. ~ zunanji plašč je iz polietilena visoke gostote - trda poliuretanska pena, kot npr. PURLEN ali enakovredno ~ cevi po standardih skupine SIST EN 13476 ~ beton C16/20 X0 | Supply and installation of a full preinsulated PEHD pipe made of rigid polyurethane foam, DN 90 for sewerage, complete with phase pieces, jointing and sealing material, together with the construction of a concrete base 10 cm thick and full concreting 20 cm above the top, and watertightness test in accordance with SIST EN 1610. ~ outer jacket made of high density polyethylene - rigid polyurethane foam, such as PURLEN or equivalent ~ pipes according to SIST EN 13476 group standards ~ concrete C16/20 X0 | m | 4 |  | 0
2.20 | Dobava in polaganje polne predizolirane PEHD cevi iz trde poliuretanske pene, DN 110 za kanalizacijo, kompletno s fazonskimi kosi, spojnim in tesnilnim materialom, skupaj z izdelavo betonske podlage deb. 10 cm in polnim obbetoniranjem 20 cm nad temenom ter izvedbo preizkusa vodotesnosti po SIST EN 1610. ~ zunanji plašč je iz polietilena visoke gostote - trda poliuretanska pena, kot npr. PURLEN ali enakovredno ~ cevi po standardih skupine SIST EN 13476 ~ beton C16/20 X0 | Supply and installation of a full preinsulated PEHD pipe made of rigid polyurethane foam, DN 110 for sewerage, complete with phase pieces, jointing and sealing material, together with the construction of a concrete base 10 cm thick and full concreting 20 cm above the top, and watertightness test in accordance with SIST EN 1610. ~ outer jacket made of high density polyethylene - rigid polyurethane foam, such as PURLEN or equivalent ~ pipes according to SIST EN 13476 group standards ~ concrete C16/20 X0 | m | 72 |  | 0
2.21 | Dobava in polaganje polne predizolirane PEHD cevi iz trde poliuretanske pene, DN 125 za kanalizacijo, kompletno s fazonskimi kosi, spojnim in tesnilnim materialom, skupaj z izdelavo betonske podlage deb. 10 cm in polnim obbetoniranjem 20 cm nad temenom ter izvedbo preizkusa vodotesnosti po SIST EN 1610. ~ zunanji plašč je iz polietilena visoke gostote - trda poliuretanska pena, kot npr. PURLEN ali enakovredno ~ cevi po standardih skupine SIST EN 13476 ~ beton C16/20 X0 | Supply and installation of a full preinsulated PEHD pipe made of rigid polyurethane foam, DN 125 for sewerage, complete with phase pieces, jointing and sealing material, together with the construction of a concrete base 10 cm thick and full concreting 20 cm above the top, and watertightness test in accordance with SIST EN 1610. ~ outer jacket made of high density polyethylene - rigid polyurethane foam, such as PURLEN or equivalent ~ pipes according to SIST EN 13476 group standards ~ concrete C16/20 X0 | m | 18 |  | 0
2.22 | Dobava in polaganje polne predizolirane PEHD cevi iz trde poliuretanske pene, DN 160 za kanalizacijo, kompletno s fazonskimi kosi, spojnim in tesnilnim materialom, skupaj z izdelavo betonske podlage deb. 10 cm in polnim obbetoniranjem 20 cm nad temenom ter izvedbo preizkusa vodotesnosti po SIST EN 1610. ~ zunanji plašč je iz polietilena visoke gostote - trda poliuretanska pena, kot npr. PURLEN ali enakovredno ~ cevi po standardih skupine SIST EN 13476 ~ beton C16/20 X0 | Supply and installation of a full preinsulated PEHD pipe made of rigid polyurethane foam, DN 160 for sewerage, complete with phase pieces, jointing and sealing material, together with the construction of a concrete base 10 cm thick and full concreting 20 cm above the top, and watertightness test in accordance with SIST EN 1610. ~ outer jacket made of high density polyethylene - rigid polyurethane foam, such as PURLEN or equivalent ~ pipes according to SIST EN 13476 group standards ~ concrete C16/20 X0 | m | 26 |  | 0
2.23 | Dobava in vgradnja PE drenažnih cevi DN 200 mm s 2/3 perforacijo, po SIST EN 13476-3, skupaj z izvedbo in polaganjem na peščeno posteljico iz drenažnega materiala, granulacije 16-32 mm, deb. 10 cm ter z izvedbo drenažnega zasipa, granulacije 16-32 mm, 30 cm nad temenom cevi , vse skupaj zaščiteno z geotekstilom; v ceni se poleg cevi upošteva še: ~drenažna posteljica/obsip granulacije 16-32 mm (10 cm pod cevjo ter obsip cevi 30 cm); cca 0,36 m3/m ~zaščita z geotekstilom 200g/m2 okrog zasipa; cca 4,00 m2/m | Supply and installation of PE drainage pipes DN 200 mm with 2/3 perforation, in accordance with SIST EN 13476-3, together with construction and laying on a sand bed of drainage material, granulation 16-32 mm, thickness 10 cm, and drainage backfill, granulation 16-32 mm, 30 cm above the top of the pipe, all protected by geotextile; the price shall include, in addition to the pipe: ~drainage bed/backfill granulation 16-32 mm (10 cm below the pipe and 30 cm of pipe backfill); approx. 0.36 m3/m ~protection with geotextile 200g/m2 around the backfill; approx. 4.00 m2/m | m | 42 |  | 0
2.24 | Dobava in vgradnja PE drenažnih cevi DN 315 mm s 2/3 perforacijo, po SIST EN 13476-3, skupaj z izvedbo in polaganjem na peščeno posteljico iz drenažnega materiala, granulacije 16-32 mm, deb. 10 cm ter z izvedbo drenažnega zasipa, granulacije 16-32 mm, 30 cm nad temenom cevi , vse skupaj zaščiteno z geotekstilom; v ceni se poleg cevi upošteva še: ~drenažna posteljica/obsip granulacije 16-32 mm (10 cm pod cevjo ter obsip cevi 30 cm); cca 0,36 m3/m ~zaščita z geotekstilom 200g/m2 okrog zasipa; cca 4,00 m2/m | Supply and installation of PE drainage pipes DN 315 mm with 2/3 perforation, in accordance with SIST EN 13476-3, together with construction and laying on a sand bed of drainage material, granulation 16-32 mm, thickness 10 cm, and drainage backfill, granulation 16-32 mm, 30 cm above the top of the pipe, all protected by geotextile; the price shall include, in addition to the pipe: ~drainage bed/backfill granulation 16-32 mm (10 cm below the pipe and 30 cm of pipe backfill); approx. 0.36 m3/m ~protection with geotextile 200g/m2 around the backfill; approx. 4.00 m2/m | m | 6 |  | 0
2.25 | Kompletna izdelava, dobava in montaža nepovratnega ventila za polno PVC cevi DN 250 za kanalizacijo, kot npr. MV STOP ali enakovredno, kompletno s spojnim in tesnilnim materialom, skupaj z vsemi potrebnimi deli in materialom ter montažo po navodilu proizvajalca. | Complete manufacture, supply and installation of a non-return valve for full PVC pipes DN 250 for sewers, such as MV STOP or equivalent, complete with jointing and sealing material, together with all necessary parts and materials and installation according to the manufacturer's instructions. | kos | 2 |  | 0
2.26 | Kompletna izdelava, dobava in montaža nepovratnega ventila za polno PEHD cevi DN 315 za kanalizacijo, kot npr. MV STOP ali enakovredno, kompletno s spojnim in tesnilnim materialom, skupaj z vsemi potrebnimi deli in materialom ter montažo po navodilu proizvajalca. | Complete manufacture, supply and installation of a non-return valve for full PEHD pipes DN 315 for sewers, such as MV STOP or equivalent, complete with jointing and sealing material, together with all necessary parts and materials and installation according to the manufacturer's instructions. | kos | 1 |  | 0
2.27 | Izdelava, dobava in montaža peskolovov iz betonskih cevi premera fi 40 cm, za odvod meteorne vode, do globine 130 cm, usedalni del min 50 cm, vključno z izdelavo in obdelavo betonskega dna, vseh priključkov z vsem potrebnim materialom in delom, ter skupaj z izdelavo, dobavo in vgradnjo jeklenega vroče cinkanega pokrova za zapolnitev, dimenzije 400x400 mm, D400, skladno s standardom EN 1253-4, kot npr. ACO pokrovi za zapolnitev Paving GS z asistenco za odpiranje ali enakovredno, pokrovi se vgradijo v tlak skupaj z vsemi potrebnimi deli in materialom po navodilu proizvajalca. | Manufacture, supply and installation of gravel pits made of concrete pipes with a diameter of 40 cm fi for the drainage of rainwater, up to a depth of 130 cm, settling part min 50 cm, including the manufacture and treatment of the concrete base, all connections with all necessary materials and work, together with the manufacture, supply and installation of a hot-dip galvanised steel backfill cover, dimensions 400x400 mm, D400, in accordance with EN 1253-4, such as the ACO Paving GS backfill covers with opening assistance or equivalent, to be installed in the pavement together with all the necessary work and materials in accordance with the manufacturer's instructions. | kos | 6 |  | 0
2.28 | Izdelava, dobava in montaža peskolovov iz betonskih cevi premera fi 40 cm, za odvod meteorne vode, do globine 150 cm, usedalni del min 50 cm, skupaj z LTŽ pokrovom fi 600, D400, vključno z izdelavo in obdelavo betonskega dna, vseh priključkov, skupaj z vsem potrebnim materialom in delom. | Manufacture, supply and installation of gravel pits made of concrete pipes with a diameter of 40 cm, for the drainage of rainwater, up to a depth of 150 cm, with a settling part of at least 50 cm, together with an LTŽ cover of 600 mm, D400, including the manufacture and treatment of the concrete bottom, all connections, together with all necessary materials and labour. | kos | 8 |  | 0
2.29 | Izdelava, dobava in montaža peskolovov iz betonskih cevi premera fi 40 cm, za odvod meteorne vode, do globine 150 cm, usedalni del min 50 cm, skupaj z armiranobetonskim pokrovom fi 40 cm, B125, vključno z izdelavo in obdelavo betonskega dna, vseh priključkov, skupaj z vsem potrebnim materialom in delom. | Construction, supply and installation of gravel pits made of concrete pipes with a diameter of 40 cm, for the drainage of rainwater, up to a depth of 150 cm, with a settling part of at least 50 cm, together with a reinforced concrete cover of 40 cm, B125, including the construction and treatment of the concrete bottom, all connections, together with all necessary materials and labour. | kos | 4 |  | 0
2.30 | Izdelava, dobava in montaža peskolovov iz betonskih cevi premera fi 40 cm, za odvod meteorne vode, do globine 150 cm, usedalni del min 50 cm, vključno z izdelavo in obdelavo betonskega dna, vseh priključkov z vsem potrebnim materialom in delom, ter skupaj z izdelavo, dobavo in vgradnjo jeklenega vroče cinkanega pokrova za zapolnitev, dimenzije 400x400 mm, B125, skladno s standardom EN 1253-4, kot npr. ACO pokrovi za zapolnitev Paving GS z asistenco za odpiranje ali enakovredno, pokrovi se vgradijo v tlak skupaj z vsemi potrebnimi deli in materialom po navodilu proizvajalca. | Manufacture, supply and installation of grit chambers made of concrete pipes with a diameter of 40 cm fi for the drainage of rainwater, up to a depth of 150 cm, settling part min 50 cm, including the manufacture and treatment of the concrete base, all connections with all necessary materials and work, together with the manufacture, supply and installation of a hot-dip galvanised steel backfill cover, dimensions 400x400 mm, B125, in accordance with EN 1253-4, such as the ACO Paving GS backfill covers with opening assistance or equivalent, to be installed in the pavement together with all the necessary work and materials in accordance with the manufacturer's instructions. | kos | 6 |  | 0
2.31 | Izdelava, dobava in montaža peskolovov iz betonskih cevi premera fi 50 cm, za odvod meteorne vode, do globine 150 cm, usedalni del min 50 cm, skupaj z LTŽ pokrovom fi 600, D400, vključno z izdelavo in obdelavo betonskega dna, vseh priključkov, skupaj z vsem potrebnim materialom in delom. | Manufacture, supply and installation of gravel pits made of concrete pipes with a diameter of 50 cm fi 50 cm, for the drainage of rainwater, up to a depth of 150 cm, settling part of min. 50 cm, together with LTŽ cover fi 600, D400, including the manufacture and treatment of the concrete bottom, all connections, together with all necessary materials and labour. | kos | 2 |  | 0
2.32 | Izdelava, dobava in montaža peskolovov iz betonskih cevi premera fi 50 cm, za odvod meteorne vode, do globine 150 cm, usedalni del min 50 cm, skupaj z armiranobetonskim pokrovom fi 50 cm, B125, vključno z izdelavo in obdelavo betonskega dna, vseh priključkov, skupaj z vsem potrebnim materialom in delom. | Construction, supply and installation of grit pits made of concrete pipes with a diameter of 50 cm, for the drainage of rainwater, up to a depth of 150 cm, settling part min. 50 cm, together with a reinforced concrete cover 50 cm fi 50, B125, including the construction and treatment of the concrete bottom, all connections, together with all necessary materials and labour. | kos | 1 |  | 0
2.33 | Izdelava, dobava in montaža peskolovov iz perforiranih betonskih cevi premera fi 50 cm, za odvod meteorne vode, do globine 150 cm, usedalni del min 50 cm, skupaj z armiranobetonskim pokrovom fi 50 cm z luknjami, B125, vključno z izdelavo in obdelavo betonskega dna, vseh priključkov, skupaj z vsem potrebnim materialom in delom. | Construction, supply and installation of perforated concrete pipe gullies, diameter fi 50 cm, for the drainage of rainwater, up to a depth of 150 cm, settling part min. 50 cm, together with reinforced concrete cover fi 50 cm with holes, B125, including the construction and treatment of the concrete bottom, all connections, together with all necessary materials and labour. | kos | 3 |  | 0
2.34 | Kompletna izdelava revizijskih protivzgonskih jaškov z dvojnim dnom iz PE rebraste cevi, premera fi 800 mm, globine do 1,00 m, z izdelavo dna, priključkov, armiranobetonskega razbremenilnega obroča in venca kot ležišče za LTŽ pokrov ter LTŽ pokrov fi 600 mm, nosilnosti D400, kot npr. LIVAR art. 600, po SIST EN 124-2. Dobava in vgradnja razbremenilnega obroča in venca mora biti upoštevana v enotni ceni dobave in vgradnje LTŽ pokrova. Opomba: Betonski razbremenilni obroč in venec s pokrovom ne smejo biti temeljeni direktno na telo jaška, temveč na utrjeni zasip okrog jaška. Dilatacije med AB ploščo, vencem in PE jaškom morajo ustrezati zahtevam izbranega proizvajalca jaškov. | Complete construction of double-bottomed inspection manholes made of PE finned pipe, diameter fi 800 mm, depth up to 1.00 m, with construction of the bottom, connections, reinforced concrete relief ring and wreath as a bed for the LTŽ cover and LTŽ cover fi 600 mm, load capacity D400, e.g. LIVAR art. 600, in accordance with SIST EN 124-2. The supply and installation of the relief ring and wreath must be included in the single price for the supply and installation of the LTŽ cover. Note: The concrete relief ring and the capped wreath shall not be founded directly on the manhole body, but on the hardened backfill around the manhole. The expansion between the AB slab, the wreath and the PE manhole shall comply with the requirements of the selected manhole manufacturer. | kos | 4 |  | 0
2.35 | Kompletna izdelava revizijskih protivzgonskih jaškov z dvojnim dnom iz PE rebraste cevi, premera fi 800 mm, globine od 1,00 do 1,50 m, z izdelavo dna, priključkov, armiranobetonskega razbremenilnega obroča in venca kot ležišče za LTŽ pokrov ter LTŽ pokrov fi 600 mm, nosilnosti D400, kot npr. LIVAR art. 600, po SIST EN 124-2. Dobava in vgradnja razbremenilnega obroča in venca mora biti upoštevana v enotni ceni dobave in vgradnje LTŽ pokrova. Opomba: Betonski razbremenilni obroč in venec s pokrovom ne smejo biti temeljeni direktno na telo jaška, temveč na utrjeni zasip okrog jaška. Dilatacije med AB ploščo, vencem in PE jaškom morajo ustrezati zahtevam izbranega proizvajalca jaškov. | Complete construction of double-bottomed inspection shafts made of PE finned pipe, diameter fi 800 mm, depth from 1.00 to 1.50 m, with construction of the bottom, connections, reinforced concrete relief ring and wreath as a bed for the LTŽ cover and LTŽ cover fi 600 mm, load capacity D400, such as LIVAR art. 600, according to SIST EN 124-2. The supply and installation of the relief ring and wreath must be included in the single price for the supply and installation of the LTŽ cover. Note: The concrete relief ring and the capped wreath shall not be founded directly on the manhole body, but on the hardened backfill around the manhole. The expansion between the AB slab, the wreath and the PE manhole shall comply with the requirements of the selected manhole manufacturer. | kos | 9 |  | 0
2.36 | Kompletna izdelava revizijskih protivzgonskih jaškov z dvojnim dnom iz PE rebraste cevi, premera fi 800 mm, globine do 1,00 m, z izdelavo dna, priključkov, armiranobetonskega razbremenilnega obroča in venca kot ležišče za LTŽ pokrov ter LTŽ pokrov fi 600 mm, nosilnosti B125, kot npr. LIVAR art. 600, po SIST EN 124-2. Dobava in vgradnja razbremenilnega obroča in venca mora biti upoštevana v enotni ceni dobave in vgradnje LTŽ pokrova. Opomba: Betonski razbremenilni obroč in venec s pokrovom ne smejo biti temeljeni direktno na telo jaška, temveč na utrjeni zasip okrog jaška. Dilatacije med AB ploščo, vencem in PE jaškom morajo ustrezati zahtevam izbranega proizvajalca jaškov. | Complete construction of double-bottomed inspection manholes made of PE finned pipe, diameter fi 800 mm, depth up to 1.00 m, with construction of the bottom, connections, reinforced concrete relief ring and wreath as a bed for the LTŽ cover and LTŽ cover fi 600 mm, load capacity B125, such as LIVAR art. 600, according to SIST EN 124-2. The supply and installation of the relief ring and wreath must be included in the single price for the supply and installation of the LTŽ cover. Note: The concrete relief ring and the capped wreath shall not be founded directly on the manhole body, but on the hardened backfill around the manhole. The expansion between the AB slab, the wreath and the PE manhole shall comply with the requirements of the selected manhole manufacturer. | kos | 6 |  | 0
2.37 | Kompletna izdelava revizijskih protivzgonskih jaškov z dvojnim dnom iz PE rebraste cevi, premera fi 800 mm, globine od 1,00 do 1,50 m, z izdelavo dna, priključkov, armiranobetonskega razbremenilnega obroča in venca kot ležišče za LTŽ pokrov ter LTŽ pokrov fi 600 mm, nosilnosti B125, kot npr. LIVAR art. 600, po SIST EN 124-2. Dobava in vgradnja razbremenilnega obroča in venca mora biti upoštevana v enotni ceni dobave in vgradnje LTŽ pokrova. Opomba: Betonski razbremenilni obroč in venec s pokrovom ne smejo biti temeljeni direktno na telo jaška, temveč na utrjeni zasip okrog jaška. Dilatacije med AB ploščo, vencem in PE jaškom morajo ustrezati zahtevam izbranega proizvajalca jaškov. | Complete construction of double-bottomed inspection shafts made of PE finned pipe, diameter fi 800 mm, depth from 1.00 to 1.50 m, with construction of the bottom, connections, reinforced concrete relief ring and wreath as a bed for the LTŽ cover and the LTŽ cover fi 600 mm, load capacity B125, such as LIVAR art. 600, according to SIST EN 124-2. The supply and installation of the relief ring and wreath must be included in the single price for the supply and installation of the LTŽ cover. Note: The concrete relief ring and the capped wreath shall not be founded directly on the manhole body, but on the hardened backfill around the manhole. The expansion between the AB slab, the wreath and the PE manhole shall comply with the requirements of the selected manhole manufacturer. | kos | 3 |  | 0
2.38 | Kompletna izdelava revizijskih protivzgonskih jaškov z dvojnim dnom iz PE rebraste cevi, premera fi 800 mm, globine od 1,00 do 1,50 m, z izdelavo dna, priključkov, armiranobetonskega razbremenilnega obroča in venca kot ležišče za jeklen pokrov ter jeklenega vroče cinkanega pokrova za zapolnitev, dimenzije 600x600 mm, D400, skladno s standardom EN 1253-4, kot npr. ACO pokrovi za zapolnitev Paving GS z asistenco za odpiranje ali enakovredno, pokrov se prilagodi glede na finalni tlak, skupaj z vsemi potrebnimi deli in materialom po navodilu proizvajalca. Dobava in vgradnja razbremenilnega obroča in venca mora biti upoštevana v enotni ceni dobave in vgradnje jeklenega pokrova. Opomba: Betonski razbremenilni obroč in venec s pokrovom ne smejo biti temeljeni direktno na telo jaška, temveč na utrjeni zasip okrog jaška. Dilatacije med AB ploščo, vencem in PE jaškom morajo ustrezati zahtevam izbranega proizvajalca jaškov. | Kompletna izdelava revizijskih protivzgonskih jaškov z dvojnim dnom iz PE rebraste cevi, premera fi 800 mm, globine od 1,00 do 1,50 m, z izdelavo dna, priključkov, armiranobetonskega razbremenilnega obroča in venca kot ležišče za jeklen pokrov ter jeklenega vroče cinkanega pokrova za zapolnitev, dimenzije 600x600 mm, D400, skladno s standardom EN 1253-4, kot npr. ACO pokrovi za zapolnitev Paving GS z asistenco za odpiranje ali enakovredno, pokrov se prilagodi glede na finalni tlak, skupaj z vsemi potrebnimi deli in materialom po navodilu proizvajalca. Dobava in vgradnja razbremenilnega obroča in venca mora biti upoštevana v enotni ceni dobave in vgradnje jeklenega pokrova. Note: The concrete relief ring and the capped wreath shall not be founded directly on the manhole body, but on the hardened backfill around the manhole. The expansion between the AB slab, the wreath and the PE manhole shall comply with the requirements of the selected manhole manufacturer. | kos | 1 |  | 0
2.39 | Revizijski jašek ZV0: Kompletna izdelava revizijskih jaškov meteorne kanalizacija za montažo nožastega zasuna na cev, iz betonskih cevi fi 120 cm, skupaj z nožastim ventilom na cevi na ročni pogon (za cev DN250), jašek globine do 1,5 m, z izdelavo betonskega dna, priključkov, armiranobetonskega razbremenilnega obroča in venca kot ležišče za LTŽ pokrov ter LTŽ pokrov 800x800 mm (D400), po sist EN 124-2. V enotni ceni je ventil na cevi, je nožasti zasun DN250 PN10 z vretenom in kolesom za ročni pogon, kot na primer nožasti zasun tip Zeta proizvajalca VAG Armaturen. Priključek nožastega zasuna na cevovod mora biti izveden preko PE ( PE100 oz. PEHD ) cevi s fazonskimi kosi medprirobično, skupaj z montažo v jašku in prehodnimi kosi za cevi in vsemi ostalimi montažnimi elementi. OPOMBA: Betonski razbremenilni obroč in venec s pokrovom ne smejo biti temeljeni direktno na telo jaška, temveč na utrjeni zasip okrog jaška. Pokrov se prilagodi glede na finalni tlak in se vgradi v naklonu tlaka. Dobava in vgradnja razbremenilnega obroča in venca mora biti upoštevana v enotni ceni dobave in vgradnje LTŽ pokrova ( kot npr. sistem LIVAR, art. 904 ali enakovredno). | Inspection shaft ZV0: Kompletna izdelava revizijskih jaškov meteorne kanalizacija za montažo nožastega zasuna na cev, iz betonskih cevi fi 120 cm, skupaj z nožastim ventilom na cevi na ročni pogon (za cev DN250), jašek globine do 1,5 m, z izdelavo betonskega dna, priključkov, armiranobetonskega razbremenilnega obroča in venca kot ležišče za LTŽ pokrov ter LTŽ pokrov 800x800 mm (D400), po sist EN 124-2. V enotni ceni je ventil na cevi, je nožasti zasun DN250 PN10 z vretenom in kolesom za ročni pogon, kot na primer nožasti zasun tip Zeta proizvajalca VAG Armaturen. Priključek nožastega zasuna na cevovod mora biti izveden preko PE ( PE100 oz. PEHD ) cevi s fazonskimi kosi medprirobično, skupaj z montažo v jašku in prehodnimi kosi za cevi in vsemi ostalimi montažnimi elementi. NOTE: The concrete relief ring and the wreath with cover shall not be founded directly on the manhole body but on the hardened backfill around the manhole. The cover shall be adjusted to the final pavement and shall be installed at the slope of the pavement. The supply and installation of the relief ring and the wreath shall be included in the uniform price for the supply and installation of the LTŽ cover (such as the LIVAR system, Art. 904 or equivalent). | kos | 1 |  | 0
2.40 | Revizijski jašek ZV1.1: Kompletna izdelava revizijskih jaškov meteorne kanalizacija za montažo nožastega zasuna na cev, iz betonskih cevi fi 120 cm, skupaj z nožastim ventilom na cevi na ročni pogon (za cev DN400), jašek globine do 2,0 m, z izdelavo betonskega dna, priključkov, armiranobetonskega razbremenilnega obroča in venca kot ležišče za LTŽ pokrov ter LTŽ pokrov 800x800 mm (D400), po sist EN 124-2. V enotni ceni je ventil na cevi, je nožasti zasun DN400 PN8 z vretenom in kolesom za ročni pogon, kot na primer nožasti zasun tip Zeta proizvajalca VAG Armaturen. Priključek nožastega zasuna na cevovod mora biti izveden preko PE ( PE100 oz. PEHD ) cevi s fazonskimi kosi medprirobično, skupaj z montažo v jašku in prehodnimi kosi za cevi in vsemi ostalimi montažnimi elementi. OPOMBA: Betonski razbremenilni obroč in venec s pokrovom ne smejo biti temeljeni direktno na telo jaška, temveč na utrjeni zasip okrog jaška. Pokrov se prilagodi glede na finalni tlak in se vgradi v naklonu tlaka. Dobava in vgradnja razbremenilnega obroča in venca mora biti upoštevana v enotni ceni dobave in vgradnje LTŽ pokrova ( kot npr. sistem LIVAR, art. 904 ali enakovredno). | Inspection shaft ZV1.1: Kompletna izdelava revizijskih jaškov meteorne kanalizacija za montažo nožastega zasuna na cev, iz betonskih cevi fi 120 cm, skupaj z nožastim ventilom na cevi na ročni pogon (za cev DN400), jašek globine do 2,0 m, z izdelavo betonskega dna, priključkov, armiranobetonskega razbremenilnega obroča in venca kot ležišče za LTŽ pokrov ter LTŽ pokrov 800x800 mm (D400), po sist EN 124-2. V enotni ceni je ventil na cevi, je nožasti zasun DN400 PN8 z vretenom in kolesom za ročni pogon, kot na primer nožasti zasun tip Zeta proizvajalca VAG Armaturen. Priključek nožastega zasuna na cevovod mora biti izveden preko PE ( PE100 oz. PEHD ) cevi s fazonskimi kosi medprirobično, skupaj z montažo v jašku in prehodnimi kosi za cevi in vsemi ostalimi montažnimi elementi. NOTE: The concrete relief ring and the wreath with cover shall not be founded directly on the manhole body but on the hardened backfill around the manhole. The cover shall be adjusted to the final pavement and shall be installed at the slope of the pavement. The supply and installation of the relief ring and the wreath shall be included in the uniform price for the supply and installation of the LTŽ cover (such as the LIVAR system, Art. 904 or equivalent). | kos | 1 |  | 0
2.41 | Izdelava, dobava in montaža revizijskih jaškov iz betonskih cevi premera fi 100 cm, globine od 1,00 do 1,50 m, vključno z izdelavo in obdelavo betonskega dna, vseh priključkov z vsem potrebnim materialom in delom, ter skupaj z izdelavo, dobavo in vgradnjo jeklenega vroče cinkanega pokrova za zapolnitev, dimenzije 600x600 mm, D400, skladno s standardom EN 1253-4, kot npr. ACO pokrovi za zapolnitev Paving GS z asistenco za odpiranje ali enakovredno, pokrovi se vgradijo v tlak skupaj z vsemi potrebnimi deli in materialom po navodilu proizvajalca. | Manufacture, supply and installation of inspection manholes made of concrete pipes with a diameter of 100 cm fi, depth from 1.00 to 1.50 m, including the manufacture and treatment of the concrete bottom, all connections with all necessary materials and work, together with the manufacture, supply and installation of a hot-dip galvanised steel backfill cover, dimensions 600x600 mm, D400, in accordance with EN 1253-4, such as ACO Paving GS backfill covers with opening assistance or equivalent, to be installed in the pavement together with all necessary work and materials according to the manufacturer's instructions. | kos | 1 |  | 0
2.42 | Izdelava, dobava in montaža revizijskih jaškov iz betonskih cevi premera fi 120 cm, globine od 1,00 do 1,50 m, vključno z izdelavo in obdelavo betonskega dna, vseh priključkov z vsem potrebnim materialom in delom, ter skupaj z izdelavo, dobavo in vgradnjo jeklenega vroče cinkanega pokrova za zapolnitev, dimenzije 600x600 mm, D400, skladno s standardom EN 1253-4, kot npr. ACO pokrovi za zapolnitev Paving GS z asistenco za odpiranje ali enakovredno, pokrovi se vgradijo v tlak skupaj z vsemi potrebnimi deli in materialom po navodilu proizvajalca. | Manufacture, supply and installation of inspection manholes made of concrete pipes with a diameter of 120 cm fi, depth from 1.00 to 1.50 m, including the manufacture and treatment of the concrete bottom, all connections with all necessary materials and work, together with the manufacture, supply and installation of a hot-dip galvanised steel backfill cover, dimensions 600x600 mm, D400, in accordance with EN 1253-4, such as ACO Paving GS backfill covers with opening assistance or equivalent, to be installed in the pavement together with all necessary work and materials according to the manufacturer's instructions. | kos | 1 |  | 0
2.43 | Lovilec olj LO: Kompletna dobava in postavitev lovilca olj GRP fi 1000 mm, pokončne izvedbe, z by - passom z 10% pretokom, kot npr. AQUAREG S 30 bp 3 S-I-P, v skladu s standardom SIST EN 858-2 in razreda I. Skupna prostornina lovilca olj je 1.000 litrov, prostornina usedalnika je 300 litrov, prostornina lovilca olj je 375 litrov, nazivne velikosti 30 l/s, s pretokom 27 l/s skozi by-pass in 3 l/s skozi lovilec olj, pokončna izvedba, z vso potrebno opremo, vključno z vsemi potrebnimi gradbenimi deli za vgradnjo po navodilih dobavitelja, priklopom na kanalizacijo, izvedbo armiranobetonskega razbremenilnega obroča in venca kot ležišče za LTŽ pokrov ter LTŽ pokrov fi 600 mm, D400, kot npr. LIVAR art. 604A, po SIST EN 124-2. Lovilec olj je predviden pod vozno površino, zato se nad njim izvede AB razbremenilna plošča skladno z zahtevami dobavitelja. Zaradi lokacije v povozni površini in globine lovilca je potrebno le temu podaljšati odprtino za pokrov do kote novega terena. Lovilec olj je predviden na območju z visoko podtalnico, zato se pod njim izvede AB sidrna plošča skladno z zahtevami dobavitelja in statičnim preračunom vzgona. Opomba: Glej shemo vgradnje lovilca olj. Vgradnja lovilca olj zajema tudi vsa potrebna zemeljska dela, morebitno varovanje gradbene jame z razpiranjem in deponiranje odvečnega materiala. Vsa gradbena dela pri vgradnji lovilca olj morajo biti izvedena po navodilih proizvajalca, po vgradnji je iz lovilca potrebno očistiti material, ki se je nabral med izvajanjem del. | Lovilec olj LO: Kompletna dobava in postavitev lovilca olj GRP fi 1000 mm, pokončne izvedbe, z by - passom z 10% pretokom, kot npr. AQUAREG S 30 bp 3 S-I-P, v skladu s standardom SIST EN 858-2 in razreda I. Skupna prostornina lovilca olj je 1.000 litrov, prostornina usedalnika je 300 litrov, prostornina lovilca olj je 375 litrov, nazivne velikosti 30 l/s, s pretokom 27 l/s skozi by-pass in 3 l/s skozi lovilec olj, pokončna izvedba, z vso potrebno opremo, vključno z vsemi potrebnimi gradbenimi deli za vgradnjo po navodilih dobavitelja, priklopom na kanalizacijo, izvedbo armiranobetonskega razbremenilnega obroča in venca kot ležišče za LTŽ pokrov ter LTŽ pokrov fi 600 mm, D400, kot npr. LIVAR art. 604A, po SIST EN 124-2. Lovilec olj je predviden pod vozno površino, zato se nad njim izvede AB razbremenilna plošča skladno z zahtevami dobavitelja. Zaradi lokacije v povozni površini in globine lovilca je potrebno le temu podaljšati odprtino za pokrov do kote novega terena. Lovilec olj je predviden na The installation of the oil trap also includes any necessary earthworks, any protection of the construction pit by blasting and the deposit of excess material. All construction work for the installation of the oil interceptor must be carried out according to the manufacturer's instructions, and after installation, the interceptor must be cleaned of any material that has accumulated during the work.
| Betonski razbremenilni obroč in venec s pokrovom ne smejo biti temeljeni direktno na telo jaška, temveč na utrjeni zasip okrog jaška. Dobava, izdelava in vgradnja sidrne in razbremenilne AB plošče mora biti upoštevana v enotni ceni dobave in vgradnje lovilca olj. Dobava in vgradnja razbremenilnega obroča in venca mora biti upoštevana v enotni ceni dobave in vgradnje LTŽ pokrova (kot npr. sistem LIVAR ali enakovredno). | The concrete relief ring and wreath with cover shall not be founded directly on the manhole body, but on the hardened backfill around the manhole. The supply, manufacture and installation of the anchoring and relief AB slab shall be included in the unit price for the supply and installation of the oil trap. The supply and installation of the relief ring and wreath shall be included in the unit price for the supply and installation of the LTŽ cover (such as the LIVAR system or equivalent). | kpl | 1 |  | 0
2.44 | Lovilec olj LO1: Kompletna dobava in postavitev lovilca olj GRP fi 2000 mm, pokončne izvedbe, z by - passom z 10% pretokom, kot npr. AQUAREG S 200 bp 20 S-I-P z avtomatsko zaporo, v skladu s standardom SIST EN 858-2 in razreda I. Skupna prostornina lovilca olj je 4.950 litrov, prostornina usedalnika je 2.000 litrov, prostornina lovilca olj je 2.500 litrov, nazivne velikosti 200 l/s, s pretokom 180 l/s skozi by-pass in 20 l/s skozi lovilec olj, pokončna izvedba, z vso potrebno opremo, vključno z vsemi potrebnimi gradbenimi deli za vgradnjo po navodilih dobavitelja, priklopom na kanalizacijo, izvedbo armiranobetonskega razbremenilnega obroča in venca kot ležišče za jeklen pokrov ter jeklenega vroče cinkanega pokrova za zapolnitev, dimenzije 1000x1000 mm, D400, skladno s standardom EN 1253-4, kot npr. ACO pokrovi za zapolnitev Paving GS z asistenco za odpiranje ali enakovredno, pokrov se prilagodi glede na finalni tlak in vgradi v naklonu tlaka, skupaj z vsemi potrebnimi deli in materialom po navodilu proizvajalca. Dobava in vgradnja razbremenilnega obroča in venca mora biti upoštevana v enotni ceni dobave in vgradnje jeklenega pokrova. Lovilec olj je predviden pod vozno površino, zato se nad njim izvede AB razbremenilna plošča skladno z zahtevami dobavitelja. Zaradi lokacije v povozni površini in globine lovilca je potrebno le temu podaljšati odprtino za pokrov do kote novega terena. Lovilec olj je predviden na območju z visoko podtalnico, zato se pod njim izvede AB sidrna plošča skladno z zahtevami dobavitelja in statičnim preračunom vzgona. Opomba: Glej shemo vgradnje lovilca olj. | Lovilec olj LO1: Kompletna dobava in postavitev lovilca olj GRP fi 2000 mm, pokončne izvedbe, z by - passom z 10% pretokom, kot npr. AQUAREG S 200 bp 20 S-I-P z avtomatsko zaporo, v skladu s standardom SIST EN 858-2 in razreda I. Skupna prostornina lovilca olj je 4.950 litrov, prostornina usedalnika je 2.000 litrov, prostornina lovilca olj je 2.500 litrov, nazivne velikosti 200 l/s, s pretokom 180 l/s skozi by-pass in 20 l/s skozi lovilec olj, pokončna izvedba, z vso potrebno opremo, vključno z vsemi potrebnimi gradbenimi deli za vgradnjo po navodilih dobavitelja, priklopom na kanalizacijo, izvedbo armiranobetonskega razbremenilnega obroča in venca kot ležišče za jeklen pokrov ter jeklenega vroče cinkanega pokrova za zapolnitev, dimenzije 1000x1000 mm, D400, skladno s standardom EN 1253-4, kot npr. ACO pokrovi za zapolnitev Paving GS z asistenco za odpiranje ali enakovredno, pokrov se prilagodi glede na finalni tlak in vgradi v naklonu tlaka, skupaj z vsemi potrebnimi deli in materialom po navodilu pr The oil trap is provided under the carriageway surface, therefore an AB relief slab shall be constructed above it in accordance with the supplier's requirements. Due to its location in the carriageway surface and the depth of the oil trap, it is only necessary to extend the opening for the cover to the angle of the new ground. The oil trap is planned in an area with high water table, therefore an AB anchor plate shall be installed underneath the oil trap in accordance with the supplier's requirements and static buoyancy calculation. Note: See oil trap installation diagram.
| Vgradnja lovilca olj zajema tudi vsa potrebna zemeljska dela, morebitno varovanje gradbene jame z razpiranjem in deponiranje odvečnega materiala. Vsa gradbena dela pri vgradnji lovilca olj morajo biti izvedena po navodilih proizvajalca, po vgradnji je iz lovilca potrebno očistiti material, ki se je nabral med izvajanjem del. Betonski razbremenilni obroč in venec s pokrovom ne smejo biti temeljeni direktno na telo jaška, temveč na utrjeni zasip okrog jaška. Dobava, izdelava in vgradnja sidrne in razbremenilne AB plošče mora biti upoštevana v enotni ceni dobave in vgradnje lovilca olj. Dobava in vgradnja razbremenilnega obroča in venca mora biti upoštevana v enotni ceni dobave in vgradnje pokrova za zapolnitev s tlakom (kot npr. sistem ACO ali enakovredno) | The installation of the oil trap also includes any necessary earthworks, any protection of the construction pit by blasting and the deposit of excess material. All construction work for the installation of the oil interceptor must be carried out according to the manufacturer's instructions, and after installation, the interceptor must be cleaned of any material that has accumulated during the work. The concrete relief ring and the capped wreath shall not be founded directly on the body of the manhole, but on the hardened backfill around the manhole. The supply, manufacture and installation of the anchor and relief AB slab shall be included in the single price for the supply and installation of the oil trap. The supply and installation of the pressure relief ring and wreath shall be included in the single price for the supply and installation of the pressure fill cap (such as ACO or equivalent) | kos | 1 |  | 0
2.45 | Dobava in vgradnja modularnega sistema za zadrževanje in ponikanje padavinskih vod kot npr. ACO Stormbrixx HD. Sistem sestoji iz posameznih PP blokov ali blokov drugega enakovrednega materiala, bloki osnovnih dimenzij: Š x D x V = 60 x 120 x 61 cm, zlaganje v 1-nivojsko vgradnjo (H = 61 cm). Modularni sistem sestoji iz dveh delov, ki sta med seboj z drenažno cevjo povezana v en sistem, ki mora vsebovati - omogočati: - najmanj 95% skupnega uporabnega volumna; - integrirane kontrolne bloke in vertikalne kontrolne priključke za priključke vtokov, kontrolo, vzdrževanje in čiščenje sistema, s sistemskimi LTŽ pokrovi DN400 (min. D400) z odprtinami za odzračevanje; - vertikalne kontrolne priključke DN150 za kontrolo sistema, z LTŽ pokrovi DN160 (s cevmi DN150 za povišanje); - integriran inšpekcijski tunel minimalnega preseka Š×V=12 × 50 cm, za premikanje kamere in opreme za čiščenje ter možnost vizualne kontrole enega odseka sistema brez pregrad za enostavno kontrolo s kamero; - adapterje za priključitev vtočnih cevi DN250 in povezovalne cevi DN315; - možnost spajanja posameznih elementov sistema v smislu zidarskega preklopa, sestavljanje čvrstih vezi med posameznimi bloki istega sloja; - minimalna tlačna trdnost 420 kN/m2; | Supply and installation of a modular rainwater retention and attenuation system such as ACO Stormbrixx HD. The system consists of individual PP blocks or blocks of other equivalent material, basic dimensions W x D x H = 60 x 120 x 61 cm, stackable in a 1 level installation (H = 61 cm). A modular system consists of two parts connected by a drainage pipe to form a single system, which must contain - enable: - at least 95% of the total usable volume; - integrated control blocks and vertical control connections for inlet connections, control, maintenance and cleaning of the system, with system LTŽ covers DN400 (min. D400) with vent holes; - vertical control connections DN150 for system control, with LTŽ covers DN160 (with DN150 pipes for elevation); - an integrated inspection tunnel with a minimum cross-section of W×H=12 × 50 cm, for the movement of the camera and cleaning equipment and the possibility to visually inspect one section of the system without barriers for easy camera inspection; - adaptors for connecting the DN250 inlet pipes and the DN315 connection pipe; - the possibility of joining the individual elements of the system in terms of masonry overlap, forming strong bonds between individual blocks of the same layer; - minimum compressive strength 420 kN/m2;
| Minimalna dimenzija prvega dela sistema mora biti Š × D × V = 2,40 × 75,60 × 0,60 m, minimalna dimenzija drugega dela sistema mora biti Š × D × V = 3,00 × 20,40 × 0,60 m, sistem mora imeti minimalni zadrževalni volumen 75 m³. Postavka vključuje dobavo in vgradnjo kompletne sistemske rešitve - potrebnih blokov, čelnih sten, pokrovov, vtočnih, varnostnih in revizijskih elementov s povišanji in pokrove revizijskih elementov, skupaj z vsemi spojnimi in montažnimi elementi, razbremenilnimi obroči in ostalo opremo potrebno za delovanje sistema. Ponikovalno polje se ovije v prepustni zaščitni geotekstil. V postavki mora biti vključena nabava in vgradnja netkanega PE geotekstila za ovijanje ponikovalnega sistema sledečih karakteristik: min. gostota 200 gr/m2, min. debelina 1,9mm, odpornosti na CBR preboj (po EN ISO 12236) ≥ 1,5kN (razred robustnosti GRC 3). Preklopi na spojih geotekstila morajo biti minimalno 30 cm do 50 cm. Vgradnja in zasipanje se vrši po navodilih proizvajalca. V ceno je potrebno vključiti dodatno preveritev ponikovalne sposobnosti zemljine po zamenjavi temeljnih tal in pripravi terena za vgradnjo (faktor propustnosti tal / koeficient ponikanja) na mikrolokaciji zadrževalnega sistema, ki jo je potrebno izvesti pred vgradnjo sistema na dnu predvidenega polja. O izvedeni meritvi je potrebno obvestiti odgovornega projektanta in odgovornega nadzornika. | The minimum dimension of the first part of the system shall be W × D × H = 2,40 × 75,60 × 0,60 m, the minimum dimension of the second part of the system shall be W × D × H = 3,00 × 20,40 × 0,60 m and the system shall have a minimum containment volume of 75 m³. Postavka vključuje dobavo in vgradnjo kompletne sistemske rešitve - potrebnih blokov, čelnih sten, pokrovov, vtočnih, varnostnih in revizijskih elementov s povišanji in pokrove revizijskih elementov, skupaj z vsemi spojnimi in montažnimi elementi, razbremenilnimi obroči in ostalo opremo potrebno za delovanje sistema. Ponikovalno polje se ovije v prepustni zaščitni geotekstil. V postavki mora biti vključena nabava in vgradnja netkanega PE geotekstila za ovijanje ponikovalnega sistema sledečih karakteristik: min. gostota 200 gr/m2, min. debelina 1,9mm, odpornosti na CBR preboj (po EN ISO 12236) ≥ 1,5kN (razred robustnosti GRC 3). Preklopi na spojih geotekstila morajo biti minimalno 30 cm do 50 cm. Installation and backfilling shall be carried out according to the manufacturer's instructions. The price shall include an additional check of the water absorption capacity of the soil after replacement of the subsoil and preparation of the ground for installation (soil permeability factor / water absorption coefficient) at the micro-location of the retention system, to be carried out prior to the installation of the system at the bottom of the intended field. The responsible designer and the responsible supervisor shall be informed of the measurements carried out and shall be informed of the results of the measurements. | kpl | 1 |  | 0
2.46 | Kompletna izvedba za cel kanalizacijski sistem: ~ geodetski posnetek osi, premera in višine temena cevi pred zasutjem, ~ geodetski posnetek pozicij in višin pokrovov, dna, vtokov ter iztokov na revizijskih jaških in ostalih elementih sistema pred zasutjem, ~ vnos tras v zbirno karto komunalnih vodov in v vzdolžni profil, ~ predaja naročniku v grafični in digitalni obliki kot podloga za izdelavo projekta izvedenih del (PID). | Complete implementation for the entire sewerage system: ~ a geodetic survey of the axis, diameter and elevation of the pipe before backfilling, ~ a geodetic survey of the positions and elevations of covers, bottoms, inlets and outlets at manholes and other system elements prior to backfilling, ~ entry of the routes in the summary map of the utility lines and in the longitudinal profile, ~ handed over to the client in graphic and digital form as a basis for the preparation of the detailed design (PID). | kpl | 1 |  | 0
2.47 | Razna pomoč pri gradbeno-obrtniških, elektro inštalaterskih in strojnih delih. ~ KV delavec | Miscellaneous assistance with building, electrical, plumbing and mechanical work. ~ KV worker | ur | 200 |  | 0
2.48 | Razna pomoč pri gradbeno-obrtniških, elektro inštalaterskih in strojnih delih. ~ PK delavec | Miscellaneous assistance with building, electrical, plumbing and mechanical work. ~ PK worker | ur | 200 |  | 0
| METEORNA KANALIZACIJA | METEORIC SEWERAGE |  |  |  | 0

## 2.6.2.3_Vodovod
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | KOMUNALNI PRIKLJUČKI OBJEKTA | UTILITY CONNECTIONS
2.6.2 | GRADBENA DELA | CONSTRUCTION WORKS
2.6.2.3 | VODOVODNI PRIKLJUČEK | WATER CONNECTION |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
3 | VODOVODNI PRIKLJUČEK | WATER CONNECTION
| OPOMBE: Pri izdelavi ponudbe upoštevati pripombe, iz poglavja 0.1 UVOD-STP Pri izdelavi ponudbe upoštevati pripombe, iz poglavja 0.2 UVOD - DGNB in dokument: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme. | NOTES: Take into account the comments made in section 0.1 INTRODUCTION-STP in the preparation of the offer When preparing the tender, take into account the comments made in Section 0.2 INTRODUCTION - DGNB and the document DGNB Quality Grades for Materials, Elements and Equipment.
| Pred pričetkom del je potrebno: ~ na licu mesta preveriti vse dimenzije navedene v načrtu in morebitna odstopanja prilagoditi dejanskemu stanju na terenu ~ vsa neskladja pravočasno / pred izvedbo uskladiti z vodjo projektiranja in ostalimi projektanti ~ vse izvedbe, materiale, obdelave in barve uskladiti s projektanti ~ pri vseh vidnih izvedbah je pred izvedbo potrebno delavniško uskladiti detajle ter jih predložiti projektantu v potrditev | Before starting work, it is necessary to: ~ on-site verification of all dimensions indicated in the plan and adjustment of any deviations to the actual situation on the ground ~ reconcile any discrepancies with the design manager and other designers in a timely manner / prior to implementation ~ all designs, materials, finishes and colours to be coordinated with the designers ~ all visible works shall be subject to workshop coordination of details and submitted to the designer for approval prior to implementation
| Osnova za izvedbo popisa za zemeljska dela je geodetski posnetek obstoječega stanja, načrti objektov, zunanje ureditve in načrti komunalne infra strukture, tehnično poročilo ter navodila in zahteve dobaviteljev za izvedbo in vgradnjo posameznih delov opreme. | The basis for the inventory for the earthworks is the existing geodetic survey, the building plans, the external layout plans and the plans of the utility infrastructure, the technical report and the instructions and requirements of the suppliers for the execution and installation of the individual pieces of equipment.
| Pri izvedbi vseh zemeljskih del mora biti prisoten geomehanski nadzor, ki preveri ustreznost predvidenih ukrepov, ustreznost homogenih tal, skladnost privzetih parametrov v PZI z dejanskim stanjem na terenu in geološko-geomehanskih raziskav iz Geološko-geotehničnega poročila (IRGO Consulting d.o.o., poročilo št. 3009776, januar 2021). | During the execution of all earthworks, geomechanical supervision must be present to verify the adequacy of the planned measures, the adequacy of the homogeneous soils, the conformity of the default parameters in the PIP with the actual situation on the ground and the geological-geomechanical investigations from the Geological-Geotechnical Report (IRGO Consulting d.o.o., Report No. 3009776, January 2021).
| V kolikor bi se v času izvajanja zemeljskih del izkazalo, da je dejansko stanje drugačno od predvidenega, geomehanik takoj obvesti projektanta in se pristopu k iskanju projektnih rešitev, ki ustrezajo dejanskemu stanju. Vsa odstopanja od PZI morata pred izvedbo pisno potrditi geomehanik in projektant. | Should the actual situation prove to be different from the intended situation during the execution of the earthworks, the geomechanic shall immediately inform the designer and the designer shall be approached to find design solutions that correspond to the actual situation. Any deviations from the PIP shall be confirmed in writing by the geomechanic and the designer prior to execution.
| Primernost izkopanega materiala za zasip ugotovi geomehanik na licu mesta. | The suitability of the excavated material for backfill shall be determined by the on-site geomechanist.
| Morebitne začasne deponije zemeljskega materijala in potrebne transporte v zvezi s tem je potrebno upoštevati v enotnih cenah. | Any temporary deposits of earth material and the necessary transport in this connection must be taken into account in the uniform prices.
| Izbrana mehanizacija mora omogočati upoštevanje varnostnih ukrepov. | The machinery chosen must be able to comply with safety precautions.
| Vsa izkopna dela in transporti izkopnih materialov se obračunajo po prostornini zemljine v raščenem stanju. Vsa nasipna dela se obračunajo po prostornini zemljine v vgrajenem stanju. Obračun količin se izvede po posnetih profilih pred in po nasipavanju. | All excavation work and transport of excavation materials shall be accounted for by the volume of soil in the loosened state. All embankment work shall be accounted for by the volume of soil in the embedded state. Quantities shall be accounted for on the basis of recorded profiles before and after embankment.
| Utrjevanje z nabijanjem do predpisane zbitosti po projektu statike. | Curing by ramming to the specified compaction according to the structural design.
| Splošne opombe za betonske konstrukcije; ~ vsi vgrajeni betoni morajo izpolnjevati zahteve SIST EN 206-1, SIST EN 1026 in SIST EN 1992-1-1 ter NAC dodatki; ~ za vse betonske konstrukcije velja zahteva za 2. izvedbeni razred in 1. tolerančni razred po SIST EN 13670 in nacionalnem dodatku, kar je potrebno upoštevati pri pripravi in izvajanju programa kontrole kakovosti in projekta betona; ~ pred nadaljevanjem del morajo biti stiki očiščeni, navlaženi in premazani s sredstvom za povečanje sprijemnosti ~ debelino krovnega sloja je potrebno kontrolirati z merjenjem ~ na proste robove vidnih površin se v opaž vgradi trikotne letve; | General notes for concrete structures; ~ All concrete installed shall comply with the requirements of SIST EN 206-1, SIST EN 1026 and SIST EN 1992-1-1 and NAC Appendices; ~ all concrete structures are subject to the requirement for performance class 2 and tolerance class 1 according to SIST EN 13670 and the National Supplement, which must be taken into account in the preparation and implementation of the quality control programme and the concrete design; ~ joints must be cleaned, moistened and coated with an adhesion promoter before work proceeds ~ the thickness of the deck layer must be controlled by measurement ~ triangular battens shall be installed in the formwork at the free edges of the visible surfaces;
| Splošne opombe za betonske konstrukcije; ~ za vse vidne površine brez posebnih arhitekturnih oz. drugih zahtev in za nevidne površine veljajo zahteve za obdelavo površin po SIST EN 13670 in nacionalnem dodatku, kar je potrebno upoštevati pri izbiri opažev: - vidne površine: • opažene vidne površine: enostavno – VB2, • neopažene vidne površine (tabela F4 v SIST EN 13670 in tabela N5 v nac, dodatku): enostavna - nevidne površine: • opažene nevidne površine: osnovna – VB0, • neopažene nevidne površine (tabela F4 v SIST EN 13670 in tabela N5 v nac. dodatku): osnovna ~ za izvedbo zaščitnih slojev glej armaturni načrt; | General notes for concrete structures; ~ all visible surfaces without special architectural or other requirements and invisible surfaces are subject to the surface treatment requirements of SIST EN 13670 and the National Supplement, which must be taken into account when selecting the formwork: - visible surfaces: - Visible surfaces observed: easy - VB2, - Unnoticed visible surfaces (Table F4 in SIST EN 13670 and Table N5 in the Appendix): simple - invisible surfaces: - observed invisible surfaces: basic - VB0, - Unnoticed invisible surfaces (Table F4 in SIST EN 13670 and Table N5 in the National Appendix): basic ~ see reinforcement plan for the design of the protective layers;
| Pri izvedbi je potrebno upoštevati načrte, kjer so prikazane trase inštalacijskih vodov ter pred vgradnjo upoštevati vse elemente, ki so zajeti v elektro in strojnem načrtu. | The plans showing the routes of the installation lines must be followed and all the elements included in the electrical and mechanical plans must be taken into account before installation.
| V primeru nejasnosti, spremenjenih pogojev ali odstopanja od projekta se je potrebno posvetovati s projektantom. | In case of any ambiguity, changed conditions or deviation from the design, the designer should be consulted.
| Med izvedbo gradbenih posegov mora biti zagotovljen strokovni nadzor, ki bo zagotavljal skladnost gradnje s pogoji iz gradbenega dovoljenja ter kvaliteto izvedenih del v skladu z gradbenimi predpisi. | During the construction works, professional supervision must be provided to ensure that the construction complies with the conditions of the building permit and that the quality of the works is in accordance with the building regulations.
| Upoštevati vse vertikalne in horizontalne transporte. | All vertical and horizontal transports must be taken into account.
| Potrebno je izvajati sprotno čiščenje. | Ongoing cleaning is necessary.
3.1 | Izkop jarka v zemljišču III.ktg. za vodovod, z nakladanjem na kamion in odvozom na začasno deponijo, do ponovne vgradnje po izvedbi novih del. | Excavation of a trench in land III.ktg. for the water supply, with loading onto a lorry and removal to a temporary landfill site, until re-installation after the new works have been carried out.
a. | ~strojni izkop (90%) | ~machine excavation (90%) | m3 | 128 |  | 0
b. | ~ročni izkop (10%) | ~hand excavation (10%) | m3 | 14 |  | 0
3.2 | Planiranje in utrjevanje dna izkopa jarkov pred izvedbo vodovodne povezave, v predpisanem naklonu in do predpisane utrditve po projektu. | Plan and consolidate the bottom of the trench excavation prior to the water connection, at the prescribed gradient and to the prescribed consolidation as per the design. | m2 | 26 |  | 0
3.3 | Kompletna dobava in vgradnja peska granulacije 4/8 mm za izdelavo peščene posteljice za polaganje cevi, debeline 10 cm in obsipa višine 30 cm nad cevjo, skladno s standardom SIST EN 1610 z utrjevanjem do zbitosti predpisane v projektu, skupaj z vsemi deli in materialom, po navodilu izvajalca vodovoda. | Complete supply and installation of 4/8 mm granular sand for the construction of a sand bed for pipe laying, 10 cm thick and 30 cm high above the pipe, in accordance with SIST EN 1610, with consolidation to the compactness specified in the design, together with all works and materials, as instructed by the water supply contractor. | m3 | 8 |  | 0
3.4 | Kompletna dobava in vgradnja jeklene zaščitne cevi fi 159 mm x 4,5 mm za vodovod, v predpisanem naklonu, skupaj z vsemi deli in materialom, po navodilu izvajalca vodovoda. | Complete supply and installation of a steel protection pipe fi 159 mm x 4,5 mm for the water main, at the prescribed gradient, together with all works and materials, as directed by the water main contractor. | m | 6 |  | 0
3.5 | Kompletna izvedba obbetoniranja različnih elementov vodovodne napeljave (kolena, zračniki, kape, ...) s pustim betonom na pravo višino - prilagoditev predvideni niveleti predvidene zunanje ureditve, skupaj z vsemi potrebnimi deli in materialom, po navodilu izvajalca vodovoda. | Complete concreting of the various elements of the water supply system (elbows, vents, caps, etc.) with lean concrete to the correct height - adjustment to the intended level of the planned external layout, together with all necessary work and materials, as instructed by the water supply contractor. | kpl | 3 |  | 0
3.6 | Zasip za vodovodom z izkopanim materialom deponiranim na začasni deponiji, komplet z nakladanjem in dovozom, raztiranjem in planiranjem ter utrjevanjem po plasteh od 20 do 30 cm s sprotnim komprimiranjem do predpisane utrditve po projektu. | Backfill behind the water main with excavated material deposited in a temporary landfill, complete with loading and access, grading and grading, and consolidation in layers of 20 to 30 cm with continuous compaction to the required design consolidation. | m3 | 134 |  | 0
3.7 | Odvoz izkopanega materiala na stalno deponijo, ki si jo priskrbi izvajalec, katero si izvajalec zagotovi sam ter plačilom taks na deponiji. | Removal of excavated material to a permanent landfill to be provided by the Contractor, which shall be provided by the Contractor, and payment of landfill charges. | m3 | 8 |  | 0
3.8 | Dobava in polaganje signalnega opozorilnega traku nad novo položenim vodovodom iz PE folije modre barve, z natisnjenim tekstom "Pozor vodovod", s kovinskim vložkom. Polaganje cca. 30 cm nad temenom cevi. | Supply and installation of a signal warning strip above a newly laid water main, made of blue PE foil with the text "Caution water main" printed on it, with a metal insert. Installation approx. 30 cm above the top of the pipe. | m | 42 |  | 0
3.9 | Kompletna izvedba križanj novega vodovoda z obstoječimi komunalnimi vodi, skupaj z vsemi potrebnimi deli in materialom, skladno z upoštevanjem načina izvedbe in vseh pogojev po navodilih upravljalca komunalnega voda. | Complete execution of the crossings of the new water main with the existing utility lines, including all necessary works and materials, in accordance with the method of execution and all conditions as specified by the utility line manager. | kpl | 3 |  | 0
3.10 | Razna pomoč pri gradbeno-obrtniških, elektro inštalaterskih in strojnih delih. ~ KV delavec | Miscellaneous assistance with building, electrical, plumbing and mechanical work. ~ KV worker | ur | 20 |  | 0
3.11 | Razna pomoč pri gradbeno-obrtniških, elektro inštalaterskih in strojnih delih. ~ PK delavec | Miscellaneous assistance with building, electrical, plumbing and mechanical work. ~ PK worker | ur | 20 |  | 0
| VODOVODNI PRIKLJUČEK | WATER CONNECTION |  |  |  | 0

## 2.6.2.4_Plin
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | KOMUNALNI PRIKLJUČKI OBJEKTA | UTILITY CONNECTIONS
2.6.2 | GRADBENA DELA | CONSTRUCTION WORKS
2.6.2.4 | PLINSKI PRIKLJUČEK | GAS CONNECTION |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
4 | PLINSKI PRIKLJUČEK | GAS CONNECTION
| OPOMBE: Pri izdelavi ponudbe upoštevati pripombe, iz poglavja 0.1 UVOD-STP Pri izdelavi ponudbe upoštevati pripombe, iz poglavja 0.2 UVOD - DGNB in dokument: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme. | NOTES: Take into account the comments made in section 0.1 INTRODUCTION-STP in the preparation of the offer When preparing the tender, take into account the comments made in Section 0.2 INTRODUCTION - DGNB and the document DGNB Quality Grades for Materials, Elements and Equipment.
| Pred pričetkom del je potrebno: ~ na licu mesta preveriti vse dimenzije navedene v načrtu in morebitna odstopanja prilagoditi dejanskemu stanju na terenu ~ vsa neskladja pravočasno / pred izvedbo uskladiti z vodjo projektiranja in ostalimi projektanti ~ vse izvedbe, materiale, obdelave in barve uskladiti s projektanti ~ pri vseh vidnih izvedbah je pred izvedbo potrebno delavniško uskladiti detajle ter jih predložiti projektantu v potrditev | Before starting work, it is necessary to: ~ on-site verification of all dimensions indicated in the plan and adjustment of any deviations to the actual situation on the ground ~ reconcile any discrepancies with the design manager and other designers in a timely manner / prior to implementation ~ all designs, materials, finishes and colours to be coordinated with the designers ~ all visible works shall be subject to workshop coordination of details and submitted to the designer for approval prior to implementation
| Osnova za izvedbo popisa za zemeljska dela je geodetski posnetek obstoječega stanja, načrti objektov, zunanje ureditve in načrti komunalne infra strukture, tehnično poročilo ter navodila in zahteve dobaviteljev za izvedbo in vgradnjo posameznih delov opreme. | The basis for the inventory for the earthworks is the existing geodetic survey, the building plans, the external layout plans and the plans of the utility infrastructure, the technical report and the instructions and requirements of the suppliers for the execution and installation of the individual pieces of equipment.
| Pri izvedbi vseh zemeljskih del mora biti prisoten geomehanski nadzor, ki preveri ustreznost predvidenih ukrepov, ustreznost homogenih tal, skladnost privzetih parametrov v PZI z dejanskim stanjem na terenu in geološko-geomehanskih raziskav iz Geološko-geotehničnega poročila (IRGO Consulting d.o.o., poročilo št. 3009776, januar 2021). | During the execution of all earthworks, geomechanical supervision must be present to verify the adequacy of the planned measures, the adequacy of the homogeneous soils, the conformity of the default parameters in the PIP with the actual situation on the ground and the geological-geomechanical investigations from the Geological-Geotechnical Report (IRGO Consulting d.o.o., Report No. 3009776, January 2021).
| V kolikor bi se v času izvajanja zemeljskih del izkazalo, da je dejansko stanje drugačno od predvidenega, geomehanik takoj obvesti projektanta in se pristopu k iskanju projektnih rešitev, ki ustrezajo dejanskemu stanju. Vsa odstopanja od PZI morata pred izvedbo pisno potrditi geomehanik in projektant. | Should the actual situation prove to be different from the intended situation during the execution of the earthworks, the geomechanic shall immediately inform the designer and the designer shall be approached to find design solutions that correspond to the actual situation. Any deviations from the PIP shall be confirmed in writing by the geomechanic and the designer prior to execution.
| Primernost izkopanega materiala za zasip ugotovi geomehanik na licu mesta. | The suitability of the excavated material for backfill shall be determined by the on-site geomechanist.
| Morebitne začasne deponije zemeljskega materijala in potrebne transporte v zvezi s tem je potrebno upoštevati v enotnih cenah. | Any temporary deposits of earth material and the necessary transport in this respect must be taken into account in the uniform prices.
| Izbrana mehanizacija mora omogočati upoštevanje varnostnih ukrepov. | The machinery chosen must be able to comply with safety precautions.
| Vsa izkopna dela in transporti izkopnih materialov se obračunajo po prostornini zemljine v raščenem stanju. Vsa nasipna dela se obračunajo po prostornini zemljine v vgrajenem stanju. Obračun količin se izvede po posnetih profilih pred in po nasipavanju. | All excavation work and transport of excavation materials shall be accounted for by the volume of soil in the loosened state. All embankment work shall be accounted for by the volume of soil in the as-built state. Quantities shall be accounted for on the basis of the recorded profiles before and after embankment.
| Utrjevanje z nabijanjem do predpisane zbitosti po projektu statike. | Curing by ramming to the specified compaction according to the structural design.
| Splošne opombe za betonske konstrukcije; ~ vsi vgrajeni betoni morajo izpolnjevati zahteve SIST EN 206-1, SIST EN 1026 in SIST EN 1992-1-1 ter NAC dodatki; ~ za vse betonske konstrukcije velja zahteva za 2. izvedbeni razred in 1. tolerančni razred po SIST EN 13670 in nacionalnem dodatku, kar je potrebno upoštevati pri pripravi in izvajanju programa kontrole kakovosti in projekta betona; ~ pred nadaljevanjem del morajo biti stiki očiščeni, navlaženi in premazani s sredstvom za povečanje sprijemnosti ~ debelino krovnega sloja je potrebno kontrolirati z merjenjem ~ na proste robove vidnih površin se v opaž vgradi trikotne letve; | General notes for concrete structures; ~ All concrete installed shall comply with the requirements of SIST EN 206-1, SIST EN 1026 and SIST EN 1992-1-1 and NAC Appendices; ~ all concrete structures are subject to the requirement for Performance Class 2 and Tolerance Class 1 in accordance with SIST EN 13670 and the National Supplement, which must be taken into account in the preparation and implementation of the quality control programme and the concrete design; ~ joints must be cleaned, moistened and coated with an adhesion promoter before work proceeds ~ the thickness of the deck layer must be controlled by measuring ~ triangular battens shall be installed in the formwork at the free edges of the visible surfaces;
| Splošne opombe za betonske konstrukcije; ~ za vse vidne površine brez posebnih arhitekturnih oz. drugih zahtev in za nevidne površine veljajo zahteve za obdelavo površin po SIST EN 13670 in nacionalnem dodatku, kar je potrebno upoštevati pri izbiri opažev: - vidne površine: • opažene vidne površine: enostavno – VB2, • neopažene vidne površine (tabela F4 v SIST EN 13670 in tabela N5 v nac, dodatku): enostavna - nevidne površine: • opažene nevidne površine: osnovna – VB0, • neopažene nevidne površine (tabela F4 v SIST EN 13670 in tabela N5 v nac. dodatku): osnovna ~ za izvedbo zaščitnih slojev glej armaturni načrt; | General notes for concrete structures; ~ all visible surfaces without special architectural or other requirements and invisible surfaces are subject to the surface treatment requirements of SIST EN 13670 and the National Supplement, which must be taken into account when selecting the formwork: - visible surfaces: - Visible surfaces observed: easy - VB2, - Unnoticed visible surfaces (Table F4 in SIST EN 13670 and Table N5 in the Appendix): simple - invisible surfaces: - observed invisible surfaces: basic - VB0, - Unnoticed invisible surfaces (Table F4 in SIST EN 13670 and Table N5 in the National Appendix): basic ~ see reinforcement plan for the design of the protective layers;
| Pri izvedbi je potrebno upoštevati načrte, kjer so prikazane trase inštalacijskih vodov ter pred vgradnjo upoštevati vse elemente, ki so zajeti v elektro in strojnem načrtu. | The plans showing the routes of the installation lines must be followed and all the elements included in the electrical and mechanical plans must be taken into account before installation.
| V primeru nejasnosti, spremenjenih pogojev ali odstopanja od projekta se je potrebno posvetovati s projektantom. | In case of any ambiguity, changed conditions or deviation from the design, the designer should be consulted.
| Med izvedbo gradbenih posegov mora biti zagotovljen strokovni nadzor, ki bo zagotavljal skladnost gradnje s pogoji iz gradbenega dovoljenja ter kvaliteto izvedenih del v skladu z gradbenimi predpisi. | During the construction works, professional supervision must be provided to ensure that the construction complies with the conditions of the building permit and that the quality of the works is in accordance with the building regulations.
| Upoštevati vse vertikalne in horizontalne transporte. | All vertical and horizontal transports must be taken into account.
| Potrebno je izvajati sprotno čiščenje. | Ongoing cleaning is necessary.
4.1 | Izkop jarka v zemljišču III.ktg. za plinovod, z nakladanjem na kamion in odvozom na začasno deponijo, do ponovne vgradnje po izvedbi novih del. | Excavation of a trench in land III.ktg. for the pipeline, with loading onto a lorry and removal to a temporary landfill site, until re-installation after the new works have been carried out.
a. | ~strojni izkop (90%) | ~machine excavation (90%) | m3 | 172 |  | 0
b. | ~ročni izkop (10%) | ~hand excavation (10%) | m3 | 19 |  | 0
4.2 | Planiranje in utrjevanje dna izkopa jarkov pred izvedbo plinovoda, v predpisanem naklonu in do predpisane utrditve po projektu. | Plan and consolidate the trench bottom prior to the pipeline, at the prescribed gradient and to the prescribed consolidation as per the design. | m2 | 30 |  | 0
4.3 | Kompletna dobava in vgradnja peska granulacije 4/8 mm za izdelavo peščene posteljice za polaganje cevi, debeline 10 cm in obsipa višine 30 cm nad cevjo, skladno s standardom SIST EN 1610 z utrjevanjem do zbitosti predpisane v projektu, skupaj z vsemi deli in materialom, po navodilu izvajalca plinovoda. | Complete supply and installation of 4/8 mm granular sand to form a sand bed for pipe laying, 10 cm thick and 30 cm high above the pipe, in accordance with SIST EN 1610, with consolidation to the compactness specified in the design, together with all works and materials, as directed by the pipeline contractor. | m3 | 11 |  | 0
4.4 | Kompletna dobava in vgradnja jeklene zaščitne cevi fi 159 mm x 4,5 mm za plinovod, v predpisanem naklonu, skupaj z vsemi deli in materialom, po navodilu izvajalca plinovoda. | Complete supply and installation of a steel protection pipe fi 159 mm x 4,5 mm for the gas pipeline, at the prescribed inclination, together with all works and materials, as directed by the pipeline contractor. | m | 6 |  | 0
4.5 | Kompletna izvedba obbetoniranja različnih elementov plinovoda - kolena s pustim betonom na pravo višino - prilagoditev predvideni niveleti predvidene zunanje ureditve, skupaj z vsemi potrebnimi deli in materialom, po navodilu izvajalca plinovoda. | Complete concreting of the various elements of the pipeline - knees with lean concrete to the correct height - adjustment to the intended level of the planned external layout, together with all necessary works and materials, as instructed by the pipeline contractor. | kpl | 2 |  | 0
4.6 | Zasip za plinovodom z izkopanim materialom deponiranim na začasni deponiji, komplet z nakladanjem in dovozom, raztiranjem in planiranjem ter utrjevanjem po plasteh od 20 do 30 cm s sprotnim komprimiranjem do predpisane utrditve po projektu. | Backfill behind the pipeline with excavated material deposited in the temporary landfill, complete with loading and access, grading and grading, and consolidation in layers of 20 to 30 cm with continuous compaction to the required design consolidation. | m3 | 180 |  | 0
4.7 | Odvoz izkopanega materiala na stalno deponijo, ki si jo priskrbi izvajalec, katero si izvajalec zagotovi sam ter plačilom taks na deponiji. | Removal of excavated material to a permanent landfill to be provided by the Contractor, which shall be provided by the Contractor, and payment of landfill charges. | m3 | 11 |  | 0
4.8 | Dobava in polaganje PVC opozorilnega traku, položenega v zasip nad cevmi. | Supply and installation of PVC warning tape laid in the backfill above the pipes. | m | 50 |  | 0
4.9 | Kompletna izvedba križanj novega plinovoda z obstoječimi komunalnimi vodi, skupaj z vsemi potrebnimi deli in materialom, skladno z upoštevanjem načina izvedbe in vseh pogojev po navodilih upravljalca komunalnega voda. | Complete execution of the crossings of the new gas pipeline with the existing utility lines, including all necessary works and materials, in accordance with the method of execution and all conditions as specified by the utility line manager. | kpl | 3 |  | 0
4.10 | Razna pomoč pri gradbeno-obrtniških, elektro inštalaterskih in strojnih delih. ~ KV delavec | Miscellaneous assistance with building, electrical, plumbing and mechanical work. ~ KV worker | ur | 30 |  | 0
4.11 | Razna pomoč pri gradbeno-obrtniških, elektro inštalaterskih in strojnih delih. ~ PK delavec | Miscellaneous assistance with building, electrical, plumbing and mechanical work. ~ PK worker | ur | 30 |  | 0
| PLINSKI PRIKLJUČEK | GAS CONNECTION |  |  |  | 0

## 2.6.2.5_SN
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | KOMUNALNI PRIKLJUČKI OBJEKTA | UTILITY CONNECTIONS
2.6.2 | GRADBENA DELA | CONSTRUCTION WORKS
2.6.2.5 | KABELSKA KANALIZACIJA - SN | CABLE DUCT - SN |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
5 | KABELSKA KANALIZACIJA - SN | CABLE DUCT - SN
| OPOMBE: Pri izdelavi ponudbe upoštevati pripombe, iz poglavja 0.1 UVOD-STP Pri izdelavi ponudbe upoštevati pripombe, iz poglavja 0.2 UVOD - DGNB in dokument: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme. | NOTES: Take into account the comments made in section 0.1 INTRODUCTION-STP in the preparation of the offer When preparing the tender, take into account the comments made in Section 0.2 INTRODUCTION - DGNB and the document DGNB Quality Grades for Materials, Elements and Equipment.
| Pred pričetkom del je potrebno: ~ na licu mesta preveriti vse dimenzije navedene v načrtu in morebitna odstopanja prilagoditi dejanskemu stanju na terenu ~ vsa neskladja pravočasno / pred izvedbo uskladiti z vodjo projektiranja in ostalimi projektanti ~ vse izvedbe, materiale, obdelave in barve uskladiti s projektanti ~ pri vseh vidnih izvedbah je pred izvedbo potrebno delavniško uskladiti detajle ter jih predložiti projektantu v potrditev | Before starting work, it is necessary to: ~ on-site verification of all dimensions indicated in the plan and adjustment of any deviations to the actual situation on the ground ~ reconcile any discrepancies with the design manager and other designers in a timely manner / prior to implementation ~ all designs, materials, finishes and colours to be coordinated with the designers ~ all visible works shall be subject to workshop coordination of details and submitted to the designer for approval prior to implementation
| Osnova za izvedbo popisa za zemeljska dela je geodetski posnetek obstoječega stanja, načrti objektov, zunanje ureditve in načrti komunalne infra strukture, tehnično poročilo ter navodila in zahteve dobaviteljev za izvedbo in vgradnjo posameznih delov opreme. | The basis for the inventory for the earthworks is the existing geodetic survey, the building plans, the external layout plans and the plans of the utility infrastructure, the technical report and the instructions and requirements of the suppliers for the execution and installation of the individual pieces of equipment.
| Pri izvedbi vseh zemeljskih del mora biti prisoten geomehanski nadzor, ki preveri ustreznost predvidenih ukrepov, ustreznost homogenih tal, skladnost privzetih parametrov v PZI z dejanskim stanjem na terenu in geološko-geomehanskih raziskav iz Geološko-geotehničnega poročila (IRGO Consulting d.o.o., poročilo št. 3009776, januar 2021). | During the execution of all earthworks, geomechanical supervision must be present to verify the adequacy of the planned measures, the adequacy of the homogeneous soils, the conformity of the default parameters in the PIP with the actual situation on the ground and the geological-geomechanical investigations from the Geological-Geotechnical Report (IRGO Consulting d.o.o., Report No. 3009776, January 2021).
| V kolikor bi se v času izvajanja zemeljskih del izkazalo, da je dejansko stanje drugačno od predvidenega, geomehanik takoj obvesti projektanta in se pristopu k iskanju projektnih rešitev, ki ustrezajo dejanskemu stanju. Vsa odstopanja od PZI morata pred izvedbo pisno potrditi geomehanik in projektant. | Should the actual situation prove to be different from the intended situation during the execution of the earthworks, the geomechanic shall immediately inform the designer and the designer shall be approached to find design solutions that correspond to the actual situation. Any deviations from the PIP shall be confirmed in writing by the geomechanic and the designer prior to execution.
| Primernost izkopanega materiala za zasip ugotovi geomehanik na licu mesta. | The suitability of the excavated material for backfill shall be determined by the on-site geomechanist.
| Morebitne začasne deponije zemeljskega materijala in potrebne transporte v zvezi s tem je potrebno upoštevati v enotnih cenah. | Any temporary deposits of earth material and the necessary transport in this connection must be taken into account in the uniform prices.
| Izbrana mehanizacija mora omogočati upoštevanje varnostnih ukrepov. | The machinery chosen must be able to comply with safety precautions.
| Vsa izkopna dela in transporti izkopnih materialov se obračunajo po prostornini zemljine v raščenem stanju. Vsa nasipna dela se obračunajo po prostornini zemljine v vgrajenem stanju. Obračun količin se izvede po posnetih profilih pred in po nasipavanju. | All excavation work and transport of excavation materials shall be accounted for by the volume of soil in the loosened state. All embankment work shall be accounted for by the volume of soil in the as-built state. Quantities shall be accounted for on the basis of the recorded profiles before and after embankment.
| Utrjevanje z nabijanjem do predpisane zbitosti po projektu statike. | Curing by ramming to the specified compaction according to the structural design.
| Splošne opombe za betonske konstrukcije; ~ vsi vgrajeni betoni morajo izpolnjevati zahteve SIST EN 206-1, SIST EN 1026 in SIST EN 1992-1-1 ter NAC dodatki; ~ za vse betonske konstrukcije velja zahteva za 2. izvedbeni razred in 1. tolerančni razred po SIST EN 13670 in nacionalnem dodatku, kar je potrebno upoštevati pri pripravi in izvajanju programa kontrole kakovosti in projekta betona; ~ pred nadaljevanjem del morajo biti stiki očiščeni, navlaženi in premazani s sredstvom za povečanje sprijemnosti ~ debelino krovnega sloja je potrebno kontrolirati z merjenjem ~ na proste robove vidnih površin se v opaž vgradi trikotne letve; | General notes for concrete structures; ~ All concrete installed shall comply with the requirements of SIST EN 206-1, SIST EN 1026 and SIST EN 1992-1-1 and NAC Appendices; ~ all concrete structures are subject to the requirement for Performance Class 2 and Tolerance Class 1 in accordance with SIST EN 13670 and the National Supplement, which must be taken into account in the preparation and implementation of the quality control programme and the concrete design; ~ joints must be cleaned, moistened and coated with an adhesion promoter before work proceeds ~ the thickness of the deck layer must be controlled by measurement ~ triangular battens shall be installed in the formwork at the free edges of the visible surfaces;
| Splošne opombe za betonske konstrukcije; ~ za vse vidne površine brez posebnih arhitekturnih oz. drugih zahtev in za nevidne površine veljajo zahteve za obdelavo površin po SIST EN 13670 in nacionalnem dodatku, kar je potrebno upoštevati pri izbiri opažev: - vidne površine: • opažene vidne površine: enostavno – VB2, • neopažene vidne površine (tabela F4 v SIST EN 13670 in tabela N5 v nac, dodatku): enostavna - nevidne površine: • opažene nevidne površine: osnovna – VB0, • neopažene nevidne površine (tabela F4 v SIST EN 13670 in tabela N5 v nac. dodatku): osnovna ~ za izvedbo zaščitnih slojev glej armaturni načrt; | General notes for concrete structures; ~ all visible surfaces without special architectural or other requirements and invisible surfaces are subject to the surface treatment requirements of SIST EN 13670 and the National Supplement, which must be taken into account when selecting the formwork: - visible surfaces: - Visible surfaces observed: easy - VB2, - Unnoticed visible surfaces (Table F4 in SIST EN 13670 and Table N5 in the Appendix): simple - invisible surfaces: - observed invisible surfaces: basic - VB0, - Unnoticed invisible surfaces (Table F4 in SIST EN 13670 and Table N5 in the National Appendix): basic ~ see reinforcement plan for the design of the protective layers;
| Pri izvedbi je potrebno upoštevati načrte, kjer so prikazane trase inštalacijskih vodov ter pred vgradnjo upoštevati vse elemente, ki so zajeti v elektro in strojnem načrtu. | The plans showing the routes of the installation lines must be followed and all the elements included in the electrical and mechanical plans must be taken into account before installation.
| Na armaturo je potrebno skladno z detajlom izbranega dobavitelja priključiti sistemske elemente za priključitev na ozemljitev - priključitev izvede izvajalec elektro del, pred betoniranjem. | System elements for connection to earth must be connected to the reinforcement in accordance with the details of the selected supplier - connection to be carried out by the electrical contractor prior to concreting.
| Na vseh betonskih površinah, ki so izvedene v kvaliteti vidnega betona, se luknje od opaža zapolnijo s sanacijsko malto v barvi betona samo v območju luknje - pazljiva obdelava, kar se upošteva v cenah na enoto. Izvajalec izdela poskusni vzorec zapolnitve, ki ga potrdi arhitekt. | On all concrete surfaces executed in visible concrete quality, holes from the formwork shall be filled with remedial mortar in the colour of the concrete in the area of the hole only - careful treatment to be taken into account in the unit prices. The Contractor shall produce a trial sample of the fill to be approved by the Architect.
| V primeru nejasnosti, spremenjenih pogojev ali odstopanja od projekta se je potrebno posvetovati s projektantom. | In case of any ambiguity, changed conditions or deviation from the design, the designer should be consulted.
| Med izvedbo gradbenih posegov mora biti zagotovljen strokovni nadzor, ki bo zagotavljal skladnost gradnje s pogoji iz gradbenega dovoljenja ter kvaliteto izvedenih del v skladu z gradbenimi predpisi. | During the construction works, professional supervision must be provided to ensure that the construction complies with the conditions of the building permit and that the quality of the works is in accordance with the building regulations.
| Upoštevati vse vertikalne in horizontalne transporte. | All vertical and horizontal transports must be taken into account.
| Potrebno je izvajati sprotno čiščenje. | Ongoing cleaning is necessary.
5.1 | Izkop jarka v zemljišču III.ktg. za kabelsko kanalizacijo - SN, z nakladanjem na kamion in odvozom na začasno deponijo, do ponovne vgradnje po izvedbi novih del. | Excavation of a trench in land III.ktg. for the cable duct - MV, with loading onto a truck and removal to a temporary landfill site, until re-installation after the new works have been carried out.
a. | ~strojni izkop (90%) | ~machine excavation (90%) | m3 | 27 |  | 0
b. | ~ročni izkop (10%) | ~hand excavation (10%) | m3 | 3 |  | 0
5.2 | Planiranje in utrjevanje dna izkopa jarkov pred izvedbo kabelske kanalizacije - SN, v predpisanem naklonu in do predpisane utrditve po projektu. | Planning and consolidation of the trench bottom prior to the installation of the cable duct - MV, at the prescribed gradient and to the prescribed consolidation as per the design. | m2 | 11 |  | 0
5.3 | Zasip za kabelsko kanalizacijo - SN z izkopanim materialom deponiranim na začasni deponiji, komplet z nakladanjem in dovozom, raztiranjem in planiranjem ter utrjevanjem po plasteh od 20 do 30 cm s sprotnim komprimiranjem do predpisane utrditve po projektu. | Backfill for the cable duct - MV with excavated material deposited in the temporary landfill, complete with loading and access, grading and grading, and consolidation in layers of 20 to 30 cm with continuous compaction to the required consolidation as per the design. | m3 | 25 |  | 0
5.4 | Odvoz izkopanega materiala na stalno deponijo, ki si jo priskrbi izvajalec, katero si izvajalec zagotovi sam ter plačilom taks na deponiji. | Removal of excavated material to a permanent landfill to be provided by the Contractor, which shall be provided by the Contractor, and payment of landfill charges. | m3 | 5 |  | 0
5.5 | Dobava in polaganje PVC opozorilnega traku, položenega v zasip nad cevmi . | Supply and installation of PVC warning tape laid in the backfill above the pipes. | m | 12 |  | 0
5.6 | Kompletna izvedba križanj nove kabelske kanalizacije - SN z obstoječimi komunalnimi vodi, skupaj z vsemi potrebnimi deli in materialom, skladno z upoštevanjem načina izvedbe in vseh pogojev po navodilih upravljalca komunalnega voda. | Complete execution of the crossings of the new MV cable duct with the existing utility lines, including all necessary works and materials, in accordance with the method of execution and all conditions as specified by the utility line manager. | kpl | 2 |  | 0
5.7 | Dobava, izdelava in montaža armaturnih mrež, iz betonskega jekla B 500A po SIST EN 10080 in SIST EN 1992-1-1. V ceni upoštevati tudi dodatek za varjenje armature (1/3 stikov) za priključitev na ozemljitve, preklop mrež je min. 3 okenca. | Supply, manufacture and installation of reinforcement grids, made of concrete steel B 500A according to SIST EN 10080 and SIST EN 1992-1-1. The price also includes an allowance for welding the reinforcement (1/3 of the contacts) for connection to earth, the switching of the grids is min. 3 windows. | kg | 150 |  | 0
5.8 | Dobava in vgrajevanje betona v nearmirane konstrukcije preseka od 0,08 do 0,12 m3/m2-m; z vsemi pomožnimi deli in prenosi do mesta vgraditve; podložni beton ~beton C12/15-XC0 ~vgradnja z naklonom in brez naklona | Supply and installation of concrete in unreinforced concrete structures with a cross-section of 0,08 to 0,12 m3/m2-m; with all ancillary works and transfers to the installation site; sub-base concrete ~concrete C12/15-XC0 ~building with and without slope | m3 | 0.5 |  | 0
5.9 | Dobava in vgrajevanje betona v nearmirane konstrukcije preseka nad 0,12 do 0,20 m3/m2/m z vsemi pomožnimi deli in prenosi do mesta vgraditve; podbetoniranje in obbetoniranje kabelskih cevi do temena (del cevi nad kletjo) ~beton C 25/30-XC2 ~izvedba po detajlu v projektni dokumentaciji | Supply and installation of concrete in unreinforced concrete structures with a cross-section exceeding 0,12 to 0,20 m3/m2/m, including all ancillary works and transfers to the installation site; under-concreting and over-concreting of cable ducts up to the top (part of the duct above the basement) ~concrete C 25/30-XC2 ~ querying a detail in the project documentation | m3 | 1 |  | 0
5.10 | Dobava in vgrajevanje betona v armirane konstrukcije preseka nad 0,30 m3/m2/m z vsemi pomožnimi deli in prenosi do mesta vgraditve; obbetoniranje kabelskih cevi (armirani bloki) ~beton C 25/30-XC2 ~izvedba po detajlu v projektni dokumentaciji | Supply and installation of concrete in reinforced concrete structures with a cross-section exceeding 0,30 m3/m2/m, including all ancillary works and transfers to the installation site; concreting of cable ducts (reinforced concrete blocks) ~concrete C 25/30-XC2 ~ querying a detail in the project documentation | m3 | 4 |  | 0
5.11 | Opaž robov podložnega betona, horizontalno in v naklonu; opaženje, razopaženje in čiščenje ~ višina opaža 10 cm ~ nevidna betonska površina | Formwork for edges of sub-base concrete, horizontal and inclined; formwork, debonding and cleaning ~ formwork height 10 cm ~ invisible concrete surface | m | 21 |  | 0
5.12 | Opaž robov kabelskih blokov, horizontalno in v naklonu; opaženje, razopaženje in čiščenje ~ višina opaža 40 cm ~ dvostranski opaž ~ nevidna betonska površina | Edgebanding of cable blocks, horizontal and inclined; formwork, debonding and cleaning ~ formwork height 40 cm ~ double-sided formwork ~ invisible concrete surface | m2 | 8 |  | 0
5.13 | Dobava in položitev zaščitnih kabelskih cevi PVC DN160 na betonsko podlago, kompletno z distančniki, spojkami, pokrovi, tesnjenjem in vsemi potrebnimi deli in materialom. Položene cevi mora pred zalitjem z betonom prevzeti izvajalec elektro montažnih del. | Supply and laying of PVC DN160 protective cable conduits on a concrete base, complete with spacers, couplings, covers, sealing and all necessary parts and materials. The laid conduits must be accepted by the electrical installation contractor before pouring with concrete. | m | 48 |  | 0
5.14 | Dobava in položitev zaščitnih kabelskih cevi PE 2xfi 50 mm - dvojček, kompletno z distančniki, spojkami, pokrovi, tesnjenjem in vsemi dodatnimi deli. Položene cevi mora pred zalitjem z betonom prevzeti izvajalec elektro montažnih del. ~ upoštevano dvojček - 2x fi 50 mm/m | Supply and laying of PE 2xfi 50 mm twin protective cable conduits, complete with spacers, couplings, caps, sealing and all ancillary parts. The laid conduits shall be accepted by the electrical installation contractor prior to pouring the concrete. ~ twin - 2x fi 50 mm/m | m | 12 |  | 0
5.15 | Kompletna izvedba prebojev s kronskim vrtanjem skozi steno jaška debeline 25 cm. Preboji do fi150 mm za PE cevi za optiko, za naknadno vgradnjo uvodnic. Lokacija preboja v steni jaška se prilagodi izvedeni kabelski trasi in izbrani uvodnici. | Complete punching through the shaft wall by crown drilling with a thickness of 25 cm. Punctures up to fi150 mm for PE fibre optic pipes, for subsequent installation of introducers. The location of the puncture in the shaft wall is adapted to the cable route and the selected introducer. | kos | 3 |  | 0
5.16 | Dobava in vgradnja plastične prirobnice za naknadno vgradnjo z vložki in vijaki za izvrtine do max. fi 150 mm oz. za privijanje na ohišje. Prirobnica iz poliamida ojačanega s steklenimi vlakni, EPDM površinsko tesnilo, vijačni material nerjavno jeklo V4A (AISI 316L), kot npr. HSI150 DFK tip EGO SMP 805, plinotesnih in vodotesnih do 2,5 bar, vključno s sistemskimi pokrovi, kot npr. sistem HAUFF TECHNIK ali enakovredno, debelina AB zidu je 25 cm. Vgradnja po navodilih proizvajalca. | Supply and installation of plastic flange for retrofitting with inserts and screws for holes up to max. fi 150 mm or for screwing onto the casing. Flange made of glass fibre reinforced polyamide, EPDM surface seal, screw material stainless steel V4A (AISI 316L), e.g. HSI150 DFK type EGO SMP 805, gas-tight and water-tight up to 2,5 bar, including system caps, e.g. HAUFF TECHNIK system or equivalent, thickness of the AB wall is 25 cm. Installation according to the manufacturer's instructions. | kos | 3 |  | 0
5.17 | Kompletna dobava in vgradnja deljivega sistemskega pokrova za tesnitev do 3 kable/cevi premera od 24 do 54 mm hkrati v eni zidni uvodnici premera 150 mm, material pritisne plošče poliamid ojačan s steklenimi vlakni, guma EPDM, vijaki in matice nerjavno jeklo V2A (AISI 304L), kot npr. HSI150 DG 3x24-54 Hauff Technik ali enakovredno, skupaj z vsemi potrebnimi deli in materialom, vgrajeno po navodilu proizvajalca. Opomba: plinotesno in vodotesno do 2,5 bara. | Complete supply and installation of a divisible system cover for sealing up to 3 cables/pipes with diameters from 24 to 54 mm in one 150 mm diameter wall inlet at the same time, pressure plate material glass fibre reinforced polyamide, EPDM rubber, nuts and bolts stainless steel V2A (AISI 304L), such as e.g. HSI150 DG 3x24-54 Hauff Technik or equivalent, together with all necessary parts and materials, installed according to the manufacturer's instructions. Note: gas-tight and watertight up to 2.5 bar. | kos | 3 |  | 0
5.18 | Razna pomoč pri gradbeno-obrtniških, elektro inštalaterskih in strojnih delih. ~ KV delavec | Miscellaneous assistance with building, electrical, plumbing and mechanical work. ~ KV worker | ur | 40 |  | 0
5.19 | Razna pomoč pri gradbeno-obrtniških, elektro inštalaterskih in strojnih delih. ~ PK delavec | Miscellaneous assistance with building, electrical, plumbing and mechanical work. ~ PK worker | ur | 40 |  | 0
| KABELSKA KANALIZACIJA - SN | CABLE DUCT - SN |  |  |  | 0

## 2.6.2.6_NN_TK_R
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | KOMUNALNI PRIKLJUČKI OBJEKTA | UTILITY CONNECTIONS
2.6.2 | GRADBENA DELA | CONSTRUCTION WORKS
2.6.2.6 | KABELSKA KANALIZACIJA - NN, TK IN RAZSVETLJAVA | CABLE DUCTING - LV, HV, HV AND LIGHTING |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
6 | KABELSKA KANALIZACIJA - NN, TK IN RAZSVETLJAVA | CABLE DUCTING - LV, HV, HV AND LIGHTING
| OPOMBE: Pri izdelavi ponudbe upoštevati pripombe, iz poglavja 0.1 UVOD-STP Pri izdelavi ponudbe upoštevati pripombe, iz poglavja 0.2 UVOD - DGNB in dokument: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme. | NOTES: Take into account the comments made in section 0.1 INTRODUCTION-STP in the preparation of the offer When preparing the tender, take into account the comments made in Section 0.2 INTRODUCTION - DGNB and the document DGNB Quality Grades for Materials, Elements and Equipment.
| Pred pričetkom del je potrebno: ~ na licu mesta preveriti vse dimenzije navedene v načrtu in morebitna odstopanja prilagoditi dejanskemu stanju na terenu ~ vsa neskladja pravočasno / pred izvedbo uskladiti z vodjo projektiranja in ostalimi projektanti ~ vse izvedbe, materiale, obdelave in barve uskladiti s projektanti ~ pri vseh vidnih izvedbah je pred izvedbo potrebno delavniško uskladiti detajle ter jih predložiti projektantu v potrditev | Before starting work, it is necessary to: ~ on-site verification of all dimensions indicated in the plan and adjustment of any deviations to the actual situation on the ground ~ reconcile any discrepancies with the design manager and other designers in a timely manner / prior to implementation ~ all designs, materials, finishes and colours to be coordinated with the designers ~ all visible works shall be subject to workshop coordination of details and submitted to the designer for approval prior to implementation
| Osnova za izvedbo popisa za zemeljska dela je geodetski posnetek obstoječega stanja, načrti objektov, zunanje ureditve in načrti komunalne infra strukture, tehnično poročilo ter navodila in zahteve dobaviteljev za izvedbo in vgradnjo posameznih delov opreme. | The basis for the inventory for the earthworks is the existing geodetic survey, the building plans, the external layout plans and the plans of the utility infrastructure, the technical report and the instructions and requirements of the suppliers for the execution and installation of the individual pieces of equipment.
| Pri izvedbi vseh zemeljskih del mora biti prisoten geomehanski nadzor, ki preveri ustreznost predvidenih ukrepov, ustreznost homogenih tal, skladnost privzetih parametrov v PZI z dejanskim stanjem na terenu in geološko-geomehanskih raziskav iz Geološko-geotehničnega poročila (IRGO Consulting d.o.o., poročilo št. 3009776, januar 2021). | During the execution of all earthworks, geomechanical supervision must be present to verify the adequacy of the planned measures, the adequacy of the homogeneous soils, the conformity of the default parameters in the PIP with the actual situation on the ground and the geological-geomechanical investigations from the Geological-Geotechnical Report (IRGO Consulting d.o.o., Report No. 3009776, January 2021).
| V kolikor bi se v času izvajanja zemeljskih del izkazalo, da je dejansko stanje drugačno od predvidenega, geomehanik takoj obvesti projektanta in se pristopu k iskanju projektnih rešitev, ki ustrezajo dejanskemu stanju. Vsa odstopanja od PZI morata pred izvedbo pisno potrditi geomehanik in projektant. | Should the actual situation prove to be different from the intended situation during the execution of the earthworks, the geomechanic shall immediately inform the designer and the designer shall be approached to find design solutions that correspond to the actual situation. Any deviations from the PIP shall be confirmed in writing by the geomechanic and the designer prior to execution.
| Primernost izkopanega materiala za zasip ugotovi geomehanik na licu mesta. | The suitability of the excavated material for backfill shall be determined by the on-site geomechanist.
| Morebitne začasne deponije zemeljskega materijala in potrebne transporte v zvezi s tem je potrebno upoštevati v enotnih cenah. | Any temporary deposits of earth material and the necessary transport in this connection must be taken into account in the uniform prices.
| Izbrana mehanizacija mora omogočati upoštevanje varnostnih ukrepov. | The machinery chosen must be able to comply with safety precautions.
| Vsa izkopna dela in transporti izkopnih materialov se obračunajo po prostornini zemljine v raščenem stanju. Vsa nasipna dela se obračunajo po prostornini zemljine v vgrajenem stanju. Obračun količin se izvede po posnetih profilih pred in po nasipavanju. | All excavation work and transport of excavation materials shall be accounted for by the volume of soil in the loosened state. All embankment work shall be accounted for by the volume of soil in the embedded state. Quantities shall be accounted for on the basis of recorded profiles before and after embankment.
| Utrjevanje z nabijanjem do predpisane zbitosti po projektu statike. | Curing by ramming to the specified compaction according to the structural design.
| Splošne opombe za betonske konstrukcije; ~ vsi vgrajeni betoni morajo izpolnjevati zahteve SIST EN 206-1, SIST EN 1026 in SIST EN 1992-1-1 ter NAC dodatki; ~ za vse betonske konstrukcije velja zahteva za 2. izvedbeni razred in 1. tolerančni razred po SIST EN 13670 in nacionalnem dodatku, kar je potrebno upoštevati pri pripravi in izvajanju programa kontrole kakovosti in projekta betona; ~ pred nadaljevanjem del morajo biti stiki očiščeni, navlaženi in premazani s sredstvom za povečanje sprijemnosti ~ debelino krovnega sloja je potrebno kontrolirati z merjenjem ~ na proste robove vidnih površin se v opaž vgradi trikotne letve; | General notes for concrete structures; ~ All concrete installed shall comply with the requirements of SIST EN 206-1, SIST EN 1026 and SIST EN 1992-1-1 and NAC Appendices; ~ all concrete structures are subject to the requirement for performance class 2 and tolerance class 1 according to SIST EN 13670 and the National Supplement, which must be taken into account in the preparation and implementation of the quality control programme and the concrete design; ~ joints must be cleaned, moistened and coated with an adhesion promoter before work proceeds ~ the thickness of the deck layer must be controlled by measuring ~ triangular battens shall be installed in the formwork at the free edges of the visible surfaces;
| Splošne opombe za betonske konstrukcije; ~ za vse vidne površine brez posebnih arhitekturnih oz. drugih zahtev in za nevidne površine veljajo zahteve za obdelavo površin po SIST EN 13670 in nacionalnem dodatku, kar je potrebno upoštevati pri izbiri opažev: - vidne površine: • opažene vidne površine: enostavno – VB2, • neopažene vidne površine (tabela F4 v SIST EN 13670 in tabela N5 v nac, dodatku): enostavna - nevidne površine: • opažene nevidne površine: osnovna – VB0, • neopažene nevidne površine (tabela F4 v SIST EN 13670 in tabela N5 v nac. dodatku): osnovna ~ za izvedbo zaščitnih slojev glej armaturni načrt; | General notes for concrete structures; ~ all visible surfaces without special architectural or other requirements and invisible surfaces are subject to the surface treatment requirements of SIST EN 13670 and the National Supplement, which must be taken into account when selecting the formwork: - visible surfaces: - Visible surfaces observed: easy - VB2, - Unnoticed visible surfaces (Table F4 in SIST EN 13670 and Table N5 in the Appendix): simple - invisible surfaces: - observed invisible surfaces: basic - VB0, - Unnoticed invisible surfaces (Table F4 in SIST EN 13670 and Table N5 in the National Appendix): basic ~ see reinforcement plan for the design of the protective layers;
| Izvajajalec je dolžan na svoje stroške izdelati projekt izvajanja betonskih konstrukcij. | The Contractor shall be obliged to draw up, at his own expense, a project for the execution of the concrete structures.
| Pri izvedbi je potrebno upoštevati načrte, kjer so prikazane trase inštalacijskih vodov ter pred vgradnjo upoštevati vse elemente, ki so zajeti v elektro in strojnem načrtu. | The plans showing the routes of the installation lines must be followed and all the elements included in the electrical and mechanical plans must be taken into account before installation.
| Na armaturo je potrebno skladno z detajlom izbranega dobavitelja priključiti sistemske elemente za priključitev na ozemljitev - priključitev izvede izvajalec elektro del, pred betoniranjem. | System elements for connection to earth must be connected to the reinforcement in accordance with the details of the selected supplier - connection to be carried out by the electrical contractor prior to concreting.
| Na vseh betonskih površinah, ki so izvedene v kvaliteti vidnega betona, se luknje od opaža zapolnijo s sanacijsko malto v barvi betona samo v območju luknje - pazljiva obdelava, kar se upošteva v cenah na enoto. Izvajalec izdela poskusni vzorec zapolnitve, ki ga potrdi arhitekt. | On all concrete surfaces executed in visible concrete quality, holes from the formwork shall be filled with remedial mortar in the colour of the concrete in the area of the hole only - careful treatment to be taken into account in the unit prices. The Contractor shall produce a trial sample of the fill to be approved by the Architect.
| Vsa popravila nepravilnosti vidnih in nevidnih betonskih površin se upošteva v cenah na enoto. | All repairs to visible and invisible concrete surface imperfections shall be taken into account in the unit prices.
| Za jeklene konstrukcije oziroma elemente se izdela, skladno s predpisi ustrezne ozemljitve, nevidno pritrjene in speljane na splošno ozemljitev objekta - obdelano v elektro projektu. | For steel structures or elements, appropriate earth connections shall be made, in accordance with the regulations, invisibly attached and connected to the general earthing of the building - to be worked out in the electrical design.
| Vsi delovni odri morajo biti upoštevani v cenah na enoto. | All working scaffolds must be included in the unit prices.
| V primeru nejasnosti, spremenjenih pogojev ali odstopanja od projekta se je potrebno posvetovati s projektantom. | In case of any ambiguity, changed conditions or deviation from the design, the designer should be consulted.
| Med izvedbo gradbenih posegov mora biti zagotovljen strokovni nadzor, ki bo zagotavljal skladnost gradnje s pogoji iz gradbenega dovoljenja ter kvaliteto izvedenih del v skladu z gradbenimi predpisi. | During the construction works, professional supervision must be provided to ensure that the construction complies with the conditions of the building permit and that the quality of the works is in accordance with the building regulations.
| Upoštevati vse vertikalne in horizontalne transporte. | All vertical and horizontal transports must be taken into account.
| Potrebno je izvajati sprotno čiščenje. | Ongoing cleaning is necessary.
6.1 | Izkop jarka v zemljišču III.ktg. za kabelsko kanalizacijo - NN, TK in R z nakladanjem na kamion in odvozom na začasno deponijo, do ponovne vgradnje po izvedbi novih del. | Excavation of a trench in land III.ktg. for cable ducts - LV, TK and R with loading on a truck and removal to a temporary landfill, until re-installation after the new works have been carried out.
a. | ~strojni izkop (90%) | ~machine excavation (90%) | m3 | 301 |  | 0
b. | ~ročni izkop (10%) | ~hand excavation (10%) | m3 | 33 |  | 0
6.2 | Planiranje in utrjevanje dna izkopa jarkov pred izvedbo kabelske kanalizacije - NN, TK in R v predpisanem naklonu in do predpisane utrditve po projektu. | Planning and consolidation of the trench bottom prior to the installation of the LV, TK and R cable ducts at the prescribed gradient and to the prescribed consolidation as per the design. | m2 | 90 |  | 0
6.3 | Zasip za kabelsko kanalizacijo - NN, TK in R z izkopanim materialom deponiranim na začasni deponiji, komplet z nakladanjem in dovozom, raztiranjem in planiranjem ter utrjevanjem po plasteh od 20 do 30 cm s sprotnim komprimiranjem do predpisane utrditve po projektu. | Backfilling for cable ducts - LV, TK and R with excavated material deposited in a temporary landfill, complete with loading and access, grading and grading, and consolidation in layers of 20 to 30 cm with continuous compaction to the required consolidation according to the design. | m3 | 303 |  | 0
6.4 | Odvoz izkopanega materiala na stalno deponijo, ki si jo priskrbi izvajalec, katero si izvajalec zagotovi sam ter plačilom taks na deponiji. | The removal of excavated material to a permanent landfill to be provided by the Contractor, which shall be provided by the Contractor and the payment of landfill charges. | m3 | 31 |  | 0
6.5 | Dobava in polaganje PVC opozorilnega traku, položenega v zasip nad cevmi . | Supply and installation of PVC warning tape laid in the backfill above the pipes. | m | 108 |  | 0
6.6 | Kompletna izvedba križanj nove kabelske kanalizacije - NN, TK in R z obstoječimi komunalnimi vodi, skupaj z vsemi potrebnimi deli in materialom, skladno z upoštevanjem načina izvedbe in vseh pogojev po navodilih upravljalca komunalnega voda. | Complete execution of the crossings of the new LV, TK and R cable ducts with the existing utility lines, including all necessary works and materials, in accordance with the method of execution and all conditions as specified by the utility line manager. | kpl | 11 |  | 0
6.7 | Dobava, izdelava in montaža armaturnih mrež, iz betonskega jekla B 500A po SIST EN 10080 in SIST EN 1992-1-1. V ceni upoštevati tudi dodatek za varjenje armature (1/3 stikov) za priključitev na ozemljitve, preklop mrež je min. 3 okenca. | Supply, manufacture and installation of reinforcement grids, made of concrete steel B 500A according to SIST EN 10080 and SIST EN 1992-1-1. The price also includes an allowance for welding of the reinforcement (1/3 of the contacts) for connection to the earthing, switching of the grids is min. 3 windows. | kg | 1100 |  | 0
6.8 | Dobava in vgrajevanje betona v nearmirane konstrukcije preseka od 0,08 do 0,12 m3/m2-m; z vsemi pomožnimi deli in prenosi do mesta vgraditve; podložni beton ~beton C12/15-XC0 ~vgradnja z naklonom in brez naklona | Supply and installation of concrete in unreinforced concrete structures with a cross-section of 0,08 to 0,12 m3/m2-m; with all ancillary works and transfers to the installation site; sub-base concrete ~concrete C12/15-XC0 ~building with and without slope | m3 | 7 |  | 0
6.9 | Dobava in vgrajevanje betona v nearmirane konstrukcije preseka nad 0,12 do 0,20 m3/m2/m z vsemi pomožnimi deli in prenosi do mesta vgraditve; obbetoniranje kabelskih cevi - posteljica debeline 10 cm in obbetoniranje 30 cm nad temenom cevi ~beton C 25/30-XC2 ~izvedba po detajlu v projektni dokumentaciji | Supply and installation of concrete in unreinforced concrete structures with a cross-section of over 0,12 to 0,20 m3/m2/m, including all ancillary works and transfers to the installation site; concreting of cable pipes - 10 cm thick bedding and 30 cm above the top of the pipe ~concrete C 25/30-XC2 ~ querying a detail in the project documentation | m3 | 5 |  | 0
6.10 | Dobava in vgrajevanje betona v armirane konstrukcije preseka nad 0,30 m3/m2/m z vsemi pomožnimi deli in prenosi do mesta vgraditve; obbetoniranje kabelskih cevi (armirani bloki) ~beton C 25/30-XC2 ~izvedba po detajlu v projektni dokumentaciji | Supply and installation of concrete in reinforced concrete structures with a cross-section exceeding 0,30 m3/m2/m, including all ancillary works and transfers to the installation site; concreting of cable ducts (reinforced concrete blocks) ~concrete C 25/30-XC2 ~ querying a detail in the project documentation | m3 | 17 |  | 0
6.11 | Opaž robov podložnega betona, horizontalno in v naklonu; opaženje, razopaženje in čiščenje ~ višina opaža 10 cm ~ nevidna betonska površina | Formwork for edges of sub-base concrete, horizontal and inclined; formwork, debonding and cleaning ~ formwork height 10 cm ~ invisible concrete surface | m | 164 |  | 0
6.12 | Opaž robov kabelskih blokov, horizontalno in v naklonu; opaženje, razopaženje in čiščenje ~ višina opaža 40 cm ~ dvostranski opaž ~ nevidna betonska površina | Edgebanding of cable blocks, horizontal and inclined; formwork, debonding and cleaning ~ formwork height 40 cm ~ double-sided formwork ~ invisible concrete surface | m2 | 58 |  | 0
6.13 | Dobava in položitev zaščitnih kabelskih cevi PE DN110 na betonsko podlago, kompletno z distančniki, spojkami, pokrovi, tesnjenjem in vsemi potrebnimi deli in materialom. Položene cevi mora pred zalitjem z betonom prevzeti izvajalec elektro montažnih del. | Supply and laying of PE DN110 protective cable conduits on a concrete substrate, complete with spacers, couplings, covers, sealing and all necessary parts and materials. The laid conduits shall be accepted by the electrical installation contractor prior to pouring with concrete. | m | 301 |  | 0
6.14 | Kompletna izdelava, dobava in vgradnja tipskih montažnih vodotesnih betonskih jaškov, z integriranimi tesnili med posameznimi sestavnimi deli, fi 1000 mm, globine od 1,50 do 2,00 m, skladnih s standardom SIST EN 1917, kot npr. PGM Žalec - betonski jaški ali enakovredno, skupaj z vsemi potrebnimi deli in materialom, vgrajeno po navodilu proizvajalca. Opomba: Jašek se višinsko prilagodi tipu pokrova z zgornjim tipskim nastavkom z integriranim tesnilom | Complete manufacture, supply and installation of standard prefabricated watertight concrete manholes, with integrated seals between the individual components, fi 1000 mm, depth from 1.50 to 2.00 m, complying with SIST EN 1917, e.g. PGM Žalec - concrete manholes or equivalent, together with all necessary parts and materials, installed according to the manufacturer's instructions. Note: The manhole is height-adjustable to the type of cover by means of a top type adaptor with integrated seal | kos | 3 |  | 0
6.15 | Kompletna izdelava, dobava in vgradnja tipskih montažnih vodotesnih betonskih jaškov, z integriranimi tesnili med posameznimi sestavnimi deli, fi 1000 mm, globine od 2,00 do 2,50 m, skladnih s standardom SIST EN 1917, kot npr. PGM Žalec - betonski jaški ali enakovredno, skupaj z vsemi potrebnimi deli in materialom, vgrajeno po navodilu proizvajalca. Opomba: Jašek se višinsko prilagodi tipu pokrova z zgornjim tipskim nastavkom z integriranim tesnilom | Complete manufacture, supply and installation of standard prefabricated watertight concrete manholes, with integrated seals between the individual components, fi 1000 mm, depth from 2.00 to 2.50 m, complying with SIST EN 1917, e.g. PGM Žalec - concrete manholes or equivalent, together with all necessary parts and materials, installed according to the manufacturer's instructions. Note: The manhole is height-adjustable to the type of cover by means of a top type adaptor with integrated seal | kos | 1 |  | 0
6.16 | Kompletna izdelava, dobava in montaža tipskih armirano betonskih vencev z LTŽ pokrovom fi 600 mm D400, kot npr. PGM Žalec - armirano betonski venci s pokrovom ali enakovredno, na montažne betonske jaške, skupaj z vsemi potrebnimi deli in materialom, vgrajeno po navodilu proizvajalca. | Complete manufacture, supply and installation of standard reinforced concrete wreaths with LTŽ cover fi 600 mm D400, as e.g. PGM Žalec - reinforced concrete wreaths with cover or equivalent, on precast concrete manholes, together with all necessary parts and materials, installed according to the manufacturer's instructions. | kos | 3 |  | 0
6.17 | Kompletna izdelava, dobava in vgradnja jeklenega vroče cinkanega pokrova za zapolnitev, dimenzije 600x600 mm, D400, skladno s standardom EN 1253-4, kot npr. ACO pokrovi za zapolnitev Paving GS 120 z asistenco za odpiranje ali enakovredno, na montažne betonske jaške. Pokrovi se vgradijo v tlak skupaj z vsemi potrebnimi deli in materialom, vgrajeno po navodilu proizvajalca. | Complete manufacture, supply and installation of hot-dip galvanised steel backfill covers, dimensions 600x600 mm, D400, in accordance with EN 1253-4, such as ACO Paving GS 120 backfill covers with opening assistance or equivalent, on precast concrete manholes. The covers shall be installed in the pavement together with all necessary parts and materials, installed according to the manufacturer's instructions. | kos | 1 |  | 0
6.18 | Razna pomoč pri gradbeno-obrtniških, elektro inštalaterskih in strojnih delih. ~ KV delavec | Miscellaneous assistance with building, electrical, plumbing and mechanical work. ~ KV worker | ur | 200 |  | 0
6.19 | Razna pomoč pri gradbeno-obrtniških, elektro inštalaterskih in strojnih delih. ~ PK delavec | Miscellaneous assistance with building, electrical, plumbing and mechanical work. ~ PK worker | ur | 200 |  | 0
| KABELSKA KANALIZACIJA - NN, TK IN RAZSVETLJAVA | CABLE DUCTING - LV, HV, HV AND LIGHTING |  |  |  | 0