## 0_Naslovnica
OPOZORILO! Vsi prevodi v angleščino so strojno izdelani in zgolj informativne narave. V primeru kakršnekoli nejasnosti ali dvoma izključno velja izvirno besedilo v slovenščini. WARNING! All translations into English have been produced by machine translation and are provided for informational purposes only. In the event of any ambiguity or uncertainty, the original Slovenian text shall prevail exclusively.
| / | / | [5 empty] | /
| Sprem./Rev.: | Opis spremembe/Description of Changes: | [5 empty] | Datum/Date: | Podpis/Signature:
| Investitor/Investor: |  |  |  |  | Gradnja/Facility
|  |  | Univerza v Ljubljani Kongresni trg 12 1000 Ljubljana, Slovenija |  |  | Fakulteta za strojništvo/Faculty of Mechanical Engineering
| Projektant/Design Engineer: |  |  |  |  | Del objekta/sistem/Building/System:
|  |  | IBE, svetovanje, projektiranje in inženiring Ljubljana, Slovenija |  |  | ZAKLONIŠČE/SHELTER
| Projektant/Design Engineer: |  |  |  |  | Vrsta načrta/Documentation:
3 NAČRT S PODROČJA ELEKTROTEHNIKE/ DOC. IN THE FIELD OF ELECTRICAL ENGINEERING
|  | Ime in priimek/Name and Surname: |  |  | Id. št./Id. No: | Vsebina risbe (dokumenta)/Document Title:
| Vodja proj./ Des. Manager: | Boštjan Vuga, univ. dipl. inž. arh., grad. dip. (AA) |  |  | ZAPS 0035 PA PPN | PR. POPIS ELEKTRO DEL/BOQ OF ELECTRICAL WORKS 3/1 Zaklonišče/Shelter
| Poobl. strok./ Cert. Profess.: | Robert Bobovnik, dipl.inž.el. |  |  | IZS E-2380
| Poobl. strok./ Cert. Profess.: |  |  |  |  | Št. proj./ Proj. No.: | 362-19 |  | Vrsta dokument./ Document. Type: | PZI
| Izdelal/ Creator: | Aleksandra Proeva, dipl.inž.el. |  |  |  | Klas. ozn./ Class. No.: | -- |  | Stran/ Page: | 1/*
| Datum/ Date: | maj/May 2026 |  | Merilo/ Scale: | / | Ident. ozn./ Id. No: | JULFS--6E9002P

## 0_Osebe
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
POOBLAŠČENI STROKOVNJAKI, ODGOVORNI ZA IZDELAVO PROJEKTANTSKEGA POPISA:
Id. št. ZAPS/IZS | Pooblaščeni strokovnjak | Strokovno področje
IZS E-2380 | Robert Bobovnik, dipl. inž. el. | Električne inštalacije
IZS E-1816 | Danijel Kure, mag. inž. energ. | Ozemljitve, izenačitev potencialov in strelovod
SODELAVCI PRI IZDELAVI PROJEKTANTSKEGA POPISA:
/ | Aleksandra Proeva, dipl. inž. el. | Električne inštalacije
CERTIFIED EXPERTS RESPONSIBLE FOR ELABORATING THE BILL OF QUANTITIES:
Id. No ZAPS/IZS | Certified Expert | Area of Expertise
IZS E-2380 | Robert Bobovnik, dipl. inž. el. | Electrical installations
IZS E-1816 | Danijel Kure, mag. inž. energ. | Earthing, equipotential bonding and lightning conductors
COLABORATORS IN THE ELABORATING THE BILL OF QUANTITIES:
/ | Aleksandra Proeva, dipl. inž. el. | Electrical installations

## 0.1_Uvod-STP
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
0.1 | SPLOŠNI TEHNIČNI POGOJI | GENERAL TECHNICAL CONDITIONS
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic operator with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
0.1.1 | Izvajalec se obveže, da bo upošteval veljavno zakonodajo, ki ureja graditev objektov v Republiki Sloveniji, vključno s povezanimi podzakonskimi akti, predpisi, tehničnimi smernicami, standardi, pravili stroke in dobro gradbeno prakso. Prav tako mora izvajalec upoštevati vse zahteve izdanega integralnega gradbenega dovoljenja in vsa dela izvesti skladno s projektno dokumentacijo ter ostalimi pogoji, objavljenimi v razpisni dokumentaciji. | The Contractor undertakes to comply with the applicable legislation governing the construction of buildings in the Republic of Slovenia, including related by-laws, regulations, technical guidelines, standards, professional rules and good construction practice. The Contractor shall also comply with all the requirements of the integral building permit issued and shall carry out all works in accordance with the project documentation and other conditions published in the tender documentation.
0.1.2 | Dela lahko izvaja samo izvajalec, ki je registriran za opravljanje gradbene dejavnosti in ima za tovrstna dela ustrezno zavarovanje za škodo, certifikate, tehnično izobražen kader, sredstva ter je usposobljen za samostojno pripravo in izvedbo del. | The work may only be carried out by a contractor who is registered to carry out construction work and who has the appropriate insurance for such work, certificates, technically trained staff, resources and is qualified to prepare and carry out the work independently.
0.1.3 | Izvajalec odgovarja za kakovost izvedbe vseh del. | The Contractor shall be responsible for the quality of the execution of all works.
0.1.4 | Izvajalec nosi vso odgovornost za nesreče in škodo, ki nastane na objektu ali v okolici zaradi njegovega dela. | The Contractor shall bear all liability for accidents and damage to the installation or the surrounding area caused by his work.
0.1.5 | Pred oddajo ponudbe se je izvajalec dolžan seznaniti z območjem predvidenim za gradnjo in temu prilagoditi vsa potrebna dela, kar mora biti zajeto v ponudbi. V neposredni bližini predvidene gradnje se nahajajo stavbe, v katerih potekajo izobraževalni in raziskovalni procesi. Zato bo izvajalec moral izvajati kontrolo hrupa in kontrolo vibracij. Dela, ki so hrupna in dela, ki povzročajo vibracije bo izvajalec moral preprečiti oziroma jih izvesti na način, da povzročajo minimalne vplive. Tehnologijo rušenja, pilotiranja in tehnologijo izvedbe ostalih del bo izvajalec moral prilagoditi tako, da bo vpliv minimalen. Izvajalec mora preprečiti in zmanjšati emisije delcev iz gradbišča na najmanjšo možno mero. | Before submitting a tender, the contractor is obliged to familiarise himself with the area to be constructed and to adapt any necessary works accordingly, which must be included in the tender. In the immediate vicinity of the proposed construction, there are buildings in which educational and research processes take place. The contractor will therefore be required to carry out noise and vibration control. Noise and vibration works will have to be avoided or carried out in such a way as to minimise the impact. Demolition, piling and other works will have to be adapted to minimise the impact. The contractor must avoid and minimise the emission of particulates emitted from the construction site as far as is reasonably practicable.
0.1.6 | Izvajalec je pred oddajo ponudbe dolžan pregledati projektno dokumentacijo in ostale pogoje, ki so del razpisne dokumentacije V primeru morebitnih napak in neskladij je izvajalec dolžan na to opozoriti naročnika pred oddajo ponudbe. | The Contractor is obliged to review the project documentation and other conditions forming part of the tender documentation before submitting the tender In case of any errors or inconsistencies, the Contractor is obliged to bring these to the attention of the Contracting Authority before submitting the tender.
0.1.7 | Pred oddajo ponudbe je izvajalec dolžan preveriti ustreznost popisov del in količin v teh popisih ter njihovo skladnost z ostalimi dokumenti projektne dokumentacije, ki so del razpisne dokumentacije. Prav tako je izvajalec dolžan preveriti vse detajle in sheme. Vse izmere je potrebno preveriti po posameznih projektih oz. načrtih, ki sestavljajo razpisno dokumentacijo. V primeru ugotovljenih neskladij je v času priprave ponudbe obvezan o tem obvestiti naročnika. | Before submitting a tender, the Contractor shall check the adequacy of the inventories of works and quantities in these Bills of Quantities and their conformity with the other documents of the project documentation forming part of the tender documentation. The Contractor shall also check all details and diagrams. All measurements shall be checked against the individual projects or plans forming part of the tender documentation. In the event of any discrepancies, the Contractor shall inform the Contracting Authority at the time of preparing the tender.
0.1.8 | Pred oddajo ponudbe je izvajalec dolžan v tem popisu preveriti zmnožke in seštevke ter prenose le-teh v rekapitulacijo. Izvajalec se s pripravo ponudbe obvezuje, da je prebral vse celice in elemente celotnega popisa, vključno z vsemi postavkami in splošnimi navodili ali določili in je preveril pravilnost preračuna ter s tem zagotavlja ponudbeno vrednost. | Before submitting a tender, the Contractor is required to check the products and totals in this Bill of Quantities (BoQ) and their transfer to the recapitulation. The Contractor undertakes, by preparing a tender, to have read all the cells and elements of the complete BoQ, including all headings and general instructions or provisions, and to have checked the correctness of the conversion, thereby guaranteeing the value of the tender.
0.1.9 | Dela bo izvajalec moral izvajati po predloženi projektni dokumentaciji, detajlih in z upoštevanjem navodil in potrditev projektanta, nadzornika in investitorja. Vso potrebno delavniško dokumentacijo zagotovi izvajalec del v okviru ponujene cene. | The Contractor shall carry out the works in accordance with the submitted design documents, details and subject to the instructions and approvals of the Designer, the Supervisor and the Investor. All necessary workshop documentation shall be provided by the Contractor within the scope of the price quoted.
0.1.10 | Pred izvedbo posameznih del je izvajalec dolžan pregledati projektno dokumentacijo za izvedbo gradnje (PZI) in elaborate. Na morebitne napake v dokumentaciji ali neskladja med posameznimi načrti ali deli načrtov (popisi del, tehnična poročila, lokacijski in tehnični prikazi) izvajalec opozori nadzornika in projektanta, in se z njima pravočasno uskladi. | The Contractor shall review the Detailed Design documentation (PZI) and the studies before carrying out the individual works. The Contractor shall draw the attention of the Supervisor and the Designer to any errors in the documentation or discrepancies between the individual designs or parts of designs (BoQ, technical reports, location and technical drawings) and shall coordinate with them in good time.
0.1.11 | Tehnični opisi, prikazi, detajli, sheme ter ostali dokumenti v PZI dokumentaciji predstavljajo dodaten opis popisnih postavk gradbeno obrtniških in inštalacijskih del ter jih je potrebno dosledno upoštevati skupaj s popisom del. | The technical descriptions, illustrations, details, diagrams and other documents in the Detailed Design documentation (PZI) are additional descriptions of the BoQ inventory items of the building, construction and installation works and must be strictly followed together with the BoQ.
0.1.12 | Specifikacije in zahteve, navedene v popisu, se ne smejo upoštevati kot edine zahteve. Izvajalec je dolžan v ceni zajeti in dobaviti vse elemente opreme ter opraviti dela in storitve, ki niso eksplicitno navedeni, a so bistvenega pomena za funkcionalnost, skladnost s predpisi ter kontinuirano, zanesljivo in varno obratovanje opreme. | The specifications and requirements set out in the BoQ shall not be taken as the only requirements. The Contractor shall be obliged to include in the price and supply all items of equipment and to carry out works and services which are not expressly mentioned but which are essential for the functionality, regulatory compliance and continuous, reliable and safe operation of the equipment.
0.1.13 | Vsa dela morajo biti izvedena kvalitetno in iz materialov z zahtevanimi lastnostmi, izvedena skladno z veljavno zakonodajo in z upoštevanjem navodil za vgradnjo za izbrane materiale in opremo, s predložitvijo predpisanih izjav o lastnostih in/ali certifikatov. Vsi gradbeni proizvodi (GP) morajo biti označeni s CE oznako. | All work shall be of good quality and be executed with materials of the required characteristics, in accordance with the applicable legislation and in compliance with the installation instructions for the materials and equipment selected, and shall be accompanied by the prescribed declarations of performance and/or certificates. All construction products (GP) shall bear the CE marking.
0.1.14 | Za vsako opisano delo v popisu je potrebno upoštevati celotno potrebno delo, ves osnovni in pomožni material, prevoz materiala in orodja na objekt, notranje transporte, delovne in pomožne odre, zaključno čiščenje in odstranitev odpadkov po dovršenem delu. | For each work described in the inventory, the total work required, all basic and ancillary materials, the transport of materials and tools to the site, internal transports, working and ancillary scaffolding, final cleaning and the disposal of waste after the work has been completed must be taken into account.
0.1.15 | Vsa delovna sredstva, organizacija in koordinacija del, pripravljalna, spremljajoča in zaključna dela, potrebni montažni in tesnilni materiali ter podkonstrukcije so sestavni del posameznih postavk. | All labour, organisation and coordination of the works, preparatory, accompanying and finishing works, necessary prefabrication and sealing materials and substructures are part of the individual items.
0.1.16 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - načrt organizacije gradbišča s podrobnim terminskim planom in izvedba vseh pripravljalnih del, postavitev, organizacija, zaščita in prijava gradbišča, gradbiščnih objektov, ureditev začasnih deponij, tekoče vzdrževanje, skupaj s plačilom splošnih stroškov pristojbin in davkov upravnih organov, pridobivanju raznih dovoljenj in soglasij za izvedbo, ograditev gradbišča in postavitev gradbene table in prometne signalizacije, zagotavljanje ustrezne varnosti na gradbišču, tekoče vzdrževanje in končna odstranitev gradbišča; - zagotovitev potrebnih začasnih površin za transportne poti in gradnjo izven območja gradbišča s plačilom stroškov za sanacijo in vzpostavitev okoliških zemljišč in objektov v prvotno stanje (soglasja, odškodnine, itd.); - začasni odvoz, deponiranje in vračanje izkopanega materiala, ki ga ne bo možno deponirati na gradbišču; - odvoz in zagotovitev odstranjevanja odpadnega gradbenega materiala skladno z zakonodajo na področju ravnanja z odpadki (odvoz na urejene deponije s plačilom komunalnih prispevkov in taks itd.); - oteženi izkop v mokrem terenu, izkop v vodi, odvod meteorne vode iz gradbene jame in vode, ki se izceja iz bočnih strani izkopov; - ustrezno varovanje izkopa gradbene jame za objekt in ostalih manjših posameznih izkopov za izvedbo komunalne infrastrukture brez posegov na sosednja zemljišča; - ustrezno varovanje obstoječih objektov, infrastrukture in okolice v času gradnje ter dokumentiranje vseh morebitnih škodnih dogodkov; - pripravljalna, spremljajoča in zaključna dela (zakoličbe, zagotovitev potrebnih komunalnih priključkov za potrebe izvajanja gradnje, izvedba začasnih inštalacij, označevanje podzemnih vodov, postavljanje in vzdrževanje zakoličbenih profilov, izvedba in označevanje novih in starih križanj ter morebitna zaščita križanj komunalnih vodov, geodetski posnetki in izdajanje vmesnih posnetkov izvedene infrastrukture naročniku, izdelava zbirnih kart, itd.), v kolikor ni to drugače določeno; - pridobivanje soglasij in izvedba morebitnih zapor na vseh cestah s plačilom stroškov, nadomestil in pristojbin; - zagotovitev oz. postavitev in končna odstranitev po zaključku gradnje začasnih skladišč in začasnega pisarniškega kontejnerskega objekta vključno z opremo za dve delovni mesti in za skupne operativne sestanke vel. ca. 40 m2 za potrebe naročnika, s tekočim vzdrževanjem in čiščenjem. | The following must also be included or taken into account in the uniform prices for individual items: - a construction site organisation plan with a detailed timetable and the execution of all preparatory works, the setting-up, organisation, protection and registration of the construction site, site facilities, the arrangement of temporary storage facilities, ongoing maintenance, including the payment of general costs of fees and taxes of the administrative authorities, the obtaining of various permits and consents for the execution, the fencing of the site and the erection of construction signs and traffic signals, the provision of adequate security on the site, ongoing maintenance and the final dismantling of the construction site; - provision of the necessary temporary areas for transport routes and off-site construction, with costs for restoration and reinstatement of surrounding land and buildings (consents, compensation, etc.); - temporary removal, storage and return of excavated material that cannot be stored on site; - removing and disposing of waste building materials in accordance with waste management legislation (removal to regulated landfill sites with payment of municipal fees and charges, etc.); - difficult excavation in wet ground, excavation in water, drainage of rainwater from the construction pit and water draining from the sides of excavations; - adequate protection of the excavation of the construction pit for the building and other small individual excavations for the implementation of the utility infrastructure without encroaching on neighbouring land; - adequate protection of existing facilities, infrastructure and the surrounding area during construction, and documentation of any damage incidents; - preparatory, accompanying and finishing works (stake-out, provision of the necessary utility connections for the needs of construction, execution of temporary installations, marking of underground lines, installation and maintenance of stake-out profiles, execution and marking of new and old crossings and possible protection of crossings of utility lines, geodetic surveys and issuing of intermediate images of the completed infrastructure to the client, production of summary maps, etc.), unless otherwise specified; - obtaining consents and implementing any road closures, with costs, compensation and fees; - provision or erection and final removal on completion of construction of temporary storage and temporary office container building including equipment for two workstations and for joint operational meetings of approx. 40 m2 for the needs of the client, with ongoing maintenance and cleaning.
0.1.17 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - izdelava montažne tehnične dokumentacije, detajlov izvedbe in vse druge potrebne delavniške dokumentacije (s področja arhitekture, gradbeništva, elektrotehnike, strojništva in zunanje ter krajinske ureditve) ter pridobitev obvezne potrditve s strani projektanta, nadzornika in investitorja; - odprava vseh vrst inštalacijskih kolizij z izvajanjem potrebnih premikov inštalacij in njihovim usklajevanjem na mestu montaže, vse v obsegu, ki ne vpliva na projektirano rešitev ali tip inštalacij oz. opreme; - zagotavljanje kompletnosti elektro-instalacijskih sistemov s področja avtomatike za doseganje njihove popolne funkcionalnosti delovanja; - stroški za nadzor in koordinacijo izvedbe vseh elektro napeljav, ki so predmet končne instalacije proizvoda (senčila, vrata, okna,…); - izdelava montažnih skic in detajlov za izvedbo v dogovoru z vodjo gradnje in nadzornikom; - izdelava in predstavitev vzorcev v ustrezni velikosti za potrditev projektanta, nadzornika in investitorja; - zagotavljanje varnosti in zdravja pri delu, zlasti izvajanje vseh del, ki izhajajo in ukrepov, ki izhajajo iz določil veljavnih predpisov varstva pri delu in zahtev Varnostnega načrta;- stroški garancij, ki jih mora izvajalec predložiti naročniku. | The following must also be included or taken into account in the uniform prices for individual items: - preparation of prefabricated technical documentation, construction details and all other necessary workshop documentation (architectural, civil, electrical, mechanical, exterior and landscaping) and obtaining the mandatory approval of the designer, the supervisor and the investor; - elimination of all types of installation conflicts by carrying out the necessary relocation of installations and their coordination at the installation site, all to the extent that it does not affect the design solution or the type of installation or equipment; - ensuring the completeness of electrical installation systems in the automation sector to achieve their full operational functionality; - the cost of supervising and coordinating the installation of all the electrical installations that are the subject of the final installation of the product (blinds, doors, windows, etc.); - preparation of erection drawings and details for implementation in agreement with the construction manager and supervisor; - production and presentation of samples in appropriate sizes for the approval of the designer, the supervisor and the investor; - ensuring health and safety at work, in particular the implementation of all the works arising from and the measures resulting from the provisions of the applicable occupational safety regulations and the requirements of the Safety Plan; - the cost of the guarantees to be provided by the contractor to the client.
0.1.18 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - strošek vodje del glavnega izvajalca, ki bo izvajal tudi koordinacijo s podizvajalci in z drugimi izvajalci, ki jih bo izbral naročnik in bo opravljal delo vodje gradbišča; - koordinacija del z ostalimi izvajalci oz. podizvajalci del, projektantom, nadzornikom in investitorjem pri medsebojnem usklajevanju organizacije gradbišča in časovnega načrta del ter pri usklajevanju izdelave plana montaže, potrjenih s strani vseh udeležencev gradnje; - stroški koordinacije, sodelovanja in usklajevanja z dobavitelji tehnološke, laboratorijske, eksperimentalne in vse ostale pohištvene ter multimedijske opreme ter z vsemi ostalimi dobavitelji oz. podizvajalci na objektu; - stroški izdelave situacij; - stroški zavarovanja objekta v času izvedbe del in delavcev ter materiala na gradbišču v času izvajanja del, od začetka del do pridobitve uporabnega dovoljenja za objekt. Zavarovanje mora biti sklenjeno pri ustrezni zavarovalni družbi najmanj v višini pogodbene vrednosti ali v zakonsko predpisani vrednosti (v kolikor zavarovanje v višini pogodbene vrednosti presega zakonsko dovoljeno), za ves čas trajanja izvedbe del do uspešne primopredaje objekta; - preizkušanje kvalitete materiala, ki se vgrajuje in dokazovanje kvalitete s certifikati oz. tehničnimi soglasji; - izvedba vseh zahtevanih testov in preizkusov (npr. tlačni preizkusi, termografski pregledi, meritve elektromagnetnega sevanja, hrupa, itd.), poskusnega obratovanja celotnega objekta s poudarkom na vseh inštalacijah ter izvajanje predpisanega monitoringa v skladu s Poročilom o vplivih na okolje (pred gradnjo, med gradnjo in po končani gradnji); - izdelava izkaza požarne varnosti, vključno s sprotnim spremljanjem gradnje in izvajanjem požarnovarnostnih zahtev ter izdelava Požarnega reda z obveznimi prilogami; - izdelava Izkaza zaščite pred hrupom v stavbah; - izdelava Izkaza energijskih lastnosti stavbe in energetske izkaznice; - sodelovanje z izvajalci gradbenega in projektantskega nadzora in investitorjem za izvedbo tehničnega pregleda in priprava primopredaje, ki mora vsebovati vso zahtevano dokumentacijo, predvsem pa: izjave o skladnosti, požarni izkaz in ostale izkaze ter obvezne tabele, dokazilo o zanesljivosti objekta (DZO), certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo in vzdrževanje ter vse ostale dokumente v skladu s predpisi in pogodbenimi določili. | The following must also be included or taken into account in the uniform prices of the individual items: - the cost of a works manager for the main contractor, who will also coordinate with subcontractors and other contractors selected by the client and act as site manager; - coordination of the works with other contractors or subcontractors, the designer, the supervisor and the investor in coordinating the organisation of the construction site and the timetable for the works, and in coordinating the production of an installation plan approved by all the participants in the construction; - the costs of coordination, cooperation and coordination with suppliers of technological, laboratory, experimental and all other furniture and multimedia equipment, as well as with all other suppliers or subcontractors on the site; - the cost of drawing up situations; - the cost of insuring the building during the execution of the works and the workers and materials on site during the execution of the works, from the start of the works until the building has been licensed for occupation. The insurance must be taken out with a suitable insurance company for at least the contract value or the legal value (if the insurance for the contract value exceeds the legal value), for the entire duration of the works until the successful handover of the building; - testing the quality of the material to be installed and proving it with certificates or technical approvals; - carrying out all required tests and trials (e.g. pressure tests, thermographic inspections, electromagnetic radiation measurements, noise measurements, etc.), trial operation of the entire building, with emphasis on all installations, and carrying out the required monitoring in accordance with the Environmental Impact Assessment Report (before, during and after construction); - preparation of a fire safety statement, including ongoing monitoring of construction and implementation of fire safety requirements, and preparation of a Fire Safety Order with mandatory annexes; - preparation of a Noise Protection Statement for buildings; - preparation of the Building Energy Performance Report and Energy Performance Certificate; - cooperation with the construction and design supervision contractors and the investor to carry out the technical inspection and prepare the handover, which must include all the required documentation, in particular: declarations of conformity, fire and other statements and mandatory tables, proof of reliability of the building (DZO), certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use and maintenance, and all other documents in accordance with the regulations and the contractual provisions.
0.1.19 | V enotnih cenah posameznih postavk, ki se nanašajo na opremo in posamezne sisteme, mora biti zajeto oz. upoštevano tudi naslednje: - dobava oz. transport, - stroški za vse delovne stroje za dvigovanje bremen in delovne košare za dostope do delovišč; - morebitni stroški povzročeni upravljavcem GJI, ki bi nastali v zvezi s predmetno gradnjo; - montaža, vključno s pomožnim montažnim materialom (vezni, tesnilni in pritrdilni material, sidra, nosilni profili, podkonstrukcije in podobno) in navodili proizvajalca, - odprava vseh kolizij sistemov s stenami in med sistemi, - izvedba vseh potrebnih tesnjenj, - priključitev in nastavitve, vključno z morebitnim kalibriranjem, - zagon, testiranje in meritve, vključno s poročili, - šolanje uporabnikov oz. vzdrževalnega osebja za uporabo in vzdrževanje sistemov, - navodila za obratovanje in vzdrževanje, - vsi potrebni certifikati, izjave o skladnosti oz. potrdila ter - vsa druga pomožna dela in material, da se zagotovi funkcionalnost posamezne postavke popisa. | The following must also be included or taken into account in the uniform prices for individual items relating to equipment and individual systems: - delivery/transport, - the cost of all lifting machines and work baskets for access to work sites; - any costs incurred to the operators of utility infrastructure (GJI) in connection with the subject construction; - installation, including ancillary installation materials (bonding, sealing and fixing materials, anchors, support profiles, substructures, etc.) and manufacturer's instructions, - eliminating all system-to-wall and system-to-system collisions, - all necessary sealing work, - connection and set-up, including calibration if necessary, - commissioning, testing and measurements, including reports, - training users or maintenance staff in the use and maintenance of the systems, - operating and maintenance instructions, - any necessary certificates, declarations of conformity or attestations; and - all other ancillary works and materials to ensure the functionality of each inventory item.
0.1.20 | Vsi odri morajo biti upoštevani v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All scaffolding must be included in the uniform prices of the items listed, except where specifically mentioned.
0.1.21 | Vsi delovni in pomožni odri, lestve in ostala potrebna pomožna sredstva, kot tudi čiščenje vseh elementov po končanih delih, mora biti upoštevano v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All working and auxiliary scaffolding, ladders and other necessary ancillaries, as well as the cleaning of all elements after completion of the works, shall be included in the uniform prices of the items listed, except those specifically mentioned.
0.1.22 | Delavniško dokumentacijo za vse nosilne jeklene konstrukcije in podkonstrukcije izdela izvajalec, strošek izdelave delavniške dokumentacije se upošteva v ponujenih cenah in se ne obračuna posebej. | The cost of the shop drawings for all steelwork and substructures shall be included in the prices quoted and shall not be charged separately.
0.1.23 | V enotnih cenah postavk mora biti vključeno tudi vgrajevanje vseh instalacijskih razvodov v opaže armirano betonskih elementov in izdelava prehodov inštalacij ter dodatno izrezovanje utorov in prebojev v kamnite, zidane ali armirano-betonske stene, ponovno demontiranje in montiranje vseh vrst montažnih sten, vsa dodatna dela za zagotavljanje primernih križanj med posameznimi instalacijskimi vodi, izdelava vseh vrst ojačitev konstrukcij in podobna dela, ki zagotavljajo kakovostno vgradnjo vseh vrst instalacijskih vodov in niso posebej navedena v popisu GOI del. V ponudbi morajo biti upoštevana vsa drobna strojna in elektro instalacijska dela in transporti. | The installation of all installation ducts in the formwork of reinforced concrete elements and the construction of installation penetrations, as well as the additional cutting of grooves and penetrations in stone, masonry or reinforced concrete walls, the reassembly and reinstallation of all types of prefabricated walls, all additional work to ensure adequate crossings between individual installation ducts, the construction of all types of structural reinforcement and similar work to ensure the quality installation of all types of installation ducts and not specifically mentioned in the BoQ of the Construction, installation and finishing works (GOI) shall also be included in the uniform prices of the items. The tender shall take into account all minor mechanical and electrical installation work and transport.
0.1.24 | Vsi kovinski elementi in konstrukcije, ki bi lahko bili izpostavljeni atmosferskim in ostalim korozijskim vplivom, morajo biti ustrezno protikorozijsko zaščiteni. | All metallic elements and structures that could be exposed to atmospheric and other corrosive influences must be adequately protected against corrosion.
0.1.25 | Za vse večje jeklene dele se skladno s predpisi, izdelajo ustrezne ozemljitve, nevidno pritrjene in speljane na splošno ozemljitev objekta. | For all major steel parts, appropriate earth connections shall be made in accordance with the regulations, invisibly attached and connected to the general earth of the building.
0.1.26 | Za vse vidne elemente in serijske elemente je obvezna predhodna uskladitev obdelav, barv in materialov s projektantom na podlagi dostavljenih vzorcev v ustrezni velikosti. Obvezna je preveritev dejanskih mer na licu mesta in posledična prilagoditev elementov in njihove montaže. | For all visible elements and serial elements, it is mandatory to coordinate the finishes, colours and materials with the designer beforehand on the basis of the supplied samples in the appropriate size. It is mandatory to check the actual dimensions on site and to adjust the elements and their installation accordingly.
0.1.27 | Dimenzije obrtniških izdelkov in količine je potrebno pred naročanjem preveriti na objektu. Potrebna je uskladitev vseh elementov (kljuke, okovje, detajlne konstrukcije in obdelave, itd.) s projektantom, nadzornikom in investitorjem. Izvajalec je dolžan pred izdelavo predložiti projektantu v potrditev ustrezne delavniške načrte in detajle. | The dimensions of the workmanship and quantities must be checked on site before ordering. All elements (hooks, fittings, detailed construction and finishes, etc.) must be coordinated with the designer, the supervisor and the investor. The contractor is obliged to submit the relevant workshop plans and details to the designer for approval before manufacture.
0.1.28 | V posameznih postavkah popisa so navedeni proizvajalci in/ali tipi posameznih sistemov, materialov ali opreme, s čimer so zgolj natančno opredeljene zahtevane tehnične lastnosti. Izvajalec del lahko ponudi nadomesten sistem, material ali opremo drugega proizvajalca in tipa, pri čemer morajo biti tehnične lastnosti ponujenega sistema, materiala ali opreme enakovredne ali boljše od opredeljenih v popisu, dimenzijsko pa ne smejo presegati projektiranih dimenzij. Vse funkcijske in tehnične karakteristike nadomestnih sistemov, materialov ali opreme mora izvajalec dokazati z ustrezno dokumentacijo. Vse morebitne posledice zaradi spremembe sistemov, materialov ali opreme vključno z morebitnimi spremembami oz. dopolnitvami BIM modelov in projektne dokumentacije, stroškovno in časovno bremenijo izvajalca. | The individual items of the Inventory shall specify the manufacturers and/or types of the individual systems, materials or equipment, thereby merely specifying the required technical characteristics. The Contractor may offer a substitute system, material or equipment of a different manufacturer and type, provided that the technical characteristics of the offered system, material or equipment shall be equivalent to or better than those specified in the BoQ, and shall not exceed the design dimensions. All functional and technical characteristics of the substitute systems, materials or equipment shall be demonstrated by the Contractor with appropriate documentation. Any consequences resulting from changes to systems, materials or equipment, including any changes or additions to the BIM models and project documentation, shall be borne by the Contractor in terms of cost and time.
0.1.29 | Vsako zamenjavo, uporabo in končni izbor nadomestnih sistemov, materialov, proizvodov in opreme morajo obvezno in pravočasno (pred dobavo in vgradnjo) pisno potrditi projektant (vseh sodelujočih strok), nadzornik in investitor. | Any replacement, use and final selection of alternative systems, materials, products and equipment must be approved in writing by the designer (of all disciplines involved), the supervisor and the investor in a timely manner (prior to delivery and installation).
0.1.30 | Izvajalec mora v ponudbeno ceno vključiti tudi: - ves čas gradnje sprotno beleženje sprememb oz. odstopanj od PZI dokumentacije, vključno z izdelavo tekstualnega opisa sprememb, - pripravo podlog na nivoju PZI, ki so potrebne za posodobitev oz. uskladitev BIM modela z izvedenim stanjem (LOD 500) in izdelavo projektne dokumentacije izvedenih del (PID), - mesečno predajanje potrjenih sprememb opreme in materiala, ki vplivajo na BIM model, v formatu IFC, - vzdrževanje in uporabljanje pri izvedbi zadnje veljavne revizije PZI dokumentacije, vključno z dopolnitvami PZI načrtov, ki so nastali zaradi sprememb med gradnjo. | The contractor must also include in the tender price: - keeping a record of changes or deviations from the construction documentation (PZI) throughout construction, including a textual description of the changes, - preparation of the Detailed Design (PZI) level documents required to update or align the BIM model with the as-built condition (LOD 500) and the preparation of the as-built project documentation for the works (PID), - monthly submission of approved equipment and material changes affecting the BIM model in IFC format, - maintenance and use in the execution of the last valid revision of the construction documentation (PZI), including additions to the construction design documentation (PZI) resulting from changes during construction.
| OPOMBE: | REMARKS:
0.1.31 | Tribune vzhodnega trga (na severni strani objekta zaklonišča), ki so oz. bodo služile kot vhod na športno igrišče, obsip objekta na V in J strani objekta, humuziranje in zatravitev, so predmet projekta št. 380-20 (Skupni uvoz in zunanja ureditev območja FS in FFA) in niso upoštevane v tem popisu. | The stands of the eastern square (on the north side of the shelter building), which are or will be used as the entrance to the sports ground, the building envelope on the E and S sides of the building, the humidification and the grassing, are the subject of project No 380-20 (Joint access and external landscaping of the FS and FFA areas) and are not included in this bill of quantities.
0.1.32 | Vsa predvidena oprema mora biti skladna s Pravilnikom o tehničnih normativih za zaklonišča in zaklonilnike (Uradni list RS, št. 17/98, 26/98 – popr., 25/00, 38/01 in 66/06). | All equipment must comply with the Regulation on Technical Standards for Shelters and Defenders (Official Gazette of the Republic of Slovenia, No. 17/98, 26/98 - corrected, 25/00, 38/01 and 66/06).

## 0.2_Uvod-DGNB
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
0.2 | SPLOŠNI TEHNIČNI POGOJI ZA PODROČJE DGNB CERTIFICIRANJA | GENERAL TECHNICAL CONDITIONS FOR DGNB CERTIFICATION
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic entity with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
| Splošni pogoji za področje DGNB certificiranja predstavljajo dopolnilo splošnim tehničnim pogojem in ne odpravljajo drugih obveznosti in odgovornosti, ki jih ima izvajalec v skladu s predpisi in pogodbo. | The General Conditions for DGNB Certification are complementary to the General Technical Conditions and do not exclude other obligations and responsibilities that the Contractor has under the Regulations and the Contract.
0.2.1 | Izvajalec mora v svojih ponudbah upoštevati, da se bo objekt certificiral v skladu z zahtevami DGNB sistema certificiranja trajnostne gradnje, ter pravočasno (vsaj 60 dni pred vgradnjo posameznega produkta) dostaviti vso ustrezno dokumentacijo za vse v ponudbi zajete materiale, elemente in opremo. Zahtevana je uporaba materialov, elementov ali opreme, ki so okolju in ljudem prijazni, energetsko učinkoviti in obenem ustrezajo zahtevam DGNB sistema. Zahtevan nivo certifikata je: ZLATI CERTIFIKAT | The Contractor shall take into account in its tenders that the building will be certified in accordance with the requirements of the DGNB Sustainable Building Certification Scheme and shall deliver all relevant documentation for all materials, elements and equipment included in the tender in a timely manner (at least 60 days before the installation of each product). The use of materials, elements or equipment that are environmentally and human friendly, energy efficient and at the same time meet the requirements of the DGNB system is required. The required level of certification is: GOLD CERTIFICATE
0.2.2 | Podrobnejši opis DGNB sistema in navodila za posamezne kriterije so dostopna v dokumentu"DGNB Criteria Set New Construction Buildings, Version 2020 International", ki je na voljo na DGNB spletni strani https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria | A more detailed description of the DGNB system and guidance on the individual criteria is available in the document "DGNB Criteria Set New Construction Buildings, Version 2020 International", available on the DGNB website https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria
0.2.3 | Izvajalec mora v svojih ponudbah upoštevati, da je potrebno skladno z določili DGNB certifikacijskega sistema, pravočasno (pred pričetkom gradnje) dostaviti vso ustrezno dokumentacijo, za vse v ponudbi zajete materiale, elemente in opremo (tehnični list, varnostni list, izjava o lastnostih, tehnična navodila za ravnanje, servisiranje, vzdrževanje,...) v slovenskem jeziku. Vgradnja kakršnihkoli materialov, elementov ali opreme, se izvede zgolj na podlagi predhodne preveritve posredovane dokumentacije in obenem potrditve s strani nadzornika. | The Contractor must take into account in its tenders that, in accordance with the provisions of the DGNB certification system, all relevant documentation for all materials, elements and equipment included in the tender (technical data sheet, safety data sheet, declaration of properties, technical instructions for handling, servicing, maintenance,...) must be delivered on time (prior to the start of construction) in the Slovene language (in accordance with the provisions of the DGNB certification system). The installation of any materials, elements or equipment shall be subject to prior checking of the submitted documentation and, at the same time, to the approval of the Supervisor.
0.2.4 | Izbrani materiali, elementi, naprave, sistemi in oprema morajo prispevati k večji trajnosti stavbe v smeri zagotavljanja energetske učinkovitosti, ekonomičnega in enostavnega vzdrževanja ter čiščenja, dolge življenjske dobe, uporabe okolju prijaznih materialov ipd. | The materials, elements, appliances, systems and equipment chosen must contribute to the sustainability of the building in terms of energy efficiency, economic and easy maintenance and cleaning, long lifetime, use of environmentally friendly materials, etc.
0.2.5 | Predloženi dokumenti za vse uporabljene materiale, elemente in opremo morajo izpolnjevati zahteve najmanj kakovostne stopnje QS3 (zaželeno QS4), iz dokumenta: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001) | The documents submitted for all materials, components and equipment used shall meet the requirements of at least quality level QS3 (preferably QS4) of the document DGNB Quality Grades for Materials, Components and Equipment (JULFS--7X9001)
0.2.6 | V kolikor izbrani materiali oz. elementi, navedeni v posameznih postavkah, ne ustrezajo vsaj kakovostni stopnji QS3 iz seznama: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), je izvajalec dolžan na to opozoriti projektanta, nadzor in investitorja ter podati predlog ustreznega materiala oz. elementa. | If the selected materials or elements listed in the individual items do not meet at least quality level QS3 of the list of DGNB quality classes for materials, elements and equipment (JULFS--7X9001), the Contractor shall draw this to the attention of the Designer, the Supervisor and the Investor, and shall make a proposal for a suitable material or element.
0.2.7 | Izvajalec lahko v svoji ponudbi predlaga alternativne produkte in rešitve glede na predvidene s projektom, pod pogojem, da le-te prav tako izpolnjujejo vse navedene zahteve. Pri morebitnih predlaganih alternativnih produktih oz. rešitvah je potrebno upoštevati najmanj enake ali boljše lastnosti v smislu življenjske dobe, obstojnosti, ter enostavnosti in stroška čiščenja ter vzdrževanja v primerjavi s projektom predpisanimi rešitvami. Za alternativne rešitve izvajalec pridobi soglasje projektanta, nadzornika in investitorja pred pričetkom gradnje. | The Contractor may propose alternative products and solutions to those envisaged by the project in its tender, provided that they also meet all the requirements set out above. Any alternative products or solutions proposed shall have at least the same or better characteristics in terms of service life, durability, and ease and cost of cleaning and maintenance compared to the solutions envisaged by the project. For alternative solutions, the contractor shall obtain the agreement of the designer, the supervisor and the investor before starting construction.
0.2.8 | Izvajalec med gradnjo dnevno beleži vsa eventualna odstopanja od PZI projektne dokumentacije ter podatke pravočasno posreduje naročniku, nadzoru in projektantu. Potrjene spremembe vnese v podlage za izdelavo PID in posodobitev BIM modelov. | During construction, the Contractor shall record on a daily basis any deviations from the Detailed Design documentation (PZI) and shall provide the information to the Client, Supervision and the Designer in a timely manner. Confirmed changes shall be entered into the basis for the As-built documentation (PID) and BIM model updates.
0.2.9 | Izvajalec med gradnjo sproti izpolnjuje Seznam vseh konstrukcijskih sestav s pripadajočimi vgrajenimi gradbenimi materiali in dokumentira naslednje podatke o vgrajenih materialih (v slovenskem jeziku): - Varnostni list - Tehnični list - Izjavo o lastnostih (če je relevantno) - Izkazovanje morebiti obstoječega okoljskega certifikata (Tip I - okoljski znak ali Tip III - okoljska produktna deklaracija /EPD) - Izjavo proizvajalca ali dobavitelja, da produkt ustreza zahtevam ENV1.2 - Tehnična navodila za ravnanje, servisiranje, vzdrževanje oziroma ostale, z zakonom predpisane dokumente in dokumentacijo. | During construction, the Contractor shall keep a List of all structural assemblies with their associated construction materials and document the following information on the materials installed (in Slovene language): - Safety Data Sheet - Technical Data Sheet - Declaration of performance (if applicable) - Demonstration of any existing environmental certification (Type I - Ecolabel or Type III - Environmental Product Declaration /EPD) - A declaration by the manufacturer or supplier that the product complies with the requirements of ENV1.2 - Technical instructions for handling, servicing, maintenance or other documents and documentation required by law.
0.2.10 | Za vse vgrajene bistvene tehnične sisteme mora izvajalec zagotoviti obstoj pooblaščenega servisa, ki deluje na območju Republike Slovenije, da ima investitor možnost skleniti ustrezno pogodbo o vzdrževanju. Med bistvene tehnične sisteme sodijo npr.: sistemi ogrevanja in hlajenja, priprava tehnoloških medijev, prezračevanje in klimatizacija, sistemi detekcije in gašenja požara, sistemi tehničnega varovanja, BMS in CNS sistemi upravljanja stavbe, razsvetljava, komunikacijski in WI-FI sistemi,... | For all installed essential technical systems, the contractor must ensure the existence of an authorised service centre operating in the territory of the Republic of Slovenia, so that the investor has the possibility of concluding an appropriate maintenance contract. The essential technical systems include, for example: heating and cooling systems, technological media preparation, ventilation and air conditioning, fire detection and extinguishing systems, technical security systems, BMS and CNS building management systems, lighting, communication and WI-FI systems,...
0.2.11 | Zaželeno je, da imajo uporabljeni elementi in materiali okoljsko oznako Tip I. (kot npr. ENCODE, BLUE ANGEL, ipd...). | It is preferable that the elements and materials used have a Type I environmental label (such as ENCODE, BLUE ANGEL, etc...).
0.2.12 | Izvajalec bo za elemente iz lesa moral dokazovati izvor z navedbo izvorne države in tipa lesa, FSC / PEFC certifikat z dodatnim pripadajočim potrdilom Chain of custody-trgovski certifikat dobavitelja - ta se dokazuje z dobavnicami, računi ali enakovredno. Za izdelke iz naravnega kamna iz EU držav je potrebna deklaracija, da je izvor in procesiranje teh izdelkov v celoti v EU državah. Za izdelke iz naravnega kamna, ki prihajajo iz držav izven EU, je potrebno predložiti dokazilo o izpolnjevanju ILO konvencije 182, ki vključuje neodvisna inšpekcijska poročila. | For wood elements, the contractor will be required to provide proof of origin, indicating the country of origin and the type of wood, FSC/PEFC certification with an additional Chain of Custody certificate - the supplier's trade certificate - this shall be evidenced by delivery notes, invoices or equivalent. For natural stone products from EU countries, a declaration that the sourcing and processing of these products is entirely in EU countries is required. For natural stone products from non-EU countries, proof of compliance with ILO Convention 182, including independent inspection reports, is required.
0.2.13 | Izobraževanje udeležencev pri gradnji Izvajalec je dolžan vse udeležence pri gradnji podrobneje seznaniti tudi z relevantnimi koncepti, študijami, elaborati, ki opredelujejo trajnostni način gradnje za naslednja področja: - zaščita pred hrupom (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)) - zaščita pred prašenjem - zaščita tal in podzemne vode (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)), Analiza tveganja za onesnaženje vodnega telesa podzemne vode št. 0346-023/2023, maj 2023 (Geološko projektiranje d.o.o.)) - ravnanje z gradbenimi odpadki (Načrt gospodarjenja z gradbenimi odpadki) Izobraževanja se izvajajo skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.1 1.2, 2.2, 3.2 in 4.2 Training for the parties implementing the construction work | Training of construction participants The contractor is also obliged to inform all construction participants in detail about relevant concepts, studies, elaborations defining sustainable construction methods for the following areas: - noise protection (Environmental Impact Assessment Report No 100123-11523, dated 11.5.2023, supplemented on 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.)) - dust protection - protection of soil and groundwater (Environmental Impact Assessment Report No. 100123-11523, dated 11.5.2023, supplemented 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.), Risk analysis for contamination of the groundwater No. 0346-023/2023, May 2023 (Geološko projektiranje d.o.o.)) - construction waste management (Construction Waste Management Plan) The training shall be carried out in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.1 1.2, 2.2, 3.2 and 4.2 Training for the parties implementing the construction work
0.2.14 | Navodila za obratovanje in vzdrževanje objekta Izvajalec pripravi Navodila za obratovanje in vzdrževanje objekta skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilih: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual | Instructions for the operation and maintenance of the facility The Contractor shall prepare the Operation and Maintenance Instructions for the Facility in accordance with the applicable Slovenian legislation and the DGNB System Instructions specified in the Criteria: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual
0.2.15 | Meritve kontrole kakovosti gradnje Izvajalec mora upoštevati, da se bodo po koncu gradnje izvedle naslednje meritve: - meritve zrakotesnosti - meritve s termokamero (termografija) - meritve akustike - meritve zvočne zaščite ovoja stavbe - meritve zvočne zaščite ločilnih elementov med posameznimi prostori različnih namembnosti - meritve udarnega zvoka - meritve vlažnosti vgrajenih elementov, pred vgradnjo finalnih tlakov - test odvoda dima in toplote Meritve morajo opraviti ustrezno usposobljeni preskusni organi ali strokovnjaki ter rezultate oceniti in primerjati z zahtevami. Obseg opravljenih meritev mora biti sorazmeren z velikostjo zgradbe in mora ustrezno odražati cilj preverjanja kakovosti zgradbe. Smiselno je, da izvajalec del tekom gradnje za sprotno kontrolo kakovosti vgrajenih materialov, elementov in opreme, sam izvaja meritve. Končne meritve (ob primopredaji) izvede tretja oseba kot neodvisna potrditev doseganja zahtev. Meritve se izvajajo skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 2. Quality control measurements | Construction quality control measurements The contractor must take into account that the following measurements will be carried out after completion of the construction: - airtightness measurements - thermal camera measurements (thermography) - acoustics measurements - measurements of the sound insulation of the building envelope - measurements of the sound insulation of the separating elements between different rooms of different uses - impact sound measurements - moisture measurements of the installed elements, prior to the installation of the final flooring - smoke and heat extraction test The measurements shall be carried out by suitably qualified test bodies or experts and the results evaluated and compared with the requirements. The extent of the measurements carried out shall be proportionate to the size of the building and shall adequately reflect the objective of the building quality verification. It is reasonable for the contractor to carry out his own measurements during construction to check the quality of the materials, elements and equipment installed. Final measurements (at handover) are carried out by a third party as an independent confirmation of compliance with the requirements. The measurements shall be carried out in accordance with the applicable Slovenian legislation and the DGNB system instructions specified in the benchmark: PRO 2.2 2. Quality control measurements
0.2.16 | Zagotavljanje kakovosti za uporabljene gradbene proizvode Izvajalec mora zagotavljati izvajanje primerjav med definiranim in dejansko uporabljenim materialom, elementom ali opremo skladno seznamom: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), vključno z dokazno dokumentacijo ugotovitev primerjav ter skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 3.1 Quality assurance for the used construction products | Quality assurance for the construction products used The Contractor shall ensure that comparisons are made between the defined and the actual material, element or equipment used in accordance with the list: DGNB Quality Grades of Installed Materials, Elements and Equipment (JULFS--7X9001), including supporting documentation of the findings of the comparisons, and in accordance with the DGNB system instructions defined in the Criterion: PRO 2.2 3.1 Quality assurance for the used construction products
0.2.17 | Zaščita pred vlago Izvajalec predloži dokumentacijo, ki dokazuje, da je bil izveden program prezračevanja, prilagojen stavbi, s čimer se zagotovi pogoje, da so vgrajeni gradbeni elementi ustrezno suhi, skladno z navodili DGNB opredeljenimi v merilu: PRO 2.2 4.1 Mould prevention | Protection against moisture The Contractor shall provide documentation demonstrating that a building-specific ventilation programme has been implemented to ensure that the building elements installed are adequately dry, in accordance with the DGNB guidelines specified in the criteria: PRO 2.2 4.1 Mould prevention
0.2.18 | Preizkusi delovanja sistemov Izvajalec sodeluje pri izvedbi predhodnega in končnega preizkusa delovanja vseh bistvenih tehničnih komponent stavbe in pripravi ustrezne dokazne dokumentacije ter pri usposabljanju vzdrževalcev/upravljalcev stavbe, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators | System performance tests The Contractor shall be involved in the performance of the preliminary and final performance tests of all essential technical components of the building and the preparation of the relevant supporting documentation, as well as in the training of the maintenance/management staff of the building, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators
0.2.19 | Poročilo o zagonu objekta Izvajalec sodeluje pri pripravi končnega poročila o zagonu objekta, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 5.1 Creation of a detailed final report | Commissioning report The Contractor shall be involved in the preparation of the final commissioning report, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 5.1 Creation of a detailed final report
0.2.20 | Koncept celovitega delovanja sistemov v stavbi Izvajalec sodeluje pri procesu implementiranja stalnega nadzora in nastavitev delovanja stavbe ter usposabljanju vzdrževalcev/upravljalcev stavbe. Navedeno se izvede v skladu z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 6.1 Creation and handover of an integral operating concept | The concept of integrated building systems The contractor is involved in the process of implementing the building's continuous monitoring and settings and training the building's maintenance/management staff. This shall be done in accordance with the DGNB system instructions defined in the benchmark: PRO 2.3 6.1 Creation and handover of an integral operating concept
0.2.21 | Prilagoditev nastavitev sistemov po začetni fazi uporabe objekta Izvajalec sodeluje pri ponovnem pregledu delovanja vseh bistvenih tehničnih sistemov ter eventualni ponovni prilagoditvi teh sistemov s strani strokovnjaka oz. (neodvisne) tretje osebe. Postopek se izvede po približno 10–14 mesecih po zaključku gradnje, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 7.1 Readjustment of the system following initial operating phase | Adjusting system settings after the initial phase of use of the building The Contractor shall be involved in the re-examination of the functioning of all essential technical systems and the possible re-adjustment of these systems by an expert or (independent) third party. The procedure shall be carried out approximately 10-14 months after completion of construction, in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.3 7.1 Readjustment of the system following initial operating phase

## 3.1.0_Rekapitulacija
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
| REKAPITULACIJA STROŠKOV ELEKTRO DEL | COST SUMMARY OF ELECTRICAL WORKS
| 3 NAČRT S PODROČJA ELEKTROTEHNIKE | 3 DOCUMENTATION IN THE FIELD OF ELECTRICAL ENGINEERING
| 3/1 Zaklonišče | 3/1 Shelter
3.1 | ELEKTRO DELA | ELECTRICAL WORKS
3.1.1 | EE DOVOD | EE MAIN POWER SUPPLY | 0
3.1.2 | RAZDELILNIKI IN ROČNI ELEKTRIČNI GENERATOR (REG) | SWITCHGEAR AND HAND-HELD ELECTRIC GENERATOR (REG) | 0
3.1.3 | RAZSVETLJAVA | LIGHTING | 0
3.1.4 | MALA MOČ | SMALL POWER AND SOCKET OUTLETS | 0
3.1.5 | INFORMACIJSKO KOMUNIKACIJSKI SISTEM (IKS) | INFORMATION AND COMMUNICATION SYSTEM (IKS) | 0
3.1.6 | AVTOMATSKO JAVLJANJE POŽARA | AUTOMATIC FIRE DETECTION | 0
3.1.7 | OZEMLJITVE IN STRELOVODNA NAPELJAVA | EARTHING AND LIGHTNING CONDUCTOR WIRING | 0
3.1.8 | IZENAČEVANJE POTENCIALA | EQUALISING POTENTIAL | 0
3.1.9 | OSTALO | OTHER | 0
0
0 | NEPREDVIDENA DELA | UNFORSEEN WORKS | 0
| SKUPAJ ELEKTRO DELA | TOTAL ELECTRICAL WORKS | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT

## 3.1.1_EE dovod
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
3.1 | ELEKTRO DELA | ELECTRICAL WORKS
3.1.1 | EE DOVOD | EE MAIN POWER SUPPLY |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
1 | EE DOVOD | EE MAIN POWER SUPPLY
1.1 | Glavni napajalni kabel, deloma položen na police (10%) deloma uvlečen v zaščitne cevi (90%), vključno z označevalnimi ploščicami, ter drobnim in spojnim materialom, odziv na ogenj vsaj Cca. Kabli brez halogena. | Main power cable, partly laid on shelves (10%) partly trapped in protective tubes (90%), including marker plates, and small and jointing material, reaction to fire at least Cca. Cables halogen-free.
| - N2XH-J 5x6 mm² | - N2XH-J 5x6 mm² | m | 200 |  | 0
| EE DOVOD | EE MAIN POWER SUPPLY |  |  |  | 0

## 3.1.2_Razdelilniki in REG
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
3.1 | ELEKTRO DELA | ELECTRICAL WORKS
3.1.2 | RAZDELILNIKI IN ROČNI ELEKTRIČNI GENERATOR (REG) | SWITCHGEAR AND HAND-HELD ELECTRIC GENERATOR (REG) | [5 empty] | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description |  |  | EM | Količina | Cena/EM | Cena
2 | RAZDELILNIKI IN ROČNI ELEKTRIČNI GENERATOR (REG) | SWITCHGEAR AND HAND-HELD ELECTRIC GENERATOR (REG)
2.1 | Razdelilnik za stensko montažo +NN.P1-Z1-R, dimenzij 600x800x250mm (ŠxVxG), TN-S, IP 66. Kot naprimer omara Spacial CRN RAL7035, tip: NSYCRN86250P, Schneider. | Wall-mounted switchgear +NN.P1-Z1-R, dimensions 600x800x250mm (WxHxD), TN-S, IP 66. As for example cabinet Spacial CRN RAL7035, type: NSYCRN86250P, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=50 kA, In=20 kA Class I+II; kot naprimer Schneider, tip: A9L16482 | - 4-pole surge arrester, Imax=50 kA, In=20 kA Class I+II; as for example Schneider, type: A9L16482 | kos | 1
| glavno ločilno stikalo In=32 A, 16 kA, 3-polni za montažo na montažno ploščo; kot naprimer NSXm tip: C11E3TM032L, Schneider in podaljšana vrtljiva ročica za krmiljenje, kot naprimer: LV426932T, Schneider | main isolating switch In=32 A, 16 kA, 3-pole for mounting on mounting plate; as for example NSXm type: C11E3TM032L, Schneider and extended rotary control arm as for example LV426932T, Schneider | kos | 1
| -tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | -3-pole circuit breaker 4 A, with C characteristic, 15kA, such as Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| -enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | -single-pole circuit breaker 10 A, with C characteristic, 15kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 8
| -kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 10 A s C karakteristiko, 30mA,¸tip A kot naprimer Acti 9 DPN Vigi K, tip: A9D21616, Schneider | -combination protection switch with overcurrent protection (KZS), 1P+N, 10 A with C characteristic, 30mA, type A as for example Acti 9 DPN Vigi K, type: A9D21616, Schneider | kos | 1
| -kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip A kot naprimer Acti 9 DPN Vigi K, tip: A9D21616, Schneider | -combination protection switch with overcurrent protection (CPS), 1P+N, 16 A with C characteristic, 30mA, type A as for example Acti 9 DPN Vigi K, type: A9D21616, Schneider | kos | 4
| - motorsko zaščitni odklopnik z integrirano termomagnetno zaščito, 0.63-1A, kot naprimer tip: GV2ME05, Schneider | - motor protection circuit breaker with integrated thermal magnetic protection, 0.63-1A, e.g. type: GV2ME05, Schneider | kos | 2
| - kontaktor, 3P, 9A , tuljav 230V/50Hz, kot naprimer TeSys D AC-3 tip: LC1D09P5, Schneider | - contactor, 3P, 9A, 230V/50Hz coil, e.g. TeSys D AC-3 type: LC1D09P5, Schneider | kos | 2
| - kontaktor, 1xNO, 16A, 230 do 240V/50Hz, kot naprimer Acti 9 iCT, tip: A9C22711, Schneider | - contactor, 1xNO, 16A, 230 to 240V/50Hz, as for example Acti 9 iCT, type: A9C22711, Schneider | kos | 3
| - signalna svetilka, LED, bela barva Ø 22 mm, 220...230V AC, kot naprimer tip: XA2EVM1LC, Schneider | - signal luminaire, LED, white Ø 22 mm, 220...230V AC, as for example type: XA2EVM1LC, Schneider | kos | 1
| - DIN vtičnica z LED indikatorsko luči za prisotnost napetosti, 2P+E, 16 A, 250 V, kot naprimer tip: A9A15035, Schneider | - DIN socket with LED indicator light for voltage presence, 2P+E, 16 A, 250 V, as for example type: A9A15035, Schneider | kos | 1
| - miniaturni vtični rele - Zelio RXM 2 C/O 230 V AC 12 A, vtičnica RPZ. tip: RXM2AB1P7 + RPZ, Schneider | - miniature plug-in relay - Zelio RXM 2 C/O 230 V AC 12 A, socket RPZ. type: RXM2AB1P7 + RPZ, Schneider | kos | 1
| - osvetljene tipke z integriranim LED, 220-230V, zelena barva Ø 22 mm, kot naprimer tip:XA2EW33B1, Schneider | - illuminated pushbuttons with integrated LED, 220-230V, green Ø 22 mm, e.g. type:XA2EW33B1, Schneider | kos | 1
| - grebenasto stikalo 1-0, 1P, 60°, 10 A - za Ø 22 mm, kot naprimer tip:K10A001ACH, Schneider | - crest switch 1-0, 1P, 60°, 10 A - for Ø 22 mm, e.g. type:K10A001ACH, Schneider | kos | 2
| - grebenasto stikalo 1-0-2, 1P, 60°, 10 A - za Ø 22 mm, kot naprimer tip:K10B001UCH, Schneider | - crest switch 1-0-2, 1P, 60°, 10 A - for Ø 22 mm, e.g. type:K10B001UCH, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
2.2 | Razdelilnik za stensko montažo +NN.P1-Z2-R, dimenzij 600x800x250mm (ŠxVxG), TN-S, IP 66. Kot naprimer omara Spacial CRN RAL7035, tip: NSYCRN86250P, Schneider. | Wall-mounted switchgear +NN.P1-Z2-R, dimensions 600x800x250mm (WxHxD), TN-S, IP 66. As for example cabinet Spacial CRN RAL7035, type: NSYCRN86250P, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=50 kA, In=20 kA Class I+II; kot naprimer Schneider, tip: A9L16482 | - 4-pole surge arrester, Imax=50 kA, In=20 kA Class I+II; as for example Schneider, type: A9L16482 | kos | 1
| glavno ločilno stikalo In=32 A, 16 kA, 3-polni za montažo na montažno ploščo; kot naprimer NSXm tip: C11E3TM032L, Schneider in podaljšana vrtljiva ročica za krmiljenje, kot naprimer: LV426932T, Schneider | main disconnecting switch In=32 A, 16 kA, 3-pole for mounting on mounting plate; as for example NSXm type: C11E3TM032L, Schneider and extended rotary control lever as for example LV426932T, Schneider | kos | 1
| -tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | -3-pole circuit breaker 4 A, with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| -enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | -single-pole circuit breaker 10 A, with C characteristic, 15kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 10
| -kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 10 A s C karakteristiko, 30mA,¸tip A kot naprimer Acti 9 DPN Vigi K, tip: A9D21616, Schneider | -combination protection switch with overcurrent protection (KZS), 1P+N, 10 A with C characteristic, 30mA, type A as for example Acti 9 DPN Vigi K, type: A9D21616, Schneider | kos | 1
| -kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip A kot naprimer Acti 9 DPN Vigi K, tip: A9D21616, Schneider | -combination protection switch with overcurrent protection (CPS), 1P+N, 16 A with C characteristic, 30mA, type A as for example Acti 9 DPN Vigi K, type: A9D21616, Schneider | kos | 5
| - motorsko zaščitni odklopnik z integrirano termomagnetno zaščito, 0.63-1A, kot naprimer tip: GV2ME05, Schneider | - motor protection circuit breaker with integrated thermal magnetic protection, 0.63-1A, e.g. type: GV2ME05, Schneider | kos | 3
| - kontaktor, 3P, 9A , tuljav 230V/50Hz, kot naprimer TeSys D AC-3 tip: LC1D09P5, Schneider | - contactor, 3P, 9A, 230V/50Hz coil, e.g. TeSys D AC-3 type: LC1D09P5, Schneider | kos | 3
| - kontaktor, 1xNO, 16A, 230 do 240V/50Hz, kot naprimer Acti 9 iCT, tip: A9C22711, Schneider | - contactor, 1xNO, 16A, 230 to 240V/50Hz, as for example Acti 9 iCT, type: A9C22711, Schneider | kos | 4
| - signalna svetilka, LED, bela barva Ø 22 mm, 220...230V AC, kot naprimer tip: XA2EVM1LC, Schneider | - signal luminaire, LED, white Ø 22 mm, 220...230V AC, as for example type: XA2EVM1LC, Schneider | kos | 3
| - DIN vtičnica z LED indikatorsko luči za prisotnost napetosti, 2P+E, 16 A, 250 V, kot naprimer tip: A9A15035, Schneider | - DIN socket with LED indicator light for voltage presence, 2P+E, 16 A, 250 V, as for example type: A9A15035, Schneider | kos | 1
| - miniaturni vtični rele - Zelio RXM 2 C/O 230 V AC 12 A, vtičnica RPZ. tip: RXM2AB1P7 + RPZ, Schneider | - miniature plug-in relay - Zelio RXM 2 C/O 230 V AC 12 A, socket RPZ. type: RXM2AB1P7 + RPZ, Schneider | kos | 1
| - osvetljene tipke z integriranim LED, 220-230V, zelena barva Ø 22 mm, kot naprimer tip:XA2EW33B1, Schneider | - illuminated pushbuttons with integrated LED, 220-230V, green Ø 22 mm, e.g. type:XA2EW33B1, Schneider | kos | 1
| - grebenasto stikalo 1-0, 1P, 60°, 10 A - za Ø 22 mm, kot naprimer tip:K10A001ACH, Schneider | - crest switch 1-0, 1P, 60°, 10 A - for Ø 22 mm, e.g. type:K10A001ACH, Schneider | kos | 3
| - grebenasto stikalo 1-0-2, 1P, 60°, 10 A - za Ø 22 mm, kot naprimer tip:K10B001UCH, Schneider | - crest switch 1-0-2, 1P, 60°, 10 A - for Ø 22 mm, e.g. type:K10B001UCH, Schneider | kos | 4
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
2.3 | Razdelilnik za stensko montažo +REG.P1-Z1.1, dimenzij 267x200x112mm (ŠxVxG), TN-S, IP 65. Kot naprimer Mini Kaedra 1x12 modulov, tip: 13979, Schneider. | Wall-mounted distributor +REG.P1-Z1.1, dimensions 267x200x112mm (WxHxD), TN-S, IP 65. As for example Mini Kaedra 1x12 modules, type: 13979, Schneider. |  |  | kpl | 1 |  | 0
| -dvopolni inštalacijski odklopnik 2 A, DC s C karakteristiko, kot naprimer Acti 9 C60H-DC tip: A9N61522, Schneider | -2 A, DC double-pole circuit breaker with C characteristic, such as Acti 9 C60H-DC type: A9N61522, Schneider | kos | 2
| -dvopolni inštalacijski odklopnik 4 A, DC s C karakteristiko, kot naprimer Acti 9 C60H-DC tip: A9N61524, Schneider | -4 A, DC double-pole circuit breaker with C characteristic, such as Acti 9 C60H-DC type: A9N61524, Schneider | kos | 1
2.4 | Razdelilnik za stensko montažo +REG.P1-Z1.2, dimenzij 267x200x112mm (ŠxVxG), TN-S, IP 65. Kot naprimer Mini Kaedra 1x12 modulov, tip: 13979, Schneider. | Wall-mounted distributor +REG.P1-Z1.2, dimensions 267x200x112mm (WxHxD), TN-S, IP 65. As for example Mini Kaedra 1x12 modules, type: 13979, Schneider. |  |  | kpl | 1 |  | 0
| -dvopolni inštalacijski odklopnik 2 A, DC s C karakteristiko, kot naprimer Acti 9 C60H-DC tip: A9N61522, Schneider | -2 A, DC double-pole circuit breaker with C characteristic, such as Acti 9 C60H-DC type: A9N61522, Schneider | kos | 3
| -dvopolni inštalacijski odklopnik 4 A, DC s C karakteristiko, kot naprimer Acti 9 C60H-DC tip: A9N61524, Schneider | -4 A, DC double-pole circuit breaker with C characteristic, such as Acti 9 C60H-DC type: A9N61524, Schneider | kos | 1
2.5 | Razdelilnik za stensko montažo +REG.P1-Z2.1, dimenzij 267x200x112mm (ŠxVxG), TN-S, IP 65. Kot naprimer Mini Kaedra 1x12 modulov, tip: 13979, Schneider. | Wall-mounted distributor +REG.P1-Z2.1, dimensions 267x200x112mm (WxHxD), TN-S, IP 65. As for example Mini Kaedra 1x12 modules, type: 13979, Schneider. |  |  | kpl | 1 |  | 0
| -dvopolni inštalacijski odklopnik 2 A, DC s C karakteristiko, kot naprimer Acti 9 C60H-DC tip: A9N61522, Schneider | -2 A, DC double-pole circuit breaker with C characteristic, such as Acti 9 C60H-DC type: A9N61522, Schneider | kos | 2
| -dvopolni inštalacijski odklopnik 3 A, DC s C karakteristiko, kot naprimer Acti 9 C60H-DC tip: A9N61523, Schneider | -3 A, DC double-pole circuit breaker with C characteristic, such as Acti 9 C60H-DC type: A9N61523, Schneider | kos | 1
2.6 | Razdelilnik za stensko montažo +REG.P1-Z2.2, dimenzij 267x200x112mm (ŠxVxG), TN-S, IP 65. Kot naprimer Mini Kaedra 1x12 modulov, tip: 13979, Schneider. | Wall-mounted distributor +REG.P1-Z2.2, dimensions 267x200x112mm (WxHxD), TN-S, IP 65. As for example Mini Kaedra 1x12 modules, type: 13979, Schneider. |  |  | kpl | 1 |  | 0
| -dvopolni inštalacijski odklopnik 2 A, DC s C karakteristiko, kot naprimer Acti 9 C60H-DC tip: A9N61522, Schneider | -2 A, DC double-pole circuit breaker with C characteristic, such as Acti 9 C60H-DC type: A9N61522, Schneider | kos | 2
| -dvopolni inštalacijski odklopnik 3 A, DC s C karakteristiko, kot naprimer Acti 9 C60H-DC tip: A9N61523, Schneider | -3 A, DC double-pole circuit breaker with C characteristic, such as Acti 9 C60H-DC type: A9N61523, Schneider | kos | 1
2.7 | Razdelilnik za stensko montažo +REG.P1-Z2.3, dimenzij 267x200x112mm (ŠxVxG), TN-S, IP 65. Kot naprimer Mini Kaedra 1x12 modulov, tip: 13979, Schneider. | Wall-mounted distributor +REG.P1-Z2.3, dimensions 267x200x112mm (WxHxD), TN-S, IP 65. As for example Mini Kaedra 1x12 modules, type: 13979, Schneider. |  |  | kpl | 1 |  | 0
| -dvopolni inštalacijski odklopnik 2 A, DC s C karakteristiko, kot naprimer Acti 9 C60H-DC tip: A9N61522, Schneider | -2 A, DC double-pole circuit breaker with C characteristic, such as Acti 9 C60H-DC type: A9N61522, Schneider | kos | 2
| -dvopolni inštalacijski odklopnik 4 A, DC s C karakteristiko, kot naprimer Acti 9 C60H-DC tip: A9N61524, Schneider | -4 A, DC double-pole circuit breaker with C characteristic, such as Acti 9 C60H-DC type: A9N61524, Schneider | kos | 1
2.8 | Ročni električni generator (REG): za enosmerni tok, 24 V, 2,5 A, 60 VA, z ročico za ročni pogon. Napetost in moč: Nazivna napetost: 24 V enosmernega toka (DC) -Nazivna moč: 60 VA -Izhodni tok: 2,5 A Mehanski pogon: -Ročni pogon z ročico -Zasnova: Kompaktna in ergonomska, omogoča enostavno uporabo tudi v stresnih razmerah. Konstrukcija in materiali: -Ohišje: Odpornost na tresljaje in udarce -Materiali: Kakovostni materiali, odporni na korozijo in obrabo. Generator mora izpolnjevati zahtevam Pravilnika o tehničnih normativih za zaklonišča in zaklonilnike. OPOMBA: Za natančno skladnost z vsemi predpisi in standardi je priporočljivo sodelovati s strokovnjaki za elektroinštalacije in zaščitno opremo, ki imajo izkušnje z načrtovanjem in implementacijo sistemov za zaklonišča. | Hand-held electric generator (REG): for DC, 24 V, 2,5 A, 60 VA, with hand crank. Tension and power: Nominal voltage: 24 V direct current (DC) -Rated power: 60 VA -Output current: 2.5 A Mechanical drive: -Manual drive with lever -Design: compact and ergonomic, it is easy to use even under stressful conditions. Construction and materials: -Housing: vibration and shock resistance -Materials: high quality materials, resistant to corrosion and abrasion. The generator must comply with the requirements of the Regulations on Technical Norms for Shelters and Shelters. NOTE: For exact compliance with all regulations and standards, it is advisable to work with electrical installation and protective equipment specialists who have experience in the design and implementation of shelter systems. |  |  | kos | 5 |  | 0
| RAZDELILNIKI IN ROČNI ELEKTRIČNI GENERATOR (REG) | SWITCHGEAR AND HAND-HELD ELECTRIC GENERATOR (REG) | [5 empty] | 0

## 3.1.3_Razsvetljava
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
3.1 | ELEKTRO DELA | ELECTRICAL WORKS
3.1.3 | RAZSVETLJAVA | LIGHTING |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
3 | RAZSVETLJAVA | LIGHTING
3.1 | LED Ladijska svetilka IP44, plastično ohišje z kovinsko mrežo za zaštito stekla, 5W, 620lm, 4000K, kot naprimer OVAL LED EVO HV 170MM 620LM 840 S.METAL, šifra: 911071, Lena Lighting. | LED Ship luminaire IP44, plastic housing with metal mesh for glass protection, 5W, 620lm, 4000K, as for example OVAL LED EVO HV 170MM 620LM 840 S.METAL, code: 911071, Lena Lighting. | kos | 171 |  | 0
3.2 | Ladijska svetilka IP44, plastično ohišje z kovinsko mrežo za zaštito stekla, kot naprimer Lena Lighting, in LED žarnica E27, 12/24V, 5W. | IP44 marine luminaire, plastic housing with metal mesh for glass protection, such as Lena Lighting, and LED bulb E27, 12/24V, 5W. | kos | 45 |  | 0
3.3 | Zasilna LED svetilka, 1W-3W, 4000K, IP65 + piktogram EXIT (montaža na steno nad vrati), avtonomija 1 ura, kot naprimer BEGHELLI | Emergency LED luminaire, 1W-3W, 4000K, IP65 + EXIT pictogram (wall mounting above door), 1 hour autonomy, like BEGHELLI | kos | 6 |  | 0
3.4 | Zasilna LED svetilka, 1W-3W, 4000K, IP65 + piktogram RAVNO (montaža na strop), avtonomija 1 ura, kot naprimer BEGHELLI | Emergency LED luminaire, 1W-3W, 4000K, IP65 + pictogram RAVNO (ceiling mounting), 1 hour autonomy, like BEGHELLI | kos | 5 |  | 0
3.5 | Pregled in preizkus vgrajenega sistema zasilne razsvetljave s pridobitvijo pozitivnega potrdila pooblaščene inštitucije. | Inspection and test of the installed emergency lighting system, with a positive certificate from an approved institution. | kpl | 1 |  | 0
3.6 | Izdelava evidenčnega lista kontrolnega pregleda zasilne razsvetljave. | Creation of an emergency lighting inspection record sheet. | kpl | 1 |  | 0
3.7 | Nadometno stikalo, 250V, 10A, kot naprimer TEM ČATEŽ | Overhead switch, 250V, 10A, as for example TEM ČATEŽ
| - enopolno stikalo, IP44, bela barva (kolesarnica) | - single-pole switch, IP44, white (bike room) | kos | 12 |  | 0
| - enopolno stikalo, IP44, siva barva (zaklonišče) | - single-pole switch, IP44, grey (shelter) | kos | 10 |  | 0
| - menjalno stikalo, IP44, bela barva (kolesarnica) | - change-over switch, IP44, white (bike room) | kos | 8 |  | 0
| - menjalno stikalo, IP44, siva barva (zaklonišče) | - change-over switch, IP44, grey (shelter) | kos | 14 |  | 0
3.8 | PIR senzor gibanja, 360°, doseg senzorija 8m,nadometne izvedbe, IP44. | PIR motion sensor, 360°, sensor range 8m, overhead version, IP44. | kos | 13 |  | 0
3.9 | Napajalni kabel uvlečen v zaščitne cevi, vključno z označevalnimi ploščicami, ter drobnim in spojnim materialom, odziv na ogenj vsaj Cca. Kabli brez halogena. | Power cable enclosed in protective tubing, including marking plates, and small and jointing material, reaction to fire at least Cca. Cables halogen-free.
| - N2XH-J 3x1,5 mm² | - N2XH-J 3x1,5 mm² | m | 500 |  | 0
3.10 | PVC zaščitna toga cev, premer 16mm, brez halogenov, s priborom za nadometno montažo. Kot naprimer KH16 LGR, M16, OBO. | PVC protective rigid hose, 16mm diameter, halogen-free, with fittings for overhead mounting. As for example KH16 LGR, M16, OBO. | m | 500 |  | 0
3.11 | Označevalne nalepke, višina črk 10 mm, rdeče barve, z napisom: "zaklonišče". | Marking labels, letter height 10 mm, red, reading 'shelter'. | kos | 22 |  | 0
3.12 | Označevalne nalepke, višina črk 10 mm, črne barve, z napisom:: "kolesarnica". | Marking stickers, letter height 10 mm, black, with the inscription: 'cycle store'. | kos | 18 |  | 0
| RAZSVETLJAVA | LIGHTING |  |  |  | 0

## 3.1.4_Mala moč
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
3.1 | ELEKTRO DELA | ELECTRICAL WORKS
3.1.4 | MALA MOČ | SMALL POWER AND SOCKET OUTLETS |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
4 | MALA MOČ | SMALL POWER AND SOCKET OUTLETS
4.1 | Nadometna vtičnica, 250V, 16A, kot naprimer TEM ČATEŽ | Overhead socket, 250V, 16A, as for example TEM ČATEŽ
| - vtičnica schuko+pokrom, IP44, 2P+E | - socket schuko+chrome, IP44, 2P+E | kos | 24 |  | 0
4.2 | Napajalni kabel uvlečen v zaščitne cevi, vključno z označevalnimi ploščicami, ter drobnim in spojnim materialom, odziv na ogenj vsaj Cca. Kabli brez halogena. | Power cable enclosed in protective tubing, including marker plates, and small and jointing material, reaction to fire at least Cca. Cables halogen-free.
| - N2XH-J 3x2,5 mm² | - N2XH-J 3x2,5 mm² | m | 270 |  | 0
4.3 | PVC zaščitna toga cev, premer 16mm, brez halogenov, s priborom za nadometno montažo. Kot naprimer KH16 LGR, M16, OBO. | PVC protective rigid hose, 16mm diameter, halogen-free, with fittings for overhead mounting. As for example KH16 LGR, M16, OBO. | m | 270 |  | 0
4.4 | PVC zaščitna toga cev, premer 25 mm, brez halogenov, s priborom za nadometno montažo. Kot naprimer KH25 LGR, M25, OBO. | PVC protective rigid hose, 25 mm diameter, halogen-free, with fittings for overhead mounting. As for example KH25 LGR, M25, OBO. | m | 100 |  | 0
| MALA MOČ | SMALL POWER AND SOCKET OUTLETS |  |  |  | 0

## 3.1.5_IKS
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
3.1 | ELEKTRO DELA | ELECTRICAL WORKS
3.1.5 | INFORMACIJSKO KOMUNIKACIJSKI SISTEM (IKS) | INFORMATION AND COMMUNICATION SYSTEM (IKS) |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
5 | INFORMACIJSKO KOMUNIKACIJSKI SISTEM (IKS) | INFORMATION AND COMMUNICATION SYSTEM (IKS)
5.1 | Dobava in polaganje kabla na kabelske police in delno uvlačenje v cevi, vključno z razvodnicami ter drobnim in spojnim materialom: | Supply and installation of cable on cable racks and partial insertion into conduits, including manifolds and small and jointing materials:
| - F/FTP-Category 6A, 4x2x23 AWG | - F/FTP-Category 6A, 4x2x23 AWG | m | 160 |  | 0
5.2 | Nadometna omrežna vtičnica CAT 6 1xRJ45, IP 44, TEM Čatež ali JUNG, R&M | Overhead network socket CAT 6 1xRJ45, IP 44, TEM Čatež or JUNG, R&M | kos | 2 |  | 0
5.3 | Komplet antenske vtičnice sat, tv, nadometna posamezna vtičnica, TEM Čatež ali JUNG, R&M | Antenna socket set sat, tv, overhead single socket, TEM Čatež or JUNG, R&M | kos | 2 |  | 0
5.4 | Dobava nosilca anten in drog antene (2 m), ki se namesti ob cevi za zajem zraka. Nosilec in drog naj bosta predvidena kot demnotažna elementa in se jih namesti v primeru delovanje zaklonišča v zaščitni funkciji v naprej pripravljeno mesto, ki jo predvidi gradbinec. | Supply of antenna bracket and antenna pole (2 m) to be installed next to the air intake pipe. The bracket and pole are to be provided as demountable elements and are to be installed in a pre-prepared location to be provided by the builder in case the shelter is operated in a protective function. | kos | 1 |  | 0
5.5 | Dobava visokofrekvenčne antene (VHF, FM), montažnega tipa v obljiki palicein v skladu z načrtom radijskih zvez v sistemu zaščite, reševanja in pomoči.. Frekvenco predpiše Uprava RS za zaščito in reševanje. Pred dobavo antene je potrebno s pomočjo URSZR določiti lastnosti antene in uglasitev predpisano frekvenco, ki bo veljala v času gradnje. Antena mora biti demontažne izvedbe. | Supply of a high frequency antenna (VHF, FM), mounting type in the form of a pole and in accordance with the plan for radio communications in the protection, rescue and aid system. The frequency shall be prescribed by the Protection and Rescue Administration of the Republic of Slovenia. Before supplying the antenna, it is necessary to determine the characteristics of the antenna with the assistance of the Ministry of Emergency Situations and to tune it to the prescribed frequency which will be in force at the time of construction. The antenna shall be of a demountable design. | kos | 1 |  | 0
| INFORMACIJSKO KOMUNIKACIJSKI SISTEM (IKS) | INFORMATION AND COMMUNICATION SYSTEM (IKS) |  |  |  | 0

## 3.1.6_AJP
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
3.1 | ELEKTRO DELA | ELECTRICAL WORKS
3.1.6 | AVTOMATSKO JAVLJANJE POŽARA | AUTOMATIC FIRE DETECTION |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
6 | AVTOMATSKO JAVLJANJE POŽARA | AUTOMATIC FIRE DETECTION
6.1 | Adresabilni optični javljalnik požara, kot naprimer FDO241 z vgrajeno ASA tehnologijo, komplet z vso potrebno dodatno opremo (podnožje FDB295 in napisno ploščico FDBZ291, (nastavitev za običajno okolje), tesnila, montažni in inštalacijski material, ...), Siemens. | Addressable optical fire detector, such as FDO241 with ASA technology, complete with all necessary accessories (base FDB295 and nameplate FDBZ291, (setup for normal environment), gaskets, mounting and installation material, etc.), Siemens. | kpl | 15 |  | 0
6.2 | Adresabilni ročni javljalnik požara, kot naprimer FDM223, rdeće barve, komplet z luminiscenčno ploščo z napisom '' ROČNI JAVLJALNIK'' in vso potrebno dodatno opremo (elektronika javljalnika FDME223, ohišje FDMH293-R, zaščita DMZ1197-AC, montažni in inštalacijski material, ...), Siemens. | Addressable manual fire detector, e.g. FDM223, red, complete with luminescent panel with the inscription ''HAND-HOLDED DETECTOR'' and all necessary accessories (detector electronics FDME223, housing FDMH293-R, protection DMZ1197-AC, mounting and installation material, etc.), Siemens. | kos | 1 |  | 0
6.3 | Adresebilna alarmna sirena, kot naprimer Siemens Sinteso FDS224-R, povezava v FDnet s podnožjem FDB226-R in luminiscenčno ploščo z napisom ''SIRENA'' izdelana skladno s SIST 1013 | Addressable alarm siren, such as Siemens Sinteso FDS224-R, FDnet connection with FDB226-R base and luminescent panel with "SIRENA" inscription, manufactured according to SIST 1013 | kos | 6 |  | 0
6.4 | Vhodni modul (4x vhod), kot naprimer Siemens Sinteso, FDCI222, z ohišjem FDCH221 | Input module (4x input), e.g. Siemens Sinteso, FDCI222, with FDCH221 housing | kos | 2 |  | 0
6.5 | Tipka za izklop alarma javljanje požara, rdeča, povratna vzmet 1NO, IP54, IK05, kot naprimer Harmony XALE, Schneider | Alarm push-button, red, 1NO return spring, IP54, IK05, as for example Harmony XALE, Schneider | kos | 2 |  | 0
6.6 | Dobava in polaganje ognje-odpornih kablov tipa JE-H(St)H 2x2x0,8 mm FE180/E30 - rdeče barve, kot naprimer LAPPKABEL, Helukabel | Supply and installation of fire-resistant cables type JE-H(St)H 2x2x0,8 mm FE180/E30 - red, e.g. LAPPKABEL, Helukabel | m | 500 |  | 0
6.7 | Sistem SB-ES, BETAfixss, E30/E90, razmik med objemkami < 800mm. Ob montaži upoštevati navodila proizvajalca: | System SB-ES, BETAfixss, E30/E90, clamp spacing < 800mm. Follow manufacturer's instructions for installation:
| - ESM 6-8 M6 enostavna objemka | - ESM 6-8 M6 single clamp | kos | 480 |  | 0
| - zidni vložek FNA M6x45 | - fNA wall insert M6x45 | kos | 480 |  | 0
6.8 | Meritve, testiranje sistema, spuščanje sistema v pogon po prejetju pisnega sporočila s terminom za primopredajo zaključenih požarnih inštalacij. Izdelava zapisnika in dokumentacije meritev,… | Measurements, testing of the system, commissioning of the system after receipt of a written communication with a deadline for handover of the completed fire installations. Preparation of minutes and documentation of measurements,.. | kpl | 1 |  | 0
6.9 | Pregled sistema avtomatskega javljanja požara s strani pooblaščene inštitucije in sodelovanje serviserja pri pregledu in pridobitev pozitivnega potrdila pooblaščene inštitucije: | Inspection of the automatic fire detection system by an approved institution and participation of the technician in the inspection and obtaining a positive certificate from an approved institution: | kpl | 1 |  | 0
| - avtomatskega javljanja požara, pregled zanke 2 centrale FC2060 zaradi priključitve dodatnih elementov javljanja požara (3 elementov javljanja požara) | - automatic fire detection, inspection of FC2060 loop 2 for connection of additional fire detection elements (3 fire detection elements)
| AVTOMATSKO JAVLJANJE POŽARA | AUTOMATIC FIRE DETECTION |  |  |  | 0

## 3.1.7_Ozemljitve
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
3.1 | ELEKTRO DELA | ELECTRICAL WORKS
3.1.7 | OZEMLJITVE IN STRELOVODNA NAPELJAVA | EARTHING AND LIGHTNING CONDUCTOR WIRING |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
7 | OZEMLJITVE IN STRELOVODNA NAPELJAVA | EARTHING AND LIGHTNING CONDUCTOR WIRING
7.1 | Ozemljitveni valjanec | Grounding roller
| - Rf (INOX V4A) 30x3,5 mm, HERMI, alternativa DEHN ali OPTIM-SF, enakih tehničnih karakteristik | - Rf (INOX V4A) 30x3,5 mm, HERMI, alternative to DEHN or OPTIM-SF, with the same technical characteristics | m | 220 |  | 0
| - FeZn 25x4 mm, HERMI, alternativa DEHN ali OPTIM-SF, enakih tehničnih karakteristik | - FeZn 25x4 mm, HERMI, alternative to DEHN or OPTIM-SF, with the same technical characteristics | m | 680 |  | 0
| - FeZn fi 8 mm, HERMI, alternativa DEHN ali OPTIM-SF, enakih tehničnih karakteristik | - FeZn fi 8 mm, HERMI, alternative to DEHN or OPTIM-SF, with the same technical characteristics | m | 80 |  | 0
7.2 | Križne sponke | Cross clamps
| - KON01 Rf, HERMI, alternativa DEHN ali OPTIM-SF, enakih tehničnih karakteristik | - KON01 Rf, HERMI, alternative to DEHN or OPTIM-SF, with the same technical characteristics | kos | 110 |  | 0
| - KON01 Rf*H4 (V4A), HERMI, alternativa DEHN ali OPTIM-SF, enakih tehničnih karakteristik | - KON01 Rf*H4 (V4A), HERMI, alternative to DEHN or OPTIM-SF, with the same technical characteristics | kos | 40 |  | 0
| - KON02 Rf, HERMI, alternativa DEHN ali OPTIM-SF, enakih tehničnih karakteristik | - KON02 Rf, HERMI, alternative to DEHN or OPTIM-SF, with the same technical characteristics | kos | 40 |  | 0
| - KON07 Rf, HERMI, alternativa DEHN ali OPTIM-SF, enakih tehničnih karakteristik | - KON07 Rf, HERMI, alternative to DEHN or OPTIM-SF, with the same technical characteristics | kos | 80 |  | 0
| - KON09 Rf, HERMI, alternativa HERMI ali OPTIM-SF, enakih tehničnih karakteristik | - KON09 Rf, HERMI, alternative to HERMI or OPTIM-SF, with the same technical characteristics | kos | 260 |  | 0
7.3 | Podporni nosilec valjanca | Roller support bracket
| - DV držalo valjanca Rf 110020, HERMI, alternativa DEHN ali OPTIM-SF, enakih tehničnih karakteristik | - DV roller holder Rf 110020, HERMI, alternative to DEHN or OPTIM-SF, with the same technical characteristics | kos | 90 |  | 0
7.4 | Merilni stik s številko merilnega stika | Measuring contact with measuring contact number
| - KON01 Rf (P do 30) + MŠ MERILNA ŠTEVILKA 80122 alternativa DEHN ali OPTIM-SF, enakih tehničnih karakteristik | - KON01 Rf (P to 30) + MŠ MEASUREMENT NUMBER 80122 alternative to DEHN or OPTIM-SF, with the same technical characteristics | kos | 14 |  | 0
7.5 | Fiksni ozemljitveni priključek | Fixed earth connection
| - KON30 + KON09A + KON31, HERMI, alternativa DEHN ali OPTIM-SF, enakih tehničnih karakteristik | - CON30 + CON09A + CON31, HERMI, alternative to DEHN or OPTIM-SF, with the same technical characteristics | kos | 2 |  | 0
| OZEMLJITVE IN STRELOVODNA NAPELJAVA | EARTHING AND LIGHTNING CONDUCTOR WIRING |  |  |  | 0

## 3.1.8_IP
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
3.1 | ELEKTRO DELA | ELECTRICAL WORKS
3.1.8 | IZENAČEVANJE POTENCIALA | EQUALISING POTENTIAL |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
8 | IZENAČEVANJE POTENCIALA | EQUALISING POTENTIAL
8.1 | Glavna zbiralka za izenačitev potenciala s pokrovom - GIP | Main collector for equipotential bonding with cover - GIP
| - za 12 priključnih mest 472 239 + 472 299, DEHN, alternativa HERMI ali OPTIM-SF, enakih tehničnih karakteristik | - for 12 connection points 472 239 + 472 299, DEHN, alternative to HERMI or OPTIM-SF, with the same technical characteristics | kos | 1 |  | 0
8.2 | Zbiralka za izenačitev potenciala s pokrovom - ZIP | Potential equalisation collector with cover - ZIP
| - za 14 priključnih mest 563 030 + 1x563 013 + 13x563 011 + 563 015, DEHN R15, alternativa HERMI ali OPTIM-SF, enakih tehničnih karakteristik | - for 14 connection points 563 030 + 1x563 013 + 13x563 011 + 563 015, DEHN R15, alternative to HERMI or OPTIM-SF, with the same technical characteristics | kos | 8 |  | 0
8.3 | Vodnik za izenačevanje potenciala - H07V-K, rumeno/zelena. | Potential equalisation lead - H07V-K, yellow/green.
| - 1x 6 mm2 | - 1x 6 mm2 | m | 600 |  | 0
| - 1x 16 mm2 | - 1x 16 mm2 | m | 140 |  | 0
| - 1x 25 mm2 | - 1x 25 mm2 | m | 120 |  | 0
8.4 | Izdelava spojev za izenačitve potencialov (premostitveni spoj iz dveh kabelskih čevljev) s kovinskimi vodili dvižne ploščadi, elektro prostorih - elektro omare, kovinske mase - podboji, okvirji vrat, tehnološke opreme, ograj, premostitev strojnih in klima instalacij, kovinski fasadni elementi, kovinski nosilci senčil, ograj, itd. povezava kovinskih mas v zunanjih energetskih jaških. | Making joints for equipotential bonding (bridging joint made of two cable shoes) with metal rails of the lifting platform, electrical rooms - electrical cabinets, metal masses - soffits, door frames, technological equipment, fences, bridging of mechanical and air-conditioning installations, metal façade elements, metal supports for blinds, fences, etc., connection of metal masses in external power shafts. | ur | 24 |  | 0
8.5 | Premostitveni spoj izdelan iz dveh kabelskih čevljev in dolžine do 1,5m žice H07V-K 1x16mm2 | Bridging joint made of two cable shoes and up to 1.5 m length of H07V-K 1x16mm2 wire | kos | 140 |  | 0
8.6 | Premostitveni spoj izdelan iz dveh kabelskih čevljev in 0,25m žice H07V-K 1x16mm2 | Bridging joint made of two cable shoes and 0,25m of H07V-K 1x16mm2 wire | kos | 64 |  | 0
8.7 | CuSn pletenica 35 mm2, dolžina do 20 cm, komplet s kabel čevelj in vijačnim priborom | CuSn stranded wire 35 mm2, length up to 20 cm, complete with cable shoe and screw fittings | kos | 10 |  | 0
8.8 | CuSn pletenica 50 mm2, dolžina do 20 cm, komplet s kabel čevelj in vijačnim priborom | CuSn stranded wire 50 mm2, length up to 20 cm, complete with cable shoe and screw fittings | kos | 2 |  | 0
8.9 | Al pletenica 50 mm2, dolžina do 20 cm, komplet s kabel čevelj in vijačnim priborom | Al braid 50 mm2, length up to 20 cm, complete with cable shoe and screw fittings | kos | 60 |  | 0
8.10 | Gibljiva zaščitna cev fi10-20 EVROFLEX, komplet s priborom in s pritrdilnim materialom. | EVROFLEX flexible protection hose fi10-20, complete with fittings and fixing material. | m | 40 |  | 0
8.11 | Nerjaveče INOX kovinske zaščitne cevi fi 16-32 s priborom za sestavo in montažo. | Stainless INOX metal protection pipes fi 16-32 with accessories for assembly and installation. | m | 10 |  | 0
| IZENAČEVANJE POTENCIALA | EQUALISING POTENTIAL |  |  |  | 0

## 3.1.9_Ostalo
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
3.1 | ELEKTRO DELA | ELECTRICAL WORKS
3.1.9 | OSTALO | OTHER |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
9 | OSTALO | OTHER
9.1 | Priprava podlog za izdelavo PID projekta. Vnos sprememb, do katerih pride med izvedbo, v en izvod PZI projekta. | Preparation of the basis for the PID project. Entry of changes that occur during implementation in one copy of the PID project. | kpl | 1 |  | 0
9.2 | Izvedba meritev in funkcionalnega pregleda elektroinstalacij z izdelavo zapisnikov in poročil za celoten sistem v sestavi : | Carrying out measurements and functional inspection of the electrical installations, producing minutes and reports for the entire system as a whole: | kpl | 1 |  | 0
| - merjenje osvetlitve z izdelavo grafičnih načrtov merilnih točk | - measuring illuminance by producing graphical plans of the measuring points
| - svetlobnotehnične meritve zunanje razsvetljave | - light-technical measurements of outdoor lighting
| - svetlobnotehnične meritve zasilne razsvetljave | - light-technical measurements of emergency lighting
| - merjenje impedance okvarne zanke | - measuring the impedance of a fault loop
| - merjenje izolacijske upornosti | - insulation resistance measurement
| - merjenje izenačitev potencialov z izdelavo grafičnih načrtov merilnih točk | - measurement of equipotential bonding by producing graphical plans of the measuring points
| - funkcionalni preizkus | - functional test
| - nastavitev zaščit | - setting safeguards
9.3 | Izdelava tesnjenja prehodov kablov skozi požarne sektorje – doseganje plinotestnosti Opis dela: -Izvedba tesnjenja prehodov kablov in kabelskih inštalacij, ki potekajo skozi požarne sektorje, z namenom zagotavljanja plinotestnosti in požarne odpornosti. -Tesnjenje mora biti izvedeno z ustreznimi certificiranimi materiali in tehnikami, ki omogočajo: -Ohranjanje plinotesnosti prostora. -Požarno odpornost po standardu EI90 (kar pomeni 90 minut ohranjanja funkcionalnosti prehoda med požarnimi sektorji). -Naknadno vstavljanje kablov brez poškodbe tesnilnega materiala. | Sealing of cable penetrations through fire sectors - achieving gas tightness Job description: -Sealing of cable penetrations and cable installations passing through fire sectors to ensure gas tightness and fire resistance. -The sealing must be carried out using appropriate certified materials and techniques to: -Maintaining the gas-tightness of the room. -Fire resistance to EI90 standard (which means 90 minutes of functionality between fire sectors). -Subsequent insertion of cables without damaging the sealing material.
| Standardi in smernice: -DIN 4102 – standard za požarno odpornost gradbenih materialov in konstrukcij. -Smernica SZPV 408 – priporočila za požarno zaščito prehodov kablov. -Načrt požarne varnosti NPV (EI90) – lokalni normativ za požarno odpornost kablov in prehodov. -Navodila proizvajalca za uporabo materiala in izvedbo. | Standards and guidelines: -DIN 4102 - standard for fire resistance of building materials and structures. -SZPV Guideline 408 - Recommendations for fire protection of cable penetrations. -NPV Fire Safety Plan (EI90) - local standard for the fire resistance of cables and penetrations. -Manufacturer's instructions for material use and performance.
| Dimenzije prehodov: Približne premerne dimenzije: fi 50 mm, fi 100 mm, fi 150 mm. Tesnjenje mora biti prilagodljivo glede na premer in število kablov ter omogočati naknadne posege. | Dimensions of gangways: Approximate diameter dimensions: fi 50 mm, fi 100 mm, fi 150 mm. The sealing must be flexible according to the diameter and number of cables and allow for subsequent interventions.
| Uporabljeni materiali (primeri): -Hilti – izvajalec: Strasberger -Intumex – izvajalec: TIM Opara -Pirofix – izvajalec: Tinde Vsi materiali morajo imeti enake tehnične karakteristike, certificirane za EI90 in plinotestnost. | Materials used (examples): -Hilti - Contractor: Strasberger -Intumex - contractor: TIM Opara -Pirofix - contractor: Tinde All materials must have the same technical characteristics, certified to EI90 and gas-tight.
| Izvajalec in certifikacija: Izvajalec mora imeti veljavno licenco za izvedbo tesnjenja prehodov kablov skozi požarne sektorje. Po izvedbi tesnjenja se izda ustrezen certifikat, ki potrjuje: -Izvedbo v skladu z normativi in standardi. -Uporabo certificiranega materiala. -Doseganje plinotestnosti in požarne odpornosti. | Operator and certification: The contractor must have a valid licence to perform cable sealing in fire sectors. Once the sealing is completed, the relevant certificate is issued to certify: -Implementation in accordance with norms and standards. -Use of certified materials. -Achieving gas and fire resistance.
| Opomba: Tesnjenje mora biti tipa, ki omogoča naknadno vstavljanje kablov, brez ponovne popolne demontaže. Pri izbiri materiala je priporočljivo uporabljati priznane proizvajalce in preverjene alternative z enakimi tehničnimi karakteristikami, ki morajo biti prilagojenim rešitvam za zaklonišča (odpornost na treslaje, ...) | Remark: The sealing shall be of a type which allows subsequent insertion of cables without complete dismantling. When selecting materials, it is recommended to use recognised manufacturers and proven alternatives with the same technical characteristics, which must be adapted to the shelter solution (resistance to vibrations, etc.) | kpl | 1 |  | 0
9.4 | Izdelava tesnjenja horizontalnih prehodov kablov in kabelskih inštalacij skozi AB stene, do Φ 25 mm. | Sealing of horizontal passages for cables and cable installations through AB walls, up to Φ 25 mm. | kpl | 2 |  | 0
9.5 | Izdelava tesnjenja horizontalnih prehodov kablov in kabelskih inštalacij skozi AB stene, do Φ 50 mm. | Sealing of horizontal passages for cables and cable installations through AB walls, up to Φ 50 mm. | kpl | 15 |  | 0
9.6 | Izdelava tesnjenja horizontalnih prehodov kablov in kabelskih inštalacij skozi AB stene, do Φ 100 mm. | Sealing of horizontal passages for cables and cable installations through AB walls, up to Φ 100 mm. | kpl | 2 |  | 0
9.7 | Vrtanje odprtin v stenah in ploščah, premer x dolžina lukenj (mm): 100x400. | Drilling holes in walls and panels, diameter x length of holes (mm): 100x400. | kos | 2 |  | 0
9.8 | Vrtanje odprtin v stenah in ploščah, premer x dolžina lukenj (mm): 25x300. | Drilling holes in walls and panels, diameter x length of holes (mm): 25x300. | kos | 2 |  | 0
9.9 | Tesnenje kabla v cevi iz dveh strani z mehanskim tesnilom, dobava tesnilnega materiala, zagotoviti plinotesnost. | Sealing of the cable in the pipe on two sides with a mechanical seal, supply of sealing material, to ensure gas-tightness. | kpl | 6 |  | 0
9.10 | Izvedba meritev in funkcionalnega pregleda strelovodne naprave in sistema izenačevanja potenciala z izdelavo zapisnikov in poročil v sestavi (skladno z dodatkom E7 standarda SIST EN 62305-3) : - merjenje ozemljitvene upornosti z izdelavo grafičnih načrtov merilnih točk - meritve in pregled strelovodne naprave z izdelavo grafičnih načrtov merilnih točk | Carrying out measurements and functional inspection of the lightning and equipotential bonding system, with the production of records and reports in a composition (in accordance with Appendix E7 of SIST EN 62305-3): - measurement of earth resistance by producing graphical plans of the measuring points - measurements and inspection of the lightning installation, including the drawing up of graphical plans of the measuring points | kpl | 1 |  | 0
9.11 | Vrtanje odprtin v stenah in ploščah, premer x dolžina lukenj (mm): 50 x 300 | Drilling holes in walls and panels, diameter x length of holes (mm): 50 x 300 | kos | 4 |  | 0
9.12 | Vrtanje in zatesnitev kabla senzorja detektorja CO (dvožilni kabel) | Drilling and sealing the CO detector sensor cable (two-wire cable) | kpl | 2 |  | 0
9.13 | Razna nepredvidena dela, ki se obračunajo po urah s potrditvijo nadzornika v gradbenem dnevniku. | Miscellaneous unforeseen work, billed by the hour with the supervisor's approval in the construction logbook. | ur | 24 |  | 0
9.14 | Certifikati in dokazila oziroma poročila testov odpornosti vgrajene opreme (razsvetljava, vtičnice, stikala, …) na tresljaje, skladno s standardi in Pravilnikom o tehničnih normativih za zaklonišča. | Certificates and evidence or test reports on the vibration resistance of the installed equipment (lighting, sockets, switches, etc.), in accordance with the standards and the Regulation on technical norms for shelters. | kpl | 1 |  | 0
| OSTALO | OTHER |  |  |  | 0