## 0_Naslovnica
OPOZORILO! Vsi prevodi v angleščino so strojno izdelani in zgolj informativne narave. V primeru kakršnekoli nejasnosti ali dvoma izključno velja izvirno besedilo v slovenščini. WARNING! All translations into English have been produced by machine translation and are provided for informational purposes only. In the event of any ambiguity or uncertainty, the original Slovenian text shall prevail exclusively.
| / | / | [5 empty] | /
| Sprem./Rev.: | Opis spremembe/Description of Changes: | [5 empty] | Datum/Date: | Podpis/Signature:
| Investitor/Investor: |  |  |  |  | Gradnja/Facility
|  |  | Univerza v Ljubljani Kongresni trg 12 1000 Ljubljana, Slovenija |  |  | Fakulteta za strojništvo/Faculty of Mechanical Engineering
| Projektant/Design Engineer: |  |  |  |  | Del objekta/sistem/Building/System:
|  |  | IBE, svetovanje, projektiranje in inženiring Ljubljana, Slovenija |  |  | STAVBA FAKULTETE/FACULTY BUILDING
| Projektant/Design Engineer: |  |  |  |  | Vrsta načrta/Documentation:
3 NAČRT S PODROČJA ELEKTROTEHNIKE/ DOC. IN THE FIELD OF ELECTRICAL ENGINEERING
|  | Ime in priimek/Name and Surname: |  |  | Id. št./Id. No: | Vsebina risbe (dokumenta)/Document Title:
| Vodja proj./ Des. Manager: | Boštjan Vuga, univ. dipl. inž. arh., grad. dip. (AA) |  |  | ZAPS 0035 PA PPN | PR. POPIS ELEKTRO DEL/BOQ OF ELECTRICAL WORKS 3/3 SN napajanje in transformatorska postaja/MV Power Supply and Transformer Substation
| Poobl. strok./ Cert. Profess.: | Anton Klemen, dipl. inž. el. |  |  | IZS E-1990
| Poobl. strok./ Cert. Profess.: |  |  |  |  | Št. proj./ Proj. No.: | 362-19 |  | Vrsta dokument./ Document. Type: | PZI
| Izdelal/ Creator: | Anton Klemen, dipl. inž. el. |  |  | IZS E-1990 | Klas. ozn./ Class. No.: | -- |  | Stran/ Page: | 1/*
| Datum/ Date: | maj/May 2026 |  | Merilo/ Scale: | / | Ident. ozn./ Id. No: | JULFS--6E9062P

## 0_Osebe
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
POOBLAŠČENI STROKOVNJAKI, ODGOVORNI ZA IZDELAVO PROJEKTANTSKEGA POPISA:
Id. št. ZAPS/IZS | Pooblaščeni strokovnjak | Strokovno področje
IZS E-1990 | Anton Klemen, dipl. inž. el. | SN in NN napajanje objekta
SODELAVCI PRI IZDELAVI PROJEKTANTSKEGA POPISA:
/ | Magdalena Stojanova, mag. inž. el. | SN in NN napajanje objekta
CERTIFIED EXPERTS RESPONSIBLE FOR ELABORATING THE BILL OF QUANTITIES:
Id. No ZAPS/IZS | Certified Expert | Area of Expertise
IZS E-1990 | Anton Klemen, dipl. inž. el. | MV and LV power supply to the building
COLABORATORS IN THE ELABORATING THE BILL OF QUANTITIES:
/ | Magdalena Stojanova, mag. inž. el. | MV and LV power supply to the building

## 0.1_Uvod-STP
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
0.1 | SPLOŠNI TEHNIČNI POGOJI | GENERAL TECHNICAL CONDITIONS
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic operator with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
0.1.1 | Izvajalec se obveže, da bo upošteval veljavno zakonodajo, ki ureja graditev objektov v Republiki Sloveniji, vključno s povezanimi podzakonskimi akti, predpisi, tehničnimi smernicami, standardi, pravili stroke in dobro gradbeno prakso. Prav tako mora izvajalec upoštevati vse zahteve izdanega integralnega gradbenega dovoljenja in vsa dela izvesti skladno s projektno dokumentacijo ter ostalimi pogoji, objavljenimi v razpisni dokumentaciji. | The Contractor undertakes to comply with the applicable legislation governing the construction of buildings in the Republic of Slovenia, including related by-laws, regulations, technical guidelines, standards, professional rules and good construction practice. The Contractor shall also comply with all the requirements of the integral building permit issued and shall carry out all works in accordance with the project documentation and other conditions published in the tender documentation.
0.1.2 | Dela lahko izvaja samo izvajalec, ki je registriran za opravljanje gradbene dejavnosti in ima za tovrstna dela ustrezno zavarovanje za škodo, certifikate, tehnično izobražen kader, sredstva ter je usposobljen za samostojno pripravo in izvedbo del. | The work may only be carried out by a contractor who is registered to carry out construction work and who has the appropriate insurance for such work, certificates, technically trained staff, resources and is qualified to prepare and carry out the work independently.
0.1.3 | Izvajalec odgovarja za kakovost izvedbe vseh del. | The Contractor shall be responsible for the quality of the execution of all works.
0.1.4 | Izvajalec nosi vso odgovornost za nesreče in škodo, ki nastane na objektu ali v okolici zaradi njegovega dela. | The Contractor shall bear all liability for accidents and damage to the installation or the surrounding area caused by his work.
0.1.5 | Pred oddajo ponudbe se je izvajalec dolžan seznaniti z območjem predvidenim za gradnjo in temu prilagoditi vsa potrebna dela, kar mora biti zajeto v ponudbi. V neposredni bližini predvidene gradnje se nahajajo stavbe, v katerih potekajo izobraževalni in raziskovalni procesi. Zato bo izvajalec moral izvajati kontrolo hrupa in kontrolo vibracij. Dela, ki so hrupna in dela, ki povzročajo vibracije bo izvajalec moral preprečiti oziroma jih izvesti na način, da povzročajo minimalne vplive. Tehnologijo rušenja, pilotiranja in tehnologijo izvedbe ostalih del bo izvajalec moral prilagoditi tako, da bo vpliv minimalen. Izvajalec mora preprečiti in zmanjšati emisije delcev iz gradbišča na najmanjšo možno mero. | Before submitting a tender, the contractor is obliged to familiarise himself with the area to be constructed and to adapt any necessary works accordingly, which must be included in the tender. In the immediate vicinity of the proposed construction, there are buildings in which educational and research processes take place. The contractor will therefore be required to carry out noise and vibration control. Noise and vibration works will have to be avoided or carried out in such a way as to minimise the impact. Demolition, piling and other works will have to be adapted to minimise the impact. The contractor must avoid and minimise the emission of particulates emitted from the construction site as far as is reasonably practicable.
0.1.6 | Izvajalec je pred oddajo ponudbe dolžan pregledati projektno dokumentacijo in ostale pogoje, ki so del razpisne dokumentacije V primeru morebitnih napak in neskladij je izvajalec dolžan na to opozoriti naročnika pred oddajo ponudbe. | The Contractor is obliged to review the project documentation and other conditions forming part of the tender documentation before submitting the tender In case of any errors or inconsistencies, the Contractor is obliged to bring these to the attention of the Contracting Authority before submitting the tender.
0.1.7 | Pred oddajo ponudbe je izvajalec dolžan preveriti ustreznost popisov del in količin v teh popisih ter njihovo skladnost z ostalimi dokumenti projektne dokumentacije, ki so del razpisne dokumentacije. Prav tako je izvajalec dolžan preveriti vse detajle in sheme. Vse izmere je potrebno preveriti po posameznih projektih oz. načrtih, ki sestavljajo razpisno dokumentacijo. V primeru ugotovljenih neskladij je v času priprave ponudbe obvezan o tem obvestiti naročnika. | Before submitting a tender, the Contractor shall check the adequacy of the inventories of works and quantities in these Bills of Quantities and their conformity with the other documents of the project documentation forming part of the tender documentation. The Contractor shall also check all details and diagrams. All measurements shall be checked against the individual projects or plans forming part of the tender documentation. In the event of any discrepancies, the Contractor shall inform the Contracting Authority at the time of preparing the tender.
0.1.8 | Pred oddajo ponudbe je izvajalec dolžan v tem popisu preveriti zmnožke in seštevke ter prenose le-teh v rekapitulacijo. Izvajalec se s pripravo ponudbe obvezuje, da je prebral vse celice in elemente celotnega popisa, vključno z vsemi postavkami in splošnimi navodili ali določili in je preveril pravilnost preračuna ter s tem zagotavlja ponudbeno vrednost. | Before submitting a tender, the Contractor is required to check the products and totals in this Bill of Quantities (BoQ) and their transfer to the recapitulation. The Contractor undertakes, by preparing a tender, to have read all the cells and elements of the complete BoQ, including all headings and general instructions or provisions, and to have checked the correctness of the conversion, thereby guaranteeing the value of the tender.
0.1.9 | Dela bo izvajalec moral izvajati po predloženi projektni dokumentaciji, detajlih in z upoštevanjem navodil in potrditev projektanta, nadzornika in investitorja. Vso potrebno delavniško dokumentacijo zagotovi izvajalec del v okviru ponujene cene. | The Contractor shall carry out the works in accordance with the submitted design documents, details and subject to the instructions and approvals of the Designer, the Supervisor and the Investor. All necessary workshop documentation shall be provided by the Contractor within the scope of the price quoted.
0.1.10 | Pred izvedbo posameznih del je izvajalec dolžan pregledati projektno dokumentacijo za izvedbo gradnje (PZI) in elaborate. Na morebitne napake v dokumentaciji ali neskladja med posameznimi načrti ali deli načrtov (popisi del, tehnična poročila, lokacijski in tehnični prikazi) izvajalec opozori nadzornika in projektanta, in se z njima pravočasno uskladi. | The Contractor shall review the Detailed Design documentation (PZI) and the studies before carrying out the individual works. The Contractor shall draw the attention of the Supervisor and the Designer to any errors in the documentation or discrepancies between the individual designs or parts of designs (BoQ, technical reports, location and technical drawings) and shall coordinate with them in good time.
0.1.11 | Tehnični opisi, prikazi, detajli, sheme ter ostali dokumenti v PZI dokumentaciji predstavljajo dodaten opis popisnih postavk gradbeno obrtniških in inštalacijskih del ter jih je potrebno dosledno upoštevati skupaj s popisom del. | The technical descriptions, illustrations, details, diagrams and other documents in the Detailed Design documentation (PZI) are additional descriptions of the BoQ inventory items of the building, construction and installation works and must be strictly followed together with the BoQ.
0.1.12 | Specifikacije in zahteve, navedene v popisu, se ne smejo upoštevati kot edine zahteve. Izvajalec je dolžan v ceni zajeti in dobaviti vse elemente opreme ter opraviti dela in storitve, ki niso eksplicitno navedeni, a so bistvenega pomena za funkcionalnost, skladnost s predpisi ter kontinuirano, zanesljivo in varno obratovanje opreme. | The specifications and requirements set out in the BoQ shall not be taken as the only requirements. The Contractor shall be obliged to include in the price and supply all items of equipment and to carry out works and services which are not expressly mentioned but which are essential for the functionality, regulatory compliance and continuous, reliable and safe operation of the equipment.
0.1.13 | Vsa dela morajo biti izvedena kvalitetno in iz materialov z zahtevanimi lastnostmi, izvedena skladno z veljavno zakonodajo in z upoštevanjem navodil za vgradnjo za izbrane materiale in opremo, s predložitvijo predpisanih izjav o lastnostih in/ali certifikatov. Vsi gradbeni proizvodi (GP) morajo biti označeni s CE oznako. | All work shall be of good quality and be executed with materials of the required characteristics, in accordance with the applicable legislation and in compliance with the installation instructions for the materials and equipment selected, and shall be accompanied by the prescribed declarations of performance and/or certificates. All construction products (GP) shall bear the CE marking.
0.1.14 | Za vsako opisano delo v popisu je potrebno upoštevati celotno potrebno delo, ves osnovni in pomožni material, prevoz materiala in orodja na objekt, notranje transporte, delovne in pomožne odre, zaključno čiščenje in odstranitev odpadkov po dovršenem delu. | For each work described in the inventory, the total work required, all basic and ancillary materials, the transport of materials and tools to the site, internal transports, working and ancillary scaffolding, final cleaning and the disposal of waste after the work has been completed must be taken into account.
0.1.15 | Vsa delovna sredstva, organizacija in koordinacija del, pripravljalna, spremljajoča in zaključna dela, potrebni montažni in tesnilni materiali ter podkonstrukcije so sestavni del posameznih postavk. | All labour, organisation and coordination of the works, preparatory, accompanying and finishing works, necessary prefabrication and sealing materials and substructures are part of the individual items.
0.1.16 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - načrt organizacije gradbišča s podrobnim terminskim planom in izvedba vseh pripravljalnih del, postavitev, organizacija, zaščita in prijava gradbišča, gradbiščnih objektov, ureditev začasnih deponij, tekoče vzdrževanje, skupaj s plačilom splošnih stroškov pristojbin in davkov upravnih organov, pridobivanju raznih dovoljenj in soglasij za izvedbo, ograditev gradbišča in postavitev gradbene table in prometne signalizacije, zagotavljanje ustrezne varnosti na gradbišču, tekoče vzdrževanje in končna odstranitev gradbišča; - zagotovitev potrebnih začasnih površin za transportne poti in gradnjo izven območja gradbišča s plačilom stroškov za sanacijo in vzpostavitev okoliških zemljišč in objektov v prvotno stanje (soglasja, odškodnine, itd.); - začasni odvoz, deponiranje in vračanje izkopanega materiala, ki ga ne bo možno deponirati na gradbišču; - odvoz in zagotovitev odstranjevanja odpadnega gradbenega materiala skladno z zakonodajo na področju ravnanja z odpadki (odvoz na urejene deponije s plačilom komunalnih prispevkov in taks itd.); - oteženi izkop v mokrem terenu, izkop v vodi, odvod meteorne vode iz gradbene jame in vode, ki se izceja iz bočnih strani izkopov; - ustrezno varovanje izkopa gradbene jame za objekt in ostalih manjših posameznih izkopov za izvedbo komunalne infrastrukture brez posegov na sosednja zemljišča; - ustrezno varovanje obstoječih objektov, infrastrukture in okolice v času gradnje ter dokumentiranje vseh morebitnih škodnih dogodkov; - pripravljalna, spremljajoča in zaključna dela (zakoličbe, zagotovitev potrebnih komunalnih priključkov za potrebe izvajanja gradnje, izvedba začasnih inštalacij, označevanje podzemnih vodov, postavljanje in vzdrževanje zakoličbenih profilov, izvedba in označevanje novih in starih križanj ter morebitna zaščita križanj komunalnih vodov, geodetski posnetki in izdajanje vmesnih posnetkov izvedene infrastrukture naročniku, izdelava zbirnih kart, itd.), v kolikor ni to drugače določeno; - pridobivanje soglasij in izvedba morebitnih zapor na vseh cestah s plačilom stroškov, nadomestil in pristojbin; - zagotovitev oz. postavitev in končna odstranitev po zaključku gradnje začasnih skladišč in začasnega pisarniškega kontejnerskega objekta vključno z opremo za dve delovni mesti in za skupne operativne sestanke vel. ca. 40 m2 za potrebe naročnika, s tekočim vzdrževanjem in čiščenjem. | The following must also be included or taken into account in the uniform prices for individual items: - a construction site organisation plan with a detailed timetable and the execution of all preparatory works, the setting-up, organisation, protection and registration of the construction site, site facilities, the arrangement of temporary storage facilities, ongoing maintenance, including the payment of general costs of fees and taxes of the administrative authorities, the obtaining of various permits and consents for the execution, the fencing of the site and the erection of construction signs and traffic signals, the provision of adequate security on the site, ongoing maintenance and the final dismantling of the construction site; - provision of the necessary temporary areas for transport routes and off-site construction, with costs for restoration and reinstatement of surrounding land and buildings (consents, compensation, etc.); - temporary removal, storage and return of excavated material that cannot be stored on site; - removing and disposing of waste building materials in accordance with waste management legislation (removal to regulated landfill sites with payment of municipal fees and charges, etc.); - difficult excavation in wet ground, excavation in water, drainage of rainwater from the construction pit and water draining from the sides of excavations; - adequate protection of the excavation of the construction pit for the building and other small individual excavations for the implementation of the utility infrastructure without encroaching on neighbouring land; - adequate protection of existing facilities, infrastructure and the surrounding area during construction, and documentation of any damage incidents; - preparatory, accompanying and finishing works (stake-out, provision of the necessary utility connections for the needs of construction, execution of temporary installations, marking of underground lines, installation and maintenance of stake-out profiles, execution and marking of new and old crossings and possible protection of crossings of utility lines, geodetic surveys and issuing of intermediate images of the completed infrastructure to the client, production of summary maps, etc.), unless otherwise specified; - obtaining consents and implementing any road closures, with costs, compensation and fees; - provision or erection and final removal on completion of construction of temporary storage and temporary office container building including equipment for two workstations and for joint operational meetings of approx. 40 m2 for the needs of the client, with ongoing maintenance and cleaning.
0.1.17 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - izdelava montažne tehnične dokumentacije, detajlov izvedbe in vse druge potrebne delavniške dokumentacije (s področja arhitekture, gradbeništva, elektrotehnike, strojništva in zunanje ter krajinske ureditve) ter pridobitev obvezne potrditve s strani projektanta, nadzornika in investitorja; - odprava vseh vrst inštalacijskih kolizij z izvajanjem potrebnih premikov inštalacij in njihovim usklajevanjem na mestu montaže, vse v obsegu, ki ne vpliva na projektirano rešitev ali tip inštalacij oz. opreme; - zagotavljanje kompletnosti elektro-instalacijskih sistemov s področja avtomatike za doseganje njihove popolne funkcionalnosti delovanja; - stroški za nadzor in koordinacijo izvedbe vseh elektro napeljav, ki so predmet končne instalacije proizvoda (senčila, vrata, okna,…); - izdelava montažnih skic in detajlov za izvedbo v dogovoru z vodjo gradnje in nadzornikom; - izdelava in predstavitev vzorcev v ustrezni velikosti za potrditev projektanta, nadzornika in investitorja; - zagotavljanje varnosti in zdravja pri delu, zlasti izvajanje vseh del, ki izhajajo in ukrepov, ki izhajajo iz določil veljavnih predpisov varstva pri delu in zahtev Varnostnega načrta;- stroški garancij, ki jih mora izvajalec predložiti naročniku. | The following must also be included or taken into account in the uniform prices for individual items: - preparation of prefabricated technical documentation, construction details and all other necessary workshop documentation (architectural, civil, electrical, mechanical, exterior and landscaping) and obtaining the mandatory approval of the designer, the supervisor and the investor; - elimination of all types of installation conflicts by carrying out the necessary relocation of installations and their coordination at the installation site, all to the extent that it does not affect the design solution or the type of installation or equipment; - ensuring the completeness of electrical installation systems in the automation sector to achieve their full operational functionality; - the cost of supervising and coordinating the installation of all the electrical installations that are the subject of the final installation of the product (blinds, doors, windows, etc.); - preparation of erection drawings and details for implementation in agreement with the construction manager and supervisor; - production and presentation of samples in appropriate sizes for the approval of the designer, the supervisor and the investor; - ensuring health and safety at work, in particular the implementation of all the works arising from and the measures resulting from the provisions of the applicable occupational safety regulations and the requirements of the Safety Plan; - the cost of the guarantees to be provided by the contractor to the client.
0.1.18 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - strošek vodje del glavnega izvajalca, ki bo izvajal tudi koordinacijo s podizvajalci in z drugimi izvajalci, ki jih bo izbral naročnik in bo opravljal delo vodje gradbišča; - koordinacija del z ostalimi izvajalci oz. podizvajalci del, projektantom, nadzornikom in investitorjem pri medsebojnem usklajevanju organizacije gradbišča in časovnega načrta del ter pri usklajevanju izdelave plana montaže, potrjenih s strani vseh udeležencev gradnje; - stroški koordinacije, sodelovanja in usklajevanja z dobavitelji tehnološke, laboratorijske, eksperimentalne in vse ostale pohištvene ter multimedijske opreme ter z vsemi ostalimi dobavitelji oz. podizvajalci na objektu; - stroški izdelave situacij; - stroški zavarovanja objekta v času izvedbe del in delavcev ter materiala na gradbišču v času izvajanja del, od začetka del do pridobitve uporabnega dovoljenja za objekt. Zavarovanje mora biti sklenjeno pri ustrezni zavarovalni družbi najmanj v višini pogodbene vrednosti ali v zakonsko predpisani vrednosti (v kolikor zavarovanje v višini pogodbene vrednosti presega zakonsko dovoljeno), za ves čas trajanja izvedbe del do uspešne primopredaje objekta; - preizkušanje kvalitete materiala, ki se vgrajuje in dokazovanje kvalitete s certifikati oz. tehničnimi soglasji; - izvedba vseh zahtevanih testov in preizkusov (npr. tlačni preizkusi, termografski pregledi, meritve elektromagnetnega sevanja, hrupa, itd.), poskusnega obratovanja celotnega objekta s poudarkom na vseh inštalacijah ter izvajanje predpisanega monitoringa v skladu s Poročilom o vplivih na okolje (pred gradnjo, med gradnjo in po končani gradnji); - izdelava izkaza požarne varnosti, vključno s sprotnim spremljanjem gradnje in izvajanjem požarnovarnostnih zahtev ter izdelava Požarnega reda z obveznimi prilogami; - izdelava Izkaza zaščite pred hrupom v stavbah; - izdelava Izkaza energijskih lastnosti stavbe in energetske izkaznice; - sodelovanje z izvajalci gradbenega in projektantskega nadzora in investitorjem za izvedbo tehničnega pregleda in priprava primopredaje, ki mora vsebovati vso zahtevano dokumentacijo, predvsem pa: izjave o skladnosti, požarni izkaz in ostale izkaze ter obvezne tabele, dokazilo o zanesljivosti objekta (DZO), certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo in vzdrževanje ter vse ostale dokumente v skladu s predpisi in pogodbenimi določili. | The following must also be included or taken into account in the uniform prices of the individual items: - the cost of a works manager for the main contractor, who will also coordinate with subcontractors and other contractors selected by the client and act as site manager; - coordination of the works with other contractors or subcontractors, the designer, the supervisor and the investor in coordinating the organisation of the construction site and the timetable for the works, and in coordinating the production of an installation plan approved by all the participants in the construction; - the costs of coordination, cooperation and coordination with suppliers of technological, laboratory, experimental and all other furniture and multimedia equipment, as well as with all other suppliers or subcontractors on the site; - the cost of drawing up situations; - the cost of insuring the building during the execution of the works and the workers and materials on site during the execution of the works, from the start of the works until the building has been licensed for occupation. The insurance must be taken out with a suitable insurance company for at least the contract value or the legal value (if the insurance for the contract value exceeds the legal value), for the entire duration of the works until the successful handover of the building; - testing the quality of the material to be installed and proving it with certificates or technical approvals; - carrying out all required tests and trials (e.g. pressure tests, thermographic inspections, electromagnetic radiation measurements, noise measurements, etc.), trial operation of the entire building, with emphasis on all installations, and carrying out the required monitoring in accordance with the Environmental Impact Assessment Report (before, during and after construction); - preparation of a fire safety statement, including ongoing monitoring of construction and implementation of fire safety requirements, and preparation of a Fire Safety Order with mandatory annexes; - preparation of a Noise Protection Statement for buildings; - preparation of the Building Energy Performance Report and Energy Performance Certificate; - cooperation with the construction and design supervision contractors and the investor to carry out the technical inspection and prepare the handover, which must include all the required documentation, in particular: declarations of conformity, fire and other statements and mandatory tables, proof of reliability of the building (DZO), certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use and maintenance, and all other documents in accordance with the regulations and the contractual provisions.
0.1.19 | V enotnih cenah posameznih postavk, ki se nanašajo na opremo in posamezne sisteme, mora biti zajeto oz. upoštevano tudi naslednje: - dobava oz. transport, - stroški za vse delovne stroje za dvigovanje bremen in delovne košare za dostope do delovišč; - morebitni stroški povzročeni upravljavcem GJI, ki bi nastali v zvezi s predmetno gradnjo; - montaža, vključno s pomožnim montažnim materialom (vezni, tesnilni in pritrdilni material, sidra, nosilni profili, podkonstrukcije in podobno) in navodili proizvajalca, - odprava vseh kolizij sistemov s stenami in med sistemi, - izvedba vseh potrebnih tesnjenj, - priključitev in nastavitve, vključno z morebitnim kalibriranjem, - zagon, testiranje in meritve, vključno s poročili, - šolanje uporabnikov oz. vzdrževalnega osebja za uporabo in vzdrževanje sistemov, - navodila za obratovanje in vzdrževanje, - vsi potrebni certifikati, izjave o skladnosti oz. potrdila ter - vsa druga pomožna dela in material, da se zagotovi funkcionalnost posamezne postavke popisa. | The following must also be included or taken into account in the uniform prices for individual items relating to equipment and individual systems: - delivery/transport, - the cost of all lifting machines and work baskets for access to work sites; - any costs incurred to the operators of utility infrastructure (GJI) in connection with the subject construction; - installation, including ancillary installation materials (bonding, sealing and fixing materials, anchors, support profiles, substructures, etc.) and manufacturer's instructions, - eliminating all system-to-wall and system-to-system collisions, - all necessary sealing work, - connection and set-up, including calibration if necessary, - commissioning, testing and measurements, including reports, - training users or maintenance staff in the use and maintenance of the systems, - operating and maintenance instructions, - any necessary certificates, declarations of conformity or attestations; and - all other ancillary works and materials to ensure the functionality of each inventory item.
0.1.20 | Vsi odri morajo biti upoštevani v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All scaffolding must be included in the uniform prices of the items listed, except where specifically mentioned.
0.1.21 | Vsi delovni in pomožni odri, lestve in ostala potrebna pomožna sredstva, kot tudi čiščenje vseh elementov po končanih delih, mora biti upoštevano v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All working and auxiliary scaffolding, ladders and other necessary ancillaries, as well as the cleaning of all elements after completion of the works, shall be included in the uniform prices of the items listed, except those specifically mentioned.
0.1.22 | Delavniško dokumentacijo za vse nosilne jeklene konstrukcije in podkonstrukcije izdela izvajalec, strošek izdelave delavniške dokumentacije se upošteva v ponujenih cenah in se ne obračuna posebej. | The cost of the shop drawings for all steelwork and substructures shall be included in the prices quoted and shall not be charged separately.
0.1.23 | V enotnih cenah postavk mora biti vključeno tudi vgrajevanje vseh instalacijskih razvodov v opaže armirano betonskih elementov in izdelava prehodov inštalacij ter dodatno izrezovanje utorov in prebojev v kamnite, zidane ali armirano-betonske stene, ponovno demontiranje in montiranje vseh vrst montažnih sten, vsa dodatna dela za zagotavljanje primernih križanj med posameznimi instalacijskimi vodi, izdelava vseh vrst ojačitev konstrukcij in podobna dela, ki zagotavljajo kakovostno vgradnjo vseh vrst instalacijskih vodov in niso posebej navedena v popisu GOI del. V ponudbi morajo biti upoštevana vsa drobna strojna in elektro instalacijska dela in transporti. | The installation of all installation ducts in the formwork of reinforced concrete elements and the construction of installation penetrations, as well as the additional cutting of grooves and penetrations in stone, masonry or reinforced concrete walls, the reassembly and reinstallation of all types of prefabricated walls, all additional work to ensure adequate crossings between individual installation ducts, the construction of all types of structural reinforcement and similar work to ensure the quality installation of all types of installation ducts and not specifically mentioned in the BoQ of the Construction, installation and finishing works (GOI) shall also be included in the uniform prices of the items. The tender shall take into account all minor mechanical and electrical installation work and transport.
0.1.24 | Vsi kovinski elementi in konstrukcije, ki bi lahko bili izpostavljeni atmosferskim in ostalim korozijskim vplivom, morajo biti ustrezno protikorozijsko zaščiteni. | All metallic elements and structures that could be exposed to atmospheric and other corrosive influences must be adequately protected against corrosion.
0.1.25 | Za vse večje jeklene dele se skladno s predpisi, izdelajo ustrezne ozemljitve, nevidno pritrjene in speljane na splošno ozemljitev objekta. | For all major steel parts, appropriate earth connections shall be made in accordance with the regulations, invisibly attached and connected to the general earth of the building.
0.1.26 | Za vse vidne elemente in serijske elemente je obvezna predhodna uskladitev obdelav, barv in materialov s projektantom na podlagi dostavljenih vzorcev v ustrezni velikosti. Obvezna je preveritev dejanskih mer na licu mesta in posledična prilagoditev elementov in njihove montaže. | For all visible elements and serial elements, it is mandatory to coordinate the finishes, colours and materials with the designer beforehand on the basis of the supplied samples in the appropriate size. It is mandatory to check the actual dimensions on site and to adjust the elements and their installation accordingly.
0.1.27 | Dimenzije obrtniških izdelkov in količine je potrebno pred naročanjem preveriti na objektu. Potrebna je uskladitev vseh elementov (kljuke, okovje, detajlne konstrukcije in obdelave, itd.) s projektantom, nadzornikom in investitorjem. Izvajalec je dolžan pred izdelavo predložiti projektantu v potrditev ustrezne delavniške načrte in detajle. | The dimensions of the workmanship and quantities must be checked on site before ordering. All elements (hooks, fittings, detailed construction and finishes, etc.) must be coordinated with the designer, the supervisor and the investor. The contractor is obliged to submit the relevant workshop plans and details to the designer for approval before manufacture.
0.1.28 | V posameznih postavkah popisa so navedeni proizvajalci in/ali tipi posameznih sistemov, materialov ali opreme, s čimer so zgolj natančno opredeljene zahtevane tehnične lastnosti. Izvajalec del lahko ponudi nadomesten sistem, material ali opremo drugega proizvajalca in tipa, pri čemer morajo biti tehnične lastnosti ponujenega sistema, materiala ali opreme enakovredne ali boljše od opredeljenih v popisu, dimenzijsko pa ne smejo presegati projektiranih dimenzij. Vse funkcijske in tehnične karakteristike nadomestnih sistemov, materialov ali opreme mora izvajalec dokazati z ustrezno dokumentacijo. Vse morebitne posledice zaradi spremembe sistemov, materialov ali opreme vključno z morebitnimi spremembami oz. dopolnitvami BIM modelov in projektne dokumentacije, stroškovno in časovno bremenijo izvajalca. | The individual items of the Inventory shall specify the manufacturers and/or types of the individual systems, materials or equipment, thereby merely specifying the required technical characteristics. The Contractor may offer a substitute system, material or equipment of a different manufacturer and type, provided that the technical characteristics of the offered system, material or equipment shall be equivalent to or better than those specified in the BoQ, and shall not exceed the design dimensions. All functional and technical characteristics of the substitute systems, materials or equipment shall be demonstrated by the Contractor with appropriate documentation. Any consequences resulting from changes to systems, materials or equipment, including any changes or additions to the BIM models and project documentation, shall be borne by the Contractor in terms of cost and time.
0.1.29 | Vsako zamenjavo, uporabo in končni izbor nadomestnih sistemov, materialov, proizvodov in opreme morajo obvezno in pravočasno (pred dobavo in vgradnjo) pisno potrditi projektant (vseh sodelujočih strok), nadzornik in investitor. | Any replacement, use and final selection of alternative systems, materials, products and equipment must be approved in writing by the designer (of all disciplines involved), the supervisor and the investor in a timely manner (prior to delivery and installation).
0.1.30 | Izvajalec mora v ponudbeno ceno vključiti tudi: - ves čas gradnje sprotno beleženje sprememb oz. odstopanj od PZI dokumentacije, vključno z izdelavo tekstualnega opisa sprememb, - pripravo podlog na nivoju PZI, ki so potrebne za posodobitev oz. uskladitev BIM modela z izvedenim stanjem (LOD 500) in izdelavo projektne dokumentacije izvedenih del (PID), - mesečno predajanje potrjenih sprememb opreme in materiala, ki vplivajo na BIM model, v formatu IFC, - vzdrževanje in uporabljanje pri izvedbi zadnje veljavne revizije PZI dokumentacije, vključno z dopolnitvami PZI načrtov, ki so nastali zaradi sprememb med gradnjo. | The contractor must also include in the tender price: - keeping a record of changes or deviations from the construction documentation (PZI) throughout construction, including a textual description of the changes, - preparation of the Detailed Design (PZI) level documents required to update or align the BIM model with the as-built condition (LOD 500) and the preparation of the as-built project documentation for the works (PID), - monthly submission of approved equipment and material changes affecting the BIM model in IFC format, - maintenance and use in the execution of the last valid revision of the construction documentation (PZI), including additions to the construction design documentation (PZI) resulting from changes during construction.

## 0.2_Uvod-DGNB
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
0.2 | SPLOŠNI TEHNIČNI POGOJI ZA PODROČJE DGNB CERTIFICIRANJA | GENERAL TECHNICAL CONDITIONS FOR DGNB CERTIFICATION
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic entity with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
| Splošni pogoji za področje DGNB certificiranja predstavljajo dopolnilo splošnim tehničnim pogojem in ne odpravljajo drugih obveznosti in odgovornosti, ki jih ima izvajalec v skladu s predpisi in pogodbo. | The General Conditions for DGNB Certification are complementary to the General Technical Conditions and do not exclude other obligations and responsibilities that the Contractor has under the Regulations and the Contract.
0.2.1 | Izvajalec mora v svojih ponudbah upoštevati, da se bo objekt certificiral v skladu z zahtevami DGNB sistema certificiranja trajnostne gradnje, ter pravočasno (vsaj 60 dni pred vgradnjo posameznega produkta) dostaviti vso ustrezno dokumentacijo za vse v ponudbi zajete materiale, elemente in opremo. Zahtevana je uporaba materialov, elementov ali opreme, ki so okolju in ljudem prijazni, energetsko učinkoviti in obenem ustrezajo zahtevam DGNB sistema. Zahtevan nivo certifikata je: ZLATI CERTIFIKAT | The Contractor shall take into account in its tenders that the building will be certified in accordance with the requirements of the DGNB Sustainable Building Certification Scheme and shall deliver all relevant documentation for all materials, elements and equipment included in the tender in a timely manner (at least 60 days before the installation of each product). The use of materials, elements or equipment that are environmentally and human friendly, energy efficient and at the same time meet the requirements of the DGNB system is required. The required level of certification is: GOLD CERTIFICATE
0.2.2 | Podrobnejši opis DGNB sistema in navodila za posamezne kriterije so dostopna v dokumentu"DGNB Criteria Set New Construction Buildings, Version 2020 International", ki je na voljo na DGNB spletni strani https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria | A more detailed description of the DGNB system and guidance on the individual criteria is available in the document "DGNB Criteria Set New Construction Buildings, Version 2020 International", available on the DGNB website https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria
0.2.3 | Izvajalec mora v svojih ponudbah upoštevati, da je potrebno skladno z določili DGNB certifikacijskega sistema, pravočasno (pred pričetkom gradnje) dostaviti vso ustrezno dokumentacijo, za vse v ponudbi zajete materiale, elemente in opremo (tehnični list, varnostni list, izjava o lastnostih, tehnična navodila za ravnanje, servisiranje, vzdrževanje,...) v slovenskem jeziku. Vgradnja kakršnihkoli materialov, elementov ali opreme, se izvede zgolj na podlagi predhodne preveritve posredovane dokumentacije in obenem potrditve s strani nadzornika. | The Contractor must take into account in its tenders that, in accordance with the provisions of the DGNB certification system, all relevant documentation for all materials, elements and equipment included in the tender (technical data sheet, safety data sheet, declaration of properties, technical instructions for handling, servicing, maintenance,...) must be delivered on time (prior to the start of construction) in the Slovene language (in accordance with the provisions of the DGNB certification system). The installation of any materials, elements or equipment shall be subject to prior checking of the submitted documentation and, at the same time, to the approval of the Supervisor.
0.2.4 | Izbrani materiali, elementi, naprave, sistemi in oprema morajo prispevati k večji trajnosti stavbe v smeri zagotavljanja energetske učinkovitosti, ekonomičnega in enostavnega vzdrževanja ter čiščenja, dolge življenjske dobe, uporabe okolju prijaznih materialov ipd. | The materials, elements, appliances, systems and equipment chosen must contribute to the sustainability of the building in terms of energy efficiency, economic and easy maintenance and cleaning, long lifetime, use of environmentally friendly materials, etc.
0.2.5 | Predloženi dokumenti za vse uporabljene materiale, elemente in opremo morajo izpolnjevati zahteve najmanj kakovostne stopnje QS3 (zaželeno QS4), iz dokumenta: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001) | The documents submitted for all materials, components and equipment used shall meet the requirements of at least quality level QS3 (preferably QS4) of the document DGNB Quality Grades for Materials, Components and Equipment (JULFS--7X9001)
0.2.6 | V kolikor izbrani materiali oz. elementi, navedeni v posameznih postavkah, ne ustrezajo vsaj kakovostni stopnji QS3 iz seznama: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), je izvajalec dolžan na to opozoriti projektanta, nadzor in investitorja ter podati predlog ustreznega materiala oz. elementa. | If the selected materials or elements listed in the individual items do not meet at least quality level QS3 of the list of DGNB quality classes for materials, elements and equipment (JULFS--7X9001), the Contractor shall draw this to the attention of the Designer, the Supervisor and the Investor, and shall make a proposal for a suitable material or element.
0.2.7 | Izvajalec lahko v svoji ponudbi predlaga alternativne produkte in rešitve glede na predvidene s projektom, pod pogojem, da le-te prav tako izpolnjujejo vse navedene zahteve. Pri morebitnih predlaganih alternativnih produktih oz. rešitvah je potrebno upoštevati najmanj enake ali boljše lastnosti v smislu življenjske dobe, obstojnosti, ter enostavnosti in stroška čiščenja ter vzdrževanja v primerjavi s projektom predpisanimi rešitvami. Za alternativne rešitve izvajalec pridobi soglasje projektanta, nadzornika in investitorja pred pričetkom gradnje. | The Contractor may propose alternative products and solutions to those envisaged by the project in its tender, provided that they also meet all the requirements set out above. Any alternative products or solutions proposed shall have at least the same or better characteristics in terms of service life, durability, and ease and cost of cleaning and maintenance compared to the solutions envisaged by the project. For alternative solutions, the contractor shall obtain the agreement of the designer, the supervisor and the investor before starting construction.
0.2.8 | Izvajalec med gradnjo dnevno beleži vsa eventualna odstopanja od PZI projektne dokumentacije ter podatke pravočasno posreduje naročniku, nadzoru in projektantu. Potrjene spremembe vnese v podlage za izdelavo PID in posodobitev BIM modelov. | During construction, the Contractor shall record on a daily basis any deviations from the Detailed Design documentation (PZI) and shall provide the information to the Client, Supervision and the Designer in a timely manner. Confirmed changes shall be entered into the basis for the As-built documentation (PID) and BIM model updates.
0.2.9 | Izvajalec med gradnjo sproti izpolnjuje Seznam vseh konstrukcijskih sestav s pripadajočimi vgrajenimi gradbenimi materiali in dokumentira naslednje podatke o vgrajenih materialih (v slovenskem jeziku): - Varnostni list - Tehnični list - Izjavo o lastnostih (če je relevantno) - Izkazovanje morebiti obstoječega okoljskega certifikata (Tip I - okoljski znak ali Tip III - okoljska produktna deklaracija /EPD) - Izjavo proizvajalca ali dobavitelja, da produkt ustreza zahtevam ENV1.2 - Tehnična navodila za ravnanje, servisiranje, vzdrževanje oziroma ostale, z zakonom predpisane dokumente in dokumentacijo. | During construction, the Contractor shall keep a List of all structural assemblies with their associated construction materials and document the following information on the materials installed (in Slovene language): - Safety Data Sheet - Technical Data Sheet - Declaration of performance (if applicable) - Demonstration of any existing environmental certification (Type I - Ecolabel or Type III - Environmental Product Declaration /EPD) - A declaration by the manufacturer or supplier that the product complies with the requirements of ENV1.2 - Technical instructions for handling, servicing, maintenance or other documents and documentation required by law.
0.2.10 | Za vse vgrajene bistvene tehnične sisteme mora izvajalec zagotoviti obstoj pooblaščenega servisa, ki deluje na območju Republike Slovenije, da ima investitor možnost skleniti ustrezno pogodbo o vzdrževanju. Med bistvene tehnične sisteme sodijo npr.: sistemi ogrevanja in hlajenja, priprava tehnoloških medijev, prezračevanje in klimatizacija, sistemi detekcije in gašenja požara, sistemi tehničnega varovanja, BMS in CNS sistemi upravljanja stavbe, razsvetljava, komunikacijski in WI-FI sistemi,... | For all installed essential technical systems, the contractor must ensure the existence of an authorised service centre operating in the territory of the Republic of Slovenia, so that the investor has the possibility of concluding an appropriate maintenance contract. The essential technical systems include, for example: heating and cooling systems, technological media preparation, ventilation and air conditioning, fire detection and extinguishing systems, technical security systems, BMS and CNS building management systems, lighting, communication and WI-FI systems,...
0.2.11 | Zaželeno je, da imajo uporabljeni elementi in materiali okoljsko oznako Tip I. (kot npr. ENCODE, BLUE ANGEL, ipd...). | It is preferable that the elements and materials used have a Type I environmental label (such as ENCODE, BLUE ANGEL, etc...).
0.2.12 | Izvajalec bo za elemente iz lesa moral dokazovati izvor z navedbo izvorne države in tipa lesa, FSC / PEFC certifikat z dodatnim pripadajočim potrdilom Chain of custody-trgovski certifikat dobavitelja - ta se dokazuje z dobavnicami, računi ali enakovredno. Za izdelke iz naravnega kamna iz EU držav je potrebna deklaracija, da je izvor in procesiranje teh izdelkov v celoti v EU državah. Za izdelke iz naravnega kamna, ki prihajajo iz držav izven EU, je potrebno predložiti dokazilo o izpolnjevanju ILO konvencije 182, ki vključuje neodvisna inšpekcijska poročila. | For wood elements, the contractor will be required to provide proof of origin, indicating the country of origin and the type of wood, FSC/PEFC certification with an additional Chain of Custody certificate - the supplier's trade certificate - this shall be evidenced by delivery notes, invoices or equivalent. For natural stone products from EU countries, a declaration that the sourcing and processing of these products is entirely in EU countries is required. For natural stone products from non-EU countries, proof of compliance with ILO Convention 182, including independent inspection reports, is required.
0.2.13 | Izobraževanje udeležencev pri gradnji Izvajalec je dolžan vse udeležence pri gradnji podrobneje seznaniti tudi z relevantnimi koncepti, študijami, elaborati, ki opredelujejo trajnostni način gradnje za naslednja področja: - zaščita pred hrupom (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)) - zaščita pred prašenjem - zaščita tal in podzemne vode (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)), Analiza tveganja za onesnaženje vodnega telesa podzemne vode št. 0346-023/2023, maj 2023 (Geološko projektiranje d.o.o.)) - ravnanje z gradbenimi odpadki (Načrt gospodarjenja z gradbenimi odpadki) Izobraževanja se izvajajo skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.1 1.2, 2.2, 3.2 in 4.2 Training for the parties implementing the construction work | Training of construction participants The contractor is also obliged to inform all construction participants in detail about relevant concepts, studies, elaborations defining sustainable construction methods for the following areas: - noise protection (Environmental Impact Assessment Report No 100123-11523, dated 11.5.2023, supplemented on 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.)) - dust protection - protection of soil and groundwater (Environmental Impact Assessment Report No. 100123-11523, dated 11.5.2023, supplemented 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.), Risk analysis for contamination of the groundwater No. 0346-023/2023, May 2023 (Geološko projektiranje d.o.o.)) - construction waste management (Construction Waste Management Plan) The training shall be carried out in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.1 1.2, 2.2, 3.2 and 4.2 Training for the parties implementing the construction work
0.2.14 | Navodila za obratovanje in vzdrževanje objekta Izvajalec pripravi Navodila za obratovanje in vzdrževanje objekta skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilih: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual | Instructions for the operation and maintenance of the facility The Contractor shall prepare the Operation and Maintenance Instructions for the Facility in accordance with the applicable Slovenian legislation and the DGNB System Instructions specified in the Criteria: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual
0.2.15 | Meritve kontrole kakovosti gradnje Izvajalec mora upoštevati, da se bodo po koncu gradnje izvedle naslednje meritve: - meritve zrakotesnosti - meritve s termokamero (termografija) - meritve akustike - meritve zvočne zaščite ovoja stavbe - meritve zvočne zaščite ločilnih elementov med posameznimi prostori različnih namembnosti - meritve udarnega zvoka - meritve vlažnosti vgrajenih elementov, pred vgradnjo finalnih tlakov - test odvoda dima in toplote Meritve morajo opraviti ustrezno usposobljeni preskusni organi ali strokovnjaki ter rezultate oceniti in primerjati z zahtevami. Obseg opravljenih meritev mora biti sorazmeren z velikostjo zgradbe in mora ustrezno odražati cilj preverjanja kakovosti zgradbe. Smiselno je, da izvajalec del tekom gradnje za sprotno kontrolo kakovosti vgrajenih materialov, elementov in opreme, sam izvaja meritve. Končne meritve (ob primopredaji) izvede tretja oseba kot neodvisna potrditev doseganja zahtev. Meritve se izvajajo skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 2. Quality control measurements | Construction quality control measurements The contractor must take into account that the following measurements will be carried out after completion of the construction: - airtightness measurements - thermal camera measurements (thermography) - acoustics measurements - measurements of the sound insulation of the building envelope - measurements of the sound insulation of the separating elements between different rooms of different uses - impact sound measurements - moisture measurements of the installed elements, prior to the installation of the final flooring - smoke and heat extraction test The measurements shall be carried out by suitably qualified test bodies or experts and the results evaluated and compared with the requirements. The extent of the measurements carried out shall be proportionate to the size of the building and shall adequately reflect the objective of the building quality verification. It is reasonable for the contractor to carry out his own measurements during construction to check the quality of the materials, elements and equipment installed. Final measurements (at handover) are carried out by a third party as an independent confirmation of compliance with the requirements. The measurements shall be carried out in accordance with the applicable Slovenian legislation and the DGNB system instructions specified in the benchmark: PRO 2.2 2. Quality control measurements
0.2.16 | Zagotavljanje kakovosti za uporabljene gradbene proizvode Izvajalec mora zagotavljati izvajanje primerjav med definiranim in dejansko uporabljenim materialom, elementom ali opremo skladno seznamom: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), vključno z dokazno dokumentacijo ugotovitev primerjav ter skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 3.1 Quality assurance for the used construction products | Quality assurance for the construction products used The Contractor shall ensure that comparisons are made between the defined and the actual material, element or equipment used in accordance with the list: DGNB Quality Grades of Installed Materials, Elements and Equipment (JULFS--7X9001), including supporting documentation of the findings of the comparisons, and in accordance with the DGNB system instructions defined in the Criterion: PRO 2.2 3.1 Quality assurance for the used construction products
0.2.17 | Zaščita pred vlago Izvajalec predloži dokumentacijo, ki dokazuje, da je bil izveden program prezračevanja, prilagojen stavbi, s čimer se zagotovi pogoje, da so vgrajeni gradbeni elementi ustrezno suhi, skladno z navodili DGNB opredeljenimi v merilu: PRO 2.2 4.1 Mould prevention | Protection against moisture The Contractor shall provide documentation demonstrating that a building-specific ventilation programme has been implemented to ensure that the building elements installed are adequately dry, in accordance with the DGNB guidelines specified in the criteria: PRO 2.2 4.1 Mould prevention
0.2.18 | Preizkusi delovanja sistemov Izvajalec sodeluje pri izvedbi predhodnega in končnega preizkusa delovanja vseh bistvenih tehničnih komponent stavbe in pripravi ustrezne dokazne dokumentacije ter pri usposabljanju vzdrževalcev/upravljalcev stavbe, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators | System performance tests The Contractor shall be involved in the performance of the preliminary and final performance tests of all essential technical components of the building and the preparation of the relevant supporting documentation, as well as in the training of the maintenance/management staff of the building, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators
0.2.19 | Poročilo o zagonu objekta Izvajalec sodeluje pri pripravi končnega poročila o zagonu objekta, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 5.1 Creation of a detailed final report | Commissioning report The Contractor shall be involved in the preparation of the final commissioning report, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 5.1 Creation of a detailed final report
0.2.20 | Koncept celovitega delovanja sistemov v stavbi Izvajalec sodeluje pri procesu implementiranja stalnega nadzora in nastavitev delovanja stavbe ter usposabljanju vzdrževalcev/upravljalcev stavbe. Navedeno se izvede v skladu z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 6.1 Creation and handover of an integral operating concept | The concept of integrated building systems The contractor is involved in the process of implementing the building's continuous monitoring and settings and training the building's maintenance/management staff. This shall be done in accordance with the DGNB system instructions defined in the benchmark: PRO 2.3 6.1 Creation and handover of an integral operating concept
0.2.21 | Prilagoditev nastavitev sistemov po začetni fazi uporabe objekta Izvajalec sodeluje pri ponovnem pregledu delovanja vseh bistvenih tehničnih sistemov ter eventualni ponovni prilagoditvi teh sistemov s strani strokovnjaka oz. (neodvisne) tretje osebe. Postopek se izvede po približno 10–14 mesecih po zaključku gradnje, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 7.1 Readjustment of the system following initial operating phase | Adjusting system settings after the initial phase of use of the building The Contractor shall be involved in the re-examination of the functioning of all essential technical systems and the possible re-adjustment of these systems by an expert or (independent) third party. The procedure shall be carried out approximately 10-14 months after completion of construction, in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.3 7.1 Readjustment of the system following initial operating phase

## 3.3.0_Rekapitulacija
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
| REKAPITULACIJA STROŠKOV ELEKTRO DEL | COST SUMMARY OF ELECTRICAL WORKS
| 3 NAČRT S PODROČJA ELEKTROTEHNIKE | 3 DOCUMENTATION IN THE FIELD OF ELECTRICAL ENGINEERING
| 3/3 SN napajanje in transformatorska postaja | 3/3 MV Power Supply and Transformer Substation
3.3 | ELEKTRO DELA | ELECTRICAL WORKS
3.3.2 | SN 24 kV STIKALNI BLOK IN SN KABLI | 24 kV MV switchgear and MV cables | 0
3.3.3 | TRANSFORMACIJA 10(20)/0,4 kV, 1600 kVA | TRANSFORMATION 10(20)/0,4 kV, 1600 kVA | 0
3.3.4 | NN STIKALNI BLOKI IN RAZDELILNIKI | LV SWITCHGEAR BLOCKS AND SWITCHGEAR DISTRIBUTORS | 0
3.3.5 | BREZPREKINITVENO NAPAJANJE (UPS) | UNINTERRUPTIBLE POWER SUPPLY (UPS) | 0
3.3.6 | DIESEL ELEKTRIČNI AGREGAT (DEA) | DIESEL ELECTRIC POWER UNIT (DEA) | 0
3.3.7 | KOMPENZACIJA JALOVE ELEKTRIČNE ENERGIJE | COMPENSATION FOR REACTIVE ELECTRICITY | 0
3.3.8 | NN ENERGETSKI ZBIRALKE IN NN ENERGETSKI KABLI | LV BUSBARS AND LV POWER CABLES | 0
3.3.9 | ZAŠČITNI CEVI IN KABELSKI POLICE | PROTECTIVE HOSES AND CABLE RACKS | 0
3.3.10 | OBRAČUNSKE MERITVE ELEKTRIČNE ENERGIJE | ELECTRICITY METERING | 0
3.3.11 | NAPRAVE ZA VODENJE IN NADZOR | COMMAND AND CONTROL EQUIPMENT | 0
3.3.12 | OZEMLJITVE IN IZENAČITVE POTENCIALOV | EARTHING AND EQUIPOTENTIAL BONDING | 0
3.3.13 | GRADBENO - OBRATNIŠKA DELA V TP | CONSTRUCTION AND PLANT WORKS IN TP | 0
3.3.14 | OSTALO | OTHER | 0
0
0 | NEPREDVIDENA DELA | UNFORSEEN WORKS | 0
| SKUPAJ ELEKTRO DELA | TOTAL ELECTRICAL WORKS | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT

## 3.3.2_SN stikalni blok
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.3 | ELEKTRO DELA | ELECTRICAL WORKS
3.3.2 | SN 24 kV STIKALNI BLOK IN SN KABLI | 24 kV MV switchgear and MV cables | [5 empty] | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description |  |  | EM | Količina | Cena/EM | Cena
2 | SN 24 kV STIKALNI BLOK IN SN KABLI | 24 kV MV switchgear and MV cables
2.1 | SN stikalni blok Fakulteta za strojništvo, IM-GBCB-QM-QM | MV switching block Faculty of Mechanical Engineering, IM-GBCB-QM-QM
| Dobava in montaža prosto stoječega stikalnega bloka v SM AirSet izvedbi z 630A zbiralkami, sestavljen iz 3 polj dimenzij: širina 2250 mm, višina 1600 mm, globina 1030 mm. IM 375 x 1600 x 1030 mm (šxvxg) GBC-B 750 x 1600 x 1110 (šxvxg) QM 375 x 1600 x 1030 mm (šxvxg) Električnih karakteristik: Un=24kV, In=630A, Ik=20 kA/s. Napetost na pomožnih kontaktih in izklopnih tuljavah je predvidena za 220V AC. Instalirane senzorje za stalni 24/7 nadzor temperature na spojih. SN stikalni blok tip SM AirSeT, sestavljen iz zračno izoliranih celic. Stikalne naprave so izolirane z zrakom/vakuumom. Ponujene SM AirSeT celice ne potrebujejo kotnih natičnih kabelskih končnikov ampak navadne kabelske končnike zaključene s kabelskim ušesom. *Možno je priključiti kable preseka do 240mm2 (2 kabla po fazi). Za kable s presekom 300mm2 je potrebno uporabiti posebne kabelske čevlje (ref. LV432506). Kot na primer tip: SM AirSet, proizvod: Schneider Electric Komplet z vezalnimi shemami za posamezna polja: | Supply and installation of a free-standing SM AirSet switchgear unit with 630A busbar, consisting of 3 bays with dimensions: width 2250 mm, height 1600 mm, depth 1030 mm. IM 375 x 1600 x 1030 mm (WxHxD) GBC-B 750 x 1600 x 1110 (WxHxD) QM 375 x 1600 x 1030 mm (WxHxD) Electrical characteristics Un=24kV, In=630A, Ik=20 kA/s. The voltage at the auxiliary contacts and trip coils is 220V AC. Installed sensors for 24/7 temperature monitoring at the joints. SM AirSeT type MV switchgear consisting of air-insulated cells. The switchgear is air/vacuum insulated. The SM AirSeT cells offered do not require angled cable lugs but regular cable lugs terminated with a cable lug. *It is possible to connect cables with a cross section up to 240mm2 (2 cables per phase). For cables with a cross section of 300mm2, special cable shoes (ref. LV432506) must be used. Such as Type:SM AirSet, Product:Schneider Electric Complete with wiring diagrams for each field:
2.2 | Celica SN_P1_TP_J4 (IM) | Cell SN_P1_TP_J4 (IM) |  |  | kpl | 1 |  | 0
a. | Odklopni ločilnik, Un=24 kV, In=630 A, Ik=20 kA/s: - s pomožnimi kontakti NO, NZ - 2kosa - Motorni pogon - 230V AC – 1kos - z možnostjo zaklepanja določenega položaja stikala | Disconnecting switch, Un=24 kV, In=630 A, Ik=20 kA/s: - with auxiliary contacts NO, NZ - 2 pieces - Motor drive - 230V AC - 1 piece - with the possibility of locking a specific switch position | kos | 1
b. | Ozemljitveno stikalo z vklopno vzmetjo (bremensko stikalo): - s pomožnimi kontakti NO, NZ - 1kos | Earthing switch with on/off spring (load switch): - with auxiliary contacts NO, NZ - 1 piece | kos | 1
c. | Komplet izoliranih bakrenih zbiralk za povezavo med polji 630A | Insulated copper busbar set for field connection 630A | kos | 1
d. | Prenapetostna zaščita | Overvoltage protection | kos | 1
e. | Signalizacija prisotnosti faz | Signalling the presence of phases | kos | 1
f. | Sistem za testiranje faznega zaporedja | Phase sequence testing system | kos | 1
g. | Temperaturni senzorji TH110 3x za stalni nadzor temperature (na spoju vsake faze) | TH110 3x temperature sensors for continuous temperature monitoring (at the junction of each phase) | kos | 1
h. | Priključne sponke | Connecting clips | kpl | 1
2.3 | Celica SN_P1_TP_J5 (GBC-B) | Celica SN_P1_TP_J5 (GBC-B) |  |  | kpl | 1 |  | 0
a. | Napetostni merilni transformator s prigrajenimi varovalkami 0,3 A, 10-20/√3 / 0,1/√3 / 0,1/3 kV. 1. navitje: 30 VA, kl. 0,5; 2. navitje: 30 VA, kl. 0,5; | Voltage measuring transformer with 0.3 A, 10-20/√3/0.1/√3/0.1/3 kV fuses attached. 1. winding: 30 VA, Kl. 0,5; 2. winding: 30 VA, Kl. 0,5; | kos | 3
b. | Tokovni merilni transformator 2x75/5/5A, 1. jedro: 10 VA, kl. 0,5, Fs=5 VA 2. jedro: 10 VA, kl. 0,5, Fs=15 VA | Current transformer 2x75/5/5A, 1. core: 10 VA, Kl. 0,5, Fs=5 VA 2. core: 10 VA, Kl. 0,5, Fs=15 VA | kos | 3
c. | Merilnik moči PM5340 z Ethernetom | PM5340 Power Meter with Ethernet | kos | 1
d. | Komplet izoliranih bakrenih zbiralk za povezavo med polji 630A | Insulated copper busbar set for field connection 630A | kos | 1
e. | Opomba: Tokovni in napetostni merilni morajo biti dobavljeni skladno s soglasjem za priključitev oziroma projektnimi pogoji Elektro Ljubljana, Naborom merilne opreme SODO in Sistemskimi obratovalnimi navodili za distribucijski sistem električne energije (Ur. l. RS 7/2021). Pred naročilom je potrebno preveriti zahteve iz zgoraj navedenih dokumentov. | Note: Current and voltage meters must be supplied in accordance with the connection consent or project conditions of Elektro Ljubljana, the SODO Metering Equipment Set and the System Operating Instructions for the Electricity Distribution System (Official Gazette of the Republic of Slovenia RS 7/2021). The requirements of the above documents must be verified prior to ordering.
2.4 | Celica SN_P1_TP_J6 (QM) | Celica SN_P1_TP_J6 (QM) |  |  | kpl | 1 |  | 0
a. | Odklopni ločilnik, Un=24 kV, In=630 A, Ik=20 kA/s: - s pomožnimi kontakti NO, NZ - 2kosa - Motorni pogon - 230V AC – 1kos - izklopna tuljava 230V AC - z možnostjo zaklepanja določenega položaja stikala | Disconnecting switch, Un=24 kV, In=630 A, Ik=20 kA/s: - with auxiliary contacts NO, NZ - 2 pieces - Motor drive - 230V AC - 1 piece - 230V AC trip coil - with the possibility of locking a specific switch position | kos | 1
b. | Ozemljitveno stikalo z vklopno vzmetjo (bremensko stikalo): - s pomožnimi kontakti NO, NZ - 1kos | Earthing switch with on/off spring (load switch): - with auxiliary contacts NO, NZ - 1 piece | kos | 1
c. | Varovalka z udarno iglo po DIN standardu 100A | DIN standard 100A needle impact fuse | kos | 3
d. | Komplet izoliranih bakrenih zbiralk za povezavo med polji 630A | Insulated copper busbar set for field connection 630A | kos | 1
e. | Prenapetostna zaščita | Overvoltage protection | kos | 1
f. | Signalizacija prisotnosti faz | Signalling the presence of phases | kos | 1
g. | Sistem za testiranje faznega zaporedja | Phase sequence testing system | kos | 1
h. | Temperaturni senzorji TH110 3x za stalni nadzor temperature (na spoju vsake faze) | TH110 3x temperature sensors for continuous temperature monitoring (at the junction of each phase) | kos | 1
i. | Priključne sponke | Connecting clips | kpl | 1
2.5 | Celica SN_P1_TP_J7 (QM) | Celica SN_P1_TP_J7 (QM) |  |  | kpl | 1 |  | 0
a. | Odklopni ločilnik, Un=24 kV, In=630 A, Ik=20 kA/s: - s pomožnimi kontakti NO, NZ - 2kosa - Motorni pogon - 230V AC – 1kos - izklopna tuljava 230V AC - z možnostjo zaklepanja določenega položaja stikala | Disconnecting switch, Un=24 kV, In=630 A, Ik=20 kA/s: - with auxiliary contacts NO, NZ - 2 pieces - Motor drive - 230V AC - 1 piece - 230V AC trip coil - with the possibility of locking a specific switch position | kos | 1
b. | Ozemljitveno stikalo z vklopno vzmetjo (bremensko stikalo): - s pomožnimi kontakti NO, NZ - 1kos | Earthing switch with on/off spring (load switch): - with auxiliary contacts NO, NZ - 1 piece | kos | 1
c. | Varovalka z udarno iglo po DIN standardu 100A | DIN standard 100A needle impact fuse | kos | 3
d. | Komplet izoliranih bakrenih zbiralk za povezavo med polji 630A | Insulated copper busbar set for field connection 630A | kos | 1
e. | Prenapetostna zaščita | Overvoltage protection | kos | 1
f. | Signalizacija prisotnosti faz | Signalling the presence of phases | kos | 1
g. | Sistem za testiranje faznega zaporedja | Phase sequence testing system | kos | 1
h. | Temperaturni senzorji TH110 3x za stalni nadzor temperature (na spoju vsake faze) | TH110 3x temperature sensors for continuous temperature monitoring (at the junction of each phase) | kos | 1
i. | Priključne sponke | Connecting clips | kpl | 1
2.6 | Celica SN_P1_TP_J8 (QM) | Celica SN_P1_TP_J8 (QM) |  |  | kpl | 1 |  | 0
a. | Odklopni ločilnik, Un=24 kV, In=630 A, Ik=20 kA/s: - s pomožnimi kontakti NO, NZ - 2kosa - Motorni pogon - 230V AC – 1kos - izklopna tuljava 230V AC - z možnostjo zaklepanja določenega položaja stikala | Disconnecting switch, Un=24 kV, In=630 A, Ik=20 kA/s: - with auxiliary contacts NO, NZ - 2 pieces - Motor drive - 230V AC - 1 piece - 230V AC trip coil - with the possibility of locking a specific switch position | kos | 1
b. | Ozemljitveno stikalo z vklopno vzmetjo (bremensko stikalo): - s pomožnimi kontakti NO, NZ - 1kos | Earthing switch with on/off spring (load switch): - with auxiliary contacts NO, NZ - 1 piece | kos | 1
c. | Varovalka z udarno iglo po DIN standardu 100A | DIN standard 100A needle impact fuse | kos | 3
d. | Komplet izoliranih bakrenih zbiralk za povezavo med polji 630A | Insulated copper busbar set for field connection 630A | kos | 1
e. | Prenapetostna zaščita | Overvoltage protection | kos | 1
f. | Signalizacija prisotnosti faz | Signalling the presence of phases | kos | 1
g. | Sistem za testiranje faznega zaporedja | Phase sequence testing system | kos | 1
h. | Temperaturni senzorji TH110 3x za stalni nadzor temperature (na spoju vsake faze) | TH110 3x temperature sensors for continuous temperature monitoring (at the junction of each phase) | kos | 1
i. | Priključne sponke | Connecting clips | kpl | 1
2.7 | Dobava in uvlečenje kabla - N2XS(FL)2Y 1×70/16 mm2 RM 12/20kV v betonske cevi | Supply and insertion of cable - N2XS(FL)2Y 1×70/16 mm2 RM 12/20kV in concrete pipes |  |  | m | 140 |  | 0
2.8 | Dobava in montaža kabelskega zaključka s priklopom in ozemljitvijo za enožilni kabel N2XS(F)2Y 1×70/16 mm2 , 12/20 kV, kot na primer tip: POLT-24D/1XI-ML-2-13 + EAKT-1657 | Supply and installation of cable termination with connection and earthing for single-core cable N2XS(F)2Y 1×70/16 mm2 , 12/20 kV, such as type: POLT-24D/1XI-ML-2-13 + EAKT-1657 |  |  | kos | 18 |  | 0
2.9 | Pritrdilne skobe za tri enožilne SN kable za kabel premera od 29 mm do 41 mm, kratkostična trdnost 25.000 N, komplet s pritrdilnim materialom, kot na primer tip: KP29/41, id-Technik | Fixing clips for three single-core MV cables for cable diameters from 29 mm to 41 mm, short-circuit strength 25,000 N, complete with fixing material, e.g. type: KP29/41, id-Technik |  |  | kos | 8 |  | 0
2.10 | Napetostni preizkus položenega kablovoda z izdelavo merilnega protokola | Voltage test of a laid cable duct with the establishment of a measurement protocol |  |  | kpl | 3 |  | 0
| SN 24 kV STIKALNI BLOK IN SN KABLI | 24 kV MV switchgear and MV cables | [5 empty] | 0

## 3.3.3_Transformacija
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.3 | ELEKTRO DELA | ELECTRICAL WORKS
3.3.3 | TRANSFORMACIJA 10(20)/0,4 kV, 1600 kVA | TRANSFORMATION 10(20)/0,4 kV, 1600 kVA | [5 empty] | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description |  |  | EM | Količina | Cena/EM | Cena
3 | TRANSFORMACIJA 10(20)/0,4 kV, 1600 kVA | TRANSFORMATION 10(20)/0,4 kV, 1600 kVA
3.1 | Dobava in montaža trifaznega suhega energetskega transformatorja, kot na primer tip: TRIHAL suhi, proizvod: Schneider Electric | Supply and installation of a three-phase dry-type power transformer, such as type TRIHAL dry-type, manufactured by Schneider Electric |  |  | kpl | 2 |  | 0
| Tehnične karakteristike: | Technical characteristics:
| Nazivna moč: 1600kVA | Rated power: 1600kVA
| Nazivna primarna napetost: 20/10 kV - prevezljivo primarno navitje | Rated primary voltage: 20/10 kV - Bonded primary winding
| Izolacijska napetost: 24 kV | Insulation voltage: 24 kV
| Regulacija napetosti na primarju: ± 2x2,5% | Primary voltage regulation: ± 2x2.5%
| Nazivna sekundarna napetost: 0,4 kV | Rated secondary voltage: 0,4 kV
| Nazivna frekvenca: 50 Hz | Nominal frequency: 50 Hz
| Vezalna skupina: Dyn5 | Binding group: Dyn5
| Hlajenje: Naravno AN | Cooling: natural AN
| Izgube: AAoAk - izgube skladne z EU uredbo 548/2014 | Losses: AAoAk - Losses compliant with EU Regulation 548/2014
| Napetost kratkega stika uk: 6% | Short-circuit voltage uk: 6%
| Termična klasa izolacije F1 | Thermal insulation class F1
| Klimatski razred po IEC 60076-11 E3 do -50°C | Climate class IEC 60076-11 E3 to -50°C
| Obratovalni razred po IEC 60076-16 C3 izjemna stopnja vlage nad 95% | Operating class according to IEC 60076-16 C3 extreme humidity above 95%
| Parcijalno dielektrično praznenje do vrednosti 5pC | Partial dielectric discharge up to 5pC
| Stalni 24/7 nadzor temperature na spojih, z možnostjo pošiljanja alarmov in prenosa podatkov na nadzorni sistem | 24/7 continuous temperature monitoring at the junctions, with the possibility of sending alarms and transmitting data to the control system
| Dobava in montaža SN kabelskih končnikov za priključitev na transformator, Raychem tip POLT | Supply and installation of MV cable terminations for connection to a transformer, Raychem type POLT
| Stranski VN priključki, dvosmerni kolesa, kljuke za dvigovanje, priključek na ozemljitve (2 lokacije), NN priključki za priklop z zgornje strani, Protokol rutinskega testiranja, Termična klasa izolacije F1 | HV side connections, bidirectional wheels, lifting hooks, earth connection (2 locations), LV connections for top side connection, Routine testing protocol, Insulation thermal class F1
a. | Ventilatorji za prisilno hlajenje transformatorja, nameščeni na transformatorju, komplet z vso potrebno opremo. | Transformer-mounted forced cooling fans, complete with all necessary accessories. | 6 | kos
b. | TP100 sonde. | TP100 probes. | 3 | kos
c. | Temperaturni senzorji TH110 10x za stalni nadzor temperature. | TH110 10x temperature sensors for continuous temperature monitoring. | 1 | kpl
| Dimenzije (okvirne): 1704x945x2070 mm (ŠxGxV), masa 3100kg | Dimensions (approximate): 1704x945x2070 mm (WxDxH), weight 3100kg
3.2 | Dobava in montaža razdelilnika za zaščito in prisilno prezračevanje transformatorja. Opremljen je z vsemi potrebnimi nosilci, blendami, vrati, izrezi, ključavnico, z označenimi priključki na stikalne elemente in žične povezave ter pripravljen za priklop. Uvod kablov v razdelilnik s pomočjo uvodnic vgrajenih v dno razdelilnika. Razdelilnik mora biti opremljen po seznamu opreme v dokumentu št. JULFS--7E9110 in JULFS--7E9111, ožičen in preizkušen. Vgrajena oprema: | Supply and installation of a switchboard for protection and forced ventilation of the transformer. It shall be equipped with all necessary brackets, blocks, doors, cut-outs, lock, marked connections to switching elements and wire connections and ready for connection. The cables shall be fed into the switchboard by means of glands built into the bottom of the switchboard. The switchboard shall be equipped according to the list of equipment in document Nos JULFS--7E9110 and JULFS--7E9111, wired and tested. Built-in equipment: |  |  | kpl | 2 |  | 0
a. | Zidna omara izdelana iz jeklene pločevino prašno barvane v RAL7035, v zaščiti IP55. Okvirnih dimenzij (širina x višina x globina) 400 x 400 x 200mm z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, ipd. Kot na primer tip:NSYS3D4420P + NSYAEFPFXSC NEW, proizvod: Schneider Electric | Wall cabinet made of powder-coated steel sheet in RAL7035, IP55 protection. Frame dimensions (width x height x depth) 400 x 400 x 200mm with mounting and fixing material including wiring channels, DIN mouldings, marking material, etc. Such as type:NSYS3D4420P + NSYAEFPFXSC NEW, product:Schneider Electric | 1 | kpl
b. | Termični zaščitni rele, 2 stopnji - alarm (140C) in izklop (150C), napajanje AC/DC 24-240V 50/60 Hz, kot na primer tip NT 935 AD ETH, proizvod: TECSSYSTEM | Thermal protection relay, 2 stages - alarm (140C) and trip (150C), AC/DC power supply 24-240V 50/60 Hz, e.g. type NT 935 AD ETH, product: TECSSYSTEM | 1 | kos
c. | Varovalčni ločilnik 3P, 32A, 10x38mm + varovalke 3x10A gG 10x38, kot na primer tip: LS1D32 + GVAE11, proizvod: Schneider Electric | Fuse disconnector 3P, 32A, 10x38mm + fuses 3x10A gG 10x38, as for example type: LS1D32 + GVAE11, product: Schneider Electric | 1 | kpl
d. | Varovalčni ločilnik 1P+N, 32A, 10x38mm + varovalke 1x2A gG 10x38, kot na primer tip: DF101N, proizvod: Schneider Electric | Fuse disconnector 1P+N, 32A, 10x38mm + 1x2A fuses gG 10x38, e.g. type: DF101N, product: Schneider Electric | 1 | kpl
e. | Varovalčni ločilnik 2P, 32A, 10x38mm + varovalke 2x2A gG 10x38, kot na primer tip: DF102, proizvod: Schneider Electric | Fuse disconnector 2P, 32A, 10x38mm + fuses 2x2A gG 10x38, e.g. type: DF102, product: Schneider Electric | 1 | kpl
f. | Močnostni kontaktor 3P, 18A, 230V 50/60HZ, kot na primer tip: LC1D18P7, proizvod: Schneider Electric | Power contactor 3P, 18A, 230V 50/60HZ, as for example type: LC1D18P7, product: Schneider Electric | 1 | kos
g. | Enonadstropna sponka 2,5 mm2, kot na primer tip: 2002.1407, proizvod: WAGO | Single-ended 2.5 mm2 terminal, e.g. type: 2002.1407, product: WAGO | 4 | kos
h. | Enonadstropna sponka 2,5 mm2, kot na primer tip: 2002.1401, proizvod: WAGO | Single-ended 2.5 mm2 terminal, e.g. type: 2002.1401, product: WAGO | 38 | kos
3.3 | Dobava in motaža nosilca za SN kable sestavljenega iz C profila dolžine 0,5 m, kabelskih objemk, kot na primer tip: KS 25/36 , proizvod: Id Technik, T vijakov z maticami in podložkami ter pritrdilnim materialom | Supply and installation of an MV cable support consisting of a C profile 0,5 m long, cable clamps such as type: KS 25/36 , product: Id Technik, T-bolts with nuts and washers and fixing material |  |  | kpl | 14 |  | 0
3.4 | Dobava in montaža antivibracijskega postavka. | Supply and installation of an anti-vibration item. |  |  | kpl | 8 |  | 0
3.5 | Izvedba meritev EMC z izdelavo poročila. | EMC measurements with report. |  |  | kpl | 2 |  | 0
| TRANSFORMACIJA 10(20)/0,4 kV, 1600 kVA | TRANSFORMATION 10(20)/0,4 kV, 1600 kVA | [5 empty] | 0

## 3.3.4_NN bloki in razdelilniki
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.3 | ELEKTRO DELA | ELECTRICAL WORKS
3.3.4 | NN STIKALNI BLOKI IN RAZDELILNIKI | LV SWITCHGEAR BLOCKS AND SWITCHGEAR DISTRIBUTORS | [5 empty] | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description |  |  | EM | Količina | Cena/EM | Cena
4 | NN STIKALNI BLOKI IN RAZDELILNIKI | LV SWITCHGEAR BLOCKS AND SWITCHGEAR DISTRIBUTORS
4.1 | 0,4 kV stikalni blok +NN_P1_TP_A… | 0,4 kV switching block +NN_P1_TP_A.. |  |  | kpl | 1 |  | 0
| NN sestav je prostostoječe, modularne izvedbe izdelani iz dekapirane jeklene pločevine in profilov, obdelana z anti-korozijsko elektroforezo in končno barvo - poliestrsko/epoksidnim prašnim nanosom, barva RAL - kot na primer kot na primer tipska barva proizvajalca. Vsak element v NN sestavu mora imeti oznako iz tripolne sheme. NN sestav mora ustrezati zahtevam standardov SIST EN 61439-1 in 2. Ponudnik mora priložiti naslednje izjave in poročila: - izjava o skladnosti s SIST EN 61439-1 in 2 - testna poročila v skladu s SIST EN 61439-1 in 2 - enopolne sheme Kot na primer tip: Prisma P, proizvod: Schneider Electric | The LV assembly shall be of a free-standing, modular design, made of decapitated steel sheet and profiles, treated with anti-corrosion electrophoresis and finished with a polyester/epoxy powder-coated finish, RAL colour - such as, for example, the manufacturer's standard colour. Each element in the LV assembly shall be marked with a marking from the three-pole scheme. The LV assembly shall comply with the requirements of SIST EN 61439-1 and 2. The tenderer must attach the following declarations and reports: - declaration of conformity to SIST EN 61439-1 and 2 - test reports in accordance with SIST EN 61439-1 and 2 - unipolar schemes Such as type Prisma P, product Schneider Electric
| Dokumentacija je na voljo v digitalni obliki v oblaku, dostopna preko QR kode na NN sestavu | The documentation is available in digital form in the cloud, accessible via QR code on the NN assembly
| Ponudnik mora dokazati selektivnost med odklopniki v sestavu s pomočjo tabel ali rezultatov izračuna programske opreme | The tenderer shall demonstrate the selectivity between the circuit-breakers in the assembly by means of tables or the results of a software calculation
| Stopnja zaščite: IP31 | Protection rating: IP31
| Število polj (z opremo): 11 | Number of fields (with equipment): 11
| Okvirna dimenzija (ŠxVxG): 7400 x 2100 x 600mm | Dimensions (WxHxD): 7400 x 2100 x 600mm
| Okvirna teža 1 polja: 600kg | Approximate weight of 1 box: 600kg
| Barva RAL: 9001 | RAL colour: 9001
| Prezračevanje: naravno | Ventilation: natural
| Forma pregrajenosti v skladu s standardom SIST EN 61439: 4a | Form of partitioning in accordance with SIST EN 61439:4a
| Priklopi: dovodi - zgoraj s Canalisom, odvodi: zgoraj s kabli | Connections: inlets - above with Canalis, outlets: above with cables
| Naznačena izolacijska napetost (Ui): 1000 V | Rated insulation voltage (Ui): 1000 V
| Naznačena obratovalna napetost (Ue): 415 / 690 V AC | Rated operating voltage (Ue): 415 / 690 V AC
| Naznačena frekvenca (fn): 50 Hz | Designated frequency (fn): 50 Hz
| Pomožna napetost za napajanje komunikacijske in druge pomožne opreme: 230 VAC, 24V DC | Auxiliary voltage supply for communication and other auxiliary equipment: 230 VAC, 24V DC
| Naznačeni tok glavnih zbiralk: 2500 A trajno, materijal Al | Main busbar current rating: 2500 A continuous, material Al
| Naznačeni kratkotrajni zdržni tok (Icw - kA rms/1s): 50 kA | Rated short-time withstand current (Icw - kA rms/1s): 50 kA
| Sistem ozemljitve TN-C-S | TN-C-S earthing system
| Presek N-vodnika enak faznemu | N-conductor cross section equal to phase
| Opombe: - Stikalni blok je predviden za ločeno obratovanje transformatorjev. - Stikalni blok mora biti opremljen po seznamu opreme v dokumentu št. JULFS--7E9094, ožičen in preizkušen. | Notes: - The switchgear block is designed to operate the transformers separately. - The switching unit shall be equipped according to the equipment list in document No JULFS--7E9094, wired and tested.
4.2 | Polje NN_P1_TP_A1_1 | Field NN_P1_TP_A1_1 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 400x2100x600mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : Prisma P, proizvod: Schneider Electric | Cabinet dimensions 400x2100x600mm (WxHxD), made of powder-coated steel sheet in RAL9001, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : Prisma P, product : Schneider Electric | kos | 1
b. | NS 1250N kompaktni odklopnik (MCCB), 3p, nazivni tok 1250A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, fiksna izvedba, kot na primer tip Compact NS, z vgrajeno opremo : - Mikroprocesorska zaščitna enota Micrologic 5.0 - 1kos - Pomožni kontakti stanja NOC - 3kos - Pomožni kontakti delovanja zaščite - 1kos - Motorni pogon - 230VAC - 1kos | NS 1250N compact circuit breaker (MCCB), 3p, rated current 1250A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, fixed version, as for example Compact NS type, with built-in accessories: - Micrologic 5.0 Microprocessor Protection Unit - 1 piece - NOC auxiliary contacts - 3pcs - Auxiliary contacts for protection operation - 1 piece - Motor drive - 230VAC - 1 piece | kos | 1
c. | Tipka za izklop, 1NO+1NC, črna, kot na primer tip: Harmony, XB4 XB4BA21+ZBE102 | Off button, 1NO+1NC, black, e.g. type Harmony, XB4 XB4BA21+ZBE102 | kos | 1
d. | Tipka za vklop, 1NO+1NC, zelena, kot na primer tip: Harmony, XB4 XB4BA31+ZBE102 | Power button, 1NO+1NC, green, e.g. type: Harmony, XB4 XB4BA31+ZBE102 | kos | 1
e. | Zelio RXM rele z ločenim podnožjem-4C/O 6A 24VDC, kot na primer tip: RXM4AB1BDPVS | Zelio RXM relay with separate base-4C/O 6A 24VDC, as for example type: RXM4AB1BDPVS | kos | 2
f. | Sistemska svetilka LED, brez vtičnice, dolžina: 437 mm, vhodna napetost: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, kot na primer tip: 2500200, proizvod: Rittal | LED system luminaire, without socket, length: 437 mm, input voltage: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, e.g. type: 2500200, product: Rittal | kos | 1
g. | Povezovalni kabel, kot na primer tip: 2500400, proizvod: Rittal | Connection cable, e.g. type: 2500400, product: Rittal | kos | 1
h. | Vratno stikalo za LED sistemsko luč, kot na primer tip: 2500460, proizvod: Rittal | Door switch for LED system light, e.g. type: 2500460, product: Rittal | kos | 1
i. | Relejski modul, 24 V DC, 1 CO kontakt, 250 V AC, 6 A, kot na primer tip: TRS 24VDC 1CO AGSNO, proizvod: Weidmüller | Relay module, 24 V DC, 1 CO contact, 250 V AC, 6 A, e.g. type: TRS 24VDC 1CO AGSNO, product: Weidmüller | kos | 2
j. | Enonadstropna vijačna sponka, kot na primer tip: WDU 2.5, proizvod: Weidmüller | Single-deck screw clamp, e.g. type: type WDU 2.5, product: Weidmüller | kos | 5
k. | Enonadstropna vijačna sponka, kot na primer tip: WDU 4, proizvod: Weidmüller | Single-deck screw clamp, e.g. type: type WDU 4, product: Weidmüller | kos | 1
l. | Enonadstropna vzmetna vrstna sponka, kot na primer tip: ZDU 2.5, proizvod: Weidmüller | Single-deck spring-type row clamp, e.g. type: ZDU 2.5, product: Weidmüller | kos | 6
4.3 | Polje NN_P1_TP_A1_2 | Field NN_P1_TP_A1_2 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 800x2100x600mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : Prisma P, proizvod: Schneider Electric | Cabinet dimensions 800x2100x600mm (WxHxD), made of powder-coated steel sheet in RAL9001, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : Prisma P, product : Schneider Electric | kos | 1
b. | NSX 630N kompaktni odklopnik (MCCB), 3p, nazivni tok 630A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, fiksne izvedbe, kot na primer tip ComPact NSX, z vgrajeno opremo: - Elektronska zaščitna enoto Micrologic 2.3 – 1kos - Pomožni kontakti stanja NOC (preklopni kontakt) – 4kos - Pomožni kontakt delovanje zaščite NOC - 4kos - Motorni pogon - 230VAC – 1kos - Zaščitni pokrovi za sponke, dolgi – 2 kosa | NSX 630N compact circuit breaker (MCCB), 3p, rated current 630A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, fixed version, as for example ComPact NSX type, with built-in accessories: - Micrologic 2.3 Electronic Protection Unit - 1 piece - Auxiliary contacts NOC (switching contact) - 4 pieces - Auxiliary contact operation of NOC protection - 4 pieces - Motor drive - 230VAC - 1 piece - Protective caps for staples, long - 2 pcs | kos | 5
c. | NSX 400N kompaktni odklopnik (MCCB), 3p, nazivni tok 400A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, fiksne izvedbe, kot na primer tip ComPact NSX, z vgrajeno opremo: - Elektronska zaščitna enoto Micrologic 2.3 – 2kos - Pomožni kontakti stanja NOC (preklopni kontakt) – 4kos - Pomožni kontakt delovanje zaščite NOC - 1kos - Motorni pogon - 230VAC – 1kos - Zaščitni pokrovi za sponke, dolgi – 2 kosa | NSX 400N compact circuit breaker (MCCB), 3p, rated current 400A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, fixed version, such as ComPact NSX type, with built-in accessories: - Micrologic 2.3 Electronic Protection Unit - 2 pieces - Auxiliary contacts NOC (switching contact) - 4 pieces - Auxiliary contact operation of NOC protection - 1 piece - Motor drive - 230VAC - 1 piece - Protective caps for staples, long - 2 pieces | kos | 2
d. | Tipka za izklop, 1NO+1NC, črna, kot na primer tip: Harmony, XB4 XB4BA21+ZBE102 | Off button, 1NO+1NC, black, e.g. type Harmony, XB4 XB4BA21+ZBE102 | kos | 7
e. | Tipka za vklop, 1NO+1NC, zelena, kot na primer tip: Harmony, XB4 XB4BA31+ZBE102 | Power button, 1NO+1NC, green, e.g. type: Harmony, XB4 XB4BA31+ZBE102 | kos | 7
f. | Zelio RXM rele z ločenim podnožjem-4C/O 6A 24VDC, kot na primer tip: RXM4AB1BDPVS | Zelio RXM relay with separate base-4C/O 6A 24VDC, as for example type: RXM4AB1BDPVS | kos | 14
g. | Sistemska svetilka LED, brez vtičnice, dolžina: 437 mm, vhodna napetost: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, kot na primer tip: 2500200, proizvod: Rittal | LED system luminaire, without socket, length: 437 mm, input voltage: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, e.g. type: 2500200, product: Rittal | kos | 1
h. | Povezovalni kabel, kot na primer tip: 2500400, proizvod: Rittal | Connection cable, e.g. type: 2500400, product: Rittal | kos | 1
i. | Vratno stikalo za LED sistemsko luč, kot na primer tip: 2500460, proizvod: Rittal | Door switch for LED system light, e.g. type: 2500460, product: Rittal | kos | 1
j. | Relejski modul, 24 V DC, 1 CO kontakt, 250 V AC, 6 A, kot na primer tip: TRS 24VDC 1CO AGSNO, proizvod: Weidmüller | Relay module, 24 V DC, 1 CO contact, 250 V AC, 6 A, e.g. type: TRS 24VDC 1CO AGSNO, product: Weidmüller | kos | 14
k. | Enonadstropna vijačna sponka, kot na primer tip: WDU 2.5, proizvod: Weidmüller | Single-deck screw clamp, e.g. type: type WDU 2.5, product: Weidmüller | kos | 8
l. | Enonadstropna vzmetna vrstna sponka, kot na primer tip: ZDU 2.5, proizvod: Weidmüller | Single-deck spring-type row clamp, e.g. type: ZDU 2.5, product: Weidmüller | kos | 49
4.4 | Polje NN_P1_TP_A1_3 | Field NN_P1_TP_A1_3 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 650x2100x600mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : Prisma P, proizvod: Schneider Electric | Cabinet dimensions 650x2100x600mm (WxHxD), made of powder-coated steel sheet in RAL9001, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : Prisma P, product : Schneider Electric | 1 | kpl
4.5 | Polje NN_P1_TP_A1_4 | Field NN_P1_TP_A1_4 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 800x2100x600mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : Prisma P, proizvod: Schneider Electric | Cabinet dimensions 800x2100x600mm (WxHxD), made of powder-coated steel sheet in RAL9001, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : Prisma P, product : Schneider Electric | kos | 1
b. | NS 1250N kompaktni odklopnik (MCCB), 3p, nazivni tok 1250A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, fiksna izvedba, kot na primer tip Compact NS, z vgrajeno opremo : - Mikroprocesorska zaščitna enota Micrologic 5.0 - 1kos - Pomožni kontakti stanja NOC - 3kos - Pomožni kontakti delovanja zaščite - 1kos - Motorni pogon - 230VAC - 1kos | NS 1250N compact circuit breaker (MCCB), 3p, rated current 1250A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, fixed version, as for example Compact NS type, with built-in accessories: - Micrologic 5.0 Microprocessor Protection Unit - 1 piece - NOC auxiliary contacts - 3pcs - Auxiliary contacts for protection operation - 1 piece - Motor drive - 230VAC - 1 piece | kos | 1
c. | NSX 630N kompaktni odklopnik (MCCB), 3p, nazivni tok 630A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, fiksne izvedbe, kot na primer tip ComPact NSX, z vgrajeno opremo: - Elektronska zaščitna enoto Micrologic 2.3 – 1kos - Pomožni kontakti stanja NOC (preklopni kontakt) – 4kos - Pomožni kontakt delovanje zaščite NOC - 1kos - Motorni pogon - 230VAC – 2kos - Zaščitni pokrovi za sponke, dolgi – 2 kosa | NSX 630N compact circuit breaker (MCCB), 3p, rated current 630A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, fixed version, such as ComPact NSX type, with built-in accessories: - Micrologic 2.3 Electronic Protection Unit - 1 piece - Auxiliary contacts NOC (switching contact) - 4 pieces - Auxiliary contact operation of NOC protection - 1 piece - Motor drive - 230VAC - 2 pieces - Protective caps for staples, long - 2 pcs | kos | 4
d. | Tipka za izklop, 1NO+1NC, črna, kot na primer tip: Harmony, XB4 XB4BA21+ZBE102 | Off button, 1NO+1NC, black, e.g. type Harmony, XB4 XB4BA21+ZBE102 | kos | 5
e. | Tipka za vklop, 1NO+1NC, zelena, kot na primer tip: Harmony, XB4 XB4BA31+ZBE102 | Power button, 1NO+1NC, green, e.g. type: Harmony, XB4 XB4BA31+ZBE102 | kos | 5
f. | Zelio RXM rele z ločenim podnožjem-4C/O 6A 24VDC, kot na primer tip: RXM4AB1BDPVS | Zelio RXM relay with separate base-4C/O 6A 24VDC, as for example type: RXM4AB1BDPVS | kos | 10
g. | Sistemska svetilka LED, brez vtičnice, dolžina: 437 mm, vhodna napetost: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, kot na primer tip: 2500200, proizvod: Rittal | LED system luminaire, without socket, length: 437 mm, input voltage: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, e.g. type: 2500200, product: Rittal | kos | 1
h. | Povezovalni kabel, kot na primer tip: 2500400, proizvod: Rittal | Connection cable, e.g. type: 2500400, product: Rittal | kos | 1
i. | Vratno stikalo za LED sistemsko luč, kot na primer tip: 2500460, proizvod: Rittal | Door switch for LED system light, e.g. type: 2500460, product: Rittal | kos | 1
j. | Relejski modul, 24 V DC, 1 CO kontakt, 250 V AC, 6 A, kot na primer tip: TRS 24VDC 1CO AGSNO, proizvod: Weidmüller | Relay module, 24 V DC, 1 CO contact, 250 V AC, 6 A, e.g. type: TRS 24VDC 1CO AGSNO, product: Weidmüller | kos | 10
k. | Enonadstropna vijačna sponka, kot na primer tip: WDU 2.5, proizvod: Weidmüller | Single-deck screw clamp, e.g. type: type WDU 2.5, product: Weidmüller | kos | 15
l. | Enonadstropna vzmetna vrstna sponka, kot na primer tip: ZDU 2.5, proizvod: Weidmüller | Single-deck spring-type row clamp, e.g. type: ZDU 2.5, product: Weidmüller | kos | 35
4.6 | Polje NN_P1_TP_A1_5 | Field NN_P1_TP_A1_5 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 800x2100x600mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : Prisma P, proizvod: Schneider Electric | Cabinet dimensions 800x2100x600mm (WxHxD), made of powder-coated steel sheet in RAL9001, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : Prisma P, product : Schneider Electric | kos | 1
b. | Tripolni zračni odklopnik (ACB) MASTERPACT MTZ2 25 H1, nazivni tok 2500A, izklopilni tok KS Icu=66 kA, servisni tok KS Ics=100% Icu 3P Splošni opis: Skaldnost s standardi: IEC/EN 60947, IEC60364-8-1, IEC61557-12, ISO 50001, Integriran merilnik v skladu z IEC61557-12. Merjenje električnih veličin toka, napetosti,moči, energije frekvence, harmonskega popačenja THD in napetostne asimetrije, Razred točnosti 1 za merive energije, v skladu z IEC60364-8-1, Odpornost na korozivno okolje Category 3C3 v skladu z IEC 60721-3-3, Stopnja odpornoti proti vibracijam 3M4 v skladu z IEC 60721-3-3, Nadgradnja funkcij zaščite in nadzora brez posegov v odklopnik (nadgradljivi programi), Komunikacijski vmesnik (Bluetooth/NFC) za povezavo z aplikacijo na mobilinih napravah, za spremljanje stanja, meritev, servisnih informaci odklopnika, Diagnostika odklopnika pri breznapetostnem stanju, Povezljivost z računalnikom preko USB vmesnika, Vzdržna temperatura elektronskih komponent v odklopniku 105 °C, kontaktne površine na notranjih povezavah pozlačene, Skladnost z REACH, RoHS in WEEE evropsko zakonodajo, Integriran prikazovalnik , prikaz U, I, Cos fi, E, f, P, obrabljenost kontaktov, števec št. preklopov, prikaz nastavitev zaščite, alarmi, zgodovina, servisne informacije. | Tripolar air circuit breaker (ACB) MASTERPACT MTZ2 25 H1, rated current 2500A, tripping current KS Icu=66 kA, service current KS Ics=100% Icu 3P General description: Skaldnost s standardi: IEC/EN 60947, IEC60364-8-1, IEC61557-12, ISO 50001, Integriran merilnik v skladu z IEC61557-12. Merjenje električnih veličin toka, napetosti,moči, energije frekvence, harmonskega popačenja THD in napetostne asimetrije, Razred točnosti 1 za merive energije, v skladu z IEC60364-8-1, Odpornost na korozivno okolje Category 3C3 v skladu z IEC 60721-3-3, Stopnja odpornoti proti vibracijam 3M4 v skladu z IEC 60721-3-3, Nadgradnja funkcij zaščite in nadzora brez posegov v odklopnik (nadgradljivi programi), Komunikacijski vmesnik (Bluetooth/NFC) za povezavo z aplikacijo na mobilinih napravah, za spremljanje stanja, meritev, servisnih informaci odklopnika, Diagnostika odklopnika pri breznapetostnem stanju, Povezljivost z računalnikom preko USB vmesnika, Vzdržna temperatura elektronskih komponent v odklopniku 105 °C, kontaktne površine na notranjih povezavah pozlačene, Skladnost z REACH, RoHS in WEEE evropsko zakonodajo, Integriran prikazovalnik , prikaz U, I, Cos fi, E, f, P, obrablje
| Vgrajena oprema: - Mikroprocesorska zaščitna enoto Micrologic 2.0 X, z integrirano meritvijo energije razreda točnosti 1 - 1kos - ULP komunikacijski izhod ter povezava na Ethernet komunikacijo (Modbus preko Etherneta), preko IFE modula - 1kos - Pomožni kontakti delovanje zaščite NOC - 1x - 1kos - Pomožni kontakti stanja vklopljen/izklopljen NOC - 4x -1kos - Motorni pogon - 230VAC - 1kos - Izklopna tuljava - 230VAC - 1kos - Vklopna tuljava - 230 VAC - 1kos - Izvedba - fiksna - 1kos | Built-in equipment: - Micrologic 2.0 X microprocessor-based protection unit, with integrated energy measurement accuracy class 1 - 1kos - ULP communication output and connection to Ethernet communication (Modbus over Ethernet), via IFE module - 1 piece - Auxiliary contacts for NOC protection operation - 1x - 1 piece - Auxiliary on/off status contacts NOC - 4x -1piece - Motor drive - 230VAC - 1 piece - Switch-off coil - 230VAC - 1 piece - Switching coil - 230 VAC - 1 piece - Version - fixed - 1 piece | kos | 1
c. | Mrežni analizator toka, napetosti in moči in harmonskega popačenja. Montaža na vrata sestava, Skladen z IEC 61557-12, Točnost meritev energije 0,5%, Mertiev individualnih harmonikov do 31 reda, 35 Alarmov, 2x digitalni izhod, 2x digitalni vhod, Modbus TCP/IP komunikacijski vmesnik, kot na primer tip: PM5320 | Network analyser for current, voltage and power and harmonic distortion. Assembly port mounting, IEC 61557-12 compliant, Energy measurement accuracy 0.5%, Individual harmonic measurement up to 31 orders of magnitude, 35 Alarms, 2x digital output, 2x digital input, Modbus TCP/IP communication interface, such as type: PM5320 | kos | 1
d. | Varovalčno stikalo ISFT400, z varovalkami 400A, DIN NH2, 3 p + Nadzor varovalk FuPacT ISFT400 - 1 NO + 1 NC, kot na primer tip: 480806+LV480825 | Fuse switch ISFT400, with 400A fuses, DIN NH2, 3 p + FuPacT fuse monitoring ISFT400 - 1 NO + 1 NC, as for example type: 480806+LV480825 | kos | 1
e. | Voltmetar 0-500 V, razred točnosti 1.5, 72x72 mm za montažo na vrata, stopenj zaščite: IP52, v skladu s standardi IEC 60051-1, IEC 61010-1 i IEC 61000-4, kot na primer tip: VLT | Voltmeter 0-500 V, accuracy class 1.5, 72x72 mm for door mounting, protection class IP52, according to IEC 60051-1, IEC 61010-1 and IEC 61000-4 standards, e.g. type VLT | kos | 1
f. | Voltmeterska preklopka - 3L in 3L-N - 45° - 12 A - za Ø 22 mm, kot na primer tip: K1F027MCH | Voltmeter switch - 3L and 3L-N - 45° - 12 A - for Ø 22 mm, e.g. type: K1F027MCH | kos | 1
g. | Inštalacijski odklopnik, 50kA, iC60N, 3P, 0.5A, C + Pomožni kontakt iOF/SD+OF, iC60, kot na primer tip: A9F74370+A9A26929 | Circuit breaker, 50kA, iC60N, 3P, 0.5A, C + Auxiliary contact iOF/SD+OF, iC60, e.g. type: A9F74370+A9A26929 | kos | 1
h. | Inštalacijski odklopnik, 36kA, NG125H, 16A, 1P, C + Pomožni kontakti - 2 OC - 6 A - 220..240 V - za NG125, kot na primer tip: 18706+19071 | Circuit breaker, 36kA, NG125H, 16A, 1P, C + Auxiliary contacts - 2 OC - 6 A - 220..240 V - for NG125, as for example type: 18706+19071 | kos | 1
i. | Inštalacijski odklopnik, 36kA, NG125H, 10A, 1P, C + Pomožni kontakti - 2 OC - 6 A - 220..240 V - za NG125, kot na primer tip: 18705+19071 | Circuit breaker, 36kA, NG125H, 10A, 1P, C + Auxiliary contacts - 2 OC - 6 A - 220..240 V - for NG125, as for example type: 18705+19071 | kos | 2
j. | Inštalacijski odklopnik, 100kA, iC60L, 3P, 4A, C+Pomožni kontakt iOF/SD+OF, iC60, kot na primer tip: A9F94304+A9A26929 | Circuit breaker, 100kA, iC60L, 3P, 4A, C+Auxiliary contact iOF/SD+OF, iC60, e.g. type: A9F94304+A9A26929 | kos | 2
k. | Odvodnik prenapetosti kot na primer tipa 1, 4p, Up: 1.5kV, In=25kA, pom. kontakt indikacije stanja, kot na primer tip; PRD1 Master (16360) | Surge arrester as for example type 1, 4p, Up: 1.5kV, In=25kA, status indication contact as for example type; PRD1 Master (16360) | kos | 3
l. | Tipka za izklop, 1NO+1NC, črna, kot na primer tip: Harmony, XB4 XB4BA21+ZBE102 | Off button, 1NO+1NC, black, e.g. type Harmony, XB4 XB4BA21+ZBE102 | kos | 1
m. | Tipka za vklop, 1NO+1NC, zelena, kot na primer tip: Harmony, XB4 XB4BA31+ZBE102 | Power button, 1NO+1NC, green, e.g. type: Harmony, XB4 XB4BA31+ZBE102 | kos | 1
n. | Tipka za preizkus svetilk, 1NO, modra, kot na primer tip: Harmony, XB4 XB4BA61 | Lamp test button, 1NO, blue, e.g. type: Harmony, XB4 XB4BA61 | kos | 1
o. | Signalna svetilka na vratih LED, 24VDC, zelena, kot na primer tip: XB4BVB3 | LED door signal lamp, 24VDC, green, e.g. type: XB4BVB3 | kos | 1
p. | Signalna svetilka na vratih LED, 24VDC, bela, kot na primer tip: XB4BVB1 | LED door signal lamp, 24VDC, white, e.g. type: XB4BVB1 | kos | 1
q. | Signalna svetilka na vratih LED, 24VDC, rdeča, kot na primer tip: XB4BVB4 | LED door signal lamp, 24VDC, red, e.g. type: XB4BVB4 | kos | 1
r. | CAM IZBIRNO STIKALO, HARMONY K, 4 POLNO, kot na primer tip: K10H014UCH | CAM SELECTABLE SWITCH, HARMONY K, 4 FULL, as for example type: K10H014UCH | kos | 1
s. | Večnamenski krmilni rele RM17-TU - območje 183..528 V AC, kot na primer tip: RM17TU00 | Multi-purpose control relay RM17-TU - 183..528 V AC range, e.g. type: RM17TU00 | kos | 1
t. | Zelio RXM rele z ločenim podnožjem-4C/O 6A 24VDC, kot na primer tip: RXM4AB1BDPVS | Zelio RXM relay with separate base-4C/O 6A 24VDC, as for example type: RXM4AB1BDPVS | kos | 6
u. | Tokovni merilni transformator, 2500/5A, Ue=720 V, sf <= 5 (za Ip od 40 do 4000 A), IP20, IEC 61869-2, kot na primer tip: MET SE CT 2500/5A | Current measuring transformer, 2500/5A, Ue=720 V, sf <= 5 (for Ip from 40 to 4000 A), IP20, IEC 61869-2, as for example type: MET SE CT 2500/5A | kos | 4
v. | Sistemska svetilka LED, brez vtičnice, dolžina: 437 mm, vhodna napetost: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, kot na primer tip: 2500200, proizvod: Rittal | LED system luminaire, without socket, length: 437 mm, input voltage: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, e.g. type: 2500200, product: Rittal | kos | 1
w. | Povezovalni kabel, kot na primer tip: 2500400, proizvod: Rittal | Connection cable, e.g. type: 2500400, product: Rittal | kos | 1
x. | Vtičnica za DIN letev, kot na primer tip: 2506120, proizvod: Rittal | DIN rail socket, e.g. type: 2506120, product: Rittal | kos | 1
y. | Vratno stikalo za LED sistemsko luč, kot na primer tip: 2500460, proizvod: Rittal | Door switch for LED system light, e.g. type: 2500460, product: Rittal | kos | 1
z. | Relejski modul, 24 V DC, 1 CO kontakt, 250 V AC, 6 A, kot na primer tip: TRS 24VDC 1CO AGSNO, proizvod: Weidmüller | Relay module, 24 V DC, 1 CO contact, 250 V AC, 6 A, e.g. type: TRS 24VDC 1CO AGSNO, product: Weidmüller | kos | 2
a1. | Enonadstropna vijačna sponka, kot na primer tip: WDU 2.5, proizvod: Weidmüller | Single-deck screw clamp, e.g. type: type WDU 2.5, product: Weidmüller | kos | 31
b1. | Enonadstropna vzmetna vrstna sponka, kot na primer tip: ZDU 2.5, proizvod: Weidmüller | Single-deck spring-type row clamp, e.g. type: ZDU 2.5, product: Weidmüller | kos | 22
c1. | Merilna sponka z vzdolžno ločitvijo in dvema vzporednima mostičema, kot na primer tip: WTL 6/1/STB, proizvod: Weidmüller | Measuring clamp with longitudinal separation and two parallel bridges, e.g. type: WTL 6/1/STB, product: Weidmüller | kos | 8
4.7 | Polje NN_P1_TP_A1_A2_1 | Field NN_P1_TP_A1_A2_1 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 650x2100x600mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : Prisma P, proizvod: Schneider Electric | Cabinet dimensions 650x2100x600mm (WxHxD), made of powder-coated steel sheet in RAL9001, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : Prisma P, product : Schneider Electric | kos | 1
b. | Tripolni zračni odklopnik (ACB) MASTERPACT MTZ2 25 H1, nazivni tok 2500A, izklopilni tok KS Icu=66 kA, servisni tok KS Ics=100% Icu 3P Splošni opis: Skladnost s standardi: IEC/EN 60947, IEC60364-8-1, IEC61557-12, ISO 50001, Integriran merilnik v skladu z IEC61557-12. Merjenje električnih veličin toka, napetosti,moči, energije frekvence, harmonskega popačenja THD in napetostne asimetrije, Razred točnosti 1 za merive energije, v skladu z IEC60364-8-1, Odpornost na korozivno okolje Category 3C3 v skladu z IEC 60721-3-3, Stopnja odpornoti proti vibracijam 3M4 v skladu z IEC 60721-3-3, Nadgradnja funkcij zaščite in nadzora brez posegov v odklopnik (nadgradljivi programi), Komunikacijski vmesnik (Bluetooth/NFC) za povezavo z aplikacijo na mobilinih napravah, za spremljanje stanja, meritev, servisnih informaci odklopnika, Diagnostika odklopnika pri breznapetostnem stanju, Povezljivost z računalnikom preko USB vmesnika, Vzdržna temperatura elektronskih komponent v odklopniku 105 °C, kontaktne površine na notranjih povezavah pozlačene, Skladnost z REACH, RoHS in WEEE evropsko zakonodajo, Integriran prikazovalnik , prikaz U, I, Cos fi, E, f, P, obrabljenost kontaktov, števec št. preklopov, prikaz nastavitev zaščite, alarmi, zgodovina, servisne informacije. | Tripolar air circuit breaker (ACB) MASTERPACT MTZ2 25 H1, rated current 2500A, tripping current KS Icu=66 kA, service current KS Ics=100% Icu 3P General description: Skladnost s standardi: IEC/EN 60947, IEC60364-8-1, IEC61557-12, ISO 50001, Integriran merilnik v skladu z IEC61557-12. Merjenje električnih veličin toka, napetosti,moči, energije frekvence, harmonskega popačenja THD in napetostne asimetrije, Razred točnosti 1 za merive energije, v skladu z IEC60364-8-1, Odpornost na korozivno okolje Category 3C3 v skladu z IEC 60721-3-3, Stopnja odpornoti proti vibracijam 3M4 v skladu z IEC 60721-3-3, Nadgradnja funkcij zaščite in nadzora brez posegov v odklopnik (nadgradljivi programi), Komunikacijski vmesnik (Bluetooth/NFC) za povezavo z aplikacijo na mobilinih napravah, za spremljanje stanja, meritev, servisnih informaci odklopnika, Diagnostika odklopnika pri breznapetostnem stanju, Povezljivost z računalnikom preko USB vmesnika, Vzdržna temperatura elektronskih komponent v odklopniku 105 °C, kontaktne površine na notranjih povezavah pozlačene, Skladnost z REACH, RoHS in WEEE evropsko zakonodajo, Integriran prikazovalnik , prikaz U, I, Cos fi, E, f, P, obrablje
| Vgrajena oprema: - Mikroprocesorska zaščitna enoto Micrologic 2.0 X, z integrirano meritvijo energije razreda točnosti 1 - 1kos - ULP komunikacijski izhod ter povezava na Ethernet komunikacijo (Modbus preko Etherneta), preko IFE modula - 1kos - Pomožni kontakti delovanje zaščite NOC - 1x - 1kos - Pomožni kontakti stanja vklopljen/izklopljen NOC - 4x -1kos - Motorni pogon - 230VAC - 1kos - Izklopna tuljava - 230VAC - 1kos - Vklopna tuljava - 230 VAC - 1kos - Izvedba - fiksna - 1kos | Built-in equipment: - Micrologic 2.0 X microprocessor-based protection unit, with integrated energy measurement accuracy class 1 - 1kos - ULP communication output and connection to Ethernet communication (Modbus over Ethernet), via IFE module - 1 piece - Auxiliary contacts NOC protection operation - 1x - 1 piece - Auxiliary on/off status contacts NOC - 4x -1piece - Motor drive - 230VAC - 1 piece - Switch-off coil - 230VAC - 1 piece - Switching coil - 230 VAC - 1 piece - Version - fixed - 1 piece | kos | 1
c. | Inštalacijski odklopnik, 50kA, iC60N, 1P, 2A, C + Pomožni kontakt iOF/SD+OF, iC60, kot na primer tip: A9F74102+A9A26929 | Circuit breaker, 50kA, iC60N, 1P, 2A, C + Auxiliary contact iOF/SD+OF, iC60, e.g. type: A9F74102+A9A26929 | kos | 10
d. | Inštalacijski odklopnik, 50kA, iC60N, 1P, 0.5A, C + Pomožni kontakt iOF/SD+OF, iC60, kot na primer tip: A9F74170+A9A26929 | Circuit breaker, 50kA, iC60N, 1P, 0.5A, C + Auxiliary contact iOF/SD+OF, iC60, e.g. type: A9F74170+A9A26929 | kos | 2
e. | Inštalacijski odklopnik, 50kA, iC60N, 1P, 13A, C + Pomožni kontakt iOF/SD+OF, iC60, kot na primer tip: A9F04113+A9A26929 | Circuit breaker, 50kA, iC60N, 1P, 13A, C + Auxiliary contact iOF/SD+OF, iC60, e.g. type: A9F04113+A9A26929 | kos | 2
f. | Inštalacijski odklopnik, 50kA, iC60N, 2P, 4A, C + Pomožni kontakt iOF/SD+OF, iC60, kot na primer tip: A9F74204+A9A26929 | Circuit breaker, 50kA, iC60N, 2P, 4A, C + Auxiliary contact iOF/SD+OF, iC60, e.g. type: A9F74204+A9A26929 | kos | 4
g. | Inštalacijski odklopnik, 36kA, NG125H, 10A, 1P, C + Pomožni kontakti - 2 OC - 6 A - 220..240 V - za NG125, kot na primer tip: 18705+19071 | Circuit breaker, 36kA, NG125H, 10A, 1P, C + Auxiliary contacts - 2 OC - 6 A - 220..240 V - for NG125, as for example type: 18705+19071 | kos | 1
h. | Tipka za izklop, 1NO+1NC, črna, kot na primer tip: Harmony, XB4 XB4BA21+ZBE102 | Power button, 1NO+1NC, black, e.g. type Harmony, XB4 XB4BA21+ZBE102 | kos | 1
i. | Tipka za vklop, 1NO+1NC, zelena, kot na primer tip: Harmony, XB4 XB4BA31+ZBE102 | Power button, 1NO+1NC, green, e.g. type: Harmony, XB4 XB4BA31+ZBE102 | kos | 1
j. | Tipka za preizkus svetilk, 1NO, modra, kot na primer tip: Harmony, XB4 XB4BA61 | Lamp test button, 1NO, blue, e.g. type: Harmony, XB4 XB4BA61 | kos | 1
k. | Signalna svetilka na vratih LED, 24VDC, zelena, kot na primer tip: XB4BVB3 | LED door signal lamp, 24VDC, green, e.g. type: XB4BVB3 | kos | 1
l. | Signalna svetilka na vratih LED, 24VDC, bela, kot na primer tip: XB4BVB1 | LED door signal lamp, 24VDC, white, e.g. type: XB4BVB1 | kos | 1
m. | Signalna svetilka na vratih LED, 24VDC, rdeča, kot na primer tip: XB4BVB4 | LED door signal lamp, 24VDC, red, e.g. type: XB4BVB4 | kos | 1
n. | CAM IZBIRNO STIKALO, HARMONY K, 4 POLNO, kot na primer tip: K10H014UCH | CAM SELECTABLE SWITCH, HARMONY K, 4 FULL, as for example type: K10H014UCH | kos | 1
o. | Ločilno stikalo iSW, 3P, 20A+Pomožni kontakt iOF, iSW, kot na primer tip: A9S60320+A9A15096 | ISW isolating switch, 3P, 20A+Auxiliary contact iOF, iSW, e.g. type: A9S60320+A9A15096 | kos | 2
p. | Zelio RXM rele z ločenim podnožjem-4C/O 6A 24VDC, kot na primer tip: RXM4AB1BDPVS | Zelio RXM relay with separate base-4C/O 6A 24VDC, as for example type: RXM4AB1BDPVS | kos | 5
q. | Univerzalni napajalnik, 1 ali 2-fazi, 100..500 V, 24 V DC, 5 A, kot na primer tip: ABL8RPS24050 | Universal power supply, 1- or 2-phase, 100..500 V, 24 V DC, 5 A, e.g. type: ABL8RPS24050 | kos | 2
r. | Sistemska svetilka LED, brez vtičnice, dolžina: 437 mm, vhodna napetost: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, kot na primer tip: 2500200, proizvod: Rittal | LED system luminaire, without socket, length: 437 mm, input voltage: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, e.g. type: 2500200, product: Rittal | kos | 1
s. | Povezovalni kabel, kot na primer tip: 2500400, proizvod: Rittal | Connection cable, e.g. type: 2500400, product: Rittal | kos | 1
t. | Vtičnica za DIN letev, kot na primer tip: 2506120, proizvod: Rittal | DIN rail socket, e.g. type: 2506120, product: Rittal | kos | 1
u. | Vratno stikalo za LED sistemsko luč, kot na primer tip: 2500460, proizvod: Rittal | Door switch for LED system light, e.g. type: 2500460, product: Rittal | kos | 1
v. | Relejski modul, 24 V DC, 1 CO kontakt, 250 V AC, 6 A, kot na primer tip: TRS 24VDC 1CO AGSNO, proizvod: Weidmüller | Relay module, 24 V DC, 1 CO contact, 250 V AC, 6 A, e.g. type: TRS 24VDC 1CO AGSNO, product: Weidmüller | kos | 2
w. | Enonadstropna vijačna sponka, kot na primer tip: WDU 2.5, proizvod: Weidmüller | Single-deck screw clamp, e.g. type: type WDU 2.5, product: Weidmüller | kos | 8
x. | Enonadstropna vijačna sponka, kot na primer tip: WDU 4, proizvod: Weidmüller | Single-deck screw clamp, e.g. type: type WDU 4, product: Weidmüller | kos | 58
y. | Enonadstropna vzmetna vrstna sponka, kot na primer tip: ZDU 2.5, proizvod: Weidmüller | Single-deck spring-type row clamp, e.g. type: ZDU 2.5, product: Weidmüller | kos | 22
4.8 | Polje NN_P1_TP_A2_1 | Field NN_P1_TP_A2_1 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 800x2100x600mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : Prisma P, proizvod: Schneider Electric | Cabinet dimensions 800x2100x600mm (WxHxD), made of powder-coated RAL9001 steel sheet, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : Prisma P, product : Schneider Electric | kos | 1
b. | Tripolni zračni odklopnik (ACB) MASTERPACT MTZ2 25 H1, nazivni tok 2500A, izklopilni tok KS Icu=66 kA, servisni tok KS Ics=100% Icu 3P Splošni opis: Skaldnost s standardi: IEC/EN 60947, IEC60364-8-1, IEC61557-12, ISO 50001, Integriran merilnik v skladu z IEC61557-12. Merjenje električnih veličin toka, napetosti,moči, energije frekvence, harmonskega popačenja THD in napetostne asimetrije, Razred točnosti 1 za merive energije, v skladu z IEC60364-8-1, Odpornost na korozivno okolje Category 3C3 v skladu z IEC 60721-3-3, Stopnja odpornoti proti vibracijam 3M4 v skladu z IEC 60721-3-3, Nadgradnja funkcij zaščite in nadzora brez posegov v odklopnik (nadgradljivi programi), Komunikacijski vmesnik (Bluetooth/NFC) za povezavo z aplikacijo na mobilinih napravah, za spremljanje stanja, meritev, servisnih informaci odklopnika, Diagnostika odklopnika pri breznapetostnem stanju, Povezljivost z računalnikom preko USB vmesnika, Vzdržna temperatura elektronskih komponent v odklopniku 105 °C, kontaktne površine na notranjih povezavah pozlačene, Skladnost z REACH, RoHS in WEEE evropsko zakonodajo, Integriran prikazovalnik , prikaz U, I, Cos fi, E, f, P, obrabljenost kontaktov, števec št. preklopov, prikaz nastavitev zaščite, alarmi, zgodovina, servisne informacije. | Tripolar air circuit breaker (ACB) MASTERPACT MTZ2 25 H1, rated current 2500A, tripping current KS Icu=66 kA, service current KS Ics=100% Icu 3P General description: Skaldnost s standardi: IEC/EN 60947, IEC60364-8-1, IEC61557-12, ISO 50001, Integriran merilnik v skladu z IEC61557-12. Merjenje električnih veličin toka, napetosti,moči, energije frekvence, harmonskega popačenja THD in napetostne asimetrije, Razred točnosti 1 za merive energije, v skladu z IEC60364-8-1, Odpornost na korozivno okolje Category 3C3 v skladu z IEC 60721-3-3, Stopnja odpornoti proti vibracijam 3M4 v skladu z IEC 60721-3-3, Nadgradnja funkcij zaščite in nadzora brez posegov v odklopnik (nadgradljivi programi), Komunikacijski vmesnik (Bluetooth/NFC) za povezavo z aplikacijo na mobilinih napravah, za spremljanje stanja, meritev, servisnih informaci odklopnika, Diagnostika odklopnika pri breznapetostnem stanju, Povezljivost z računalnikom preko USB vmesnika, Vzdržna temperatura elektronskih komponent v odklopniku 105 °C, kontaktne površine na notranjih povezavah pozlačene, Skladnost z REACH, RoHS in WEEE evropsko zakonodajo, Integriran prikazovalnik , prikaz U, I, Cos fi, E, f, P, obrablje
| Vgrajena oprema: - Mikroprocesorska zaščitna enoto Micrologic 2.0 X, z integrirano meritvijo energije razreda točnosti 1 - 1kos - ULP komunikacijski izhod ter povezava na Ethernet komunikacijo (Modbus preko Etherneta), preko IFE modula - 1kos - Pomožni kontakti delovanje zaščite NOC - 1x - 1kos - Pomožni kontakti stanja vklopljen/izklopljen NOC - 4x -1kos - Motorni pogon - 230VAC - 1kos - Izklopna tuljava - 230VAC - 1kos - Vklopna tuljava - 230 VAC - 1kos - Izvedba - fiksna - 1kos | Built-in equipment: - Micrologic 2.0 X microprocessor-based protection unit, with integrated energy measurement accuracy class 1 - 1kos - ULP communication output and connection to Ethernet communication (Modbus over Ethernet), via IFE module - 1 piece - Auxiliary contacts NOC protection operation - 1x - 1 piece - Auxiliary on/off status contacts NOC - 4x -1piece - Motor drive - 230VAC - 1 piece - Switch-off coil - 230VAC - 1 piece - Switching coil - 230 VAC - 1 piece - Version - fixed - 1 piece | kos | 1
c. | Mrežni analizator toka, napetosti in moči in harmonskega popačenja. Montaža na vrata sestava, Skladen z IEC 61557-12, Točnost meritev energije 0,5%, Mertiev individualnih harmonikov do 31 reda, 35 Alarmov, 2x digitalni izhod, 2x digitalni vhod, Modbus TCP/IP komunikacijski vmesnik, kot na primer tip: PM5320 | Network analyser for current, voltage and power and harmonic distortion. Assembly port mounting, IEC 61557-12 compliant, Energy measurement accuracy 0.5%, Individual harmonic measurement up to 31 orders of magnitude, 35 Alarms, 2x digital output, 2x digital input, Modbus TCP/IP communication interface, such as type: PM5320 | kos | 1
d. | Varovalčno stikalo ISFT400, z varovalkami 400A, DIN NH2, 3 p + Nadzor varovalk FuPacT ISFT400 - 1 NO + 1 NC, kot na primer tip: 480806+LV480825 | Fuse switch ISFT400, with 400A fuses, DIN NH2, 3 p + FuPacT fuse monitoring ISFT400 - 1 NO + 1 NC, as for example type: 480806+LV480825 | kos | 1
e. | Voltmetar 0-500 V, razred točnosti 1.5, 72x72 mm za montažo na vrata, stopenj zaščite: IP52, v skladu s standardi IEC 60051-1, IEC 61010-1 i IEC 61000-4, kot na primer tip: VLT | Voltmeter 0-500 V, accuracy class 1.5, 72x72 mm for door mounting, protection class IP52, according to IEC 60051-1, IEC 61010-1 and IEC 61000-4 standards, e.g. type VLT | kos | 1
f. | Voltmeterska preklopka - 3L in 3L-N - 45° - 12 A - za Ø 22 mm, kot na primer tip: K1F027MCH | Voltmeter switch - 3L and 3L-N - 45° - 12 A - for Ø 22 mm, e.g. type: K1F027MCH | kos | 1
g. | Inštalacijski odklopnik, 50kA, iC60N, 3P, 0.5A, C + Pomožni kontakt iOF/SD+OF, iC60, kot na primer tip: A9F74370+A9A26929 | Circuit breaker, 50kA, iC60N, 3P, 0.5A, C + Auxiliary contact iOF/SD+OF, iC60, e.g. type: A9F74370+A9A26929 | kos | 1
h. | Inštalacijski odklopnik, 36kA, NG125H, 16A, 1P, C + Pomožni kontakti - 2 OC - 6 A - 220..240 V - za NG125, kot na primer tip: 18706+19071 | Circuit breaker, 36kA, NG125H, 16A, 1P, C + Auxiliary contacts - 2 OC - 6 A - 220..240 V - for NG125, as for example type: 18706+19071 | kos | 1
i. | Inštalacijski odklopnik, 36kA, NG125H, 10A, 1P, C + Pomožni kontakti - 2 OC - 6 A - 220..240 V - za NG125, kot na primer tip: 18705+19071 | Circuit breaker, 36kA, NG125H, 10A, 1P, C + Auxiliary contacts - 2 OC - 6 A - 220..240 V - for NG125, as for example type: 18705+19071 | kos | 1
j. | Inštalacijski odklopnik, 100kA, iC60L, 3P, 4A, C+Pomožni kontakt iOF/SD+OF, iC60, kot na primer tip: A9F94304+A9A26929 | Circuit breaker, 100kA, iC60L, 3P, 4A, C+Auxiliary contact iOF/SD+OF, iC60, e.g. type: A9F94304+A9A26929 | kos | 2
k. | Odvodnik prenapetosti kot na primer tipa 1, 4p, Up: 1.5kV, In=25kA, pom. kontakt indikacije stanja, kot na primer tip; PRD1 Master (16360) | Surge arrester as for example type 1, 4p, Up: 1.5kV, In=25kA, status indication contact as for example type; PRD1 Master (16360) | kos | 3
l. | Tipka za izklop, 1NO+1NC, črna, kot na primer tip: Harmony, XB4 XB4BA21+ZBE102 | Off button, 1NO+1NC, black, e.g. type Harmony, XB4 XB4BA21+ZBE102 | kos | 1
m. | Tipka za vklop, 1NO+1NC, zelena, kot na primer tip: Harmony, XB4 XB4BA31+ZBE102 | Power button, 1NO+1NC, green, e.g. type: Harmony, XB4 XB4BA31+ZBE102 | kos | 1
n. | Tipka za preizkus svetilk, 1NO, modra, kot na primer tip: Harmony, XB4 XB4BA61 | Lamp test button, 1NO, blue, e.g. type: Harmony, XB4 XB4BA61 | kos | 1
o. | Signalna svetilka na vratih LED, 24VDC, zelena, kot na primer tip: XB4BVB3 | LED door signal lamp, 24VDC, green, e.g. type: XB4BVB3 | kos | 1
p. | Signalna svetilka na vratih LED, 24VDC, bela, kot na primer tip: XB4BVB1 | LED door signal lamp, 24VDC, white, e.g. type: XB4BVB1 | kos | 1
q. | Signalna svetilka na vratih LED, 24VDC, rdeča, kot na primer tip: XB4BVB4 | LED door signal lamp, 24VDC, red, e.g. type: XB4BVB4 | kos | 1
r. | CAM IZBIRNO STIKALO, HARMONY K, 4 POLNO, kot na primer tip: K10H014UCH | CAM SELECTABLE SWITCH, HARMONY K, 4 FULL, as for example type: K10H014UCH | kos | 1
s. | Večnamenski krmilni rele RM17-TU - območje 183..528 V AC, kot na primer tip: RM17TU00 | Multi-purpose control relay RM17-TU - 183..528 V AC range, e.g. type: RM17TU00 | kos | 1
t. | Zelio RXM rele z ločenim podnožjem-4C/O 6A 24VDC, kot na primer tip: RXM4AB1BDPVS | Zelio RXM relay with separate base-4C/O 6A 24VDC, as for example type: RXM4AB1BDPVS | kos | 7
u. | Tokovni merilni transformator, 2500/5A, Ue=720 V, sf <= 5 (za Ip od 40 do 4000 A), IP20, IEC 61869-2, kot na primer tip: MET SE CT 2500/5A | Current measuring transformer, 2500/5A, Ue=720 V, sf <= 5 (for Ip from 40 to 4000 A), IP20, IEC 61869-2, as for example type: MET SE CT 2500/5A | kos | 4
v. | Sistemska svetilka LED, brez vtičnice, dolžina: 437 mm, vhodna napetost: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, kot na primer tip: 2500200, proizvod: Rittal | LED system luminaire, without socket, length: 437 mm, input voltage: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, e.g. type: 2500200, product: Rittal | kos | 1
w. | Povezovalni kabel, kot na primer tip: 2500400, proizvod: Rittal | Connection cable, e.g. type: 2500400, product: Rittal | kos | 1
x. | Vtičnica za DIN letev, kot na primer tip: 2506120, proizvod: Rittal | DIN rail socket, e.g. type: 2506120, product: Rittal | kos | 1
y. | Vratno stikalo za LED sistemsko luč, kot na primer tip: 2500460, proizvod: Rittal | Door switch for LED system light, e.g. type: 2500460, product: Rittal | kos | 1
z. | Relejski modul, 24 V DC, 1 CO kontakt, 250 V AC, 6 A, kot na primer tip: TRS 24VDC 1CO AGSNO, proizvod: Weidmüller | Relay module, 24 V DC, 1 CO contact, 250 V AC, 6 A, e.g. type: TRS 24VDC 1CO AGSNO, product: Weidmüller | kos | 2
a1. | Enonadstropna vijačna sponka, kot na primer tip: WDU 2.5, proizvod: Weidmüller | Single-deck screw clamp, e.g. type: type WDU 2.5, product: Weidmüller | kos | 35
b1. | Enonadstropna vzmetna vrstna sponka, kot na primer tip: ZDU 2.5, proizvod: Weidmüller | Single-deck spring-type row clamp, e.g. type: ZDU 2.5, product: Weidmüller | kos | 24
c1. | Merilna sponka z vzdolžno ločitvijo in dvema vzporednima mostičema, kot na primer tip: WTL 6/1/STB, proizvod: Weidmüller | Measuring clamp with longitudinal separation and two parallel bridges, e.g. type: WTL 6/1/STB, product: Weidmüller | kos | 8
4.9 | Polje NN_P1_TP_A2_2 | Field NN_P1_TP_A2_2 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 650x2100x600mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : Prisma P, proizvod: Schneider Electric | Cabinet dimensions 650x2100x600mm (WxHxD), made of powder-coated RAL9001 steel sheet, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : Prisma P, product : Schneider Electric | kos | 1
b. | NSX 630N kompaktni odklopnik (MCCB), 3p, nazivni tok 630A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, fiksne izvedbe, kot na primer tip ComPact NSX, z vgrajeno opremo: - Elektronska zaščitna enoto Micrologic 2.3 – 1kos - Pomožni kontakti stanja NOC (preklopni kontakt) – 4kos - Pomožni kontakt delovanje zaščite NOC - 4kos - Motorni pogon - 230VAC – 1kos - Zaščitni pokrovi za sponke, dolgi – 2 kosa | NSX 630N compact circuit breaker (MCCB), 3p, rated current 630A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, fixed version, such as the ComPact NSX type, with built-in accessories: - Micrologic 2.3 Electronic Protection Unit - 1 piece - Auxiliary contacts NOC (switching contact) - 4 pieces - Auxiliary contact operation of NOC protection - 4 pieces - Motor drive - 230VAC - 1 piece - Protective caps for staples, long - 2 pcs | kos | 7
c. | Tipka za izklop, 1NO+1NC, črna, kot na primer tip: Harmony, XB4 XB4BA21+ZBE102 | Off button, 1NO+1NC, black, e.g. type Harmony, XB4 XB4BA21+ZBE102 | kos | 7
d. | Tipka za vklop, 1NO+1NC, zelena, kot na primer tip: Harmony, XB4 XB4BA31+ZBE102 | Power button, 1NO+1NC, green, e.g. type: Harmony, XB4 XB4BA31+ZBE102 | kos | 7
e. | Zelio RXM rele z ločenim podnožjem-4C/O 6A 24VDC, kot na primer tip: RXM4AB1BDPVS | Zelio RXM relay with separate base-4C/O 6A 24VDC, as for example type: RXM4AB1BDPVS | kos | 14
f. | Sistemska svetilka LED, brez vtičnice, dolžina: 437 mm, vhodna napetost: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, kot na primer tip: 2500200, proizvod: Rittal | LED system luminaire, without socket, length: 437 mm, input voltage: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, e.g. type: 2500200, product: Rittal | kos | 1
g. | Povezovalni kabel, kot na primer tip: 2500400, proizvod: Rittal | Connection cable, e.g. type: 2500400, product: Rittal | kos | 1
h. | Vratno stikalo za LED sistemsko luč, kot na primer tip: 2500460, proizvod: Rittal | Door switch for LED system light, e.g. type: 2500460, product: Rittal | kos | 1
i. | Relejski modul, 24 V DC, 1 CO kontakt, 250 V AC, 6 A, kot na primer tip: TRS 24VDC 1CO AGSNO, proizvod: Weidmüller | Relay module, 24 V DC, 1 CO contact, 250 V AC, 6 A, e.g. type: TRS 24VDC 1CO AGSNO, product: Weidmüller | kos | 14
j. | Enonadstropna vijačna sponka, kot na primer tip: WDU 2.5, proizvod: Weidmüller | Single-deck screw clamp, e.g. type: type WDU 2.5, product: Weidmüller | kos | 8
k. | Enonadstropna vzmetna vrstna sponka, kot na primer tip: ZDU 2.5, proizvod: Weidmüller | Single-deck spring-type row clamp, e.g. type: ZDU 2.5, product: Weidmüller | kos | 49
4.10 | Polje NN_P1_TP_A2_3 | Field NN_P1_TP_A2_3 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 650x2100x600mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : Prisma P, proizvod: Schneider Electric | Cabinet dimensions 650x2100x600mm (WxHxD), made of powder-coated RAL9001 steel sheet, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : Prisma P, product : Schneider Electric | kpl | 1
4.11 | Polje NN_P1_TP_A2_4 | Field NN_P1_TP_A2_4 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 800x2100x600mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : Prisma P, proizvod: Schneider Electric | Cabinet dimensions 800x2100x600mm (WxHxD), made of powder-coated steel sheet in RAL9001, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : Prisma P, product : Schneider Electric | kpl | 1
b. | NSX 630N kompaktni odklopnik (MCCB), 3p, nazivni tok 630A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, fiksne izvedbe, kot na primer tip ComPact NSX, z vgrajeno opremo: - Elektronska zaščitna enoto Micrologic 2.3 – 1kos - Pomožni kontakti stanja NOC (preklopni kontakt) – 4kos - Pomožni kontakt delovanje zaščite NOC - 2kos - Motorni pogon - 230VAC - 1kos - Zaščitni pokrovi za sponke, dolgi – 2 kosa | NSX 630N compact circuit breaker (MCCB), 3p, rated current 630A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, fixed version, such as ComPact NSX type, with built-in accessories: - Micrologic 2.3 Electronic Protection Unit - 1 piece - Auxiliary contacts NOC (switching contact) - 4 pieces - Auxiliary contact operation of NOC protection - 2 pieces - Motor drive - 230VAC - 1 piece - Protective caps for staples, long - 2 pcs | kos | 4
c. | NSX 400N kompaktni odklopnik (MCCB), 3p, nazivni tok 400A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, z vgrajeno opremo: - Elektronska zaščitna enoto Micrologic 2.3 – 1kos - Pomožni kontakti stanja NOC (preklopni kontakt) – 4kos - Pomožni kontakt delovanje zaščite NOC - 4kos - Motorni pogon - 230VAC - 1kos - Zaščitni pokrovi za sponke, dolgi – 2 kosa | NSX 400N compact circuit breaker (MCCB), 3p, rated current 400A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, with built-in accessories: - Micrologic 2.3 Electronic Protection Unit - 1 piece - Auxiliary contacts NOC (switching contact) - 4 pieces - Auxiliary contact operation of NOC protection - 4 pieces - Motor drive - 230VAC - 1 piece - Protective caps for staples, long - 2 pcs | kos | 2
d. | NSX 250N kompaktni odklopnik (MCCB), 3p, nazivni tok 250A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, z vgrajeno opremo: - Elektronska zaščitna enoto Micrologic 2.2 – 1kos - Pomožni kontakti stanja NOC (preklopni kontakt) – 4kos - Pomožni kontakt delovanje zaščite NOC - 4kos - Motorni pogon - 230VAC - 1kos - Zaščitni pokrovi za sponke, dolgi – 2 kosa | NSX 250N compact circuit breaker (MCCB), 3p, rated current 250A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, with built-in accessories: - Micrologic 2.2 Electronic Protection Unit - 1 piece - Auxiliary contacts NOC (switching contact) - 4 pieces - Auxiliary contact operation of NOC protection - 4 pieces - Motor drive - 230VAC - 1 piece - Protective caps for staples, long - 2 pcs | kos | 2
e. | Tipka za izklop, 1NO+1NC, črna, kot na primer tip: Harmony, XB4 XB4BA21+ZBE102 | Off button, 1NO+1NC, black, e.g. type Harmony, XB4 XB4BA21+ZBE102 | kos | 8
f. | Tipka za vklop, 1NO+1NC, zelena, kot na primer tip: Harmony, XB4 XB4BA31+ZBE102 | Power button, 1NO+1NC, green, e.g. type: Harmony, XB4 XB4BA31+ZBE102 | kos | 8
g. | Zelio RXM rele z ločenim podnožjem-4C/O 6A 24VDC, kot na primer tip: RXM4AB1BDPVS | Zelio RXM relay with separate base-4C/O 6A 24VDC, as for example type: RXM4AB1BDPVS | kos | 16
h. | Sistemska svetilka LED, brez vtičnice, dolžina: 437 mm, vhodna napetost: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, kot na primer tip: 2500200, proizvod: Rittal | LED system luminaire, without socket, length: 437 mm, input voltage: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, e.g. type: 2500200, product: Rittal | kos | 1
i. | Povezovalni kabel, kot na primer tip: 2500400, proizvod: Rittal | Connection cable, e.g. type: 2500400, product: Rittal | kos | 1
j. | Vratno stikalo za LED sistemsko luč, kot na primer tip: 2500460, proizvod: Rittal | Door switch for LED system light, e.g. type: 2500460, product: Rittal | kos | 1
k. | Relejski modul, 24 V DC, 1 CO kontakt, 250 V AC, 6 A, kot na primer tip: TRS 24VDC 1CO AGSNO, proizvod: Weidmüller | Relay module, 24 V DC, 1 CO contact, 250 V AC, 6 A, e.g. type: TRS 24VDC 1CO AGSNO, product: Weidmüller | kos | 16
l. | Enonadstropna vijačna sponka, kot na primer tip: WDU 2.5, proizvod: Weidmüller | Single-deck screw clamp, e.g. type: type WDU 2.5, product: Weidmüller | kos | 15
m. | Enonadstropna vzmetna vrstna sponka, kot na primer tip: ZDU 2.5, proizvod: Weidmüller | Single-deck spring-type row clamp, e.g. type: ZDU 2.5, product: Weidmüller | kos | 56
4.12 | Polje NN_P1_TP_A2_5 | Field NN_P1_TP_A2_5 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 400x2100x600mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : Prisma P, proizvod: Schneider Electric | Cabinet dimensions 400x2100x600mm (WxHxD), made of powder-coated RAL9001 steel sheet, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : Prisma P, product : Schneider Electric | kpl | 1
b. | NS 1250N kompaktni odklopnik (MCCB), 3p, nazivni tok 1250A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, fiksna izvedba, kot na primer tip Compact NS, z vgrajeno opremo : - Mikroprocesorska zaščitna enota Micrologic 5.0- 1kos - Pomožni kontakti stanja NOC - 3kos - Pomožni kontakti delovanja zaščite - 1kos - Motorni pogon - 230VAC - 1kos | NS 1250N compact circuit breaker (MCCB), 3p, rated current 1250A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, fixed version, as for example Compact NS type, with built-in accessories: - Micrologic 5.0 microprocessor protection unit - 1 piece - NOC auxiliary contacts - 3pcs - Auxiliary contacts for protection operation - 1 piece - Motor drive - 230VAC - 1 piece | kos | 1
c. | Tipka za izklop, 1NO+1NC, črna, kot na primer tip: Harmony, XB4 XB4BA21+ZBE102 | Off button, 1NO+1NC, black, e.g. type Harmony, XB4 XB4BA21+ZBE102 | kos | 1
d. | Tipka za vklop, 1NO+1NC, zelena, kot na primer tip: Harmony, XB4 XB4BA31+ZBE102 | Power button, 1NO+1NC, green, e.g. type: Harmony, XB4 XB4BA31+ZBE102 | kos | 1
e. | Zelio RXM rele z ločenim podnožjem-4C/O 6A 24VDC, kot na primer tip: RXM4AB1BDPVS | Zelio RXM relay with separate base-4C/O 6A 24VDC, as for example type: RXM4AB1BDPVS | kos | 2
f. | Sistemska svetilka LED, brez vtičnice, dolžina: 437 mm, vhodna napetost: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, kot na primer tip: 2500200, proizvod: Rittal | LED system luminaire, without socket, length: 437 mm, input voltage: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, e.g. type: 2500200, product: Rittal | kos | 1
g. | Povezovalni kabel, kot na primer tip: 2500400, proizvod: Rittal | Connection cable, e.g. type: 2500400, product: Rittal | kos | 1
h. | Vratno stikalo za LED sistemsko luč, kot na primer tip: 2500460, proizvod: Rittal | Door switch for LED system light, e.g. type: 2500460, product: Rittal | kos | 1
i. | Relejski modul, 24 V DC, 1 CO kontakt, 250 V AC, 6 A, kot na primer tip: TRS 24VDC 1CO AGSNO, proizvod: Weidmüller | Relay module, 24 V DC, 1 CO contact, 250 V AC, 6 A, e.g. type: TRS 24VDC 1CO AGSNO, product: Weidmüller | kos | 2
j. | Enonadstropna vijačna sponka, kot na primer tip: WDU 2.5, proizvod: Weidmüller | Single-deck screw clamp, e.g. type: type WDU 2.5, product: Weidmüller | kos | 5
k. | Enonadstropna vijačna sponka, kot na primer tip: WDU 4, proizvod: Weidmüller | Single-deck screw clamp, e.g. type: type WDU 4, product: Weidmüller | kos | 1
l. | Enonadstropna vzmetna vrstna sponka, kot na primer tip: ZDU 2.5, proizvod: Weidmüller | Single-deck spring-type row clamp, e.g. type: ZDU 2.5, product: Weidmüller | kos | 6
4.13 | 0,4 kV razdelilnik NN_P1_TP_RG1 | 0.4 kV switchgear NN_P1_TP_RG1
| NN sestav je prostostoječe, modularne izvedbe izdelani iz dekapirane jeklene pločevine in profilov, obdelana z anti-korozijsko elektroforezo in končno barvo - poliestrsko/epoksidnim prašnim nanosom, barva RAL - kot na primer tipska barva proizvajalca. Vsak element v NN sestavu mora imeti oznako iz tripolne sheme. NN sestav mora ustrezati zahtevam standardov SIST EN 61439-1 in 2. Ponudnik mora priložiti naslednje izjave in poročila: - izjava o skladnosti s SIST EN 61439-1 in 2 - testna poročila v skladu s SIST EN 61439-1 in 2 - testna poročila o komunikacijskem sistemu (communication report) - enopolne sheme Kot na primer tip: PrismaSeT P, proizvod: Schneider Electric | The LV assembly shall be of a free-standing, modular design, made of decapitated steel sheet and profiles, treated with anti-corrosion electrophoresis and finished with a polyester/epoxy powder coating, RAL colour - such as the manufacturer's standard colour. Each element in the LV assembly shall be marked with a marking from the three-pole scheme. The LV assembly shall comply with the requirements of SIST EN 61439-1 and 2. The tenderer must attach the following declarations and reports: - declaration of conformity to SIST EN 61439-1 and 2 - test reports in accordance with SIST EN 61439-1 and 2 - communication system test reports (communication report) - unipolar schemes Such as type: PrismaSeT P, product: Schneider Electric
| Dokumentacija je na voljo v digitalni obliki v oblaku, dostopna preko QR kode na NN sestavu | The documentation is available in digital form in the cloud, accessible via QR code on the NN assembly
| Ponudnik mora dokazati selektivnost med odklopniki v sestavu s pomočjo tabel ali rezultatov izračuna programske opreme | The tenderer shall demonstrate the selectivity between the circuit breakers in the assembly by means of tables or the results of a software calculation
| Stopnja zaščite: IP31 | Protection rating: IP31
| Število polj (z opremo): | Number of fields (with equipment):
| Okvirna dimenzija (ŠxVxG) 1600 x 2000 x 400mm + podnožje višine: 50mm | Dimensions (WxHxD) 1600 x 2000 x 400mm + base height: 50mm
| Okvirna teža 1 polja: 600kg | Approximate weight of 1 box: 600kg
| Barva RAL: 9001 | RAL colour: 9001
| Prezračevanje: naravno | Ventilation: natural
| Forma pregrajenosti v skladu s standardom SIST EN 61439: 2A | Form of partitioning according to SIST EN 61439:2A
| Priklopi: dovodi - zgoraj s kabli, odvodi: zgoraj s kabli | Connections: inlets - top with cables, outlets: top with cables
| Naznačena izolacijska napetost (Ui): 1000 V | Rated insulation voltage (Ui): 1000 V
| Naznačena obratovalna napetost (Ue): 415 / 690 V AC | Rated operating voltage (Ue): 415 / 690 V AC
| Naznačena frekvenca (fn): 50 Hz | Designated frequency (fn): 50 Hz
| Pomožna napetost za napajanje komunikacijske in druge pomožne opreme: 24 VDC | Auxiliary voltage for power supply of communication and other auxiliary equipment: 24 VDC
| Naznačeni tok glavnih zbiralk: 630 A trajno, materijal Al | Rated current of main busbars: 630 A continuous, material Al
| Naznačeni kratkotrajni zdržni tok (Icw - kA rms/1s): 50 kA | Rated short-time withstand current (Icw - kA rms/1s): 50 kA
| Sistem ozemljitve TN-S | TN-S earthing system
| Presek N-vodnika enak faznemu | N-conductor cross section equal to phase
| Opombe: - Razdelilnik mora biti opremljen po seznamu opreme v dokumentu št. JULFS--7E9102, ožičen in preizkušen. | Notes: - The distributor shall be equipped according to the equipment list in document No JULFS--7E9102, wired and tested.
4.14 | Polje NN_P1_TP_RG1_1 | Field NN_P1_TP_RG1_1 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 400x2050x400mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : PrismaSeT P, proizvod: Schneider Electric | Cabinet dimensions 400x2050x400mm (WxHxD), made of powder-coated RAL9001 steel sheet, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : PrismaSeT P, product : Schneider Electric | kpl | 1
b. | NSX 630 NA kompaktno tripolno stikalo, nazivni tok 630A, kot na primer tip NSXNA, z vgrajeno opremo: - Zaščitni pokrovi za sponke, dolgi - 1kos - Pomožni kontakt 1 OF - 1kos | NSX 630 NA compact three-pole switch, rated current 630A, as for example type NSXNA, with built-in accessories: - Protective covers for staples, long - 1 piece - Auxiliary contact 1 OF - 1 piece | kos | 1
c. | EasyLogic PM2230, Merilnik moči in energije, kot na primer tip: PM2230 | EasyLogic PM2230, Power and energy meter, as for example type: PM2230 | kos | 1
d. | Odvodnik prenapetosti kot na primer tipa 2, 3P + N, Up=1.5kV, In (8/20)=20kA, Imax(8/20)=65kA, pom. kontakt indikacije stanja, kot na primer tip: kot na primer tip iPRD65r | Surge arrester as e.g. type 2, 3P+N, Up=1.5kV, In (8/20)=20kA, Imax(8/20)=65kA, auxiliary contact status indication as e.g. type: as e.g. type iPRD65r | kos | 1
e. | Varovalčno stikalo ISFT160, 160A, DIN NH00, 3 p, z varovalkami 3x80A + Nadzor varovalk FuPacT ISFT160 - 1 NO + 1 NC, kot na primer tip: 480803+LV480810 | Fuse switch ISFT160, 160A, DIN NH00, 3 p, with 3x80A fuses + Fuse monitoring FuPacT ISFT160 - 1 NO + 1 NC, as for example type: 480803+LV480810 | kos | 1
f. | Inštalacijski odklopnik, 50kA, iC60N, 1P, 0.5A, C + Pomožni kontakt iOF/SD+OF, iC60, kot na primer tip: A9F74170+A9A26929 | Circuit breaker, 50kA, iC60N, 1P, 0.5A, C + Auxiliary contact iOF/SD+OF, iC60, e.g. type: A9F74170+A9A26929 | kos | 1
g. | Inštalacijski odklopnik, 50kA, iC60N, 3P, 0.5A, C + Pomožni kontakt iOF/SD+OF, iC60, kot na primer tip: A9F74370+A9A26929 | Circuit breaker, 50kA, iC60N, 3P, 0.5A, C + Auxiliary contact iOF/SD+OF, iC60, e.g. type: A9F74370+A9A26929 | kos | 1
h. | Inštalacijski odklopnik, 36kA, NG125H, 10A, 1P, C + Pomožni kontakti - 2 OC - 6 A - 220..240 V - za NG125, kot na primer tip: 18705+19071 | Circuit breaker, 36kA, NG125H, 10A, 1P, C + Auxiliary contacts - 2 OC - 6 A - 220..240 V - for NG125, as for example type: 18705+19071 | kos | 2
i. | Tokovni merilni transformator, 600/5A, Ue=720 V, sf <= 5 (za Ip od 40 do 4000 A), IP20, IEC 61869-2, kot na primer tip: MET SE CT 600/5A | Current measuring transformer, 600/5A, Ue=720 V, sf <= 5 (for Ip from 40 to 4000 A), IP20, IEC 61869-2, as for example type: MET SE CT 600/5A | kos | 3
j. | Sistemska svetilka LED, brez vtičnice, dolžina: 437 mm, vhodna napetost: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, kot na primer tip: 2500200, proizvod: Rittal | LED system luminaire, without socket, length: 437 mm, input voltage: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, e.g. type: 2500200, product: Rittal | kos | 1
k. | Povezovalni kabel, kot na primer tip: 2500400, proizvod: Rittal | Connection cable, e.g. type: 2500400, product: Rittal | kos | 1
l. | Vtičnica za DIN letev, kot na primer tip: 2506120, proizvod: Rittal | DIN rail socket, e.g. type: 2506120, product: Rittal | kos | 1
m. | Vratno stikalo za LED sistemsko luč, kot na primer tip: 2500460, proizvod: Rittal | Door switch for LED system light, e.g. type: 2500460, product: Rittal | kos | 1
n. | Enonadstropna vzmetna vrstna sponka, kot na primer tip: ZDU 2.5, proizvod: Weidmüller | Single-deck spring-type row clamp, e.g. type: ZDU 2.5, product: Weidmüller | kos | 35
o. | Merilna sponka z vzdolžno ločitvijo in dvema vzporednima mostičema, kot na primer tip: WTL 6/1/STB, proizvod: Weidmüller | Measuring clamp with longitudinal separation and two parallel bridges, e.g. type: WTL 6/1/STB, product: Weidmüller | kos | 6
4.15 | Polje NN_P1_TP_RG1_2 | Field NN_P1_TP_RG1_2 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 800x2050x400mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : PrismaSeT P, proizvod: Schneider Electric | Cabinet dimensions 800x2050x400mm (WxHxD), made of powder-coated RAL9001 steel sheet, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : PrismaSeT P, product : Schneider Electric | kpl | 1
b. | NSX 250N kompaktni tripolni odklopnik (MCCB),nazivni tok 250A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, z vgrajeno opremo: - Mikroprocesorska zaščitna enoto Micrologic 2.2, brez meritev ALI - 1kos - Pomožni kontakti (1xNO/NC, 1xSDE) - 2kosa - Zaščitni pokrovi za sponke, dolgi - 1kos - izvedba - fiksna | NSX 250N compact three-pole circuit breaker (MCCB), rated current 250A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, with built-in accessories: - Micrologic 2.2 microprocessor protection unit, without ALI measurements - 1 piece - Auxiliary contacts (1xNO/NC, 1xSDE) - 2 pieces - Protective covers for staples, long - 1 piece - design - fixed | kos | 2
c. | NSX 160N kompaktni tripolni odklopnik (MCCB),nazivni tok 160A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, z vgrajeno opremo: - Mikroprocesorska zaščitna enoto Micrologic 2.2, brez meritev ALI - 1kos - Pomožni kontakti (1xNO/NC, 1xSDE) - 2kosa - Zaščitni pokrovi za sponke, dolgi - 1kos - izvedba - fiksna | NSX 160N compact three-pole circuit breaker (MCCB), rated current 160A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, with built-in accessories: - Micrologic 2.2 microprocessor protection unit, without ALI measurements - 1 piece - Auxiliary contacts (1xNO/NC, 1xSDE) - 2 pieces - Protective covers for staples, long - 1 piece - design - fixed | kos | 6
d. | NSX 100N kompaktni tripolni odklopnik (MCCB),nazivni tok 100A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, z vgrajeno opremo: - Mikroprocesorska zaščitna enoto Micrologic 2.2, brez meritev ALI - 1kos - Pomožni kontakti (1xNO/NC, 1xSDE) - 2kosa - Zaščitni pokrovi za sponke, dolgi - 1kos - izvedba - fiksna | NSX 100N compact three-pole circuit breaker (MCCB), rated current 100A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, with built-in accessories: - Micrologic 2.2 microprocessor protection unit, without ALI measurements - 1 piece - Auxiliary contacts (1xNO/NC, 1xSDE) - 2 pieces - Protective covers for staples, long - 1 piece - design - fixed | kos | 2
e. | Sistemska svetilka LED, brez vtičnice, dolžina: 437 mm, vhodna napetost: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, kot na primer tip: 2500200, proizvod: Rittal | LED system luminaire, without socket, length: 437 mm, input voltage: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, e.g. type: 2500200, product: Rittal | kos | 1
f. | Povezovalni kabel, kot na primer tip: 2500400, proizvod: Rittal | Connection cable, e.g. type: 2500400, product: Rittal | kos | 1
g. | Vratno stikalo za LED sistemsko luč, kot na primer tip: 2500460, proizvod: Rittal | Door switch for LED system light, e.g. type: 2500460, product: Rittal | kos | 1
4.16 | Polje NN_P1_TP_RG1_3 | Field NN_P1_TP_RG1_3 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 400x2050x400mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : PrismaSeT P, proizvod: Schneider Electric | Cabinet dimensions 400x2050x400mm (WxHxD), made of powder-coated RAL9001 steel sheet, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : PrismaSeT P, product : Schneider Electric | kpl | 1
4.17 | 0,4 kV razdelilnik NN_P1_TP_RG2 | 0.4 kV switchgear NN_P1_TP_RG2
| NN sestav je prostostoječe, modularne izvedbe izdelani iz dekapirane jeklene pločevine in profilov, obdelana z anti-korozijsko elektroforezo in končno barvo - poliestrsko/epoksidnim prašnim nanosom, barva RAL - kot na primer tipska barva proizvajalca. Vsak element v NN sestavu mora imeti oznako iz tripolne sheme. NN sestav mora ustrezati zahtevam standardov SIST EN 61439-1 in 2. Ponudnik mora priložiti naslednje izjave in poročila: - izjava o skladnosti s SIST EN 61439-1 in 2 - testna poročila v skladu s SIST EN 61439-1 in 2 - testna poročila o komunikacijskem sistemu (communication report) - enopolne sheme Kot na primer tip: PrismaSeT P, proizvod: Schneider Electric | The LV assembly shall be of a free-standing, modular design, made of decapitated steel sheet and profiles, treated with anti-corrosion electrophoresis and finished with a polyester/epoxy powder coating, RAL colour - such as the manufacturer's standard colour. Each element in the LV assembly shall be marked with a marking from the three-pole scheme. The LV assembly shall comply with the requirements of SIST EN 61439-1 and 2. The tenderer must attach the following declarations and reports: - declaration of conformity to SIST EN 61439-1 and 2 - test reports in accordance with SIST EN 61439-1 and 2 - communication system test reports (communication report) - unipolar schemes Such as type: type: PrismaSeT P, product: Schneider Electric
| Dokumentacija je na voljo v digitalni obliki v oblaku, dostopna preko QR kode na NN sestavu | The documentation is available in digital form in the cloud, accessible via QR code on the NN assembly
| Ponudnik mora dokazati selektivnost med odklopniki v sestavu s pomočjo tabel ali rezultatov izračuna programske opreme | The tenderer shall demonstrate the selectivity between the circuit-breakers in the assembly by means of tables or the results of a software calculation
| Stopnja zaščite: IP31 | Protection rating: IP31
| Število polj (z opremo): | Number of fields (with equipment):
| Okvirna dimenzija (ŠxVxG) 1600 x 2000 x 400mm + podnožje višine: 50mm | Dimensions (WxHxD) 1600 x 2000 x 400mm + base height: 50mm
| Okvirna teža 1 polja: 600kg | Approximate weight of 1 box: 600kg
| Barva RAL: 9001 | RAL colour: 9001
| Prezračevanje: naravno | Ventilation: natural
| Forma pregrajenosti v skladu s standardom SIST EN 61439: 2A | Form of partitioning in accordance with SIST EN 61439:2A
| Priklopi: dovodi - zgoraj s kabli, odvodi: zgoraj s kabli | Connections: inlets - top with cables, outlets: top with cables
| Naznačena izolacijska napetost (Ui): 1000 V | Rated insulation voltage (Ui): 1000 V
| Naznačena obratovalna napetost (Ue): 415 / 690 V AC | Rated operating voltage (Ue): 415 / 690 V AC
| Naznačena frekvenca (fn): 50 Hz | Designated frequency (fn): 50 Hz
| Pomožna napetost za napajanje komunikacijske in druge pomožne opreme: 24 VDC | Auxiliary voltage for power supply of communication and other auxiliary equipment: 24 VDC
| Naznačeni tok glavnih zbiralk: 630 A trajno, materijal Al | Rated current of main busbars: 630 A continuous, material Al
| Naznačeni kratkotrajni zdržni tok (Icw - kA rms/1s): 50 kA | Rated short-time withstand current (Icw - kA rms/1s): 50 kA
| Sistem ozemljitve TN-S | TN-S earthing system
| Presek N-vodnika enak faznemu | N-conductor cross section equal to phase
| Opombe: - Razdelilnik mora biti opremljen po seznamu opreme v dokumentu št. JULFS--7E9103, ožičen in preizkušen. | Notes: - The distributor shall be equipped according to the equipment list in document No JULFS--7E9103, wired and tested.
4.18 | Polje NN_P1_TP_RG2_1 | Field NN_P1_TP_RG2_1 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 400x2050x400mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : PrismaSeT P, proizvod: Schneider Electric | Cabinet dimensions 400x2050x400mm (WxHxD), made of powder-coated RAL9001 steel sheet, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : PrismaSeT P, product : Schneider Electric | kpl | 1
b. | NS 1250 NA kompaktno tripolno stikalo, nazivni tok 1250A, kot na primer tip NS NA, z vgrajeno opremo: - Zaščitni pokrovi za sponke, dolgi - 1kos - Pomožni kontakt 1 OF - 1kos | NS 1250 NA compact three-pole switch, rated current 1250A, as for example type NS NA, with built-in accessories: - Protective covers for staples, long - 1 piece - Auxiliary contact 1 OF - 1 piece | kos | 1
c. | EasyLogic PM2230, Merilnik moči in energije, kot na primer tip: PM2230 | EasyLogic PM2230, Power and energy meter, as for example type: PM2230 | kos | 1
d. | Odvodnik prenapetosti kot na primer tipa 2, 3P + N, Up=1.5kV, In (8/20)=20kA, Imax(8/20)=65kA, pom. kontakt indikacije stanja, kot na primer tip: kot na primer tip iPRD65r | Surge arrester as e.g. type 2, 3P+N, Up=1.5kV, In (8/20)=20kA, Imax(8/20)=65kA, auxiliary contact status indication as e.g. type: as e.g. type iPRD65r | kos | 1
e. | Varovalčno stikalo ISFT160, 160A, DIN NH00, 3 p, z varovalkami 3x80A + Nadzor varovalk FuPacT ISFT160 - 1 NO + 1 NC, kot na primer tip: 480803+LV480810 | Fuse switch ISFT160, 160A, DIN NH00, 3 p, with 3x80A fuses + Fuse monitoring FuPacT ISFT160 - 1 NO + 1 NC, as for example type: 480803+LV480810 | kos | 1
f. | Inštalacijski odklopnik, 50kA, iC60N, 1P, 0.5A, C + Pomožni kontakt iOF/SD+OF, iC60, kot na primer tip: A9F74170+A9A26929 | Circuit breaker, 50kA, iC60N, 1P, 0.5A, C + Auxiliary contact iOF/SD+OF, iC60, e.g. type: A9F74170+A9A26929 | kos | 1
g. | Inštalacijski odklopnik, 50kA, iC60N, 3P, 0.5A, C + Pomožni kontakt iOF/SD+OF, iC60, kot na primer tip: A9F74370+A9A26929 | Circuit breaker, 50kA, iC60N, 3P, 0.5A, C + Auxiliary contact iOF/SD+OF, iC60, e.g. type: A9F74370+A9A26929 | kos | 1
h. | Inštalacijski odklopnik, 36kA, NG125H, 10A, 1P, C + Pomožni kontakti - 2 OC - 6 A - 220..240 V - za NG125, kot na primer tip: 18705+19071 | Circuit breaker, 36kA, NG125H, 10A, 1P, C + Auxiliary contacts - 2 OC - 6 A - 220..240 V - for NG125, as for example type: 18705+19071 | kos | 2
i. | Tokovni merilni transformator, 1250/5A, Ue=720 V, sf <= 5 (za Ip od 40 do 4000 A), IP20, IEC 61869-2, kot na primer tip: MET SE CT 1250/5A | Current measuring transformer, 1250/5A, Ue=720 V, sf <= 5 (for Ip from 40 to 4000 A), IP20, IEC 61869-2, as for example type: MET SE CT 1250/5A | kos | 3
j. | Sistemska svetilka LED, brez vtičnice, dolžina: 437 mm, vhodna napetost: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, kot na primer tip: 2500200, proizvod: Rittal | LED system luminaire, without socket, length: 437 mm, input voltage: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, e.g. type: 2500200, product: Rittal | kos | 1
k. | Povezovalni kabel, kot na primer tip: 2500400, proizvod: Rittal | Connection cable, e.g. type: 2500400, product: Rittal | kos | 1
l. | Vtičnica za DIN letev, kot na primer tip: 2506120, proizvod: Rittal | DIN rail socket, e.g. type: 2506120, product: Rittal | kos | 1
m. | Vratno stikalo za LED sistemsko luč, kot na primer tip: 2500460, proizvod: Rittal | Door switch for LED system light, e.g. type: 2500460, product: Rittal | kos | 1
n. | Enonadstropna vzmetna vrstna sponka, kot na primer tip: ZDU 2.5, proizvod: Weidmüller | Single-deck spring-type row clamp, e.g. type: ZDU 2.5, product: Weidmüller | kos | 35
o. | Merilna sponka z vzdolžno ločitvijo in dvema vzporednima mostičema, kot na primer tip: WTL 6/1/STB, proizvod: Weidmüller | Measuring clamp with longitudinal separation and two parallel bridges, e.g. type: WTL 6/1/STB, product: Weidmüller | kos | 6
4.19 | Polje NN_P1_TP_RG2_2 | Field NN_P1_TP_RG2_2 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 800x2050x400mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : PrismaSeT P, proizvod: Schneider Electric | Cabinet dimensions 800x2050x400mm (WxHxD), made of powder-coated RAL9001 steel sheet, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : PrismaSeT P, product : Schneider Electric | kpl | 1
b. | NSX 630N kompaktni tripolni odklopnik (MCCB),nazivni tok 630A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, z vgrajeno opremo: - 'Mikroprocesorska zaščitna enoto Micrologic 2.3, brez meritev ALI - 1kos - Pomožni kontakti (1xNO/NC, 1xSDE) - 2kosa - Zaščitni pokrovi za sponke, dolgi - 1kos - izvedba - fiksna | NSX 630N compact three-pole circuit breaker (MCCB), rated current 630A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, with built-in accessories: - 'Micrologic 2.3 microprocessor protection unit, without ALI measurements - 1 piece - Auxiliary contacts (1xNO/NC, 1xSDE) - 2 pieces - Protective covers for staples, long - 1 piece - design - fixed | kos | 1
c. | NSX 400N kompaktni tripolni odklopnik (MCCB),nazivni tok 400A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, z vgrajeno opremo: - 'Mikroprocesorska zaščitna enoto Micrologic 2.3, brez meritev ALI - 1kos - Pomožni kontakti (1xNO/NC, 1xSDE) - 2kosa - Zaščitni pokrovi za sponke, dolgi - 1kos - izvedba - fiksna | NSX 400N compact three-pole circuit breaker (MCCB), rated current 400A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, with built-in accessories: - 'Micrologic 2.3 microprocessor protection unit, without ALI measurements - 1 piece - Auxiliary contacts (1xNO/NC, 1xSDE) - 2 pieces - Protective covers for staples, long - 1 piece - design - fixed | kos | 2
d. | NSX 250N kompaktni tripolni odklopnik (MCCB),nazivni tok 250A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, z vgrajeno opremo: - 'Mikroprocesorska zaščitna enoto Micrologic 2.2, brez meritev ALI - 1kos - Pomožni kontakti (1xNO/NC, 1xSDE) - 2kosa - Zaščitni pokrovi za sponke, dolgi - 1kos - izvedba - fiksna | NSX 250N compact three-pole circuit breaker (MCCB), rated current 250A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, with built-in accessories: - 'Micrologic 2.2 microprocessor protection unit, without ALI measurements - 1 piece - Auxiliary contacts (1xNO/NC, 1xSDE) - 2 pieces - Protective covers for staples, long - 1 piece - design - fixed | kos | 5
e. | NSX 160N kompaktni tripolni odklopnik (MCCB),nazivni tok 160A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, z vgrajeno opremo: - 'Mikroprocesorska zaščitna enoto Micrologic 2.2, brez meritev ALI - 1kos - Pomožni kontakti (1xNO/NC, 1xSDE) - 2kosa - Zaščitni pokrovi za sponke, dolgi - 1kos - izvedba - fiksna | NSX 160N compact three-pole circuit breaker (MCCB), rated current 160A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, with built-in accessories: - 'Micrologic 2.2 microprocessor protection unit, without ALI measurements - 1 piece - Auxiliary contacts (1xNO/NC, 1xSDE) - 2 pieces - Protective covers for staples, long - 1 piece - design - fixed | kos | 2
f. | Sistemska svetilka LED, brez vtičnice, dolžina: 437 mm, vhodna napetost: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, kot na primer tip: 2500200, proizvod: Rittal | LED system luminaire, without socket, length: 437 mm, input voltage: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, e.g. type: 2500200, product: Rittal | kos | 1
g. | Povezovalni kabel, kot na primer tip: 2500400, proizvod: Rittal | Connection cable, e.g. type: 2500400, product: Rittal | kos | 1
h. | Vratno stikalo za LED sistemsko luč, kot na primer tip: 2500460, proizvod: Rittal | Door switch for LED system light, e.g. type: 2500460, product: Rittal | kos | 1
4.20 | Polje NN_P1_TP_RG2_3 | Field NN_P1_TP_RG2_3 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 400x2050x400mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : PrismaSeT P, proizvod: Schneider Electric | Cabinet dimensions 400x2050x400mm (WxHxD), made of powder-coated RAL9001 steel sheet, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : PrismaSeT P, product : Schneider Electric | kpl | 1
4.21 | 0,4 kV razdelilnik NN_P1_TP_RG3 | 0.4 kV switchgear NN_P1_TP_RG3
| NN sestav je prostostoječe, modularne izvedbe izdelani iz dekapirane jeklene pločevine in profilov, obdelana z anti-korozijsko elektroforezo in končno barvo - poliestrsko/epoksidnim prašnim nanosom, barva RAL - kot na primer tipska barva proizvajalca. Vsak element v NN sestavu mora imeti oznako iz tripolne sheme. NN sestav mora ustrezati zahtevam standardov SIST EN 61439-1 in 2. Ponudnik mora priložiti naslednje izjave in poročila: - izjava o skladnosti s SIST EN 61439-1 in 2 - testna poročila v skladu s SIST EN 61439-1 in 2 - testna poročila o komunikacijskem sistemu (communication report) - enopolne sheme Kot na primer tip: PrismaSeT P, proizvod: Schneider Electric | The LV assembly shall be of a free-standing, modular design, made of decapitated steel sheet and profiles, treated with anti-corrosion electrophoresis and finished with a polyester/epoxy powder coating, RAL colour - such as the manufacturer's standard colour. Each element in the LV assembly shall be marked with a marking from the three-pole scheme. The LV assembly shall comply with the requirements of SIST EN 61439-1 and 2. The tenderer must attach the following declarations and reports: - declaration of conformity to SIST EN 61439-1 and 2 - test reports in accordance with SIST EN 61439-1 and 2 - communication system test reports (communication report) - unipolar schemes Such as type: type: PrismaSeT P, product: Schneider Electric
| Dokumentacija je na voljo v digitalni obliki v oblaku, dostopna preko QR kode na NN sestavu | The documentation is available in digital form in the cloud, accessible via QR code on the NN assembly
| Ponudnik mora dokazati selektivnost med odklopniki v sestavu s pomočjo tabel ali rezultatov izračuna programske opreme | The tenderer shall demonstrate the selectivity between the circuit-breakers in the assembly by means of tables or the results of a software calculation
| Stopnja zaščite: IP31 | Protection rating: IP31
| Število polj (z opremo): | Number of fields (with equipment):
| Okvirna dimenzija (ŠxVxG) 1600 x 2000 x 400mm + podnožje višine: 50mm | Dimensions (WxHxD) 1600 x 2000 x 400mm + base height: 50mm
| Okvirna teža 1 polja: 600kg | Approximate weight of 1 box: 600kg
| Barva RAL: 9001 | RAL colour: 9001
| Prezračevanje: naravno | Ventilation: natural
| Forma pregrajenosti v skladu s standardom SIST EN 61439: 2A | Form of partitioning in accordance with SIST EN 61439:2A
| Priklopi: dovodi - zgoraj s kabli, odvodi: zgoraj s kabli | Connections: inlets - top with cables, outlets: top with cables
| Naznačena izolacijska napetost (Ui): 1000 V | Rated insulation voltage (Ui): 1000 V
| Naznačena obratovalna napetost (Ue): 415 / 690 V AC | Rated operating voltage (Ue): 415 / 690 V AC
| Naznačena frekvenca (fn): 50 Hz | Designated frequency (fn): 50 Hz
| Pomožna napetost za napajanje komunikacijske in druge pomožne opreme: 24 VDC | Auxiliary voltage for power supply of communication and other auxiliary equipment: 24 VDC
| Naznačeni tok glavnih zbiralk: 630 A trajno, materijal Al | Rated current of main busbars: 630 A continuous, material Al
| Naznačeni kratkotrajni zdržni tok (Icw - kA rms/1s): 50 kA | Rated short-time withstand current (Icw - kA rms/1s): 50 kA
| Sistem ozemljitve TN-S | TN-S earthing system
| Presek N-vodnika enak faznemu | N-conductor cross section equal to phase
| Opombe: - Razdelilnik mora biti opremljen po seznamu opreme v dokumentu št. JULFS--7E9104, ožičen in preizkušen. | Notes: - The distributor shall be equipped according to the equipment list in document No JULFS--7E9104, wired and tested.
4.22 | Polje NN_P1_TP_RG3_1 | Field NN_P1_TP_RG3_1 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 400x2050x400mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : PrismaSeT P, proizvod: Schneider Electric | Cabinet dimensions 400x2050x400mm (WxHxD), made of powder-coated RAL9001 steel sheet, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : PrismaSeT P, product : Schneider Electric | kpl | 1
b. | NSX 630 NA kompaktno tripolno stikalo, nazivni tok 630A, kot na primer tip NSXNA, z vgrajeno opremo: - Zaščitni pokrovi za sponke, dolgi - 1kos - Pomožni kontakt 1 OF - 1kos | NSX 630 NA compact three-pole switch, rated current 630A, as for example type NSXNA, with built-in accessories: - Protective covers for staples, long - 1 piece - Auxiliary contact 1 OF - 1 piece | kos | 1
c. | EasyLogic PM2230, Merilnik moči in energije, kot na primer tip: PM2230 | EasyLogic PM2230, Power and energy meter, as for example type: PM2230 | kos | 1
d. | Odvodnik prenapetosti kot na primer tipa 2, 3P + N, Up=1.5kV, In (8/20)=20kA, Imax(8/20)=65kA, pom. kontakt indikacije stanja, kot na primer tip: kot na primer tip iPRD65r | Surge arrester as e.g. type 2, 3P+N, Up=1.5kV, In (8/20)=20kA, Imax(8/20)=65kA, auxiliary contact status indication as e.g. type: as e.g. type iPRD65r | kos | 1
e. | Varovalčno stikalo ISFT160, 160A, DIN NH00, 3 p, z varovalkami 3x80A + Nadzor varovalk FuPacT ISFT160 - 1 NO + 1 NC, kot na primer tip: 480803+LV480810 | Fuse switch ISFT160, 160A, DIN NH00, 3 p, with 3x80A fuses + Fuse monitoring FuPacT ISFT160 - 1 NO + 1 NC, as for example type: 480803+LV480810 | kos | 1
f. | Inštalacijski odklopnik, 50kA, iC60N, 1P, 0.5A, C + Pomožni kontakt iOF/SD+OF, iC60, kot na primer tip: A9F74170+A9A26929 | Circuit breaker, 50kA, iC60N, 1P, 0.5A, C + Auxiliary contact iOF/SD+OF, iC60, e.g. type: A9F74170+A9A26929 | kos | 1
g. | Inštalacijski odklopnik, 50kA, iC60N, 3P, 0.5A, C + Pomožni kontakt iOF/SD+OF, iC60, kot na primer tip: A9F74370+A9A26929 | Circuit breaker, 50kA, iC60N, 3P, 0.5A, C + Auxiliary contact iOF/SD+OF, iC60, e.g. type: A9F74370+A9A26929 | kos | 1
h. | Inštalacijski odklopnik, 36kA, NG125H, 10A, 1P, C + Pomožni kontakti - 2 OC - 6 A - 220..240 V - za NG125, kot na primer tip: 18705+19071 | Circuit breaker, 36kA, NG125H, 10A, 1P, C + Auxiliary contacts - 2 OC - 6 A - 220..240 V - for NG125, as for example type: 18705+19071 | kos | 2
i. | Tokovni merilni transformator, 600/5A, Ue=720 V, sf <= 5 (za Ip od 40 do 4000 A), IP20, IEC 61869-2, kot na primer tip: MET SE CT 600/5A | Current measuring transformer, 600/5A, Ue=720 V, sf <= 5 (for Ip from 40 to 4000 A), IP20, IEC 61869-2, as for example type: MET SE CT 600/5A | kos | 3
j. | Sistemska svetilka LED, brez vtičnice, dolžina: 437 mm, vhodna napetost: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, kot na primer tip: 2500200, proizvod: Rittal | LED system luminaire, without socket, length: 437 mm, input voltage: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, e.g. type: 2500200, product: Rittal | kos | 1
k. | Povezovalni kabel, kot na primer tip: 2500400, proizvod: Rittal | Connection cable, e.g. type: 2500400, product: Rittal | kos | 1
l. | Vtičnica za DIN letev, kot na primer tip: 2506120, proizvod: Rittal | DIN rail socket, e.g. type: 2506120, product: Rittal | kos | 1
m. | Vratno stikalo za LED sistemsko luč, kot na primer tip: 2500460, proizvod: Rittal | Door switch for LED system light, e.g. type: 2500460, product: Rittal | kos | 1
n. | Enonadstropna vzmetna vrstna sponka, kot na primer tip: ZDU 2.5, proizvod: Weidmüller | Single-deck spring-type row clamp, e.g. type: ZDU 2.5, product: Weidmüller | kos | 35
o. | Merilna sponka z vzdolžno ločitvijo in dvema vzporednima mostičema, kot na primer tip: WTL 6/1/STB, proizvod: Weidmüller | Measuring clamp with longitudinal separation and two parallel bridges, e.g. type: WTL 6/1/STB, product: Weidmüller | kos | 6
4.23 | Polje NN_P1_TP_RG3_2 | Field NN_P1_TP_RG3_2 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 800x2050x400mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : PrismaSeT P, proizvod: Schneider Electric | Cabinet dimensions 800x2050x400mm (WxHxD), made of powder-coated RAL9001 steel sheet, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : PrismaSeT P, product : Schneider Electric | kpl | 1
b. | NSX 400N kompaktni tripolni odklopnik (MCCB),nazivni tok 400A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, z vgrajeno opremo: - 'Mikroprocesorska zaščitna enoto Micrologic 2.3, brez meritev ALI - 1kos - Pomožni kontakti (1xNO/NC, 1xSDE) - 2kosa - Zaščitni pokrovi za sponke, dolgi - 1kos - izvedba - fiksna | NSX 400N compact three-pole circuit breaker (MCCB), rated current 400A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, with built-in accessories: - 'Micrologic 2.3 microprocessor protection unit, without ALI measurements - 1 piece - Auxiliary contacts (1xNO/NC, 1xSDE) - 2 pieces - Protective covers for staples, long - 1 piece - design - fixed | kos | 1
c. | NSX 160N kompaktni tripolni odklopnik (MCCB),nazivni tok 160A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, z vgrajeno opremo: - 'Mikroprocesorska zaščitna enoto Micrologic 2.2, brez meritev ALI - 1kos - Pomožni kontakti (1xNO/NC, 1xSDE) - 2kosa - Zaščitni pokrovi za sponke, dolgi - 1kos - izvedba - fiksna | NSX 160N compact three-pole circuit breaker (MCCB), rated current 160A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, with built-in accessories: - 'Micrologic 2.2 microprocessor protection unit, without ALI measurements - 1 piece - Auxiliary contacts (1xNO/NC, 1xSDE) - 2 pieces - Protective covers for staples, long - 1 piece - design - fixed | kos | 6
d. | NSX 100N kompaktni tripolni odklopnik (MCCB),nazivni tok 100A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, z vgrajeno opremo: - 'Mikroprocesorska zaščitna enoto Micrologic 2.2, brez meritev ALI - 1kos - Pomožni kontakti (1xNO/NC, 1xSDE) - 2kosa - Zaščitni pokrovi za sponke, dolgi - 1kos - izvedba - fiksna | NSX 100N compact three-pole circuit breaker (MCCB), rated current 100A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, with built-in accessories: - 'Micrologic 2.2 microprocessor protection unit, without ALI measurements - 1 piece - Auxiliary contacts (1xNO/NC, 1xSDE) - 2 pieces - Protective covers for staples, long - 1 piece - design - fixed | kos | 1
e. | NSX 100N kompaktni tripolni odklopnik (MCCB),nazivni tok 40A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, z vgrajeno opremo: - 'Mikroprocesorska zaščitna enoto Micrologic 2.2, brez meritev ALI - 1kos - Pomožni kontakti (1xNO/NC, 1xSDE) - 2kosa - Zaščitni pokrovi za sponke, dolgi - 1kos - izvedba - fiksna | NSX 100N compact three-pole circuit breaker (MCCB), rated current 40A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, with built-in accessories: - 'Micrologic 2.2 microprocessor protection unit, without ALI measurements - 1 piece - Auxiliary contacts (1xNO/NC, 1xSDE) - 2 pieces - Protective covers for staples, long - 1 piece - design - fixed | kos | 2
f. | Sistemska svetilka LED, brez vtičnice, dolžina: 437 mm, vhodna napetost: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, kot na primer tip: 2500200, proizvod: Rittal | LED system luminaire, without socket, length: 437 mm, input voltage: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, e.g. type: 2500200, product: Rittal | kos | 1
g. | Povezovalni kabel, kot na primer tip: 2500400, proizvod: Rittal | Connection cable, e.g. type: 2500400, product: Rittal | kos | 1
h. | Vratno stikalo za LED sistemsko luč, kot na primer tip: 2500460, proizvod: Rittal | Door switch for LED system light, e.g. type: 2500460, product: Rittal | kos | 1
4.24 | Polje NN_P1_TP_RG3_3 | Field NN_P1_TP_RG3_3 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 400x2050x400mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : PrismaSeT P, proizvod: Schneider Electric | Cabinet dimensions 400x2050x400mm (WxHxD), made of powder-coated RAL9001 steel sheet, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : PrismaSeT P, product : Schneider Electric | kpl | 1
4.25 | 0,4 kV razdelilnik NN_P1_TP_RG4 | 0.4 kV switchgear NN_P1_TP_RG4
| NN sestav je prostostoječe, modularne izvedbe izdelani iz dekapirane jeklene pločevine in profilov, obdelana z anti-korozijsko elektroforezo in končno barvo - poliestrsko/epoksidnim prašnim nanosom, barva RAL - kot na primer tipska barva proizvajalca. Vsak element v NN sestavu mora imeti oznako iz tripolne sheme. NN sestav mora ustrezati zahtevam standardov SIST EN 61439-1 in 2. Ponudnik mora priložiti naslednje izjave in poročila: - izjava o skladnosti s SIST EN 61439-1 in 2 - testna poročila v skladu s SIST EN 61439-1 in 2 - testna poročila o komunikacijskem sistemu (communication report) - enopolne sheme Kot na primer tip: PrismaSeT P, proizvod: Schneider Electric | The LV assembly shall be of a free-standing, modular design, made of decapitated steel sheet and profiles, treated with anti-corrosion electrophoresis and finished with a polyester/epoxy powder coating, RAL colour - such as the manufacturer's standard colour. Each element in the LV assembly shall be marked with a marking from the three-pole scheme. The LV assembly shall comply with the requirements of SIST EN 61439-1 and 2. The tenderer must attach the following declarations and reports: - declaration of conformity to SIST EN 61439-1 and 2 - test reports in accordance with SIST EN 61439-1 and 2 - communication system test reports (communication report) - unipolar schemes Such as type: type: PrismaSeT P, product: Schneider Electric
| Dokumentacija je na voljo v digitalni obliki v oblaku, dostopna preko QR kode na NN sestavu | The documentation is available in digital form in the cloud, accessible via QR code on the NN assembly
| Ponudnik mora dokazati selektivnost med odklopniki v sestavu s pomočjo tabel ali rezultatov izračuna programske opreme | The tenderer shall demonstrate the selectivity between the circuit-breakers in the assembly by means of tables or the results of a software calculation
| Stopnja zaščite: IP31 | Protection rating: IP31
| Število polj (z opremo): | Number of fields (with equipment):
| Okvirna dimenzija (ŠxVxG) 1600 x 2000 x 400mm + podnožje višine: 50mm | Dimensions (WxHxD) 1600 x 2000 x 400mm + base height: 50mm
| Okvirna teža 1 polja: 600kg | Approximate weight of 1 box: 600kg
| Barva RAL: 9001 | RAL colour: 9001
| Prezračevanje: naravno | Ventilation: natural
| Forma pregrajenosti v skladu s standardom SIST EN 61439: 2A | Form of partitioning in accordance with SIST EN 61439:2A
| Priklopi: dovodi - zgoraj s kabli, odvodi: zgoraj s kabli | Connections: inlets - top with cables, outlets: top with cables
| Naznačena izolacijska napetost (Ui): 1000 V | Rated insulation voltage (Ui): 1000 V
| Naznačena obratovalna napetost (Ue): 415 / 690 V AC | Rated operating voltage (Ue): 415 / 690 V AC
| Naznačena frekvenca (fn): 50 Hz | Designated frequency (fn): 50 Hz
| Pomožna napetost za napajanje komunikacijske in druge pomožne opreme: 24 VDC | Auxiliary voltage for power supply of communication and other auxiliary equipment: 24 VDC
| Naznačeni tok glavnih zbiralk: 630 A trajno, materijal Al | Rated current of main busbars: 630 A continuous, material Al
| Naznačeni kratkotrajni zdržni tok (Icw - kA rms/1s): 50 kA | Rated short-time withstand current (Icw - kA rms/1s): 50 kA
| Sistem ozemljitve TN-S | TN-S earthing system
| Presek N-vodnika enak faznemu | N-conductor cross section equal to phase
| Opombe: - Razdelilnik mora biti opremljen po seznamu opreme v dokumentu št. JULFS--7E9105, ožičen in preizkušen. | Notes: - The distributor shall be equipped according to the equipment list in document No JULFS--7E9105, wired and tested.
4.26 | Polje NN_P1_TP_RG4_1 | Field NN_P1_TP_RG4_1 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 400x2050x400mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : PrismaSeT P, proizvod: Schneider Electric | Cabinet dimensions 400x2050x400mm (WxHxD), made of powder-coated RAL9001 steel sheet, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : PrismaSeT P, product : Schneider Electric | kpl | 1
b. | NSX 630 NA kompaktno tripolno stikalo, nazivni tok 630A, kot na primer tip NSXNA, z vgrajeno opremo: - Zaščitni pokrovi za sponke, dolgi - 1kos - Pomožni kontakt 1 OF - 1kos | NSX 630 NA compact three-pole switch, rated current 630A, as for example type NSXNA, with built-in accessories: - Protective covers for staples, long - 1 piece - Auxiliary contact 1 OF - 1 piece | kos | 1
c. | EasyLogic PM2230, Merilnik moči in energije, kot na primer tip: PM2230 | EasyLogic PM2230, Power and energy meter, as for example type: PM2230 | kos | 1
d. | Odvodnik prenapetosti kot na primer tipa 2, 3P + N, Up=1.5kV, In (8/20)=20kA, Imax(8/20)=65kA, pom. kontakt indikacije stanja, kot na primer tip: kot na primer tip iPRD65r | Surge arrester as e.g. type 2, 3P+N, Up=1.5kV, In (8/20)=20kA, Imax(8/20)=65kA, auxiliary contact status indication as e.g. type: as e.g. type iPRD65r | kos | 1
e. | Varovalčno stikalo ISFT160, 160A, DIN NH00, 3 p, z varovalkami 3x80A + Nadzor varovalk FuPacT ISFT160 - 1 NO + 1 NC, kot na primer tip: 480803+LV480810 | Fuse switch ISFT160, 160A, DIN NH00, 3 p, with 3x80A fuses + Fuse monitoring FuPacT ISFT160 - 1 NO + 1 NC, as for example type: 480803+LV480810 | kos | 1
f. | Inštalacijski odklopnik, 50kA, iC60N, 1P, 0.5A, C + Pomožni kontakt iOF/SD+OF, iC60, kot na primer tip: A9F74170+A9A26929 | Circuit breaker, 50kA, iC60N, 1P, 0.5A, C + Auxiliary contact iOF/SD+OF, iC60, e.g. type: A9F74170+A9A26929 | kos | 1
g. | Inštalacijski odklopnik, 50kA, iC60N, 3P, 0.5A, C + Pomožni kontakt iOF/SD+OF, iC60, kot na primer tip: A9F74370+A9A26929 | Circuit breaker, 50kA, iC60N, 3P, 0.5A, C + Auxiliary contact iOF/SD+OF, iC60, e.g. type: A9F74370+A9A26929 | kos | 1
h. | Inštalacijski odklopnik, 36kA, NG125H, 10A, 1P, C + Pomožni kontakti - 2 OC - 6 A - 220..240 V - za NG125, kot na primer tip: 18705+19071 | Circuit breaker, 36kA, NG125H, 10A, 1P, C + Auxiliary contacts - 2 OC - 6 A - 220..240 V - for NG125, as for example type: 18705+19071 | kos | 2
i. | Tokovni merilni transformator, 600/5A, Ue=720 V, sf <= 5 (za Ip od 40 do 4000 A), IP20, IEC 61869-2, kot na primer tip: MET SE CT 600/5A | Current measuring transformer, 600/5A, Ue=720 V, sf <= 5 (for Ip from 40 to 4000 A), IP20, IEC 61869-2, as for example type: MET SE CT 600/5A | kos | 3
j. | Sistemska svetilka LED, brez vtičnice, dolžina: 437 mm, vhodna napetost: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, kot na primer tip: 2500200, proizvod: Rittal | LED system luminaire, without socket, length: 437 mm, input voltage: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, e.g. type: 2500200, product: Rittal | kos | 1
k. | Povezovalni kabel, kot na primer tip: 2500400, proizvod: Rittal | Connection cable, e.g. type: 2500400, product: Rittal | kos | 1
l. | Vtičnica za DIN letev, kot na primer tip: 2506120, proizvod: Rittal | DIN rail socket, e.g. type: 2506120, product: Rittal | kos | 1
m. | Vratno stikalo za LED sistemsko luč, kot na primer tip: 2500460, proizvod: Rittal | Door switch for LED system light, e.g. type: 2500460, product: Rittal | kos | 1
n. | Enonadstropna vzmetna vrstna sponka, kot na primer tip: ZDU 2.5, proizvod: Weidmüller | Single-deck spring-type row clamp, e.g. type: ZDU 2.5, product: Weidmüller | kos | 35
o. | Merilna sponka z vzdolžno ločitvijo in dvema vzporednima mostičema, kot na primer tip: WTL 6/1/STB, proizvod: Weidmüller | Measuring clamp with longitudinal separation and two parallel bridges, e.g. type: WTL 6/1/STB, product: Weidmüller | kos | 6
4.27 | Polje NN_P1_TP_RG4_2 | Field NN_P1_TP_RG4_2 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 800x2050x400mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : PrismaSeT P, proizvod: Schneider Electric | Cabinet dimensions 800x2050x400mm (WxHxD), made of powder-coated RAL9001 steel sheet, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : PrismaSeT P, product : Schneider Electric | kpl | 1
b. | NSX 160N kompaktni tripolni odklopnik (MCCB),nazivni tok 160A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, z vgrajeno opremo: - 'Mikroprocesorska zaščitna enoto Micrologic 2.2, brez meritev ALI - 1kos - Pomožni kontakti (1xNO/NC, 1xSDE) - 2kosa - Zaščitni pokrovi za sponke, dolgi - 1kos - izvedba - fiksna | NSX 160N compact three-pole circuit breaker (MCCB), rated current 160A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, with built-in accessories: - 'Micrologic 2.2 microprocessor protection unit, without ALI measurements - 1 piece - Auxiliary contacts (1xNO/NC, 1xSDE) - 2 pieces - Protective covers for staples, long - 1 piece - design - fixed | kos | 1
| NSX 100N kompaktni tripolni odklopnik (MCCB),nazivni tok 100A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, z vgrajeno opremo: - 'Mikroprocesorska zaščitna enoto Micrologic 2.2, brez meritev ALI - 1kos - Pomožni kontakti (1xNO/NC, 1xSDE) - 2kosa - Zaščitni pokrovi za sponke, dolgi - 1kos - izvedba - fiksna | NSX 100N compact three-pole circuit breaker (MCCB), rated current 100A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, with built-in accessories: - 'Micrologic 2.2 microprocessor protection unit, without ALI measurements - 1 piece - Auxiliary contacts (1xNO/NC, 1xSDE) - 2 pieces - Protective covers for staples, long - 1 piece - design - fixed | kos | 6
c. | NSX 100N kompaktni tripolni odklopnik (MCCB),nazivni tok 40A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, z vgrajeno opremo: - 'Mikroprocesorska zaščitna enoto Micrologic 2.2, brez meritev ALI - 1kos - Pomožni kontakti (1xNO/NC, 1xSDE) - 2kosa - Zaščitni pokrovi za sponke, dolgi - 1kos - izvedba - fiksna | NSX 100N compact three-pole circuit breaker (MCCB), rated current 40A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, with built-in accessories: - 'Micrologic 2.2 microprocessor protection unit, without ALI measurements - 1 piece - Auxiliary contacts (1xNO/NC, 1xSDE) - 2 pieces - Protective covers for staples, long - 1 piece - design - fixed | kos | 3
d. | Sistemska svetilka LED, brez vtičnice, dolžina: 437 mm, vhodna napetost: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, kot na primer tip: 2500200, proizvod: Rittal | LED system luminaire, without socket, length: 437 mm, input voltage: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, e.g. type: 2500200, product: Rittal | kos | 1
e. | Povezovalni kabel, kot na primer tip: 2500400, proizvod: Rittal | Connection cable, e.g. type: 2500400, product: Rittal | kos | 1
f. | Vratno stikalo za LED sistemsko luč, kot na primer tip: 2500460, proizvod: Rittal | Door switch for LED system light, e.g. type: 2500460, product: Rittal | kos | 1
4.28 | Polje NN_P1_TP_RG4_3 | Field NN_P1_TP_RG4_3 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 400x2050x400mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : PrismaSeT P, proizvod: Schneider Electric | Cabinet dimensions 400x2050x400mm (WxHxD), made of powder-coated RAL9001 steel sheet, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : PrismaSeT P, product : Schneider Electric | kpl | 1
4.29 | 0,4 kV razdelilnik NN_N3_4_RG1 | 0.4 kV switchgear NN_N3_4_RG1
| NN sestav je prostostoječe, modularne izvedbe izdelani iz dekapirane jeklene pločevine in profilov, obdelana z anti-korozijsko elektroforezo in končno barvo - poliestrsko/epoksidnim prašnim nanosom, barva RAL - kot na primer tipska barva proizvajalca. Vsak element v NN sestavu mora imeti oznako iz tripolne sheme. NN sestav mora ustrezati zahtevam standardov SIST EN 61439-1 in 2. Ponudnik mora priložiti naslednje izjave in poročila: - izjava o skladnosti s SIST EN 61439-1 in 2 - testna poročila v skladu s SIST EN 61439-1 in 2 - testna poročila o komunikacijskem sistemu (communication report) - enopolne sheme Kot na primer tip: PrismaSeT P, proizvod: Schneider Electric | The LV assembly shall be of a free-standing, modular design, made of decapitated steel sheet and profiles, treated with anti-corrosion electrophoresis and finished with a polyester/epoxy powder coating, RAL colour - such as the manufacturer's standard colour. Each element in the LV assembly shall be marked with a marking from the three-pole scheme. The LV assembly shall comply with the requirements of SIST EN 61439-1 and 2. The tenderer must attach the following declarations and reports: - declaration of conformity to SIST EN 61439-1 and 2 - test reports in accordance with SIST EN 61439-1 and 2 - communication system test reports (communication report) - unipolar schemes Such as type: PrismaSeT P, product: Schneider Electric
| Dokumentacija je na voljo v digitalni obliki v oblaku, dostopna preko QR kode na NN sestavu | The documentation is available in digital form in the cloud, accessible via QR code on the NN assembly
| Ponudnik mora dokazati selektivnost med odklopniki v sestavu s pomočjo tabel ali rezultatov izračuna programske opreme | The tenderer shall demonstrate the selectivity between the circuit-breakers in the assembly by means of tables or the results of a software calculation
| Stopnja zaščite: IP31 | Protection rating: IP31
| Število polj (z opremo): | Number of fields (with equipment):
| Okvirna dimenzija (ŠxVxG) 1600 x 2000 x 400mm + podnožje višine: 50mm | Dimensions (WxHxD) 1600 x 2000 x 400mm + base height: 50mm
| Okvirna teža 1 polja: 600kg | Approximate weight of 1 box: 600kg
| Barva RAL: 9001 | RAL colour: 9001
| Prezračevanje: naravno | Ventilation: natural
| Forma pregrajenosti v skladu s standardom SIST EN 61439: 2A | Form of partitioning according to SIST EN 61439:2A
| Priklopi: dovodi - zgoraj s kabli, odvodi: zgoraj s kabli | Connections: inlets - top with cables, outlets: top with cables
| Naznačena izolacijska napetost (Ui): 1000 V | Rated insulation voltage (Ui): 1000 V
| Naznačena obratovalna napetost (Ue): 415 / 690 V AC | Rated operating voltage (Ue): 415 / 690 V AC
| Naznačena frekvenca (fn): 50 Hz | Designated frequency (fn): 50 Hz
| Pomožna napetost za napajanje komunikacijske in druge pomožne opreme: 24 VDC | Auxiliary voltage for power supply of communication and other auxiliary equipment: 24 VDC
| Naznačeni tok glavnih zbiralk: 250 A trajno, materijal Al | Main busbar current rating: 250 A continuous, material Al
| Naznačeni kratkotrajni zdržni tok (Icw - kA rms/1s): 15 kA | Rated short-time withstand current (Icw - kA rms/1s): 15 kA
| Sistem ozemljitve TN-S | TN-S earthing system
| Presek N-vodnika enak faznemu | N-conductor cross section equal to phase
| Opombe: - Razdelilnik mora biti opremljen po seznamu opreme v dokumentu št. JULFS--7E9106, ožičen in preizkušen. | Notes: - The distributor shall be equipped according to the equipment list in document No JULFS--7E9106, wired and tested.
4.30 | Polje NN_N3_4_RG1_1 | Field NN_N3_4_RG1_1 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 400x2050x400mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : PrismaSeT P, proizvod: Schneider Electric | Cabinet dimensions 400x2050x400mm (WxHxD), made of powder-coated RAL9001 steel sheet, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : PrismaSeT P, product : Schneider Electric | kpl | 1
b. | NSX 250 NA kompaktno tripolno stikalo, nazivni tok 250A, kot na primer tip NSXNA, z vgrajeno opremo: - Zaščitni pokrovi za sponke, dolgi - 1kos - Pomožni kontakt 1 OF - 1kos | NSX 250 NA compact three-pole switch, rated current 250A, as for example type NSXNA, with built-in accessories: - Protective covers for staples, long - 1 piece - Auxiliary contact 1 OF - 1 piece | kos | 1
c. | EasyLogic PM2230, Merilnik moči in energije, kot na primer tip: PM2230 | EasyLogic PM2230, Power and energy meter, as for example type: PM2230 | kos | 1
d. | Odvodnik prenapetosti kot na primer tipa 2, 3P + N, Up=1.5kV, In (8/20)=20kA, Imax(8/20)=65kA, pom. kontakt indikacije stanja, kot na primer tip: kot na primer tip iPRD65r | Surge arrester as e.g. type 2, 3P+N, Up=1.5kV, In (8/20)=20kA, Imax(8/20)=65kA, auxiliary contact status indication as e.g. type: as e.g. type iPRD65r | kos | 1
e. | Varovalčno stikalo ISFT160, 160A, DIN NH00, 3 p, z varovalkami 3x80A + Nadzor varovalk FuPacT ISFT160 - 1 NO + 1 NC, kot na primer tip: 480803+LV480810 | Fuse switch ISFT160, 160A, DIN NH00, 3 p, with 3x80A fuses + Fuse monitoring FuPacT ISFT160 - 1 NO + 1 NC, as for example type: 480803+LV480810 | kos | 1
f. | Inštalacijski odklopnik, 50kA, iC60N, 1P, 0.5A, C + Pomožni kontakt iOF/SD+OF, iC60, kot na primer tip: A9F74170+A9A26929 | Circuit breaker, 50kA, iC60N, 1P, 0.5A, C + Auxiliary contact iOF/SD+OF, iC60, e.g. type: A9F74170+A9A26929 | kos | 1
g. | Inštalacijski odklopnik, 50kA, iC60N, 3P, 0.5A, C + Pomožni kontakt iOF/SD+OF, iC60, kot na primer tip: A9F74370+A9A26929 | Circuit breaker, 50kA, iC60N, 3P, 0.5A, C + Auxiliary contact iOF/SD+OF, iC60, e.g. type: A9F74370+A9A26929 | kos | 1
h. | Inštalacijski odklopnik, 36kA, NG125H, 10A, 1P, C + Pomožni kontakti - 2 OC - 6 A - 220..240 V - za NG125, kot na primer tip: 18705+19071 | Circuit breaker, 36kA, NG125H, 10A, 1P, C + Auxiliary contacts - 2 OC - 6 A - 220..240 V - for NG125, as for example type: 18705+19071 | kos | 2
i. | Tokovni merilni transformator, 200/5A, Ue=720 V, sf <= 5 (za Ip od 40 do 4000 A), IP20, IEC 61869-2, kot na primer tip: MET SE CT 200/5A | Current measuring transformer, 200/5A, Ue=720 V, sf <= 5 (for Ip from 40 to 4000 A), IP20, IEC 61869-2, as for example type: MET SE CT 200/5A | kos | 3
j. | Sistemska svetilka LED, brez vtičnice, dolžina: 437 mm, vhodna napetost: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, kot na primer tip: 2500200, proizvod: Rittal | LED system luminaire, without socket, length: 437 mm, input voltage: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, e.g. type: 2500200, product: Rittal | kos | 1
k. | Povezovalni kabel, kot na primer tip: 2500400, proizvod: Rittal | Connection cable, e.g. type: 2500400, product: Rittal | kos | 1
l. | Vtičnica za DIN letev, kot na primer tip: 2506120, proizvod: Rittal | DIN rail socket, e.g. type: 2506120, product: Rittal | kos | 1
m. | Vratno stikalo za LED sistemsko luč, kot na primer tip: 2500460, proizvod: Rittal | Door switch for LED system light, e.g. type: 2500460, product: Rittal | kos | 1
n. | Enonadstropna vzmetna vrstna sponka, kot na primer tip: ZDU 2.5, proizvod: Weidmüller | Single-deck spring-type row clamp, e.g. type: ZDU 2.5, product: Weidmüller | kos | 35
o. | Merilna sponka z vzdolžno ločitvijo in dvema vzporednima mostičema, kot na primer tip: WTL 6/1/STB, proizvod: Weidmüller | Measuring clamp with longitudinal separation and two parallel bridges, e.g. type: WTL 6/1/STB, product: Weidmüller | kos | 6
4.31 | Polje NN_N3_4_RG1_2 | Field NN_N3_4_RG1_2 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 800x2050x400mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : PrismaSeT P, proizvod: Schneider Electric | Cabinet dimensions 800x2050x400mm (WxHxD), made of powder-coated RAL9001 steel sheet, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : PrismaSeT P, product : Schneider Electric | kpl | 1
b. | NSX 100B kompaktni tripolni odklopnik (MCCB),nazivni tok 100A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, z vgrajeno opremo: - 'Mikroprocesorska zaščitna enoto Micrologic 2.2, brez meritev ALI - 1kos - Pomožni kontakti (1xNO/NC, 1xSDE) - 2kosa - Zaščitni pokrovi za sponke, dolgi - 1kos - izvedba - fiksna | NSX 100B compact three-pole circuit breaker (MCCB), rated current 100A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, with built-in accessories: - 'Micrologic 2.2 microprocessor protection unit, without ALI measurements - 1 piece - Auxiliary contacts (1xNO/NC, 1xSDE) - 2 pieces - Protective covers for staples, long - 1 piece - design - fixed | kos | 4
c. | NSX 100B kompaktni tripolni odklopnik (MCCB),nazivni tok 40A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, z vgrajeno opremo: - 'Mikroprocesorska zaščitna enoto Micrologic 2.2, brez meritev ALI - 1kos - Pomožni kontakti (1xNO/NC, 1xSDE) - 2kosa - Zaščitni pokrovi za sponke, dolgi - 1kos - izvedba - fiksna | NSX 100B compact three-pole circuit breaker (MCCB), rated current 40A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, with built-in accessories: - 'Micrologic 2.2 microprocessor protection unit, without ALI measurements - 1 piece - Auxiliary contacts (1xNO/NC, 1xSDE) - 2 pieces - Protective covers for staples, long - 1 piece - design - fixed | kos | 6
d. | Sistemska svetilka LED, brez vtičnice, dolžina: 437 mm, vhodna napetost: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, kot na primer tip: 2500200, proizvod: Rittal | LED system luminaire, without socket, length: 437 mm, input voltage: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, e.g. type: 2500200, product: Rittal | kos | 1
e. | Povezovalni kabel, kot na primer tip: 2500400, proizvod: Rittal | Connection cable, e.g. type: 2500400, product: Rittal | kos | 1
f. | Vratno stikalo za LED sistemsko luč, kot na primer tip: 2500460, proizvod: Rittal | Door switch for LED system light, e.g. type: 2500460, product: Rittal | kos | 1
4.32 | Polje NN_N3_4_RG1_3 | Field NN_N3_4_RG1_3 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 400x2050x400mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : PrismaSeT P, proizvod: Schneider Electric | Cabinet dimensions 400x2050x400mm (WxHxD), made of powder-coated RAL9001 steel sheet, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : PrismaSeT P, product : Schneider Electric | kpl | 1
4.33 | 0,4 kV razdelilnik UPS_P1_TP_RG1 | 0.4 kV UPS_P1_TP_RG1
| NN sestav je prostostoječe, modularne izvedbe izdelani iz dekapirane jeklene pločevine in profilov, obdelana z anti-korozijsko elektroforezo in končno barvo - poliestrsko/epoksidnim prašnim nanosom, barva RAL - kot na primer tipska barva proizvajalca. Vsak element v NN sestavu mora imeti oznako iz tripolne sheme. NN sestav mora ustrezati zahtevam standardov SIST EN 61439-1 in 2. Ponudnik mora priložiti naslednje izjave in poročila: - izjava o skladnosti s SIST EN 61439-1 in 2 - testna poročila v skladu s SIST EN 61439-1 in 2 - testna poročila o komunikacijskem sistemu (communication report) - enopolne sheme Kot na primer tip: PrismaSeT P, proizvod: Schneider Electric | The LV assembly shall be of a free-standing, modular design, made of decapitated steel sheet and profiles, treated with anti-corrosion electrophoresis and finished with a polyester/epoxy powder coating, RAL colour - such as the manufacturer's standard colour. Each element in the LV assembly shall be marked with a marking from the three-pole scheme. The LV assembly shall comply with the requirements of SIST EN 61439-1 and 2. The tenderer must attach the following declarations and reports: - declaration of conformity to SIST EN 61439-1 and 2 - test reports in accordance with SIST EN 61439-1 and 2 - communication system test reports (communication report) - unipolar schemes Such as type: type: PrismaSeT P, product: Schneider Electric
| Dokumentacija je na voljo v digitalni obliki v oblaku, dostopna preko QR kode na NN sestavu | The documentation is available in digital form in the cloud, accessible via QR code on the NN assembly
| Ponudnik mora dokazati selektivnost med odklopniki v sestavu s pomočjo tabel ali rezultatov izračuna programske opreme | The tenderer shall demonstrate the selectivity between the circuit-breakers in the assembly by means of tables or the results of a software calculation
| Stopnja zaščite: IP31 | Protection rating: IP31
| Število polj (z opremo): | Number of fields (with equipment):
| Okvirna dimenzija (ŠxVxG) 1850 x 2000 x 400mm + podnožje višine: 50mm | Dimensions (WxHxD) 1850 x 2000 x 400mm + base height: 50mm
| Okvirna teža 1 polja: 600kg | Approximate weight of 1 box: 600kg
| Barva RAL: 9001 | RAL colour: 9001
| Prezračevanje: naravno | Ventilation: natural
| Forma pregrajenosti v skladu s standardom SIST EN 61439: 2A | Form of partitioning according to SIST EN 61439:2A
| Priklopi: dovodi - zgoraj s kabli, odvodi: zgoraj s kabli | Connections: inlets - top with cables, outlets: top with cables
| Naznačena izolacijska napetost (Ui): 1000 V | Rated insulation voltage (Ui): 1000 V
| Naznačena obratovalna napetost (Ue): 415 / 690 V AC | Rated operating voltage (Ue): 415 / 690 V AC
| Naznačena frekvenca (fn): 50 Hz | Designated frequency (fn): 50 Hz
| Pomožna napetost za napajanje komunikacijske in druge pomožne opreme: 24 VDC | Auxiliary voltage for power supply of communication and other auxiliary equipment: 24 VDC
| Naznačeni tok glavnih zbiralk: 400 A trajno, materijal Al | Main busbar current rating: 400 A continuous, material Al
| Naznačeni kratkotrajni zdržni tok (Icw - kA rms/1s): 25 kA | Rated short-time withstand current (Icw - kA rms/1s): 25 kA
| Sistem ozemljitve TN-S | TN-S earthing system
| Presek N-vodnika enak faznemu | N-conductor cross section equal to phase
| Opombe: - Razdelilnik mora biti opremljen po seznamu opreme v dokumentu št. JULFS--7E9108, ožičen in preizkušen. | Notes: - The distributor shall be equipped according to the equipment list in document No JULFS--7E9108, wired and tested.
4.34 | Polje UPS_P1_TP_RG1_1 | Field UPS_P1_TP_RG1_1 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 650x2050x400mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : PrismaSeT P, proizvod: Schneider Electric | Cabinet dimensions 650x2050x400mm (WxHxD), made of powder-coated RAL9001 steel sheet, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : PrismaSeT P, product : Schneider Electric | kpl | 1
b. | NSX 400 NA kompaktno tripolno stikalo, nazivni tok 400A, kot na primer tip NSXNA, z vgrajeno opremo: - Zaščitni pokrovi za sponke, dolgi - 1kos - Ključavnica za zaklepanje - 1kos - Pomožni kontakt stanja OF1 - 1kos | NSX 400 NA compact three-pole switch, rated current 400A, as for example type NSXNA, with built-in accessories: - Protective covers for staples, long - 1 piece - Lock for locking - 1 piece - Auxiliary contact sheet OF1 - 1 piece | kos | 2
c. | EasyLogic PM2230, Merilnik moči in energije, kot na primer tip: PM2230 | EasyLogic PM2230, Power and energy meter, as for example type: PM2230 | kos | 1
d. | Odvodnik prenapetosti kot na primer tipa 2, 3P + N, Up=1.5kV, In (8/20)=20kA, Imax(8/20)=65kA, pom. kontakt indikacije stanja, kot na primer tip: kot na primer tip iPRD65r | Surge arrester as e.g. type 2, 3P+N, Up=1.5kV, In (8/20)=20kA, Imax(8/20)=65kA, auxiliary contact status indication as e.g. type: as e.g. type iPRD65r | kos | 1
e. | Varovalčno stikalo ISFT160, 160A, DIN NH00, 3 p, z varovalkami 3x80A + Nadzor varovalk FuPacT ISFT160 - 1 NO + 1 NC, kot na primer tip: 480803+LV480810 | Fuse switch ISFT160, 160A, DIN NH00, 3 p, with 3x80A fuses + Fuse monitoring FuPacT ISFT160 - 1 NO + 1 NC, as for example type: 480803+LV480810 | kos | 1
f. | Voltmetar 0-500 V, razred točnosti 1.5, 72x72 mm za montažo na vrata, stopenj zaščite: IP52, v skladu s standardi IEC 60051-1, IEC 61010-1 i IEC 61000-4, kot na primer tip: VLT | Voltmeter 0-500 V, accuracy class 1.5, 72x72 mm for door mounting, protection class IP52, according to IEC 60051-1, IEC 61010-1 and IEC 61000-4 standards, e.g. type VLT | kos | 2
g. | Voltmetrska preklopka za merjenje trifazne napetosti, Un=415 V Ac, In=10A, za montažo na DIN letev, kot na primer tip: CMV 415V | Voltmeter switch for measuring three-phase voltage, Un=415 V Ac, In=10 A, for DIN rail mounting, e.g. type: CMV 415V | kos | 2
h. | Inštalacijski odklopnik, 50kA, iC60N, 1P, 0.5A, C + Pomožni kontakt iOF/SD+OF, iC60, kot na primer tip: A9F74170+A9A26929 | Circuit breaker, 50kA, iC60N, 1P, 0.5A, C + Auxiliary contact iOF/SD+OF, iC60, e.g. type: A9F74170+A9A26929 | kos | 1
i. | Inštalacijski odklopnik, 50kA, iC60N, 3P, 0.5A, C + Pomožni kontakt iOF/SD+OF, iC60, kot na primer tip: A9F74370+A9A26929 | Circuit breaker, 50kA, iC60N, 3P, 0.5A, C + Auxiliary contact iOF/SD+OF, iC60, e.g. type: A9F74370+A9A26929 | kos | 1
j. | Inštalacijski odklopnik, 25kA, iC60L, 3P, 6A, C + Pomožni kontakt iOF/SD+OF, iC60, kot na primer tip: A9F94306+A9A26929 | Circuit breaker, 25kA, iC60L, 3P, 6A, C + Auxiliary contact iOF/SD+OF, iC60, as for example type: A9F94306+A9A26929 | kos | 2
k. | Inštalacijski odklopnik, 36kA, NG125H, 16A, 3P, C + Pomožni kontakti - 2 OC - 6 A - 220..240 V - za NG125, kot na primer tip: 18724+19071 | Circuit breaker, 36kA, NG125H, 16A, 3P, C + Auxiliary contacts - 2 OC - 6 A - 220..240 V - for NG125, as for example type: 18724+19071 | kos | 6
l. | Inštalacijski odklopnik, 36kA, NG125H, 10A, 3P, C + Pomožni kontakti - 2 OC - 6 A - 220..240 V - za NG125, kot na primer tip: 18723+19071 | Circuit breaker, 36kA, NG125H, 10A, 3P, C + Auxiliary contacts - 2 OC - 6 A - 220..240 V - for NG125, as for example type: 18723+19071 | kos | 2
m. | Inštalacijski odklopnik, 36kA, NG125H, 16A, 1P, C + Pomožni kontakti - 2 OC - 6 A - 220..240 V - za NG125, kot na primer tip: 18706+19071 | Circuit breaker, 36kA, NG125H, 16A, 1P, C + Auxiliary contacts - 2 OC - 6 A - 220..240 V - for NG125, as for example type: 18706+19071 | kos | 6
n. | Inštalacijski odklopnik, 36kA, NG125H, 10A, 1P, C + Pomožni kontakti - 2 OC - 6 A - 220..240 V - za NG125, kot na primer tip: 18705+19071 | Circuit breaker, 36kA, NG125H, 10A, 1P, C + Auxiliary contacts - 2 OC - 6 A - 220..240 V - for NG125, as for example type: 18705+19071 | kos | 2
o. | Tokovni merilni transformator, 200/5A, Ue=720 V, sf <= 5 (za Ip od 40 do 4000 A), IP20, IEC 61869-2, kot na primer tip: MET SE CT 300/5A | Current measuring transformer, 200/5A, Ue=720 V, sf <= 5 (for Ip from 40 to 4000 A), IP20, IEC 61869-2, as for example type: MET SE CT 300/5A | kos | 3
p. | Sistemska svetilka LED, brez vtičnice, dolžina: 437 mm, vhodna napetost: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, kot na primer tip: 2500200, proizvod: Rittal | LED system luminaire, without socket, length: 437 mm, input voltage: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, e.g. type: 2500200, product: Rittal | kos | 1
q. | Povezovalni kabel, kot na primer tip: 2500400, proizvod: Rittal | Connection cable, e.g. type: 2500400, product: Rittal | kos | 1
r. | Vratno stikalo za LED sistemsko luč, kot na primer tip: 2500460, proizvod: Rittal | Door switch for LED system light, e.g. type: 2500460, product: Rittal | kos | 1
s. | Vtičnica za DIN letev, kot na primer tip: 2506120, proizvod: Rittal | DIN rail socket, e.g. type: 2506120, product: Rittal | kos | 1
t. | Enonadstropna vzmetna vrstna sponka, kot na primer tip: ZDU 2.5, proizvod: Weidmüller | Single-deck spring-type row clamp, e.g. type: ZDU 2.5, product: Weidmüller | kos | 52
u. | Enonadstropna vijačna sponka, kot na primer tip: WDU 4, proizvod: Weidmüller | Single-deck screw clamp, e.g. type: WDU 4, product: Weidmüller | kos | 35
v. | Merilna sponka z vzdolžno ločitvijo in dvema vzporednima mostičema, kot na primer tip: WTL 6/1/STB, proizvod: Weidmüller | Measuring clamp with longitudinal separation and two parallel bridges, e.g. type: WTL 6/1/STB, product: Weidmüller | kos | 6
4.35 | Polje UPS_P1_TP_RG1_2 | Field UPS_P1_TP_RG1_2 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 800x2050x400mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : PrismaSeT P, proizvod: Schneider Electric | Cabinet dimensions 800x2050x400mm (WxHxD), made of powder-coated RAL9001 steel sheet, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : PrismaSeT P, product : Schneider Electric | kpl | 1
b. | NSX 100B kompaktni tripolni odklopnik (MCCB),nazivni tok 100A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, z vgrajeno opremo: - 'Mikroprocesorska zaščitna enoto Micrologic 2.2, brez meritev ALI - 1kos - Pomožni kontakti (1xNO/NC, 1xSDE) - 2kosa - Zaščitni pokrovi za sponke, dolgi - 1kos - izvedba - fiksna | NSX 100B compact three-pole circuit breaker (MCCB), rated current 100A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, with built-in accessories: - 'Micrologic 2.2 microprocessor protection unit, without ALI measurements - 1 piece - Auxiliary contacts (1xNO/NC, 1xSDE) - 2 pieces - Protective covers for staples, long - 1 piece - design - fixed | kos | 4
c. | NSX 100B kompaktni tripolni odklopnik (MCCB),nazivni tok 40A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, z vgrajeno opremo: - 'Mikroprocesorska zaščitna enoto Micrologic 2.2, brez meritev ALI - 1kos - Pomožni kontakti (1xNO/NC, 1xSDE) - 2kosa - Zaščitni pokrovi za sponke, dolgi - 1kos - izvedba - fiksna | NSX 100B compact three-pole circuit breaker (MCCB), rated current 40A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, with built-in accessories: - 'Micrologic 2.2 microprocessor protection unit, without ALI measurements - 1 piece - Auxiliary contacts (1xNO/NC, 1xSDE) - 2 pieces - Protective covers for staples, long - 1 piece - design - fixed | kos | 6
d. | Sistemska svetilka LED, brez vtičnice, dolžina: 437 mm, vhodna napetost: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, kot na primer tip: 2500200, proizvod: Rittal | LED system luminaire, without socket, length: 437 mm, input voltage: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, e.g. type: 2500200, product: Rittal | kos | 1
e. | Povezovalni kabel, kot na primer tip: 2500400, proizvod: Rittal | Connection cable, e.g. type: 2500400, product: Rittal | kos | 1
f. | Vratno stikalo za LED sistemsko luč, kot na primer tip: 2500460, proizvod: Rittal | Door switch for LED system light, e.g. type: 2500460, product: Rittal | kos | 1
4.36 | Polje UPS_P1_TP_RG1_3 | Field UPS_P1_TP_RG1_3 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 400x2050x400mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : PrismaSeT P, proizvod: Schneider Electric | Cabinet dimensions 400x2050x400mm (WxHxD), made of powder-coated RAL9001 steel sheet, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : PrismaSeT P, product : Schneider Electric | kpl | 1
4.37 | 0,4 kV razdelilnik DEA_P1_TP_RG1 | 0,4 kV switchgear DEA_P1_TP_RG1 |  |  | kpl | 1 |  | 0
| NN sestav je prostostoječe, modularne izvedbe izdelani iz dekapirane jeklene pločevine in profilov, obdelana z anti-korozijsko elektroforezo in končno barvo - poliestrsko/epoksidnim prašnim nanosom, barva RAL - kot na primer tipska barva proizvajalca. Vsak element v NN sestavu mora imeti oznako iz tripolne sheme. NN sestav mora ustrezati zahtevam standardov SIST EN 61439-1 in 2. Ponudnik mora priložiti naslednje izjave in poročila: - izjava o skladnosti s SIST EN 61439-1 in 2 - testna poročila v skladu s SIST EN 61439-1 in 2 - testna poročila o komunikacijskem sistemu (communication report) - enopolne sheme Kot na primer tip: PrismaSeT P, proizvod: Schneider Electric | The LV assembly shall be of a free-standing, modular design, made of decapitated steel sheet and profiles, treated with anti-corrosion electrophoresis and finished with a polyester/epoxy powder coating, RAL colour - such as the manufacturer's standard colour. Each element in the LV assembly shall be marked with a marking from the three-pole scheme. The LV assembly shall comply with the requirements of SIST EN 61439-1 and 2. The tenderer must attach the following declarations and reports: - declaration of conformity to SIST EN 61439-1 and 2 - test reports in accordance with SIST EN 61439-1 and 2 - communication system test reports (communication report) - unipolar schemes Such as type: PrismaSeT P, product: Schneider Electric
| Dokumentacija je na voljo v digitalni obliki v oblaku, dostopna preko QR kode na NN sestavu | The documentation is available in digital form in the cloud, accessible via QR code on the NN assembly
| Ponudnik mora dokazati selektivnost med odklopniki v sestavu s pomočjo tabel ali rezultatov izračuna programske opreme | The tenderer shall demonstrate the selectivity between the circuit-breakers in the assembly by means of tables or the results of a software calculation
| Stopnja zaščite: IP31 | Protection rating: IP31
| Število polj (z opremo): | Number of fields (with equipment):
| Okvirna dimenzija (ŠxVxG) 1950 x 2000 x 400mm + podnožje višine: 50mm | Dimensions (WxHxD) 1950 x 2000 x 400mm + base height: 50mm
| Okvirna teža 1 polja: 600kg | Approximate weight of 1 box: 600kg
| Barva RAL: 9001 | RAL colour: 9001
| Prezračevanje: naravno | Ventilation: natural
| Forma pregrajenosti v skladu s standardom SIST EN 61439: 2A | Form of partitioning according to SIST EN 61439:2A
| Priklopi: dovodi - zgoraj s kabli, odvodi: zgoraj s kabli | Connections: inlets - top with cables, outlets: top with cables
| Naznačena izolacijska napetost (Ui): 1000 V | Rated insulation voltage (Ui): 1000 V
| Naznačena obratovalna napetost (Ue): 415 / 690 V AC | Rated operating voltage (Ue): 415 / 690 V AC
| Naznačena frekvenca (fn): 50 Hz | Designated frequency (fn): 50 Hz
| Pomožna napetost za napajanje komunikacijske in druge pomožne opreme: 24 VDC | Auxiliary voltage for power supply of communication and other auxiliary equipment: 24 VDC
| Naznačeni tok glavnih zbiralk: 630 A trajno, materijal Al | Rated current of main busbars: 630 A continuous, material Al
| Naznačeni kratkotrajni zdržni tok (Icw - kA rms/1s): 36 kA | Rated short-time withstand current (Icw - kA rms/1s): 36 kA
| Sistem ozemljitve TN-S | TN-S earthing system
| Presek N-vodnika enak faznemu | N-conductor cross section equal to phase
| Opombe: - Razdelilnik mora biti opremljen po seznamu opreme v dokumentu št. JULFS--7E9107, ožičen in preizkušen. | Notes: - The distributor shall be equipped according to the equipment list in document No JULFS--7E9107, wired and tested.
4.38 | Polje DEA_P1_TP_RG1_1 | Field DEA_P1_TP_RG1_1 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 800x2050x400mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : PrismaSeT P, proizvod: Schneider Electric | Cabinet dimensions 800x2050x400mm (WxHxD), made of powder-coated RAL9001 steel sheet, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : PrismaSeT P, product : Schneider Electric | kpl | 1
b. | NSX 630F kompaktni tripolni odklopnik (MCCB),nazivni tok 630A, izklopilni tok KS Icu= 36kA, servisni tok KS Ics=100% Icu, z vgrajeno opremo: - Mikroprocesorska zaščitna enoto Micrologic 2.3, brez meritev ALI - 1kos - Motorni pogon 230VAC - 1kos - Izlopilna tuljava za NSX odklopnike, 220-240V AC, 50/60 Hz - 1kos - Pomožni kontakti (4xNO/NC, 2xSDE) - 6kosi - Zaščitni pokrovi za sponke, kratki - 2kos - izvedba - fiksna | NSX 630F compact three-pole circuit breaker (MCCB), rated current 630A, tripping current KS Icu= 36kA, service current KS Ics=100% Icu, with built-in accessories: - Micrologic 2.3 microprocessor protection unit, without ALI measurements - 1 piece - Motor drive 230VAC - 1 piece - Trip coil for NSX circuit breakers, 220-240V AC, 50/60 Hz - 1 piece - Auxiliary contacts (4xNO/NC, 2xSDE) - 6 axes - Protective caps for staples, short - 2 pieces - design - fixed | kos | 1
c. | NSX 630F kompaktni tripolni odklopnik (MCCB),nazivni tok 630A, izklopilni tok KS Icu= 36kA, servisni tok KS Ics=100% Icu, z vgrajeno opremo: - Mikroprocesorska zaščitna enoto Micrologic 2.3, brez meritev ALI - 1kos - Motorni pogon 230VAC - 1kos - Podnapetostni rele MN 220-240V AC 50/60Hz, dodatna oprema za odklopnik NSX100-630 - 1kos - Pomožni kontakti (4xNO/NC, 2xSDE) - 6kosi - Zaščitni pokrovi za sponke, kratki - 2kos - izvedba - fiksna | NSX 630F compact three-pole circuit breaker (MCCB), rated current 630A, tripping current KS Icu= 36kA, service current KS Ics=100% Icu, with built-in accessories: - Micrologic 2.3 microprocessor protection unit, without ALI measurements - 1 piece - Motor drive 230VAC - 1 piece - Undervoltage relay MN 220-240V AC 50/60Hz, accessory for NSX100-630 circuit breaker - 1 piece - Auxiliary contacts (4xNO/NC, 2xSDE) - 6 axes - Protective caps for staples, short - 2 pieces - design - fixed | kos | 1
d. | NSXm TM100F kompletni fiksni tripolni odklopnik (MCCB),nazivni tok 100A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu (do 415V), z vgrajeno opremo: - Elektro-mehanska zaščitna enota MicroLogic Vigi 4.1 (nastavljiva od 0.4 to 1 x Ir) - 1kos - Pomožni kontakti (1xNO/NC, 1xSDE) - 2kosa | NSXm TM100F complete fixed three-pole circuit breaker (MCCB), rated current 100A, tripping current KS Icu=50kA, service current KS Ics=100% Icu (up to 415V), with built-in accessories: - MicroLogic Vigi 4.1 electro-mechanical protection unit (adjustable from 0.4 to 1 x Ir) - 1 piece - Auxiliary contacts (1xNO/NC, 1xSDE) - 2 pieces | kos | 6
e. | NSXm TM040F kompletni fiksni tripolni odklopnik (MCCB),nazivni tok 40A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu (do 415V), z vgrajeno opremo: - Elektro-mehanska zaščitna enota 40 TMD (nastavljiva od 0.7 to 1 x Ir) - 1kos - Pomožni kontakti (1xNO/NC, 1xSDE) - 2kosa | NSXm TM040F complete fixed three-pole circuit breaker (MCCB), rated current 40A, tripping current KS Icu=50kA, service current KS Ics=100% Icu (up to 415V), with built-in accessories: - Electro-mechanical protection unit 40 TMD (adjustable from 0.7 to 1 x Ir) - 1 piece - Auxiliary contacts (1xNO/NC, 1xSDE) - 2 pieces | kos | 3
f. | NSXm TM025F kompletni fiksni tripolni odklopnik (MCCB),nazivni tok 25A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu (do 415V), z vgrajeno opremo: - Elektro-mehanska zaščitna enota 25 TMD (nastavljiva od 0.7 to 1 x Ir) - 1kos - Pomožni kontakti (1xNO/NC, 1xSDE) - 2kosa | NSXm TM025F complete fixed three-pole circuit breaker (MCCB), rated current 25A, tripping current KS Icu=50kA, service current KS Ics=100% Icu (up to 415V), with built-in accessories: - Electro-Mechanical Protection Unit 25 TMD (adjustable from 0.7 to 1 x Ir) - 1 piece - Auxiliary contacts (1xNO/NC, 1xSDE) - 2 pieces | kos | 3
g. | EasyLogic PM2230, Merilnik moči in energije, kot na primer tip: PM2230 | EasyLogic PM2230, Power and energy meter, as for example type: PM2230 | kos | 1
h. | Odvodnik prenapetosti kot na primer tipa 2, 3P + N, Up=1.5kV, In (8/20)=20kA, Imax(8/20)=65kA, pom. kontakt indikacije stanja, kot na primer tip: kot na primer tip iPRD65r | Surge arrester as e.g. type 2, 3P+N, Up=1.5kV, In (8/20)=20kA, Imax(8/20)=65kA, auxiliary contact status indication as e.g. type: as e.g. type iPRD65r | kos | 1
i. | Varovalčno stikalo ISFT160, 160A, DIN NH00, 3 p, z varovalkami 3x80A + Nadzor varovalk FuPacT ISFT160 - 1 NO + 1 NC, kot na primer tip: 480803+LV480810 | Fuse switch ISFT160, 160A, DIN NH00, 3 p, with 3x80A fuses + Fuse monitoring FuPacT ISFT160 - 1 NO + 1 NC, as for example type: 480803+LV480810 | kos | 1
j. | Inštalacijski odklopnik, 50kA, iC60N, 1P, 0.5A, C + Pomožni kontakt iOF/SD+OF, iC60, kot na primer tip: A9F74170+A9A26929 | Circuit breaker, 50kA, iC60N, 1P, 0.5A, C + Auxiliary contact iOF/SD+OF, iC60, e.g. type: A9F74170+A9A26929 | kos | 1
k. | Inštalacijski odklopnik, 50kA, iC60N, 3P, 0.5A, C + Pomožni kontakt iOF/SD+OF, iC60, kot na primer tip: A9F74370+A9A26929 | Circuit breaker, 50kA, iC60N, 3P, 0.5A, C + Auxiliary contact iOF/SD+OF, iC60, e.g. type: A9F74370+A9A26929 | kos | 1
l. | Inštalacijski odklopnik, 36kA, NG125H, 16A, 3P, C + Pomožni kontakti - 2 OC - 6 A - 220..240 V - za NG125, kot na primer tip: 18724+19071 | Circuit breaker, 36kA, NG125H, 16A, 3P, C + Auxiliary contacts - 2 OC - 6 A - 220..240 V - for NG125, as for example type: 18724+19071 | kos | 5
m. | Inštalacijski odklopnik, 36kA, NG125H, 10A, 1P, C + Pomožni kontakti - 2 OC - 6 A - 220..240 V - za NG125, kot na primer tip: 18705+19071 | Circuit breaker, 36kA, NG125H, 10A, 1P, C + Auxiliary contacts - 2 OC - 6 A - 220..240 V - for NG125, as for example type: 18705+19071 | kos | 5
n. | Signalna svetilka na vratih LED, 24VDC, zelena, kot na primer tip: XB4BVB3 | LED door signal lamp, 24VDC, green, e.g. type: XB4BVB3 | kos | 3
o. | Signalna svetilka na vratih LED, 24VDC, rdeča, kot na primer tip: XB4BVB4 | LED door signal lamp, 24VDC, red, e.g. type: XB4BVB4 | kos | 1
p. | kot na primer tipka za preizkus svetilk, 1NO, modra, kot na primer tip: Harmony, XB4 XB4BA61 | such as lamp test button, 1NO, blue, such as type: Harmony, XB4 XB4BA61 | kos | 1
q. | Tokovni merilni transformator, 600/5A, Ue=720 V, sf <= 5 (za Ip od 40 do 4000 A), IP20, IEC 61869-2, kot na primer tip: MET SE CT 600/5A | Current measuring transformer, 600/5A, Ue=720 V, sf <= 5 (for Ip from 40 to 4000 A), IP20, IEC 61869-2, as for example type: MET SE CT 600/5A | kos | 7
r. | Sistemska svetilka LED, brez vtičnice, dolžina: 437 mm, vhodna napetost: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, kot na primer tip: 2500200, proizvod: Rittal | LED system luminaire, without socket, length: 437 mm, input voltage: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, e.g. type: 2500200, product: Rittal | kos | 1
s. | Povezovalni kabel, kot na primer tip: 2500400, proizvod: Rittal | Connection cable, e.g. type: 2500400, product: Rittal | kos | 1
t. | Vtičnica za DIN letev, kot na primer tip: 2506120, proizvod: Rittal | DIN rail socket, e.g. type: 2506120, product: Rittal | kos | 1
u. | Vratno stikalo za LED sistemsko luč, kot na primer tip: 2500460, proizvod: Rittal | Door switch for LED system light, e.g. type: 2500460, product: Rittal | kos | 1
v. | Enonadstropna vzmetna vrstna sponka, kot na primer tip: ZDU 2.5, proizvod: Weidmüller | Single-deck spring-type row clamp, e.g. type: ZDU 2.5, product: Weidmüller | kos | 50
w. | Enonadstropna vijačna sponka, kot na primer tip: WDU 4, proizvod: Weidmüller | Single-deck screw clamp, e.g. type: type WDU 4, product: Weidmüller | kos | 4
z. | Merilna sponka z vzdolžno ločitvijo in dvema vzporednima mostičema, kot na primer tip: WTL 6/1/STB, proizvod: Weidmüller | Measuring clamp with longitudinal separation and two parallel bridges, e.g. type: WTL 6/1/STB, product: Weidmüller | kos | 14
4.39 | Polje DEA_P1_TP_RG1_2 | Field DEA_P1_TP_RG1_2 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 650x2050x400mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : PrismaSeT P, proizvod: Schneider Electric | Cabinet dimensions 650x2050x400mm (WxHxD), made of powder-coated RAL9001 steel sheet, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : PrismaSeT P, product : Schneider Electric | kpl | 1
4.40 | Polje DEA_P1_TP_RG1_3 | Field DEA_P1_TP_RG1_3 |  |  | kpl | 1 |  | 0
a. | Omara dimenzij 650x2050x400mm (ŠxVxG), iz jeklene pločevine prašno barvane v RAL9001, z montažnim in pritrdilnim materialom vključno s kanali za ožičenje, DIN letvami, označevalnim materialom, zbiralkami ipd. Kot na primer tip : PrismaSeT P, proizvod: Schneider Electric | Cabinet dimensions 650x2050x400mm (WxHxD), made of powder-coated RAL9001 steel sheet, with mounting and fixing material including wiring channels, DIN mouldings, marking material, collectors, etc. Such as type : PrismaSeT P, product : Schneider Electric | kpl | 1
b. | NSX 400F kompaktni tripolni odklopnik (MCCB),nazivni tok 400A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, z vgrajeno opremo: - Mikroprocesorska zaščitna enoto Micrologic 2.3, brez meritev ALI - 1kos - Pomožni kontakti (1xNO/NC, 1xSDE) - 2kosa - Zaščitni pokrovi za sponke, dolgi - 1kos - izvedba - fiksna | NSX 400F compact three-pole circuit breaker (MCCB), rated current 400A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, with built-in accessories: - Micrologic 2.3 microprocessor protection unit, without ALI measurements - 1 piece - Auxiliary contacts (1xNO/NC, 1xSDE) - 2 pieces - Protective covers for staples, long - 1 piece - design - fixed | kos | 4
c. | NSX 250F kompaktni tripolni odklopnik (MCCB),nazivni tok 250A, izklopilni tok KS Icu= 50kA, servisni tok KS Ics=100% Icu, z vgrajeno opremo: - Mikroprocesorska zaščitna enoto Micrologic 2.2, brez meritev ALI - 1kos - Pomožni kontakti (1xNO/NC, 1xSDE) - 2kosa - Zaščitni pokrovi za sponke, dolgi - 1kos - izvedba - fiksna | NSX 250F compact three-pole circuit breaker (MCCB), rated current 250A, tripping current KS Icu=50kA, service current KS Ics=100% Icu, with built-in accessories: - Micrologic 2.2 microprocessor protection unit, without ALI measurements - 1 piece - Auxiliary contacts (1xNO/NC, 1xSDE) - 2 pieces - Protective covers for staples, long - 1 piece - design - fixed | kos | 1
d. | Inštalacijski odklopnik, 36kA, NG125H, 16A, 3P, C + Pomožni kontakti - 2 OC - 6 A - 220..240 V - za NG125, kot na primer tip: 18724+19071 | Circuit breaker, 36kA, NG125H, 16A, 3P, C + Auxiliary contacts - 2 OC - 6 A - 220..240 V - for NG125, as for example type: 18724+19071 | kos | 3
e. | Inštalacijski odklopnik, 36kA, NG125H, 10A, 1P, C + Pomožni kontakti - 2 OC - 6 A - 220..240 V - za NG125, kot na primer tip: 18705+19071 | Circuit breaker, 36kA, NG125H, 10A, 1P, C + Auxiliary contacts - 2 OC - 6 A - 220..240 V - for NG125, as for example type: 18705+19071 | kos | 1
f. | Inštalacijski odklopnik, 36kA, NG125H, 16A, 1P, C + Pomožni kontakti - 2 OC - 6 A - 220..240 V - za NG125, kot na primer tip: 18706+19071 | Circuit breaker, 36kA, NG125H, 16A, 1P, C + Auxiliary contacts - 2 OC - 6 A - 220..240 V - for NG125, as for example type: 18706+19071 | kos | 3
g. | Inštalacijski odklopnik, 36kA, NG125H, 10A, 1P, C + Pomožni kontakti - 2 OC - 6 A - 220..240 V - za NG125, kot na primer tip: 18705+19071 | Circuit breaker, 36kA, NG125H, 10A, 1P, C + Auxiliary contacts - 2 OC - 6 A - 220..240 V - for NG125, as for example type: 18705+19071 | kos | 1
h. | Sistemska svetilka LED, brez vtičnice, dolžina: 437 mm, vhodna napetost: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, kot na primer tip: 2500200, proizvod: Rittal | LED system luminaire, without socket, length: 437 mm, input voltage: 100 V - 240 V, 1~, 50 Hz/60 Hz, 900 lm, 11W, e.g. type: 2500200, product: Rittal | kos | 1
i. | Povezovalni kabel, kot na primer tip: 2500400, proizvod: Rittal | Connection cable, e.g. type: 2500400, product: Rittal | kos | 1
j. | Vratno stikalo za LED sistemsko luč, kot na primer tip: 2500460, proizvod: Rittal | Door switch for LED system light, e.g. type: 2500460, product: Rittal | kos | 1
k. | Enonadstropna vzmetna vrstna sponka, kot na primer tip: ZDU 2.5, proizvod: Weidmüller | Single-deck spring-type row clamp, e.g. type: ZDU 2.5, product: Weidmüller | kos | 16
l. | Enonadstropna vijačna sponka, kot na primer tip: WDU 4, proizvod: Weidmüller | Single-deck screw clamp, e.g. type: type WDU 4, product: Weidmüller | kos | 16
| NN STIKALNI BLOKI IN RAZDELILNIKI | LV SWITCHGEAR BLOCKS AND SWITCHGEAR DISTRIBUTORS | [5 empty] | 0

## 3.3.5_UPS
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.3 | ELEKTRO DELA | ELECTRICAL WORKS
3.3.5 | BREZPREKINITVENO NAPAJANJE (UPS) | UNINTERRUPTIBLE POWER SUPPLY (UPS) | [5 empty] | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description |  |  | EM | Količina | Cena/EM | Cena
5 | BREZPREKINITVENO NAPAJANJE (UPS) | UNINTERRUPTIBLE POWER SUPPLY (UPS)
5.1 | Naprava za brezprekinitveno napajanje (UPS) | Uninterruptible Power Supply (UPS) |  |  | kpl | 1 |  | 0
a. | Naprava za brezprekinitveno napajanje (UPS) v vertikalni modularni redundantni izvedbi N+X, vgrajeni "plug-in, hot swap" močnostni moduli po 25 kW z izhodnim faktorjem moči 1, skupne nazivne moči v možni končni konfiguraciji 175 kVA/175 kW + 1 redundantni modul, v ON - line IGBT, visoko učinkoviti 3 nivojski tehnologiji (izkoristek do 96,5%) skladno z EN62040-3 (VFI-SS-111) ter 13 minutno avtonomijo pri obremenitvi 125kW, akumulatorji vgrajeni minimalno v dveh nizih. | Uninterruptible Power Supply (UPS) in vertical modular redundant N+X design, plug-in, hot swap power modules of 25 kW each with an output power factor of 1, total rated power in a possible final configuration of 175 kVA/175 kW + 1 redundant module, in ON - line IGBT, high efficiency 3 level technology (efficiency up to 96,5%) in accordance with EN62040-3 (VFI-SS-111) and 13 minutes autonomy at a load of 125 kW, batteries installed in a minimum of two arrays.
b. | Sistemska omara mora imeti vgrajene kontaktorje za zaščito pred povratnim napajanjem UPS-a v omrežje. UPS sistem mora biti pripravljen tudi za možnost priključitve Li-Ion akumulatorjev. Arhitektura modularnega UPS sistema mora omogočati avtomatsko odključitev posameznega modula od celotnega sistema z galvansko ločitvijo tako na vhodu kot na izhodu modula. Sistem mora omogočati menjavo modulov na uporabniku prijazen način tako, da pri menjavi modula ni potrebe po izvedbi posebnih ukazov bodisi na modulu samem bodisi na nadzornem panelu (menjava poteka po sistemu plug-out in plug-in brez dodatnih intervencij, ukazov ali nastavitev parametrov). Modul in sistem morajo biti izvedeni na način, ki omogoča samodejno prilagoditev programske opreme modula v primeru, ko se ta razlikuje od trenutne različice v sistemu. Sistem mora ob vstavitvi novega ali dodatnega modula izvesti avtomatsko in samodejno testiranje modula. V primeru neuspešnega testa mora sistem sam poskrbeti, da modul ni električno vključen v sistem. | The system cabinet shall have built-in contactors to protect the UPS against back-feeding into the mains. The UPS system must also be able to connect Li-Ion batteries. The architecture of the modular UPS system shall allow automatic isolation of a single module from the whole system by galvanic isolation at both the input and output of the module. The system shall allow changing modules in a user-friendly way, so that no special commands are needed to change modules, either on the module itself or on the control panel (plug-out and plug-in change without any additional interventions, commands or parameter settings). The module and the system must be implemented in a way that allows the module software to be automatically adapted in case it differs from the current version in the system. When a new or additional module is inserted, the system shall automatically and automatically test the module. In the event of a failed test, the system shall ensure that the module is not electrically connected to the system.
| UPS sistem v začetni konfiguraciji sestavlja: | In its initial configuration, a UPS system consists of:
a. | Sistemska omara za vključitev modulov do nazivne moči 200 kVA/kW, ki mora biti opremljeno z vhodnim, izhodnim in ročnim servisnim bypas stikalom. | System cabinet for the integration of modules up to a rated power of 200 kVA/kW, which shall be equipped with an input, output and manual service bypass switch. | kos | 1
b. | Vgrajeni kontaktorji znotraj UPS naprave za zaščito pred povratnim napajanjem. | Built-in contactors inside the UPS device to protect against power back-up.
c. | Dvojni dovod, posebej za usmerniški del, posebej za bypas del. | Dual inlet, separately for the rectifier part, separately for the bypass part.
d. | Vgrajeni močnostni moduli po 25 kW stopnjah za zagotavljanje napajanja 125 kVA/kW porabnikov + 1x redundantni modul 25 kW | Built-in power modules in 25 kW stages to provide power to 125 kVA/kW consumers + 1x 25 kW redundant module | kos | 6
e. | Akumulatorski kabineti z vgrajenimi akumulatorji z dolgo življenjsko dobo 10- 12 let za avtonomijo 13 minut pri obremenitvi 125 kW. | Battery cabs with built-in long-life batteries 10- 12 years for 13 minutes autonomy at 125 kW load. | kos | 1
f. | Vgrajen komunikacijski vmesnik SNMP/WEB za daljinski nadzor UPS naprave in nastavitve »shutdown« procedur različnih operacijskih sistemov, obvezna skladnost vmesnika z varnostnim certifikatom po ISO27002:2022 | Built-in SNMP/WEB communication interface for remote control of the UPS device and setting of "shutdown" procedures of different operating systems, mandatory interface compliance with ISO27002:2022 security certification | kos | 1
g. | Mrežni elektronski bypas v "plug-in, hot swap" tehnologiji za preklop celotnega modularnega UPS sistema na pomožno mrežo, zamenljiv tudi v delovanju sistema, | Grid electronic bypass in "plug-in, hot swap" technology for switching the entire modular UPS system to the auxiliary grid, also interchangeable in system operation, | kos | 1
| Tehnične zahteve za UPS sistem: | Technical requirements for the UPS system:
a. | Vhodna napetost 3x400V + N, | Input voltage 3x400V + N,
b. | toleranca vhodne napetosti med 340 V do 480 V (+20 /-15 %) | input voltage tolerance between 340 V and 480 V (+20 /-15%)
c. | vhodni faktor moči ≥ 0,99, | input power factor ≥ 0.99,
d. | vhodna frekvenca 50/60 Hz ±10%, | input frequency 50/60 Hz ±10%,
e. | popačenje vhodnega toka THDI pri polnem bremenu <1,5%, | tHDI input current distortion at full load <1.5%,
f. | Izhodna napetost 3x400V + N ±1% (izberljivo 380/400/415V), | Output voltage 3x400V + N ±1% (selectable 380/400/415V),
g. | tolerance izhodne napetosti ±1% pri statičnem bremenu, pri dinamičnem bremenu skladno z VFI-SS-111, | output voltage tolerances ±1% for static load, for dynamic load according to VFI-SS-111,
h. | izhodni faktor moči 1, | power output factor 1,
i. | izhodna frekvenca 50 Hz ±0.05 % (v avtonomnem delovanju) | output frequency 50 Hz ±0.05% (in autonomous operation)
j. | skupno napetostno popačenje < 1 % (linearni porabniki), < 3 % (nelinearni porabniki v skladu z lEC 62040-3), | total voltage distortion < 1 % (linear consumers), < 3 % (non-linear consumers according to lEC 62040-3),
k. | kratkostična sposobnost inverterja do 3xIn, | short-circuit capability of the inverter up to 3xIn,
l. | zmožnost preobremenitve inverterja ob mrežni napetosti 125% za 10 minut, 150% za 1 minuto, | inverter overload capability at line voltage 125% for 10 minutes, 150% for 1 minute,
m. | Srednji čas do odpovedi močnostnega modula (MTBF) >1.000.000 h | Mean Time to Failure (MTBF) >1,000,000 h
n. | Izkoristek celotnega sistema v On-line režimu delovanja do 96,5 %, v Eco načinu delovanja do 99,3 % | System efficiency up to 96.5% in On-line mode, 99.3% in Eco mode
o. | Maksimalna toplotna disipacija v najslabših pogojih obratovanja ob znižani vhodni mreži, obremenitvi 125 kW in polnjenju akumulatorjev do 4,6 kW. | Maximum thermal dissipation under worst-case operating conditions with reduced input grid, 125 kW load and battery charging up to 4.6 kW.
p. | Temperaturno področje delovanja od 0ºC do +40ºC ( od 15ºC do 25ºC za doseganje najdaljše življenjske dobe akumulatorjev), | Operating temperature range from 0ºC to +40ºC (15ºC to 25ºC for maximum battery life),
q. | Hrupnost na razdalji 1 m; <56 dBA | Noise at 1 m; <56 dBA
r. | Vlažnost 0-95% (brez kondenzacije), | Humidity 0-95% (non-condensing),
s. | Stopnja IP zaščite - IP20 | IP degree of protection - IP20
| Upravljanje in komunikacija: | Governance and communication:
a. | Napredni barvni grafični LCD zaslon na dotik za odčitavanje delovnih parametrov na napravi | Advanced colour graphic LCD touchscreen for reading operating parameters on the device
| Dimenzije: | Dimensions:
a. | UPS sistemska omara : šxgxv 600x890x2000, masa 450 kg | UPS system cabinet : wxwxh 600x890x2000, weight 450 kg
b. | Akumulatorska omara: šxgxv 810x890x1990 , skupna masa 1700 kg | Battery cabinet: wxwxh 810x890x1990 , total weight 1700 kg
| Akumulatorji: | Batteries:
a. | Vgrajeni morajo biti ventilsko regulirani (VRLA) 12V akumulatorji z dolgo življenjsko dobo 10-12 klet po Eurobat 2015, svinčeni hermetično zaprti, brez vzdrževanja, proizvodnje po zahtevah standarda ISO 9001 in ISO 14001, | Valve regulated (VRLA) 12V batteries with a long life of 10-12 kyr according to Eurobat 2015, lead sealed, maintenance free, production according to ISO 9001 and ISO 14001 requirements shall be installed,
b. | Vgrajen sistem za doseganje maksimalne življenjske dobe akumulatorjev na osnovi inteligentnega polnjenja akumulatorjev, | Built-in system to maximise battery life based on intelligent battery charging,
| Dobava, montaža in zagon: | Delivery, installation and commissioning:
a. | Dobava, montaža, postavitev in priključitev naprave na predviden prostor v objektu, na pripravljene električne instalacije, | Supply, installation, set-up and connection of the appliance to the intended space in the building, to the prepared electrical installations,
b. | Nastavitve naprave, zagon in preizkus delovanja, | Setting up, starting and testing the device,
c. | Izdelava poročila o zagonu UPS naprave, | Preparation of a report on the commissioning of the UPS device,
d. | Usposabljanje uporabnikov sistema, | Training for system users,
e. | Navodila za uporabo in vzdrževanje v slovenskem jeziku. | Operating and maintenance instructions in Slovenian.
| Standardi: | Standards:
a. | Varnostni EN 62040-1, EMC EN 62040-2 (C2), tip in lastnosti EN 62040-3 (VFI-SS-111), | Safety EN 62040-1, EMC EN 62040-2 (C2), type and characteristics EN 62040-3 (VFI-SS-111),
b. | Skladnost izdelka direktivam ROHS, standardom IEC62040-4, ISO14001, ISO14040 | Product compliance to ROHS, IEC62040-4, ISO14001, ISO14040
c. | Seizmična skladnost UBC:1997, IEC 60068-2-57:2013 za potresno stopnjo 4 (ob vgrajeni dodatni opremi) | Seismic compliance UBC:1997, IEC 60068-2-57:2013 for seismic level 4 (with optional equipment installed)
d. | Certifikat CE in dokumentacija o tehnični ustreznosti, | CE certificate and technical conformity documentation,
e. | Certifikat neodvisne institucije o učinkovitosti naprave, | Certificate from an independent institution on the efficiency of the device,
f. | Certifikat neodvisne institucije za MTBF (MTTF) močnostnega modula | Independent Institution Certificate for the MTBF (MTTF) of the power module
g. | Ponudnik opreme mora imeti poslovanje urejeno skladno s standardom ISO9001, kar dokazuje z ustreznim veljavnim certifikatom. | The equipment supplier must have an ISO9001 compliant business, evidenced by an appropriate valid certificate.
| Kot na primer tip: Modulys GP2.0 200, proizvod: SOCOMEC | Such as type: modulys GP2.0 200, product: SOCOMEC
| BREZPREKINITVENO NAPAJANJE (UPS) | UNINTERRUPTIBLE POWER SUPPLY (UPS) | [5 empty] | 0

## 3.3.6_DEA
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.3 | ELEKTRO DELA | ELECTRICAL WORKS
3.3.6 | DIESEL ELEKTRIČNI AGREGAT (DEA) | DIESEL ELECTRIC POWER UNIT (DEA) | [5 empty] | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description |  |  | EM | Količina | Cena/EM | Cena
6 | DIESEL ELEKTRIČNI AGREGAT (DEA) | DIESEL ELECTRIC POWER UNIT (DEA)
| Opis delovanja sistema | Description of how the system works
| Dizel električna agregat z dizel motorjem in sinhronim generatorjem ter vso ostalo pomožno opremo mora omogočati varno in zanesljivo delovanje DEA v sistemu rezervnega napajanja z električno energijo. | The diesel-electric genset with diesel engine and synchronous generator and all other auxiliary equipment shall enable the DEA to operate safely and reliably in a back-up power supply system.
| Vsa dobaljena oprema mora biti tipsko preizkušena ter imeti ustrezne CE certifikate. | All equipment supplied must be type-tested and have the relevant CE certificates.
| Dizel električna agregat bo postavljen v prostor objekta, zato mora protihrupno ohišje zagotavljati ustrezno dušenje hrupa skladno z direktico9 2000/14/EC ter ustrezati max. nivoju hrupa 68DbA/7m. | The diesel-electric generator will be located within the building, therefore the noise enclosure must provide adequate noise attenuation in accordance with Directive 2000/14/EC and comply with a maximum noise level of 68DbA/7m.
| DEA sistem mora zagotavljati napajanje z rezervno električno energijo v slučaju izpada primarnega mrežnega vira z avtomatskim prevzemom porabnikov obeh objektov in obratno. | The DEA system must provide backup power in the event of a failure of the primary grid source, with automatic takeover of the consumers of both facilities and vice versa.
| Poleg paralelnega delovanja DEA enote z mrežo mora sistem omogočati tudi sinhronizirane brezprekinitvene preklope med mrežnim in agregatskim virom v smislu sledečih funkcij: - Ob izpadu mrežnega vira in avtomatskem prevzemu porabnikov s strani agregata, se mora ob povratku mrežnega vira izvršiti preklop nazaj na mrežni vir brez prekinitve s pomočjo sinhronizacije agregata na mrežni vir. Omogočeno mora biti trejno paralelno obratovanje z omrežjem in oddajanje električne energije v omrežje. - Sistem mora omogočati bremensko testiranje agregata z avtomatskimi sinhroniziranimi brezprekinitvenimi preklopi v obe smeri (preklop iz mrežnega vira na generatorski vir in obratno) brez motenja porabnikov po sistemu mehkega obremenjevanja in razbremenjevanja po časovno linearnem poteku. - Sistem za brezprekinitvene preklope mora biti poleg ustreznih zaščit opremljen še s prikazovalnikom sinhronizacije z jasnim prikazom frekvenčne in napetostne diference, ter razliko faznega kota. | In addition to the parallel operation of the DEA unit with the grid, the system shall also allow synchronised failover between the grid and the aggregate source in terms of the following functions: - In the event of a failure of the grid source and automatic takeover of the consumers by the genset, a switch-back to the grid source shall be carried out without interruption by synchronisation of the genset to the grid source when the grid source returns. Three-way parallel operation with the grid and the supply of electricity to the grid shall be possible. - The system shall allow load testing of the generator set by automatic synchronised interrupted switching in both directions (switching from the grid source to the generator source and vice versa) without disturbing the consumers by a system of soft load and load shedding according to a time linear path. - In addition to appropriate protection, the system for interrupted switching shall be equipped with a synchronisation display clearly indicating the frequency and voltage difference, and the phase angle difference.
| Mrežni vir mora biti opremljen s setom zaščit, ki omogočajo hitri odklop mrežnega vira v času paralelnega spoja z generatorjem vprimeru mrežne anomalije (pod/nad napetost, pod/nad frekvenca, nenadni zamik vektorskega kota /dt, nenadna sprememba frekvence df/dt, smerna zaščita). | The network source shall be equipped with a set of protections that allow the rapid disconnection of the network source during a parallel connection with the generator in the event of a network anomaly (under/over voltage, under/frequency, sudden vector angle offset /dt, sudden frequency change df/dt, directional protection).
| Prav tako mora biti sistem opremljen z vsemi funkcijami za vključitev v Virtualno elektrarno (VE) - električna meritev proizvodnega vira po zahtevah SONDSEE in priprava avtomatike za priklop katerega koli agregatorja. Ponudnik mora predložiti podroben tehnični opis integracije v VE. | The system must also be equipped with all the functions to integrate into the Virtual Power Plant (VPP) - electrical metering of the generating source according to SONDSEE requirements and preparation of the automation to connect any aggregator. The tenderer must provide a detailed technical description of the integration into the VE.
| Obratovalni pogoji na mestu vgradnje | Operating conditions at the installation site
| Nadmorska višina: 162m | Altitude: 162m
| Temperaturno območje: -25°C do +40°C | Temperature range: -25°C to +40°C
| Relativna vlažnost: od 5 % do 100 % | Relative humidity: 5% to 100%
| Zračni tlak: od 900 mbar do 1100 mbar | Air pressure: 900 mbar to 1100 mbar
6.1 | DEA naprava kot na primer P450-2, FG WILSON ali enakovredno | DEA device such as P450-2, FG WILSON or equivalent |  |  | kpl | 1 |  | 0
| Nazivna (trajna – Prime Power) moč minimalno 400 kVA /320 kW, pri cosfi=0,8 kVA in max. temperaturi okolice 40°C, dovoljena 10 % preobremenitev za 1 uro na vsakih 12ur. | Rated (sustained - Prime Power) power minimum 400 kVA /320 kW, at cosfi=0,8 kVA and max. ambient temperature 40°C, 10% overload allowed for 1 hour every 12 hours.
| Nazivna medfazna napetost: 400V | Nominal interphase voltage: 400V
| Nazivna fazna napetost: 230 V | Nominal phase voltage: 230 V
| Nazivna frekvenca: 50 Hz | Nominal frequency: 50 Hz
| Nazivni faktor moči: 0,8 | Nominal power factor: 0,8
| Nazivno število vrtljajev: 1500 /min | Rated speed: 1500 /min
| Prevzem bremena po izpadu mreže v maks. 15s. | Load recovery after net failure in max. 15s.
| Statične in dinamične karakteristike: ISO 8528, Class G2 | Static and dynamic characteristics ISO 8528, Class G2
| Naprava mora omogočati sinhronizirane brezprekinitvene preklope med mrežnim in agregatskim virom v smislu naslednjih funkcionalnosti: - Ob izpadu mrežnega vira sledi samodejni zagon agregata in napajanje električnih porabnikov iz agregata. Ob povratku mrežnega vira se samodejno izvrši preklop električnih porabnikov na omrežni vir brez prekinitve, v načinu mehkega razbremenjevanja agregata (1-2% moči bremena / sek, kontrolirano prelivanje obremenitve na mrežni vir glede na trenutni odjem preklopnega mesta). - Bremensko otočno testiranje agregata s sinhroniziranim preklopom iz mrežnega na agregatsko napajanje in obratno se vrši brez motenj električnih porabnikov v načinu mehkega obremenjevanja in razbremenjevanja agregata (1-2% moči bremena / sek, kontrolirano prelivanje obremenitve na agregatski ali mrežni vir glede na trenutni odjem preklopnega mesta). - Sistem za brezprekinitveni preklop mora biti poleg ustreznih zaščit opremljen še s prikazovalnikom sinhronizacije z jasnim prikazom frekvenčne in napetostne diference, ter razliko faznega kota. | The device shall be capable of synchronised failover between the grid and aggregate sources in terms of the following functionalities: - When the grid source fails, the genset automatically starts up and supplies the electrical consumers from the genset. When the grid source returns, the electrical consumers are automatically switched over to the grid source without interruption, in soft load shedding mode (1-2% of the load power/sec, controlled load shedding to the grid source according to the current demand of the switching point). - Load island testing of the genset with synchronised switching from grid to genset supply and vice versa is performed without disturbing the electrical consumers in soft load and load shedding mode (1-2% of load power/sec, controlled load shedding to the genset or grid source according to the current load demand of the switching point). load shedding to the genset or grid source according to the current load demand of the switching point). - In addition to the appropriate protections, the fail-safe system shall be equipped with a synchronisation display clearly indicating the frequency and voltage differential, and the phase angle difference.
| Generator in vsi kovinski deli sklopa morajo biti ozemljeni. | The generator and all metal parts of the assembly must be earthed.
a. | Pogonski motor: kot na primer 2206D-E13TAG3A, proizvajalec Perkins ali enakovredno | Drive motor: such as 2206D-E13TAG3A, manufactured by Perkins or equivalent | 1 | kpl
| 4-taktni dizelski motor z direktnim vbrizgom in turbinskim polnilnikom | 4-stroke direct-injection diesel engine with turbocharger
| "Gross" moč motorja (v režimu "Prime Power"): ≥258kW | "Gross" engine power (in "Prime Power" mode): ≥258kW
| Število vrtljajev: 1500 /min | Speed: 1500 /min
| Nastavitveno področje vrtljajev: največ +/- 5% | Adjustable speed range: maximum +/- 5%
| Elektronska regulacija vrtljajev, nadzor nad številom vrtljajev: skladno z ISO 8528, Class G2 | Electronic speed control, speed control: according to ISO 8528, Class G2
| Prevzem 100% bremena po izpadu mreže v: maks. 15 s | 100% load recovery after net failure in: max. 15 s
| Možnost diagnosticiranja, parametriranja in spreminjanja delovanja motorja na PC | Ability to diagnose, parameterise and modify engine operation on a PC
| Ponudnik mora priložiti originalno dokumentacijo ponujenega motorja! | The original documentation of the offered engine must be attached!
| Dieselski motor mora biti namenjen za uporabo dieselskega goriva D2 (plinskega olja), ki je skladen s standardom EN 590. | The diesel engine must be designed to use D2 diesel fuel (gas oil) complying with EN 590.
| Emisije izpušnh plinov morajo ustrezati standardu Stage EUIIIa. | Exhaust emissions must comply with Stage EUIIIa.
| Ponudnik mora v ponudbi priložiti tehnično dokumentacijo proizvajalca s katero dokazuje izpolnjevanje tehničnih zahtev! | The tenderer must enclose the manufacturer's technical documentation in the tender to prove that the technical requirements are met!
b. | Generator: kot na primer Proizvajalec Leroy Somer ali enakovredno | Generator: such as Leroy Somer or equivalent | 1 | kpl
| Nazivna moč (Prime Power): 400kVA/320kW, Class H rise BR | Rated power (Prime Power): 400kVA/320kW, Class H rise BR
| Nazivna medfazna napetost: 400V | Nominal inter-phase voltage: 400V
| Nazivna fazna napetost: 230V | Nominal phase voltage: 230V
| Nazivna frekvenca: 50 Hz | Nominal frequency: 50 Hz
| Stopnja zaščite najmanj IP23 | Protection rating at least IP23
| Regulacija napetosti največ +/- 0,5 % | Voltage regulation max +/- 0,5 %
| Dovoljena preobremenitev: 10% za 1 uro na vsakih 12 ur. | Permitted overload: 10% for 1 hour every 12 hours.
| Vzbujanje in napetostna regulacija: arep in napetostna regulacijo vseh treh faz | Excitation and voltage regulation: arep and voltage regulation of all three phases
| Natančnost statične regulacije napetosti: maks. +/- 0,5 % | Static voltage regulation accuracy: max. +/- 0,5 %
| THD (LL/LN): <= 4% | THD (LL/LN): <= 4%
| Izolacijski razred statorskih navitij: H Class | Insulation class of stator windings: H Class
| Prirastek temperature ob trajni nazivni obremenitvi ekvivalenten prirastku temperature razreda izolacije F | Temperature increment at continuous rated load equivalent to the temperature increment of insulation class F
| Generatorski priključek je opremljen z močnostnim odklopnikom za zaščito generatorja pred preobremenitvijo oz. kratkim stikom. Odklopnik mora biti opremljen s pomožnimi kontakti za signalizacijo položaja. | The generator connection shall be equipped with a circuit breaker to protect the generator against overload or short circuit. The circuit breaker shall be equipped with auxiliary contacts to indicate the position.
| Stopnja radijske interference skladno: s Pravilnikom o elektromagnetni združljivosti EMC (ponudnik navede uporabljene standarde) | Radio interference level in accordance with: the EMC Regulation (the supplier shall specify the standards used)
| Ponudnik mora v ponudbi priložiti tehnično dokumentacijo proizvajalca s katero dokazuje izpolnjevanje tehničnih zahtev! | The tenderer must enclose the manufacturer's technical documentation to prove that the technical requirements are met!
c. | Zagonski akumulatorji z avtomatskim polnilnikom akumulatorjev | Starting batteries with automatic battery charger | 1 | kpl
| Zagonski akumulatorji | Starting batteries
| Napetost akumulatorja: 24V | Battery voltage: 24V
| Kapaciteta akumulatorja: zagotavlja najmanj 10 zaporednih zagonov | Battery capacity: provides at least 10 consecutive starts
| Elektrolit: žveplena kislina | Electrolyte: sulphuric acid
d. | Akumulatorski polnilnik s sistemom za nadzor zagonskih akumulatorjev | Battery charger with start-up battery monitoring system | 1 | kpl
| Inteligentni polnilnik startnih baterij 24VDC/10A s komunikacijskim portom RS485 Modbus RTU, prikaz izhodnih parametrov na HMI prikazovalniku. Tudi osnovni krmilnik agregata neodvisno od inteligentnega polnilnika stalno spremlja spodnjo in zgornjo napetostno mejo zagonskih baterij in alarmira povečan stalni tok. | Intelligent 24VDC/10A starting battery charger with RS485 Modbus RTU communication port, display of output parameters on HMI display. Also, the basic controller of the genset, independent of the intelligent charger, continuously monitors the lower and upper voltage limits of the starting batteries and alarms for increased continuous current.
e. | Električni grelnik pogonskega motorja | Electric heater for the drive motor | 1 | kpl
| Električni grelnik pogonskega motorja montiran na podnožje agregata. Vzdržuje ustrezno temperaturo in omogoča lažji zagon motorja. | Electric heater for the propulsion engine, mounted on the base of the generator set. Maintains the correct temperature and facilitates engine start-up.
f. | Rezervoar goriva | Fuel tank | 1 | kpl
| Dvoplaščni rezervoar goriva v podstavku uporabne kapacitete 880 litrov | Twin-walled fuel tank in base with a usable capacity of 880 litres
| Rezervoar je opremljen z zvezno meritvijo nivoja goriva. | The tank is equipped with a continuous fuel level gauge.
| Nivo se signalizira lokalno in daljinsko. | The level is signalled locally and remotely.
| Mora biti opremljen s sistemom za meritev porabe razreda natančnosti 1%. | It must be equipped with a consumption metering system with an accuracy of 1%.
g. | Ročna črpalka za črpanje motornega olja | Hand pump for pumping engine oil | 1 | kpl
| Ročna črpalka montirana na podnožje agregata omogoča črpanje starega motornega olja iz oljnega korita ob rednih vzdrževalnih pregledih. | A hand pump mounted on the base of the unit allows old engine oil to be pumped out of the oil sump during regular maintenance checks.
h. | Zvočno izolirano ohišje | Sound-insulated enclosure | 1 | kpl
| Zvočna izolacija ohišja mora zagotavljati naslednje mejne vrednosti na razdalji 7m: - 75% (Prime Power)=68dBA - 100% (Prome Power) = 69dBA | The sound insulation of the enclosure shall comply with the following limits at a distance of 7m: - 75% (Prime Power)=68dBA - 100% (Prome Power) = 69dBA
| Ohišje mora biti atestirano po direktivi EC 2000/14/EC. | The enclosure must be certified according to EC Directive 2000/14/EC.
| Max. dimenzije ohišja: 3787x1131x2156 mm (L x W x H) | Max. housing dimensions: 3787x1131x2156 mm (L x W x H)
| Vsi elementi za dušenje hrupa morajo biti vgrajeni v ohišju (dušilci na zajemu in izstopu zraka, dušilniki zvoka na izpuhu, ..) | All noise attenuation elements must be integrated in the enclosure (air intake and outlet silencers, exhaust silencers, etc.)
| Ohišje mora biti opremljeno z vratci, ki omogočajo enostaven dostop za potrebe servisiranja. Vsa vratca morajo biti opremljena s kljuko in ključavnico. | The enclosure shall be fitted with a door allowing easy access for servicing. All doors shall be fitted with a handle and lock.
| Ponudnik mora v ponudbi priložiti tehnično dokumentacijo proizvajalca s katero dokazuje izpolnjevanje tehničnih zahtev! | The tenderer must enclose the manufacturer's technical documentation to prove that the technical requirements are met!
6.2 | Komandna omara kot na primer KO DEAP450-2, Prinsis ali enakovredno | Command cabinet such as KO DEAP450-2, Prinsis or equivalent |  |  | kpl | 1 |  | 0
| V komandni omari se nahaja krmilni del, preklopni del se nahaja v NN razdelilnku. | The control part is located in the control cabinet, the switching part is located in the LV switchboard.
| Glavni krmilnik DEA enote mora biti industrijski modularni PLC krmilnik priznanega svetovnega proizvajalca. Pogeg modularnosti in razširljivosti mora omogočati povezljivost z nadrejenimi nadzornimi sistemi preko Modbus RTU komunikacijskega protokola ter preko Modbus TCP IP Ethernet protokola. Omogočati mora alarmiranje preko e-mail in SMS sporočil. Krmilnik naj bo opremljen z breznapetostnimi programabilnimi kontakti za prenos vsaj 16 različnih informacij. | The main controller of the DEA unit shall be an industrial modular PLC controller from a recognised worldwide manufacturer. It shall be modular and scalable, allowing connectivity to higher-level control systems via Modbus RTU communication protocol and Modbus TCP IP Ethernet protocol. It shall allow alarming via e-mail and SMS. The controller shall be equipped with voltage-free programmable contacts for the transmission of at least 16 different pieces of information.
| Omogočena mora biti signalizacija izklopa sončne elektrarne. | It must be possible to signal the switching off of the solar power plant.
| Glavni krmilnik mora omogočati: | The main controller must be able to:
| Samodejni zagon agregata ob izpadu omrežne napetosti | Automatic start-up of the generator in the event of a mains voltage failure
| Sinhronizacijo z omrežno napetostjo ob povratku | Synchronisation with mains voltage on return
| Ročno in samodejno krmiljenje mrežnega in generatorskega odklopnika | Manual and automatic control of mains and generator circuit breakers
| Ročni zagon in zaustavitev agregata | Manual start and stop of the generator
| Testni zagon agregata (bremensko testiranje agregata, paralelni način delovanja z mrežnim virom v namen brezprekinitvenih preklopov z mehkim načinom obremenjevanja ali razbremenjevanja) | Test run of the genset (load testing of the genset, parallel mode of operation with the grid source for the purpose of soft load or soft load shedding intermittent switching)
| Samodejni testni zagon agregata (uporabnik nastavi dan, uro in čas trajanja testa. Test se lahko izvede v prostem teku agregata ali pod obremenitvijo) | Automatic test run of the genset (the user sets the day, time and duration of the test. The test can be carried out at idle or under load)
| Regulacijo dizelskega električnega agregata | Regulating the diesel electric generator
| Merjenje električnih veličin dizelskega agregata: | Measuring the electrical quantities of a diesel generator set:
| Napetost generatorja (fazna in medfazna) | Generator voltage (phase and interphase)
| Frekvenca | Frequency
| Tok (posameznih faz) | Current (individual phases)
| Merjenje električnih veličin električnega omrežja: | Measuring the electrical quantities of an electricity network:
| Tok v vseh treh fazah | Current in all three phases
| Delovna moč | Working power
| Jalova moč | Futile power
| Faktor moči | Power factor
| Frekvenca | Frequency
| Napetost omrežja (fazna in medfazna) | Mains voltage (phase and inter-phase)
| Prikaz R.O.C.O.F., trenutna meritev in najvišje zabeleženo odstopanje | Display of R.O.C.O.F., current measurement and maximum recorded deviation
| Prikaz Vector shift, trenutna meritev in najvišje zabeleženo odstopanje | Vector shift display, current measurement and maximum recorded deviation
| Števec mrežne delovne energije | Network operating energy counter
| Števec mrežne jalove energije | Grid reactive energy counter
| Merjenje mehanskih veličin pogonskega motorja dizelskega agregata: | Measurement of mechanical quantities of a diesel power unit:
| Tlak motornega olja | Engine oil pressure
| Temperatura hladilne tekočine | Coolant temperature
| Nivo goriva | Fuel level
| Napetost zagonskih akumulatorjev | Starting battery voltage
| Merjenje električne moči dizelskega agregata: | Measuring the electrical power of a diesel generator set:
| Delovna moč (posameznih faz in Σ) | Operating power (individual phases and Σ)
| Faktor moči (posameznih faz in Σ) | Power factor (individual phases and Σ)
| Jalova moč (posameznih faz in Σ) | Reactive power (individual phases and Σ)
| Navidezna moč (posameznih faz in Σ) | Apparent power (individual phases and Σ)
| Beleženje statistike: | Recording statistics:
| Električna delovna energija (kWh) | Electric working energy (kWh)
| Električna jalovna energija (kWarh) | Electricity reactive power (kWarh)
| Število delovnih ur | Number of working hours
| Število zagonov pogonskega motorja | Number of starts of the propulsion engine
| Število delovnih ur pogonskega motorja do rednega servisa | Number of hours the propulsion engine is running before regular servicing
| Sinhronizacija: | Synchronisation:
| Fazni kot napetosti med mrežno in agregatsko napetostjo - sinhronoskop | Phase angle of the voltage between the grid voltage and the aggregate voltage - synchroscope
| Fazno napetost generatorja (L1) | Generator phase voltage (L1)
| Fazno napetost omrežja (L1) | Mains phase voltage (L1)
| Diferenca frekvenc | Frequency Difference
| Diferenca napetosti | Voltage differential
| Zaščite motor: | Protect the engine:
| Nastavljiva zaščita obratov motorja z zgornjo in spodnjo mejo | Adjustable motor speed protection with upper and lower limits
| Nastavljiva zaščita pritiska olja motorja | Adjustable engine oil pressure protection
| Nastavljiva zaščita temperature motorja | Adjustable engine temperature protection
| Nastavljiva zaščita napetosti zagonskih akumulatorjev z zgornjo in spodnjo mejo (samo predalarm) | Adjustable voltage protection of starting batteries with upper and lower limits (pre-alarm only)
| Nastavljiva zaščita polnjenja zagonskih akumulatorjev preko alternatorja med delovanjem | Adjustable protection for charging the starting batteries via the alternator during operation
| Nastavljiva zaščita servisnih intervalov | Adjustable service interval protection
| Zaščite generator: | Protect the generator:
| Nastavljiva zaščita frekvence z zgornjo in spodnjo mejo | Adjustable frequency protection with upper and lower limits
| Nastavljiva zaščita napetosti z zgornjo in spodnjo mejo | Adjustable voltage protection with upper and lower limits
| Nastavljiva zaščita preobremenitve in kratkega stika | Adjustable overload and short-circuit protection
| Nastavljiva zaščita motorskega teka | Adjustable motor run protection
| Nastavljiva zaščita zemeljskega stika generatorja | Adjustable generator earth contact protection
| Zaščite mreža: | Protection net:
| Nastavljiva zaščita frekvence z zgornjo in spodnjo mejo | Adjustable frequency protection with upper and lower limits
| Nastavljiva zaščita napetosti z zgornjo in spodnjo mejo | Adjustable voltage protection with upper and lower limits
| Nastavljiva smerna zaščita proti mrežnemu viru | Adjustable directional protection against mains source
| R.O.C.O.F. – nenadna sprememba frekvence df/dt, | R.O.C.O.F. - sudden change in frequency df/dt,
| Vector shift – nenadna sprememba vektorskega kota dv/dt, | Vector shift - sudden change in vector angle dv/dt,
| Mrežna povratna energija. | Grid energy feedback.
| Upravljalna omara naj bo opremljena s Posluževalni panelom , na katerem je omogočen kompleten vpogled in upravljanje sistema. Panel, občutljiv na dotik, barvni TFT, 1024x768 točk, velikosti 7", s funkcionalnostjo za izvedbo lokalnega/servisnega upravljanja, ethernet, RS232, CANopen, USB, integrirana Web server aplikacija, komunikacija s PLC krmilnikom mora biti neodvisna in ločena od komunikacije s SCADA nadzornim sistemom, ter ločena od web server komunikacije PLC krmilnika. | The control cabinet shall be equipped with a service panel allowing a complete view and control of the system. The panel shall be touch-sensitive, TFT colour, 1024x768 pixels, 7" size, with functionality for local/service management, Ethernet, RS232, CANopen, USB, integrated Web server application, communication with the PLC controller shall be independent and separate from the communication with the SCADA control system, and separate from the web server communication of the PLC controller.
| LIC-OS-CE30; Licenčna programska oprema WindowsCE za posluževalni panel - programska oprema mora prikazovati vse podsestave z ustrezno animacijo ob delovanju oziroma okvarah. Na panelu morajo biti prikazane vse meritve in informacije, ki jih omogočata krmilnika DEA enote in preklopnih mest. Dodatno mora biti obdelana lista alarmnih stanj in historizacija dogodkov. Vse meritve na mrežnem in generatorskem viru se intervalno shranjujejo in omogočajo grafični prikaz posameznih parametrov. Na elektro energetski shemi mora biti jasno prikazano in alarmirano havarijsko napajanje nasprotnih napajalnih vej v slučaju okvar posamezne napajalne veje. | LIC-OS-CE30; WindowsCE licensed software for the service panel - the software shall display all sub-assemblies with appropriate animation in the event of operation or failure. The panel shall display all measurements and information provided by the DEA unit and switching point controllers. In addition, a list of alarm conditions and historisation of events shall be processed. All measurements on the grid and generator source shall be stored at interval intervals and shall allow for a graphical display of the individual parameters. The power diagram shall clearly display and alarm the emergency power supply to the opposite supply branches in the event of a failure of a single supply branch.
| Upravljanje in nastavitve DEA se lahko izvaja iz operatorskega panela na Komandni omari ali daljinsko iz centra vodenja. | The DEA can be controlled and set from the operator panel in the Command Box or remotely from the Control Centre.
| Ponudnik mora v ponudbi priložiti tehnično dokumentacijo proizvajalca s katero dokazuje izpolnjevanje tehničnih zahtev! | The tenderer must enclose the manufacturer's technical documentation to prove that the technical requirements are met!
| - Alarmiranje in daljinski dostop do naprave s pomočjo pametnih telefonov: | - Alarm and remote access to the device via smartphones:
| * Za potrebe alarmiranja mora biti v komandni omari nameščen GSM modem, ki omogoča obveščanje pristojnih oseb o vsakem nenormalnem dogodku preko SMS obvestil s pričetkom in zaključkom dogodka (izpad mreže, delovanje agregata, izklop mrežnega vira, vklop generatorskega vira, opozorilni alarmi, okvarni alarmi itd.) | * For alarm purposes, a GSM modem shall be installed in the control cabinet to enable the competent persons to be informed of any abnormal event by SMS notifications with the start and end of the event (mains failure, operation of the generator set, switching off of the mains source, switching on of the generator source, warning alarms, fault alarms, etc.)
| * Komunikacijski sistem mora omogočati internetni dostop do naprave preko VPN povezave s pametnim telefonom in aplikacijo, ki omogoča popolno vizualizacijo stanja naprave (ekranski prikaz napajalne sheme z vsemi meritvami mrežnega in generatorskega vira, parametri motorja, stanje goriva glavnega in dnevnega rezervoarja, alarmna stanja, kompletno upravljanje in ponastavitve napak, grafične meritve poljubno izbranih parametrov mrežnega in generatorskega vira, statistika delovanja, število zagonov, proizvedena energija, čas do servisa). Komunikacija med krmilnikom agregata in pametnim telefonom mora potekati direktno brez vmesniške programske opreme. | * The communication system shall allow internet access to the plant via a VPN connection to a smartphone and an app that allows full visualisation of the plant status (on-screen display of the power scheme with all measurements of the grid and generator source, engine parameters, fuel status of the main and day tanks, alarm conditions, complete control and fault reset, graphical measurements of arbitrarily selected parameters of the grid and generator source, operating statistics, number of starts, energy produced, time to service). Communication between the genset controller and the smartphone shall be direct without any middleware.
6.3 | Kabelske povezave | Cable connections
| Kabli za izvedbo komunikacijskih, merilnih in krmilnik povezav, odziv na ogenj vsaj Cca s1 d2 a1: | Cables for communication, instrumentation and controller connections, fire response at least Cca s1 d2 a1:
| - N2XH 3x1,5 mm² | - N2XH 3x1,5 mm² |  |  | m | 70 |  | 0
| - N2XH 3x2,5 mm² | - N2XH 3x2,5 mm² |  |  | m | 20 |  | 0
| - N2XH 4x1,5 mm² | - N2XH 4x1,5 mm² |  |  | m | 20 |  | 0
| - N2XH 4x2,5 mm² | - N2XH 4x2,5 mm² |  |  | m | 20 |  | 0
| - N2XH 5x2,5 mm² | - N2XH 5x2,5 mm² |  |  | m | 20 |  | 0
| - N2XCH 3x2,5 mm² | - N2XCH 3x2,5 mm² |  |  | m | 20 |  | 0
| - N2XCH 4x2,5 mm² | - N2XCH 4x2,5 mm² |  |  | m | 30 |  | 0
| - N2XCH 7x1,5 mm² | - N2XCH 7x1,5 mm² |  |  | m | 70 |  | 0
| - N2XCH 3x1,5 mm² | - N2XCH 3x1,5 mm² |  |  | m | 40 |  | 0
| - J-H(St)H 4x0,8 mm² | - J-H(St)H 4x0,8 mm² |  |  | m | 100 |  | 0
| - J-H(St)H 12x0,8 mm² | - J-H(St)H 12x0,8 mm² |  |  | m | 90 |  | 0
| - J-H(St)H 20x0,8 mm² | - J-H(St)H 20x0,8 mm² |  |  | m | 30 |  | 0
| - CPR6003 2x0,5 mm² | - CPR6003 2x0,5 mm² |  |  | m | 40 |  | 0
6.4 | Strojna oprema in dela | Hardware and works
| Sistem za odvod in dušenje izpušnih plinov. Sistem mora biti izveden v skladu z zahtevanimi mejnimi vrednostmi hrupa. Sistem sestavljajo naslednji elementi: | Exhaust extraction and exhaust silencing system. The system shall be designed to comply with the required noise limits. The system shall consist of the following elements: |  |  | m | 12 |  | 0
a. | - Dušilniki zvoka, komplet z obešalnim materialom, s cevnimi loki in kompenzacijskimi kosi. | - Silencers, complete with hanging material, hose arches and compensation pieces.
b. | - Izpušna cev ustreznega premera iz nerjavečega jekla INOX, za povezavo notranjega in zunanjega dušilnika zvoka, kompletno s prirobnicami, koleni in montažnim materialom. | - Exhaust pipe of suitable diameter in INOX stainless steel, for connection of the internal and external silencer, complete with flanges, elbows and mounting material.
c. | - Konstrukcija za pritrditev izpušnega sistema v prostoru DEA | - Structure for mounting the exhaust system in the DEA compartment
d. | - Konstrukcije za pritrditev izpušnega sistema na strehi | - Structures for mounting the exhaust system on the roof
e. | - Tesnilni vmesnik pri prehodu izpuha skozi streho, z ustrezno temperaturno izolacijo, max temperatura izpuha 550°C | - Sealing interface at the exhaust passage through the roof, with appropriate temperature insulation, max exhaust temperature 550°C
f. | - Toplotna izolacija iz mineralne volne za izolacijo izpušnega sistema DEA, debeline 50mm, oplaščeno z Al pločevino. | - Mineral wool thermal insulation for DEA exhaust system insulation, 50mm thick, sheathed with Al sheet.
g. | - Zaščitno barvanje vseh nezaščitenih delov izpuha DEA (obešala, nosilni material) s temperaturno odporno barvo, po predhodnem čiščenju. | - Protective painting of all unprotected parts of the DEA exhaust (hangers, support material) with temperature-resistant paint, after prior cleaning.
6.5 | Izvedba SAT (Site Acceptance Test) | SAT (Site Acceptance Test)
| Izvajalec izdela protokol SAT preizkusa. V primeru neuspešnega SAT preizkusa mora izvajalec odpraviti pomanjkljivosti in ponoviti preizkus. ('Tlačni preizkus sistema, izvedba meritev, polnjenje sistema z gorivom, poskusno obratovanje,…). | The contractor shall draw up a SAT test protocol. In the event of a failed SAT test, the contractor shall rectify the deficiencies and repeat the test. ('System pressure test, taking measurements, refuelling the system, trial operation,...). |  |  | kpl | 1 |  | 0
6.6 | Usposabljanje uporabnika | User training
| Ponudnik pripravi izobraževanje za naročnikove obratovalcev ter strojnih in elektro vzdrževalcev delavcev (strokovni nivo: inženir, tehnik elektrikar, elektrotehnik). Za vsakega udeleženca bo moral ponudnik pripraviti pisno gradivo. Izobraževanje mora zajemati teoretični in praktični del. Ponudnik k ponudbi priloži vsebinski plan usposabljanja. | The tenderer shall provide training for the client's plant operators and mechanical and electrical maintenance workers (professional level: engineer, electrician technician, electrician). The tenderer will be required to prepare written material for each participant. The training must cover both theoretical and practical parts. The tenderer shall attach to the tender a training content plan. |  |  | kpl | 1 |  | 0
6.7 | Gorivo | Fuel
| Dieselsko gorivo D2, skladno s standardom EN 590 | Diesel fuel D2, in accordance with EN 590 |  |  | l | 880 |  | 0
6.8 | Zagon | Start
| Zagon naprave s strani pooblaščenega serviserja in izdaja garancijskih listin. | Commissioning of the appliance by an authorised repairer and issue of warranty documents. |  |  | kpl | 1 |  | 0
| DIESEL ELEKTRIČNI AGREGAT (DEA) | DIESEL ELECTRIC POWER UNIT (DEA) | [5 empty] | 0

## 3.3.7_Kompenzacija
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.3 | ELEKTRO DELA | ELECTRICAL WORKS
3.3.7 | KOMPENZACIJA JALOVE ELEKTRIČNE ENERGIJE | COMPENSATION FOR REACTIVE ELECTRICITY |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
7 | KOMPENZACIJA JALOVE ELEKTRIČNE ENERGIJE | COMPENSATION FOR REACTIVE ELECTRICITY
7.1 | Dobava, transport in montaža trifazne kompenzacijske naprave jalove energije 0,4 kV, 400 kvar, sestavljene iz dveh omar, dimenzij cca: (šxgxv) (2x600)x600x2100 mm, s filtriranjem višjih harmonikov v omrežju, deljena na 9 stopenj (2x25 + 7x50) kvar, komplet z varovalkami, kontaktorji, dušilkami in kondenzatorji, notranjim termostatom v ohišju, krmiljena z avtomatskim elektronskim regulatorjem jalove moči, za priklop na TMT 2500/5 A in 400/230 V,AC. | Supply, transport and installation of a three-phase reactive power compensation device 0,4 kV, 400 kvar, consisting of two cabinets, dimensions approx.: (2x600x600x2100 mm), with filtering of higher harmonics in the network, divided into 9 stages (2x25 + 7x50) kvar, complete with fuses, contactors, chokes and capacitors, internal thermostat in the housing, controlled by an automatic electronic reactive power regulator, for connection to TMT 2500/5 A and 400/230 V,AC. | kos | 2 |  | 0
| Kot na primer tip: FASK5-400/440-7; proizvod: Enerprom | Such as type: FASK5-400/440-7; product: Enerprom
| Opomba: | Remark:
| Avtomatska dinamična, filtrska kompenzacijska naprava jalove energije bo dobavljena po zagonu objekta, na osnovi opravljenih meritev parametrov omrežja. | The automatic dynamic reactive energy filter compensator will be delivered after the commissioning of the facility, based on the measurements of the network parameters.
7.2 | Dobava, transport in montaža trifazne direktne kompenzacijske naprave 0,4 kV, 75 kvar, za kompenzacijo energetskih transformatorjev cca: (šxgxv) 900x350x700 mm, s filtriranjem višjih harmonikov v omrežju, z dušilkami in kondenzatorji, z varovalčnim stikalom. | Supply, transport and installation of a three-phase direct compensation device 0,4 kV, 75 kvar, for compensation of power transformers approx.: (wxdxh) 900x350x700 mm, with filtering of higher harmonics in the network, with chokes and capacitors, with fuse switch. | kos | 2 |  | 0
| Kot na primer tip: FDSK2-75/440-7; proizvod: Enerprom | Such as type: FDSK2-75/440-7; product: Enerprom
| KOMPENZACIJA JALOVE ELEKTRIČNE ENERGIJE | COMPENSATION FOR REACTIVE ELECTRICITY |  |  |  | 0

## 3.3.8_NN zbiralke in kabli
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.3 | ELEKTRO DELA | ELECTRICAL WORKS
3.3.8 | NN ENERGETSKI ZBIRALKE IN NN ENERGETSKI KABLI | LV BUSBARS AND LV POWER CABLES | [5 empty] | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description |  |  | EM | Količina | Cena/EM | Cena
8 | NN ENERGETSKI ZBIRALKE IN NN ENERGETSKI KABLI | LV BUSBARS AND LV POWER CABLES
8.1 | Zbiralčni razvod Canalis Schneider Electric KTA. Ohišje iz galvarizirane pločevine, poliesterska prekrivna barva, stopnja zaščite IP55, robustne izvedbe - stopnja mehanske odpornosti IK08 , izolacija razreda B (130C), brez vsebnosti halogenskih snovi. Posrebreni, bimetalni kontakti za zagotavljanje dobrega in trajnega kontakta med elementi. Skladnost s standardoma SIST EN IEC 60439-1 & 2. ZBIRALČNI RAZVOD 2500A - Povezava med TR1 in glavnim NN sestatvom Vertikalna postavitev, dolžina cca. 5m, priklop v stikalni blok od spodaj. Kot na primer tip: Canalis KTA2500, 2500A, 3P+PEN Sestavljen iz priključnih elementov, ravnih elementov, kolen, ravnih elementov za priključne omarice in spojnih elementov. Opozorilo: Pred naročilom je potrebno preveriti dimenzije stikalnih blokov in transformatorjev ter postavitev le teh. Prav tako je potrebno preveriti dimenzije in lokacije gradbenih odprtin predvidenih za prehod zbiralk! | Canalis Schneider Electric KTA busbar. Galvanised sheet metal housing, polyester overcoat, protection rating IP55, robust design - mechanical resistance rating IK08, insulation class B (130C), halogen-free. Silver-plated, bimetallic contacts to ensure good and permanent contact between the elements. Conforms to SIST EN IEC 60439-1 & 2 standards. COLLECTOR LINE 2500A - Connection between TR1 and the main LV substation Vertical installation, length approx. 5 m, connection to the switching block from below. Such as type Canalis KTA2500, 2500A, 3P+PEN Consisting of connectors, straight elements, elbows, straight elements for junction boxes and coupling elements. Note: Before ordering, it is necessary to check the dimensions of the switchgear blocks and transformers and their location. It is also necessary to check the dimensions and locations of the construction openings planned for the busbar passage! |  |  | kpl | 1 |  | 0
a. | Priključni element za priklop na suhi transformator - 2500A | Connecting element for connection to dry-type transformer - 2500A | kos | 1
b. | Canalis vmesnik - 2500A, 4P - za povezavo NN omare na Canalis zbiralčni sistem | Canalis interface - 2500A, 4P - for connecting LV cabinets to Canalis busbar system | kos | 1
c. | Ravni element, brez odcepov, po meri, 0.5-1.5m | Flat element, without spurs, custom, 0.5-1.5m | kos | 1
d. | Kotni element - koleno - navpično, po meri | Corner element - knee - vertical, custom | kos | 1
e. | Kotni element - koleno - vodoravno, po meri | Angle element - knee - horizontal, custom | kos | 1
f. | Kotni element - koleno - vodoravno, standardno | Angle element - knee - horizontal, standard | kos | 1
g. | Flexibilne zbiralke za povezavo na transformator, 2500A, dolžine 300-600mm | Flexible busbars for transformer connection, 2500A, length 300-600mm | kos | 12
h. | Požarna bariera | Fire barrier | kos | 1
i. | Pritrdilni element, horizontalni | Fastening element, horizontal | kos | 4
j. | Spojni element | Connecting element | kos | 1
8.2 | Zbiralčni razvod Canalis Schneider Electric KTA. Ohišje iz galvarizirane pločevine, poliesterska prekrivna barva, stopnja zaščite IP55, robustne izvedbe - stopnja mehanske odpornosti IK08 , izolacija razreda B (130C), brez vsebnosti halogenskih snovi. Posrebreni, bimetalni kontakti za zagotavljanje dobrega in trajnega kontakta med elementi. Skladnost s standardoma SIST EN IEC 60439-1 & 2. ZBIRALČNI RAZVOD 2500A - Povezava med TR2 in glavnim NN sestatvom Vertikalna postavitev, dolžina cca. 4m, priklop v stikalni blok od spodaj. Kot na primer tip: Canalis KTA2500, 2500A, 3P+PEN Sestavljen iz priključnih elementov, ravnih elementov, kolen, ravnih elementov za priključne omarice in spojnih elementov. Opozorilo: Pred naročilom je potrebno preveriti dimenzije stikalnih blokov in transformatorjev ter postavitev le teh. Prav tako je potrebno preveriti dimenzije in lokacije gradbenih odprtin predvidenih za prehod zbiralk! | Canalis Schneider Electric KTA busbar. Galvanised sheet metal housing, polyester overcoat, protection rating IP55, robust design - mechanical resistance rating IK08 , insulation class B (130C), halogen-free. Silver-plated, bimetallic contacts to ensure good and permanent contact between elements. Compliance with SIST EN IEC 60439-1 & 2. COLLECTOR LINE 2500A - Connection between TR2 and the main LV substation Vertical installation, length approx. 4m, connection to the switching block from below. Such as type Canalis KTA2500, 2500A, 3P+PEN Consisting of connectors, straight elements, elbows, straight elements for junction boxes and coupling elements. Note: Before ordering, it is necessary to check the dimensions of the switchgear blocks and transformers and their location. It is also necessary to check the dimensions and locations of the construction openings planned for the busbar passage! |  |  | kpl | 1 |  | 0
a. | Priključni element za priklop na suhi transformator - 2500A | Connecting element for connection to dry-type transformer - 2500A | kos | 1
b. | Canalis vmesnik - 2500A, 4P - za povezavo NN omare na Canalis zbiralčni sistem | Canalis interface - 2500A, 4P - for connecting LV cabinets to Canalis busbar system | kos | 1
c. | Ravni element, brez odcepov, po meri, 0.5-1.5m | Flat element, without spurs, custom, 0.5-1.5m | kos | 2
d. | Kotni element - dvojno koleno - navpično-vodoravno, po meri | Corner element - double knee - vertical-horizontal, custom | kos | 1
e. | Flexibilne zbiralke za povezavo na transformator, 2500A, dolžine 300-600mm | Flexible busbars for transformer connection, 2500A, length 300-600mm | kos | 12
f. | Požarna bariera | Fire barrier | kos | 1
g. | Pritrdilni element, horizontalni | Fastening element, horizontal | kos | 4
h. | Spojni element | Connecting element | kos | 1
8.3 | Ostalo | Other |  |  | kpl | 1 |  | 0
a. | Meritve poteka zbiralčnega sistema na objektu in izdelava natančne specifikacije | Measurements of the collection system on site and detailed specification | kpl | 1
b. | Montaža celotnega zbiralčnega sistema | Installation of the complete collection system | kpl | 1
c. | Pregled celotnega zbiralčnega sistema in izdaja izjave/potrdila o ustreznosti nameščenega sistema | Inspection of the complete collection system and issue of a declaration/certificate of adequacy of the installed system | kpl | 1
d. | Izdelava montažnega načrta, izris detajlov vpetja zbiralčnega razvoda, sodelovanje in svetovanje dobavitelja zbiralk pri montaži | Preparation of the installation plan, drawing of the details of the manifold installation, cooperation and advice of the manifold supplier in the installation process | kpl | 1
e. | Drobni montažni material, transport in manipulacijski stroški | Small assembly materials, transport and handling costs | % | 4
8.4 | Dobava in montaža energetskih napajalnih kablov za nazivno napetost Un=0,4 kV, položenenih na police, vključno z označevalnimi ploščicami, odziv na ogenj vsaj Cca s1 d2 a1: | Supply and installation of power supply cables for rated voltage Un=0,4 kV, laid on shelves, including marker plates, reaction to fire not less than Cca s1 d2 a1:
| - 3x(N2XH-O 4x240 mm² + N2XH-J 1x120 mm²) (NN_P1_TP_RG2_1) | - 3x(N2XH-O 4x240 mm² + N2XH-J 1x120 mm²) (NN_P1_TP_RG2_1) |  |  | m | 51 |  | 0
| - 2x(N2XH-O 4x150 mm² + N2XH-J 1x95 mm²) (NN_P1_TP_RG1_1) | - 2x(N2XH-O 4x150 mm² + N2XH-J 1x95 mm²) (NN_P1_TP_RG1_1) |  |  | m | 30 |  | 0
| - 2x(N2XH-O 4x150 mm² + N2XH-J 1x95 mm²) (NN_P1_TP_RG3_1) | - 2x(N2XH-O 4x150 mm² + N2XH-J 1x95 mm²) (NN_P1_TP_RG3_1) |  |  | m | 38 |  | 0
| - 2x(N2XH-O 4x95 mm² + N2XH-J 1x50 mm²) (NN_P1_6_R_LICEM) | - 2x(N2XH-O 4x95 mm² + N2XH-J 1x50 mm²) (NN_P1_6_R_LICEM) |  |  | m | 150 |  | 0
| - 2x(N2XH-O 4x150 mm² + N2XH-J 1x95 mm²) (NN_P1_6_R_LICEM_300_1) | - 2x(N2XH-O 4x150 mm² + N2XH-J 1x95 mm²) (NN_P1_6_R_LICEM_300_1) |  |  | m | 110 |  | 0
| - 4x(N2XH-O 4x185 mm² + N2XH-J 1x95 mm²) (NN_P1_6_R_1) | - 4x(N2XH-O 4x185 mm² + N2XH-J 1x95 mm²) (NN_P1_6_R_1) |  |  | m | 132 |  | 0
| - 2x(N2XH-O 4x240 mm²+ N2XH-J 1x120 mm²) (NN_P1_TP_C1_2) | - 2x(N2XH-O 4x240 mm²+ N2XH-J 1x120 mm²) (NN_P1_TP_C1_2) |  |  | m | 20 |  | 0
| - 2x(N2XH-O 4x240 mm²+ N2XH-J 1x120 mm²) (NN_P1_TP_C1_3) | - 2x(N2XH-O 4x240 mm²+ N2XH-J 1x120 mm²) (NN_P1_TP_C1_3) |  |  | m | 20 |  | 0
| - N2XH-J 4x70 mm² (NN_P1_TP_C1_1) | - N2XH-J 4x70 mm² (NN_P1_TP_C1_1) |  |  | m | 12 |  | 0
| - N2XH-J 4x70 mm² (NN_P1_TP_C2_1) | - N2XH-J 4x70 mm² (NN_P1_TP_C2_1) |  |  | m | 12 |  | 0
| - 2x(N2XH-O 4x150 mm² + N2XH-J 1x95 mm²) (NN_P1_6_R_LICEM_300_2) | - 2x(N2XH-O 4x150 mm² + N2XH-J 1x95 mm²) (NN_P1_6_R_LICEM_300_2) |  |  | m | 120 |  | 0
| - 2x(N2XH-O 4x150 mm² + N2XH-J 1x95 mm²) (NN_K1_AP1_R) | - 2x(N2XH-O 4x150 mm² + N2XH-J 1x95 mm²) (NN_K1_AP1_R) |  |  | m | 380 |  | 0
| - 2x(N2XH-O 4x150 mm² + N2XH-J 1x95 mm²) (NN_K1_AP2_R) | - 2x(N2XH-O 4x150 mm² + N2XH-J 1x95 mm²) (NN_K1_AP2_R) |  |  | m | 250 |  | 0
| - 2x(N2XH-O 4x150 mm² + N2XH-J 1x95 mm²) (NN_K1_AP3_R) | - 2x(N2XH-O 4x150 mm² + N2XH-J 1x95 mm²) (NN_K1_AP3_R) |  |  | m | 300 |  | 0
| - N2XH-O 4x240 mm² + N2XH-J 1x120 mm² (NN_P1_TP_RG4_1) | - N2XH-O 4x240 mm² + N2XH-J 1x120 mm² (NN_P1_TP_RG4_1) |  |  | m | 16 |  | 0
| - 2x(N2XH-O 4x240 mm²+ N2XH-J 1x120 mm²) (NN_P1_TP_C2_2) | - 2x(N2XH-O 4x240 mm²+ N2XH-J 1x120 mm²) (NN_P1_TP_C2_2) |  |  | m | 16 |  | 0
| - 2x(N2XH-O 4x240 mm²+ N2XH-J 1x120 mm²) (NN_P1_TP_C2_3) | - 2x(N2XH-O 4x240 mm²+ N2XH-J 1x120 mm²) (NN_P1_TP_C2_3) |  |  | m | 16 |  | 0
| - N2XH-O 4x240 mm² + N2XH-J 1x120 mm² (ENS_K1_R1) | - N2XH-O 4x240 mm² + N2XH-J 1x120 mm² (ENS_K1_R1) |  |  | m | 65 |  | 0
| - N2XH-O 4x240 mm² + N2XH-J 1x120 mm² (ENS_K1_R2) | - N2XH-O 4x240 mm² + N2XH-J 1x120 mm² (ENS_K1_R2) |  |  | m | 70 |  | 0
| - 2x(N2XH-O 4x150 mm² + N2XH-J 1x95 mm²) (DEA_P1_TP_RG1_1) | - 2x(N2XH-O 4x150 mm² + N2XH-J 1x95 mm²) (DEA_P1_TP_RG1_1) |  |  | m | 42 |  | 0
| - N2XH-O 4x70 mm² + N2XH-J 1x35 mm² (NN_N3_4_RG1_1) | - N2XH-O 4x70 mm² + N2XH-J 1x35 mm² (NN_N3_4_RG1_1) |  |  | m | 85 |  | 0
| - N2XH-O 4x95 mm² + N2XH-J 1x50 mm² (NN_P1_1_R) | - N2XH-O 4x95 mm² + N2XH-J 1x50 mm² (NN_P1_1_R) |  |  | m | 160 |  | 0
| - N2XH-O 4x95 mm² + N2XH-J 1x50 mm² (NN_N1_1_R) | - N2XH-O 4x95 mm² + N2XH-J 1x50 mm² (NN_N1_1_R) |  |  | m | 170 |  | 0
| - N2XH-O 4x150 mm² + N2XH-J 1x95 mm² (NN_N2_1_R) | - N2XH-O 4x150 mm² + N2XH-J 1x95 mm² (NN_N2_1_R) |  |  | m | 175 |  | 0
| - N2XH-O 4x70 mm² + N2XH-J 1x35 mm² (NN_N3_1_R) | - N2XH-O 4x70 mm² + N2XH-J 1x35 mm² (NN_N3_1_R) |  |  | m | 180 |  | 0
| - N2XH-O 4x95 mm² + N2XH-J 1x50 mm² (NN_P1_2_R) | - N2XH-O 4x95 mm² + N2XH-J 1x50 mm² (NN_P1_2_R) |  |  | m | 147 |  | 0
| - N2XH-O 4x95 mm² + N2XH-J 1x50 mm² (NN_N1_2_R) | - N2XH-O 4x95 mm² + N2XH-J 1x50 mm² (NN_N1_2_R) |  |  | m | 115 |  | 0
| - N2XH-O 4x150 mm² + N2XH-J 1x95 mm² (NN_N2_2_R) | - N2XH-O 4x150 mm² + N2XH-J 1x95 mm² (NN_N2_2_R) |  |  | m | 120 |  | 0
| - N2XH-O 4x95 mm² + N2XH-J 1x50 mm² (NN_N3_2_R) | - N2XH-O 4x95 mm² + N2XH-J 1x50 mm² (NN_N3_2_R) |  |  | m | 125 |  | 0
| - 2x(N2XH-O 4x95 mm² + N2XH-J 1x50 mm²) (NN_P1_3_R) | - 2x(N2XH-O 4x95 mm² + N2XH-J 1x50 mm²) (NN_P1_3_R) |  |  | m | 226 |  | 0
| - N2XH-O 4x150 mm² + N2XH-J 1x95 mm² (NN_N1_3_R) | - N2XH-O 4x150 mm² + N2XH-J 1x95 mm² (NN_N1_3_R) |  |  | m | 155 |  | 0
| - N2XH-O 4x150 mm² + N2XH-J 1x95 mm² (NN_N2_3_R) | - N2XH-O 4x150 mm² + N2XH-J 1x95 mm² (NN_N2_3_R) |  |  | m | 160 |  | 0
| - N2XH-O 4x150 mm² + N2XH-J 1x95 mm² (NN_N3_3_R) | - N2XH-O 4x150 mm² + N2XH-J 1x95 mm² (NN_N3_3_R) |  |  | m | 165 |  | 0
| - 2x(N2XH-O 4x185 mm² + N2XH-J 1x95 mm²) (NN_P1_4_R) | - 2x(N2XH-O 4x185 mm² + N2XH-J 1x95 mm²) (NN_P1_4_R) |  |  | m | 140 |  | 0
| - N2XH-O 4x150 mm² + N2XH-J 1x95 mm² (NN_N1_4_R) | - N2XH-O 4x150 mm² + N2XH-J 1x95 mm² (NN_N1_4_R) |  |  | m | 80 |  | 0
| - 2x(N2XH-O 4x95 mm² + N2XH-J 1x50 mm²) (NN_N2_4_R) | - 2x(N2XH-O 4x95 mm² + N2XH-J 1x50 mm²) (NN_N2_4_R) |  |  | m | 170 |  | 0
| - N2XH-O 4x95 mm² + N2XH-J 1x50 mm² (NN_N3_4_R) | - N2XH-O 4x95 mm² + N2XH-J 1x50 mm² (NN_N3_4_R) |  |  | m | 90 |  | 0
| - 2x(N2XH-O 4x95 mm² + N2XH-J 1x50 mm²) (NN_P1_5_R) | - 2x(N2XH-O 4x95 mm² + N2XH-J 1x50 mm²) (NN_P1_5_R) |  |  | m | 166 |  | 0
| - N2XH-O 4x70 mm² + N2XH-J 1x35 mm² (NN_N1_5_R) | - N2XH-O 4x70 mm² + N2XH-J 1x35 mm² (NN_N1_5_R) |  |  | m | 190 |  | 0
| - N2XH-O 4x70 mm² + N2XH-J 1x35 mm² (NN_N1_6_R) | - N2XH-O 4x70 mm² + N2XH-J 1x35 mm² (NN_N1_6_R) |  |  | m | 20 |  | 0
| - N2XH-O 4x70 mm² + N2XH-J 1x35 mm² (NN_K1_1_R) | - N2XH-O 4x70 mm² + N2XH-J 1x35 mm² (NN_K1_1_R) |  |  | m | 150 |  | 0
| - N2XH-O 4x70 mm² + N2XH-J 1x35 mm² (NN_K1_2_R) | - N2XH-O 4x70 mm² + N2XH-J 1x35 mm² (NN_K1_2_R) |  |  | m | 125 |  | 0
| - N2XH-J 5x16 mm² (NN.P1-Z1-R) | - N2XH-J 5x16 mm² (NN.P1-Z1-R) |  |  | m | 135 |  | 0
| - N2XH-J 5x16 mm² (NN.P1-Z2-R) | - N2XH-J 5x16 mm² (NN.P1-Z2-R) |  |  | m | 95 |  | 0
| - N2XH-O 4x35 mm² + N2XH-J 1x16 mm² (HVAC_K1-R1) | - N2XH-O 4x35 mm² + N2XH-J 1x16 mm² (HVAC_K1-R1) |  |  | m | 220 |  | 0
| - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (HVAC_K1-R2) | - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (HVAC_K1-R2) |  |  | m | 185 |  | 0
| - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (HVAC_K1-R3) | - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (HVAC_K1-R3) |  |  | m | 180 |  | 0
| - N2XH-J 5x16 mm² (HVAC_K1-R4) | - N2XH-J 5x16 mm² (HVAC_K1-R4) |  |  | m | 170 |  | 0
| - N2XH-O 4x50 mm² + N2XH-J 1x25 mm² (HVAC_K1-R5) | - N2XH-O 4x50 mm² + N2XH-J 1x25 mm² (HVAC_K1-R5) |  |  | m | 80 |  | 0
| - N2XH-O 4x50 mm² + N2XH-J 1x25 mm² (HVAC_S1-R1) | - N2XH-O 4x50 mm² + N2XH-J 1x25 mm² (HVAC_S1-R1) |  |  | m | 180 |  | 0
| - N2XH-O 4x70 mm² + N2XH-J 1x35 mm² (HVAC_S1-R2) | - N2XH-O 4x70 mm² + N2XH-J 1x35 mm² (HVAC_S1-R2) |  |  | m | 240 |  | 0
| - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (HVAC_S1-R3) | - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (HVAC_S1-R3) |  |  | m | 240 |  | 0
| - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (HVAC_S1-R4) | - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (HVAC_S1-R4) |  |  | m | 125 |  | 0
| - N2XH-J 5x16 mm² (HVAC_S1-R5) | - N2XH-J 5x16 mm² (HVAC_S1-R5) |  |  | m | 125 |  | 0
| - N2XH-J 5x16 mm² (NN_N3_4_RD1) | - N2XH-J 5x16 mm² (NN_N3_4_RD1) |  |  | m | 94 |  | 0
| - N2XH-J 5x16 mm² (NN_N3_4_RD2) | - N2XH-J 5x16 mm² (NN_N3_4_RD2) |  |  | m | 92 |  | 0
| - N2XH-J 5x16 mm² (NN_N3_4_RD3) | - N2XH-J 5x16 mm² (NN_N3_4_RD3) |  |  | m | 90 |  | 0
| - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (NN_N3_4_RD4) | - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (NN_N3_4_RD4) |  |  | m | 100 |  | 0
| - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (NN_N3_4_RD5) | - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (NN_N3_4_RD5) |  |  | m | 108 |  | 0
| - N2XH-J 5x16 mm² (NN_N3_4_RD6) | - N2XH-J 5x16 mm² (NN_N3_4_RD6) |  |  | m | 70 |  | 0
| - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (NN_N3_4_RD7) | - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (NN_N3_4_RD7) |  |  | m | 17 |  | 0
| - 2x(N2XH-O 4x150 mm² + N2XH-J 1x95 mm²) (DEA_P1_TP_RG1_1) | - 2x(N2XH-O 4x150 mm² + N2XH-J 1x95 mm²) (DEA_P1_TP_RG1_1) |  |  | m | 15 |  | 0
| - N2XH-J N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (DEA_P1_1_R) | - N2XH-J N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (DEA_P1_1_R) |  |  | m | 156 |  | 0
| - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (DEA_N1_1_R) | - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (DEA_N1_1_R) |  |  | m | 17 |  | 0
| - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (DEA_N2_1_R) | - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (DEA_N2_1_R) |  |  | m | 17 |  | 0
| - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (DEA_N3_1_R) | - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (DEA_N3_1_R) |  |  | m | 17 |  | 0
| - N2XH-O 4x70 mm² + N2XH-J 1x70 mm² (DEA_P1_2_R) | - N2XH-O 4x70 mm² + N2XH-J 1x70 mm² (DEA_P1_2_R) |  |  | m | 142 |  | 0
| - N2XH-J N2XH-O 4x70 mm² + N2XH-J 1x70 mm² (DEA_N1_2_R) | - N2XH-J N2XH-O 4x70 mm² + N2XH-J 1x70 mm² (DEA_N1_2_R) |  |  | m | 15 |  | 0
| - N2XH-J N2XH-O 4x70 mm² + N2XH-J 1x70 mm² (DEA_N2_2_R) | - N2XH-J N2XH-O 4x70 mm² + N2XH-J 1x70 mm² (DEA_N2_2_R) |  |  | m | 15 |  | 0
| - N2XH-J N2XH-O 4x70 mm² + N2XH-J 1x70 mm² (DEA_N3_2_R) | - N2XH-J N2XH-O 4x70 mm² + N2XH-J 1x70 mm² (DEA_N3_2_R) |  |  | m | 15 |  | 0
| - N2XH-O 4x50 mm² + N2XH-J 1x50 mm² (DEA_P1_3_R) | - N2XH-O 4x50 mm² + N2XH-J 1x50 mm² (DEA_P1_3_R) |  |  | m | 110 |  | 0
| - N2XH-O 4x50 mm² + N2XH-J 1x50 mm² (DEA_N1_3_R) | - N2XH-O 4x50 mm² + N2XH-J 1x50 mm² (DEA_N1_3_R) |  |  | m | 15 |  | 0
| - N2XH-O 4x50 mm² + N2XH-J 1x50 mm² (DEA_N2_3_R) | - N2XH-O 4x50 mm² + N2XH-J 1x50 mm² (DEA_N2_3_R) |  |  | m | 15 |  | 0
| - N2XH-O 4x50 mm² + N2XH-J 1x50 mm² (DEA_N3_3_R) | - N2XH-O 4x50 mm² + N2XH-J 1x50 mm² (DEA_N3_3_R) |  |  | m | 15 |  | 0
| - N2XH-J 5x16 mm² (DEA_P1_4_R) | - N2XH-J 5x16 mm² (DEA_P1_4_R) |  |  | m | 67 |  | 0
| - N2XH-J 5x16 mm² (DEA_N1_4_R) | - N2XH-J 5x16 mm² (DEA_N1_4_R) |  |  | m | 15 |  | 0
| - N2XH-J 5x16 mm² (DEA_N2_4_R) | - N2XH-J 5x16 mm² (DEA_N2_4_R) |  |  | m | 15 |  | 0
| - N2XH-J 5x16 mm² (DEA_N3_4_R) | - N2XH-J 5x16 mm² (DEA_N3_4_R) |  |  | m | 15 |  | 0
| - N2XH-O 4x50 mm² + N2XH-J 1x50 mm² (DEA_P1_5_R) | - N2XH-O 4x50 mm² + N2XH-J 1x50 mm² (DEA_P1_5_R) |  |  | m | 82 |  | 0
| - N2XH-O 4x50 mm² + N2XH-J 1x25 mm² (DEA_N1_5_R) | - N2XH-O 4x50 mm² + N2XH-J 1x25 mm² (DEA_N1_5_R) |  |  | m | 17 |  | 0
| - N2XH-J 5x16 mm² (DEA_P1_6_R) | - N2XH-J 5x16 mm² (DEA_P1_6_R) |  |  | m | 32 |  | 0
| - N2XH-J 5x16 mm² (DEA_N1_6_R) | - N2XH-J 5x16 mm² (DEA_N1_6_R) |  |  | m | 17 |  | 0
| - N2XH-O 4x95 mm² + N2XH-J 1x50 mm² (DEA_SPRINKLER_GK) | - N2XH-O 4x95 mm² + N2XH-J 1x50 mm² (DEA_SPRINKLER_GK) |  |  | m | 170 |  | 0
| - N2XH-J 5x16 mm² (DEA_K1_1_R) | - N2XH-J 5x16 mm² (DEA_K1_1_R) |  |  | m | 150 |  | 0
| - N2XH-J 5x16 mm² (DEA_K1_2_R) | - N2XH-J 5x16 mm² (DEA_K1_2_R) |  |  | m | 125 |  | 0
| - N2XH-O 4x95 mm² + N2XH-J 1x50 mm² (ODT_K1_R1) | - N2XH-O 4x95 mm² + N2XH-J 1x50 mm² (ODT_K1_R1) |  |  | m | 75 |  | 0
| - N2XH-O 4x95 mm² + N2XH-J 1x50 mm² (ODT_K1_R2) | - N2XH-O 4x95 mm² + N2XH-J 1x50 mm² (ODT_K1_R2) |  |  | m | 40 |  | 0
| - N2XH-J 5x2,5 mm² (DEA_P1_TP_DEA1-LASTNA RABA) | - N2XH-J 5x2,5 mm² (DEA_P1_TP_DEA1-LAST RABA) |  |  | m | 10 |  | 0
| - 2x(N2XH-O 4x150 mm² + N2XH-J 1x95 mm²) (UPS_P1_TP_UPS1) | - 2x(N2XH-O 4x150 mm² + N2XH-J 1x95 mm²) (UPS_P1_TP_UPS1) |  |  | m | 16 |  | 0
| - N2XH-O 4x150 mm² + N2XH-J 1x95 mm² (UPS_P1_TP_RG1) napajano od DEA | - N2XH-O 4x150 mm² + N2XH-J 1x95 mm² (UPS_P1_TP_RG1) powered by DEA |  |  | m | 25 |  | 0
| - N2XH-O 4x150 mm² + N2XH-J 1x95 mm² (UPS_P1_TP_RG1) napajano od UPS naprava | - N2XH-O 4x150 mm² + N2XH-J 1x95 mm² (UPS_P1_TP_RG1) powered from UPS device |  |  | m | 11 |  | 0
| - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (UPS_P1_1_R) | - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (UPS_P1_1_R) |  |  | m | 152 |  | 0
| - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (UPS_N1_1_R) | - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (UPS_N1_1_R) |  |  | m | 15 |  | 0
| - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (UPS_N2_1_R) | - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (UPS_N2_1_R) |  |  | m | 17 |  | 0
| - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (UPS_N3_1_R) | - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (UPS_N3_1_R) |  |  | m | 17 |  | 0
| - N2XH-J 5x16 mm² (UPS_P1_2_R) | - N2XH-J 5x16 mm² (UPS_P1_2_R) |  |  | m | 139 |  | 0
| - N2XH-J 5x16 mm² (UPS_N1_2_R) | - N2XH-J 5x16 mm² (UPS_N1_2_R) |  |  | m | 15 |  | 0
| - N2XH-J 5x16 mm² (UPS_N2_2_R) | - N2XH-J 5x16 mm² (UPS_N2_2_R) |  |  | m | 15 |  | 0
| - N2XH-J 5x16 mm² (UPS_N3_2_R) | - N2XH-J 5x16 mm² (UPS_N3_2_R) |  |  | m | 15 |  | 0
| - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (UPS_P1_3_R) | - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (UPS_P1_3_R) |  |  | m | 113 |  | 0
| - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (UPS_N1_3_R) | - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (UPS_N1_3_R) |  |  | m | 15 |  | 0
| - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (UPS_N2_3_R) | - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (UPS_N2_3_R) |  |  | m | 15 |  | 0
| - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (UPS_N3_3_R) | - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (UPS_N3_3_R) |  |  | m | 15 |  | 0
| - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (UPS_P1_4_R) | - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (UPS_P1_4_R) |  |  | m | 70 |  | 0
| - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (UPS_N1_4_R) | - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (UPS_N1_4_R) |  |  | m | 15 |  | 0
| - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (UPS_N2_4_R) | - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (UPS_N2_4_R) |  |  | m | 15 |  | 0
| - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (UPS_N3_4_R) | - N2XH-O 4x25 mm² + N2XH-J 1x16 mm² (UPS_N3_4_R) |  |  | m | 15 |  | 0
| - N2XH-J 5x16 mm² (UPS_P1_5_R) | - N2XH-J 5x16 mm² (UPS_P1_5_R) |  |  | m | 83 |  | 0
| - N2XH-J 5x16 mm² (UPS_N1_5_R) | - N2XH-J 5x16 mm² (UPS_N1_5_R) |  |  | m | 17 |  | 0
| - N2XH-J 5x16 mm² (UPS_P1_6_R) | - N2XH-J 5x16 mm² (UPS_P1_6_R) |  |  | m | 33 |  | 0
| - N2XH-J 5x16 mm² (UPS_N1_6_R) | - N2XH-J 5x16 mm² (UPS_N1_6_R) |  |  | m | 17 |  | 0
| - N2XH-J 5x16 mm² (UPS_P1_6_R_LICEM) | - N2XH-J 5x16 mm² (UPS_P1_6_R_LICEM) |  |  | m | 80 |  | 0
| - N2XH-J 5x2,5 mm² (NN_P1_TP_A1) | - N2XH-J 5x2,5 mm² (NN_P1_TP_A1) |  |  | m | 10 |  | 0
| - N2XH-J 5x2,5 mm² (NN_P1_TP_A2) | - N2XH-J 5x2.5 mm² (NN_P1_TP_A2) |  |  | m | 15 |  | 0
| - N2XH-J 3x2,5 mm² (SN_P1_TP_J_4) | - N2XH-J 3x2,5 mm² (SN_P1_TP_J_4) |  |  | m | 15 |  | 0
| - N2XH-J 3x2,5 mm² (TK_P1_TP_R1) | - N2XH-J 3x2,5 mm² (TK_P1_TP_R1) |  |  | m | 8 |  | 0
8.5 | Dobava in montaža krmilnih kablov za nazivno napetost Un=0,4 kV, deloma položenih na police, deloma uvlečenih v zaščitne cevi vključno z označevalnimi ploščicami, odziv na ogenj vsaj Cca s1 d2 a1: | Supply and installation of control cables for rated voltage Un=0,4 kV, partly laid on shelves, partly encased in protective conduits including marker plates, reaction to fire not less than Cca s1 d2 a1:
| - N2XH-J 3x1,5 mm² | - N2XH-J 3x1,5 mm² |  |  | m | 200 |  | 0
| - N2XH-J 4x1,5 mm² | - N2XH-J 4x1,5 mm² |  |  | m | 20 |  | 0
| - N2XH-J 3x2,5 mm² | - N2XH-J 3x2,5 mm² |  |  | m | 110 |  | 0
| - N2XH-J 4x2,5 mm² | - N2XH-J 4x2,5 mm² |  |  | m | 30 |  | 0
| - N2XH-J 5x2,5 mm² | - N2XH-J 5x2,5 mm² |  |  | m | 50 |  | 0
| - N2XCH-J 2x1,5 mm² | - N2XCH-J 2x1,5 mm² |  |  | m | 120 |  | 0
| - N2XCH-J 2x2,5 mm² | - N2XCH-J 2x2,5 mm² |  |  | m | 20 |  | 0
| - N2XCH-J 3x1,5 mm² | - N2XCH-J 3x1,5 mm² |  |  | m | 60 |  | 0
| - N2XCH-J 3x2,5 mm² | - N2XCH-J 3x2,5 mm² |  |  | m | 40 |  | 0
| - N2XCH-J 4x1,5 mm² | - N2XCH-J 4x1,5 mm² |  |  | m | 50 |  | 0
| - N2XCH-J 4x2,5 mm² | - N2XCH-J 4x2,5 mm² |  |  | m | 40 |  | 0
| - N2XCH-J 7x1,5 mm² | - N2XCH-J 7x1,5 mm² |  |  | m | 190 |  | 0
| - N2XCH-J 7x2,5 mm² | - N2XCH-J 7x2,5 mm² |  |  | m | 20 |  | 0
| - ÖLFLEX® CLASSIC 110 H 3x1,5 mm² | - ÖLFLEX® CLASSIC 110 H 3x1,5 mm² |  |  | m | 240 |  | 0
| - ÖLFLEX® CLASSIC 110 H 8x1,5 mm² | - ÖLFLEX® CLASSIC 110 H 8x1,5 mm² |  |  | m | 20 |  | 0
| - CTSE 4x3x0,5 mm² | - CTSE 4x3x0,5 mm² |  |  | m | 30 |  | 0
| - CPR6003 | - CPR6003 |  |  | m | 40 |  | 0
| NN ENERGETSKI ZBIRALKE IN NN ENERGETSKI KABLI | LV BUSBARS AND LV POWER CABLES | [5 empty] | 0

## 3.3.9_Pritrdilna oprema za NN k
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.3 | ELEKTRO DELA | ELECTRICAL WORKS
3.3.9 | ZAŠČITNI CEVI IN KABELSKI POLICE | PROTECTIVE HOSES AND CABLE RACKS |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
9 | ZAŠČITNI CEVI IN KABELSKI POLICE | PROTECTIVE HOSES AND CABLE RACKS
9.1 | Dobava in montaža izolirnih gibljivih in trdih PN cevi, brez halogena: | Supply and installation of insulating flexible and rigid PN pipes, halogen-free:
a. | - izolirna PN cev fi 13,5 mm do 23 mm | - pN insulation pipe fi 13,5 mm to 23 mm | m | 200 |  | 0
b. | - izolirna giblljiva cev fi 13,5 mm do 23 mm | - insulating flexible hose fi 13,5 mm to 23 mm | m | 60 |  | 0
9.2 | Dobava in montaža perforiranih kabelskih polic, komplet pokrovi, s pritrdilnim priborom, obešalnim priborom, koleni, spojnim materialom in višinskimi prehodi, kot na primer proizvod Hermi: | Supply and installation of perforated cable racks, complete with covers, fixings, hanging accessories, elbows, joining material and height transitions, such as the Hermi product:
a. | - kabelska polica PK 100/60mm | - cable shelf PK 100/60mm | m | 20 |  | 0
b. | - kabelska polica PK 200/60mm | - cable shelf PK 200/60mm | m | 30 |  | 0
c. | - kabelska polica PK 300/60mm | - cable shelf PK 300/60mm | m | 10 |  | 0
d. | - kabelska polica PK 400/60mm | - cable shelf PK 400/60mm | m | 60 |  | 0
9.3 | Označevanje kabelskih polic s trajnimi oznakami (na 6m) | Permanent marking of cable shelves (at 6m) | kos | 15 |  | 0
| ZAŠČITNI CEVI IN KABELSKI POLICE | PROTECTIVE HOSES AND CABLE RACKS |  |  |  | 0

## 3.3.10_Meritve el. energije
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.3 | ELEKTRO DELA | ELECTRICAL WORKS
3.3.10 | OBRAČUNSKE MERITVE ELEKTRIČNE ENERGIJE | ELECTRICITY METERING | [5 empty] | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description |  |  | EM | Količina | Cena/EM | Cena
10 | OBRAČUNSKE MERITVE ELEKTRIČNE ENERGIJE | ELECTRICITY METERING
10.1 | Dobava in montaža predfabricirane, pločevinaste zidne omare, za namestitev števca delovne in jalove energije za obračunske meritve na SN nivoju - NN_P1_TP_Q1. Opremljene je z vsemi potrebnimi nosilci, blendami, vrati, izrezi, ključavnico, z označenimi priključki na stikalne elemente in žične povezave ter pripravljena za priklop. Uvod kablov v omaro s pomočjo uvodnic vgrajenih v dno razdelilnika. Omara mora biti opremljen po seznamu opreme v dokumentu št. JULFS--7E9100, ožičena in preizkušena. Opomba: Omarica mora biti opremljena skladno s soglasjem za priključitev oziroma projektnimi pogoji Elektro Ljubljana, Sistemskimi obratovalnimi navodili za distribucijski sistem električne energije (Ur. l. RS 77/2024) in Prilogo 2 - Tipizacija merilnih mest. Vgrajena oprema: | Supply and installation of a prefabricated, sheet metal, wall-mounted cabinet for the installation of an active and reactive energy meter for billing measurements at MV level - NN_P1_TP_Q1. It shall be equipped with all necessary brackets, blocks, doors, cut-outs, lock, marked connections to switching elements and wire connections and ready for connection. The cabinet shall be wired and tested for cable entry by means of glands installed in the bottom of the manifold. The cabinet shall be equipped according to the equipment list in document No. JULFS--7E9100, and shall be wired and tested. Note: The cabinet must be equipped in accordance with the connection consent or project conditions of Elektro Ljubljana, the System Operating Instructions for the Electricity Distribution System (Official Gazette of the Republic of Slovenia 77/2024) and Annex 2 - Typisation of Metering Points. Built-in equipment: |  |  | kpl | 1 |  | 0
a. | Zidna omara iz jeklene pločevine, dimenzij cca (šxvxg) 500x700x250 mm, opleskana v sivi barvi RAL 7035, zaščita IP43, s ključavnico Elektro Ljubljana, komplet z ožičenjem, veznim in pritrdilnim materialom, opremljena po namembnosti za: | Wall cabinet made of sheet steel, dimensions approx. (wxwxd) 500x700x250 mm, grey RAL 7035, protection IP43, with Elektro Ljubljana lock, complete with wiring, connecting and fixing material, equipped according to the intended use for: | kpl | 1
b. | Indirektni trifazni dvosmerni števec delovne in jalove energije z merjeno močjo, razreda točnosti C ali 0,5 za delovno energijo ter 1 ali 2 za jalovo energijo, s komunikacijskim vmesnikom, tip MT880-T1A32R46 (šifra tipa 1644), osnovne lastnosti: 3x58/100 V ... 3x230/400 V, 5A. Osnovne lastnosti: GSM/GPRS.. Tip: MT880-T1A32R46, proizvajalec: ISKRAEMECO | Indirect three-phase bidirectional active and reactive energy meter with measured power, accuracy class C or 0,5 for active energy and 1 or 2 for reactive energy, with communication interface, type MT880-T1A32R46 (type code 1644), basic characteristics: 3x58/100 V ... 3x230/400 V, 5A. Basic characteristics: GSM/GPRS... Type: MT880-T1A32R46, manufacturer: ISKRAEMECO | kos | 1
c. | Komunikacijski vmesnik Iskraemec, tip: CM-v-3; GSM/GPRS (šifra tipa 1646). | Iskraemec communication interface, type: CM-v-3; GSM/GPRS (type code 1646). | kos | 1
d. | Merilna spončna garnitura: - Tokovna in napetostna priključna sponka 6 mm2 (14x) - Ozemljitvena sponka (1x) - Tripolni inštalacijski odklopnik 6 A, karakt. B (1x) - Nosilci, oznake, pokrovi, ... (1x) | Measuring clamp set: - Current and voltage connection terminal 6 mm2 (14x) - Earthing clip (1x) - Tri-pole circuit breaker 6 A, cart. B (1x) - Carriers, labels, covers, ... (1x) | kpl | 1
e. | GSM antena s kablom | GSM antenna with cable | kpl | 1
f. | Odvodnik prenapetosti, razred I, Uc=150V, Up=1,0kV pri In=25kA (8/20µs), impulzni odvodni tok 25kA (10/350µs); kot na primer tip: PROTEC B2S(R) 37,5/150 (3+0), proizvod: Iskra zaščite (506.052) | Surge arrester, class I, Uc=150V, Up=1,0kV at In=25kA (8/20µs), impulse discharge current 25kA (10/350µs); as for example type: PROTEC B2S(R) 37,5/150 (3+0), product: Iskra Protection (506.052) | kos | 1
g. | Drobni montažni material, ožičenje, števčna plošča, označevalni material ipd. | Minor assembly material, wiring, counter plate, marking material, etc. | kpl | 1
10.2 | Dobava in montaža predfabricirane, pločevinaste zidne omare, za namestitev števca delovne in jalove energije za obračunske meritve DEA - NN_P1_TP_Q2. Opremljene je z vsemi potrebnimi nosilci, blendami, vrati, izrezi, ključavnico, z označenimi priključki na stikalne elemente in žične povezave ter pripravljena za priklop. Uvod kablov v omaro s pomočjo uvodnic vgrajenih v dno razdelilnika. Omara mora biti opremljen po seznamu opreme v dokumentu št. JULFS--7E9101, ožičena in preizkušena. Opomba: Omarica mora biti opremljena skladno s soglasjem za priključitev oziroma projektnimi pogoji Elektro Ljubljana, Sistemskimi obratovalnimi navodili za distribucijski sistem električne energije (Ur. l. RS 77/2024) in Prilogo 2 - Tipizacija merilnih mest. Vgrajena oprema: | Supply and installation of a prefabricated, sheet metal, wall-mounted cabinet for the installation of a DEA - NN_P1_TP_Q2 working and reactive energy meter for billing measurements. It shall be fitted with all necessary brackets, blocks, doors, cut-outs, lock, marked connections to switching elements and wire connections and ready for connection. The cables shall be fed into the cabinet by means of glands installed in the bottom of the manifold. The cabinet shall be equipped according to the equipment list in document No JULFS--7E9101, wired and tested. Note: The cabinet must be equipped in accordance with the connection consent or project conditions of Elektro Ljubljana, the System Operating Instructions for the Electricity Distribution System (Official Gazette of the Republic of Slovenia 77/2024) and Annex 2 - Typisation of Metering Points. Built-in equipment: |  |  | kpl | 1 |  | 0
a. | Zidna omara iz jeklene pločevine, dimenzij cca (šxvxg) 500x700x250 mm, opleskana v sivi barvi RAL 7035, zaščita IP43, s ključavnico Elektro Ljubljana, komplet z ožičenjem, veznim in pritrdilnim materialom, opremljena po namembnosti za: | Wall cabinet made of sheet steel, dimensions approx. (wxwxd) 500x700x250 mm, grey RAL 7035, protection IP43, with Elektro Ljubljana lock, complete with wiring, connecting and fixing material, equipped according to the intended use for: | kpl | 1
b. | Indirektni trifazni dvosmerni števec delovne in jalove energije z merjeno močjo, razreda točnosti B ali 1 za delovno energijo ter 2 za jalovo energijo, s komunikacijskim vmesnikom - za odjemalce in proizvajalce (šifra tipa 1643), osnovne lastnosti: 3x58/100 V ... 3x230/400 V, 5A. Tip: MT880-T1A42R56, proizvajalec: ISKRAEMECO | Indirect three-phase bidirectional active and reactive power meter with metered power, accuracy class B or 1 for active power energy and 2 for reactive energy, with communication interface - for consumers and producers (type code 1643), basic characteristics: 3x58/100 V ... 3x230/400 V, 5A. Type: MT880-T1A42R56, manufacturer: ISKRAEMECO | kos | 1
c. | Komunikacijski vmesnik Iskraemec, tip: CM-e-3; Ethernet (šifra tipa 1646). | Iskraemec communication interface, type: CM-e-3; Ethernet (type code 1646). | kos | 1
d. | Merilna spončna garnitura: - Tokovna in napetostna priključna sponka 6 mm2 (14x) - Ozemljitvena sponka (1x) - Tripolni inštalacijski odklopnik 6 A, karakt. B (1x) - Nosilci, oznake, pokrovi, ... (1x) | Measuring clamp set: - Current and voltage connection terminal 6 mm2 (14x) - Earthing clip (1x) - Tri-pole circuit breaker 6 A, cart. B (1x) - Carriers, labels, covers, ... (1x) | kpl | 1
e. | Odvodnik prenapetosti s pomožnim kontaktom, tip 1+2, Uc=320V, In=25kA, Imax=60kA (8/20µs), Iimp=12,5kA (10/350µs); kot na primer tip: PROTEC B2S(R) 37,5/320 (3+0), proizvod: Iskra zaščite (506.054) | Surge arrester with auxiliary contact, type 1+2, Uc=320V, In=25kA, Imax=60kA (8/20µs), Iimp=12,5kA (10/350µs); as for example type: PROTEC B2S(R) 37,5/320 (3+0), product: Iskra Protection (506.054) | kos | 1
f. | Drobni montažni material, ožičenje, števčna plošča, označevalni material ipd. | Minor assembly material, wiring, counter plate, marking material, etc. | kpl | 1
| OBRAČUNSKE MERITVE ELEKTRIČNE ENERGIJE | ELECTRICITY METERING | [5 empty] | 0

## 3.3.11_Vodenje in nadzor
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.3 | ELEKTRO DELA | ELECTRICAL WORKS
3.3.11 | NAPRAVE ZA VODENJE IN NADZOR | COMMAND AND CONTROL EQUIPMENT | [5 empty] | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description |  |  | EM | Količina | Cena/EM | Cena
11 | NAPRAVE ZA VODENJE IN NADZOR | COMMAND AND CONTROL EQUIPMENT
11.1 | Priprava podatkov za zajem na krmilnik za vodenje z možnostjo serijske ali paralelne komunikacije z nadzornim računalnikom v obeh smereh: | Preparation of data for capture on the control controller with the possibility of serial or parallel communication with the control computer in both directions: |  |  | kpl | 1 |  | 0
a. | zajem podatkov SN bloka: | capture of SN block data:
| - signalizacija položaja odklopnikov, odklopnih ločilnikov (DI); povezava na krmilnik energetike in SCADA energetika | - signalling of the position of circuit breakers, disconnectors (DI); connection to the energy controller and SCADA energy | kpl | 1
| - signalizacija ob pregoretju varovalk (DI); povezava na krmilnik TP | - fuse blown alarm (DI); connection to TP controller | kpl | 1
b. | zajem podatkov transformatorja: | transformer data capture:
| - signalizacija delovanja ventilatorjev (DI); povezava na krmilnik TP | - fan operation signalling (DI); connection to TP controller | kpl | 1
| - signalizacija izpada transformatorjev (DI); povezava na krmilnik TP | - transformer outage (DI) signalling; connection to TP controller | kpl | 1
c. | zajem podatkov NN bloka: | capture of LV block data:
| - signalizacija položajev odklopnikov in delovanje zaščite (DI); povezava na krmilnik TP | - signalling of circuit breaker positions and protection operation (DI); connection to TP controller | kpl | 1
| - Ethernet komunikacija digitalnih naprav za merjenje osnovnih električnih veličin; povezava na krmilnik TP | - Ethernet communication of digital devices for measuring basic electrical quantities; connection to TP controller | kpl | 1
| - RS485 komunikacija digitalnih naprav za merjenje osnovnih električnih veličin; povezava na krmilnik TP | - RS485 communication of digital devices for measuring basic electrical quantities; connection to TP controller | kpl | 1
d. | zajem podatkov kompenzacije jalove energije: | capture of reactive energy compensation data:
| - signalizacija napake na napravi (DI); povezava na krmilnik TP | - device fault indication (DI); connection to TP controller | kpl | 1
e. | zajem naprave za brezprekinitveno napajanje: | capture of an uninterruptible power supply device:
| - WEB/SNMP nadzor nad UPS-om; povezava na krmilnik TP | - WEB/SNMP control of UPS; connection to TP controller | kpl | 1
| - signalizacija izpada inštalacijskih odklopnikov v razdelilniku za brezprekinitveno napajanje (DI); povezava na krmilnik TP | - failure signalling of the installation circuit breakers in the uninterruptible power supply (UPS) distribution box (DI); connection to the TP controller | kpl | 1
f. | zajem podatkov diesel električnega agregata in DEA glavnega razdelilnika: | data capture of the diesel generator set and DEA of the main distributor:
| - signalizacija napak DEA, signalizacija delovanja DEA, signalizacija položaja odklopnikov; preko Modbus TPC na krmilnik TP | - dEA fault signalling, DEA operation signalling, circuit breaker position signalling; via Modbus TPC to TP controller | kpl | 1
g. | zajem podatkov Virtualne elektrarne: | virtual Power Plant data capture:
| - povezava na SCADA DEA | - link to SCADA DEA | kpl | 1
h. | zajem podatkov števcev električne energije: | capture electricity meter data:
| - povezava preko RS-485 na krmilnik TP | - rS-485 connection to the TP controller | kpl | 1
| - povezava preko GSM na Elektro Ljubljana | - gSM connection to Elektro Ljubljana | kpl | 1
11.2 | Dobava in montaža prostostoječe kovinske omare za potrebe vodenja in nadzora TP. Omara, kot na primer: Rittal, VX 8606.000, dimenzije: 2000 mm x 600 mm x 600 mm (VxŠXG), na podstavku višine 100 mm. Omara ima enokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. Kot na primer tip: VX 8606.000, proizvod: Rittal Sestava omare je naslednja: | Supply and installation of a freestanding metal cabinet for the control and monitoring of TP. The cabinet, e.g. type: Rittal, VX 8606.000, dimensions: 2000 mm x 600 mm x 600 mm (HxWxD), on a base height of 100 mm. The cabinet has a full-height single-leaf door at the front, a comfort handle and a two-hinge key-operated locking system. e.g. type: VX 8606.000, manufactured by: Rittal The wardrobe is composed as follows: |  |  | kpl | 1 |  | 0
a. | - osnovna omara VX 8606.000 (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor). | - vX 8606.000 base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories). | kos | 1
b. | - podstavek 100 mm, širine 600 mm, 8660.002. | - base 100 mm, width 600 mm, 8660.002. | kos | 2
c. | - stranica podstavka 100 mm, globine 600 mm, 8660.033. | - base side 100 mm, depth 600 mm, 8660.033. | kos | 2
d. | - stranska desna stena 8106.245. | - right side wall 8106.245. | kos | 1
e. | - stranska leva stena 8106.245. | - left side wall 8106.245. | kos | 1
f. | - ročka za odpiranje 8618.250. | - 8618.250 opening handle. | kos | 1
g. | - cilinder vložek 2467.000. | - cylinder insert 2467.000. | kos | 1
h. | - torba za načrte A4 2514.000. | - a4 plan bag 2514.000. | kos | 1
i. | - EMC spojka opleta SZ 2388.100 (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ 2388.100 (for cables with braid diameter fi=3-10mm), | kos | 10
j. | - objemka za pritrjevanje kabla DK 7077.000 (za kable premera fi=6-14mm). | - cable clamp DK 7077.000 (for cables with diameter fi=6-14mm). | kos | 50
k. | - Glavno stikalo, 3-polno, 25 A, montaža na vrata Kot na primer Schneider Electric/WBD0 | - Main switch, 3-pole, 25 A, door mounting Such as Schneider Electric/WBD0 | kos | 2
l. | - Svetilka za omaro, 13W LED, 230VAC Kot na primer: RITTAL/SZ 2500.300 | - Cabinet light, 13W LED, 230VAC As for example: RITTAL/SZ 2500.300 | kos | 1
m. | - Termostat Kot na primer: Rittal/SK 3110.000 | - Thermostat Such as Rittal/SK 3110.000 | kos | 1
n. | - Grelec za omaro 100W, 230V AC Kot na primer: RITTAL/SK/SK-3105.360 | - Cupboard heater 100W, 230V AC Such as RITTAL/SK/SK-3105.360 | kos | 1
o. | - Vtičnica v omari z zaščitnim kontaktom, 250VAC, 16A Kot na primer: RITTAL/SZ 2506.100 | - Socket outlet in enclosure with protective contact, 250VAC, 16A As for example: RITTAL/SZ 2506.100 | kos | 1
p. | - Stikalo pozicije vrat, 1NO+1NC 400VAC, 6A Kot na primer: RITTAL/SZ 4127.010 | - Door position switch, 1NO+1NC 400VAC, 6A As for example: RITTAL/SZ 4127.010 | kos | 1
q. | - Signalna svetilka na vratih LED, 230VAC, bela, Kot na primer: Schneider Electric/XB4FVM1 | - LED door signal lamp, 230VAC, white, Such as Schneider Electric/XB4FVM1 | kos | 2
r. | - Ventilator komplet s filtrom 255 x 255 Kot na primer: RITTAL/SK.3240100+SK.3240200 | - Fan complete with filter 255 x 255 Such as RITTAL/SK.3240100+SK.3240200 | kos | 1
s. | - Univerzalni napajalnik, 1 - fazi, 100-240 V AC, 24 V DC, 10 A Kot na primer: Schneider Electric/ABLS1A24100 | - Universal power supply, 1-phase, 100-240 V AC, 24 V DC, 10 A Such as Schneider Electric/ABLS1A24100 | kos | 1
t. | - Inštalacijski odklopnik, 50kA, iC60N, 1P, 4A, C + Pomožni kontakt iOF/SD+OF, iC60 Kot na primer: Schneider Electric/A9F04104+A9A26929 | - Circuit breaker, 50kA, iC60N, 1P, 4A, C + Auxiliary contact iOF/SD+OF, iC60 Such as Schneider Electric/A9F04104+A9A26929 | kos | 2
u. | - Inštalacijski odklopnik, 50kA, iC60N, 1P, 6A, C + Pomožni kontakt iOF/SD+OF, iC60 Kot na primer: Schneider Electric/A9F04106+A9A26929 | - Circuit breaker, 50kA, iC60N, 1P, 6A, C + Auxiliary contact iOF/SD+OF, iC60 Such as Schneider Electric/A9F04106+A9A26929 | kos | 1
v. | - Inštalacijski odklopnik, 50kA, iC60N, 1P, 10A, C + Pomožni kontakt iOF/SD+OF, iC60 Kot na primer: Schneider Electric/A9F04110+A9A26929 | - Circuit breaker, 50kA, iC60N, 1P, 10A, C + Auxiliary contact iOF/SD+OF, iC60 Such as Schneider Electric/A9F04110+A9A26929 | kos | 4
w. | - Inštalacijski odklopnik, 50kA, iC60N, 2P, 6A, C + Pomožni kontakt iOF/SD+OF, iC60 Kot na primer: Schneider Electric/A9F74206+A9A26929 | - Circuit breaker, 50kA, iC60N, 2P, 6A, C + Auxiliary contact iOF/SD+OF, iC60 Such as Schneider Electric/A9F74206+A9A26929 | kos | 4
x. | - Inštalacijski odklopnik, 50kA, iC60N, 1P+N, 40A, C + Pomožni kontakt iOF/SD+OF, iC60 Kot na primer: Schneider Electric/A9F04640+A9A26929 | - Circuit breaker, 50kA, iC60N, 1P+N, 40A, C + Auxiliary contact iOF/SD+OF, iC60 Such as Schneider Electric/A9F04640+A9A26929 | kos | 2
y. | - Odvodnik prenapetosti 1P+N za TN-S sistem, Uc=340V, In=15kA, Imax (8/20)=40kA Kot na primer: Schneider Electric/iPF K 40 | - Surge arrester 1P+N for TN-S system, Uc=340V, In=15kA, Imax (8/20)=40kA Such as Schneider Electric/iPF K 40 | kos | 2
z. | - Rele sponka,vhodna napetost 24V AC/DC, 1 preklopni kontakt Kot na primer: Phoenix Contact/APLC-RSC- 24UC/21 | - Relay terminal, input voltage 24V AC/DC, 1 switching contact Such as Phoenix Contact/APLC-RSC- 24UC/21 | kos | 4
a1. | - Krmilnik TP, kot na primer tip: PLC M340, proizvod Schneider Electric, v konfiguraciji: | - A TP controller, such as type: PLC M340, Schneider Electric, in the configuration: | kpl | 1
| Modicon M340 rack (plošča) z 12 ražami (utori) BMXXBP1200 - 1 kos | Modicon M340 rack (panel) with 12 slots (grooves) BMXXBP1200 - 1 piece
| Modicon X80 napajalni modul - primarna napetost: 18...62.4 V DC izoliran - sekundarna moč: 31.2 W - kompatibilen z BMXXBE… BMXCPS3020 - 1 kos | Modicon X80 power supply module - primary voltage: 18...62.4 V DC isolated - secondary power: 31.2 W - compatible with BMXXBE.. BMXCPS3020 - 1 piece
| Modicon M340 procesor CPU340-20 Modbus Ethernet - število lokalnih rack-ov: 4 (z 4, 6, 8 ali 12 režami), 48 rež (bez napajanja) - I/O: 1024 diskretnih in 256 analognih kanalov v rack-kih - distribuirani I/O: 63 Modbus TCP naprav (IO scanning funkcija), 32 Modbus RTU naprav - možnost dodajanja 2 dodatnih Ethernet komunikacijskih modulov - kapaciteta notranjega pomnilnika: 4094 kB notranjega uporabniškega RAM-a, 3584 kB za programe, konstante in simbole, 256 kB za locirane/nelocirane podatke - pomnilniškakartica 8MB za varnostno kopiranje programov, konstant in simbolov - struktura aplikacije: 1 Master task, 1 Fast task, 64 Event task BMXP342020 - 1 kos | Modicon M340 CPU340-20 Modbus Ethernet processor - number of local racks: 4 (with 4, 6, 8 or 12 slots), 48 slots (without power supply) - I/O: 1024 discrete and 256 analogue channels in rack-mounted units - distributed I/O: 63 Modbus TCP devices (IO scanning function), 32 Modbus RTU devices - possibility to add 2 additional Ethernet communication modules - internal memory capacity: 4094 kB internal user RAM, 3584 kB for programs, constants and symbols, 256 kB for localised/unlocalised data - 8MB memory card for backing up programs, constants and symbols - application structure: 1 Master task, 1 Fast task, 64 Event tasks BMXP342020 - 1 piece
| Modicon M340 Ethernet TCP/IP komunikacijski modul - 4 x RJ45 10/100 Mbit/s - funkcije: Bandwidth management, Data Editor (via PC terminal), FDR server, Rack Viewer, SNMP network administrator, Modbus TCP I/O Scanner and Messaging, Ethernet/IP I/O Scanner and Messaging, Embedded 4-port switch, RSTP support, Port mirroring BMXNOC0401 - kos | Modicon M340 Ethernet TCP/IP communication module - 4 x RJ45 10/100 Mbit/s - features: Bandwidth management, Data Editor (via PC terminal), FDR server, Rack Viewer, SNMP network administrator, Modbus TCP I/O Scanner and Messaging, Ethernet/IP I/O Scanner and Messaging, Embedded 4-port switch, RSTP support, Port mirroring BMXNOC0401 - piece
| Komunikacijski modul s serijskim vhodom, 2-kanalni RS–485/232 v načinu dela Modbus in Character. RS232 vmesnik: RJ45 priključek, 115.2 kbit/s 8-žilni RS485 vmesnik: RJ45 priključek, 57.6 kbit/s 1 sukana parica. BMXNOM0200 - 1 kos | Communication module with serial input, 2-channel RS-485/232 in Modbus and Character working mode. RS232 interface: RJ45 connector, 115.2 kbit/s 8-wire RS485 interface: RJ45 connector, 57.6 kbit/s 1 twisted pair. BMXNOM0200 - 1 piece
| Digitalni vhodni modul, 64 vhodov, vhodna napetost 24 V DC, z dvema 40-pinskima konektorjema za tovarniški kabel. BMXDDI6402K - 7 kosov | Digital input module, 64 inputs, input voltage 24 V DC, with two 40-pin connectors for factory cable. BMXDDI6402K - 7 pieces
| Pasivna priključna podlaga, 16 digitalnih vhodov/izhodov, 20-pinski konektor. Napajanje 19...30 V DC, steklena varovalka 5x20 mm za zaščito pred kratkim stikom. ABE7H16C11 - 36 kosov | Passive connection base, 16 digital inputs/outputs, 20-pin connector. Power supply 19...30 V DC, 5x20 mm glass fuse for short-circuit protection. ABE7H16C11 - 36 pieces
| Priključni kabel za digitalni vhodni modul, 2 x HE10 konektor na eni strani in 4-pinski konektor na drugi strani, dolžina 3 m. BMXFCC303 - 18 kosov | Connection cable for digital input module, 2 x HE10 connectors on one side and 4-pin connector on the other side, length 3 m. BMXFCC303 - 18 pieces
| Digitalni izhodni modul Modicon X80, 64 izhodov, tranzistorski, izhodna napetost 24 V DC, kanalski tok 0,1 A, z dvema 40-pinskima konektorjema za tovarniški kabel. BMXDDO6402K - 2 kosa | Modicon X80 digital output module, 64 outputs, transistor, output voltage 24 V DC, channel current 0.1 A, with two 40-pin connectors for factory cable. BMXDDO6402K - 2 pieces
| Izolacijska omarica za signal RS485 - RJ45 in vijačni priključek - predpolarizirane linije (2 R 620 Ohm) - izolacija linije RS485 - končni adapter linije (RC 120 Ohm, 1 nF) TWDXCAISO - 4 kose | Isolation box for RS485 signal - RJ45 and screw connector - pre-polarised lines (2 R 620 Ohm) - rS485 line isolation - line termination adapter (RC 120 Ohm, 1 nF) TWDXCAISO - 4 pieces
| Zaslon na dotik HMI Harmony ST6 - velikost 10" - resolucija 1024x600 - 16 milijuna barv TFT - napajanje 24 V DC - delovna temperatura 0-50°C - zaščita zaslona IP65 - procesor s hitrostjo 800MHz - pomnilnik naprave 1 GB, backup pomnilnik 512 kB NVRAM i 128 MB uporabniškega pomnilnika - integrirani vhod tipa USB 2.0 port tipa micro B, Ethernet TCP/IP z 2 RJ45 portoma, COM1 serijski port SUB-D 9 RS232C, COM2 serijski port RJ45 RS485, USB 2.0 port tipa A - komunikacijski protokoli Modbus, Modbus TCP/IP, Uni-Telway, protokoli drugih proizvajalcev - v skladu s standardi EN, UL, CSA HMIST6500 - 1 kos | Harmony ST6 HMI touchscreen - size 10" - resolution 1024x600 - 16 million TFT colours - 24 V DC power supply - operating temperature 0-50°C - iP65 screen protection - 800MHz processor - 1 GB device memory, 512 KB NVRAM backup memory and 128 MB user memory - integrated USB 2.0 type micro B port, Ethernet TCP/IP with 2 RJ45 ports, COM1 serial port SUB-D 9 RS232C, COM2 serial port RJ45 RS485, USB 2.0 type A port - communication protocols Modbus, Modbus TCP/IP, Uni-Telway, protocols from other manufacturers - in accordance with EN, UL, CSA standards HMIST6500 - 1 piece
| Modicon upravljalno stikalo L2 - 16 x RJ45 portov - napajanje 24 V DC - podpira protokole Ethernet TCP/IP, SSH, HTTP, HTTPS, SNMP, RS232, LLDP, Telnet, SNTP, MRP (Media Redundancy Protocol) MCSESM163F23F0 - 1 kos | Modicon control switch L2 - 16 x RJ45 ports - 24 V DC power supply - supports Ethernet TCP/IP, SSH, HTTP, HTTPS, SNMP, RS232, LLDP, Telnet, SNTP, MRP (Media Redundancy Protocol) protocols MCSESM163F23F0 - 1 piece
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. - 1 kpl | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc. - 1 pcs
11.3 | Dobava in montaža krmilnih kablov za nazivno napetost Un=0,4 kV, deloma položenih na police, deloma uvlečenih v zaščitne cevi vključno z označevalnimi ploščicami, odziv na ogenj vsaj Cca s1 d2 a1: | Supply and installation of control cables for rated voltage Un=0,4 kV, partly laid on shelves, partly encased in protective conduits including marker plates, reaction to fire not less than Cca s1 d2 a1:
| - J-H(St)H 2x2x0,8 mm² | - J-H(St)H 2x2x0,8 mm² |  |  | m | 510 |  | 0
| - J-H(St)H 4x2x0,8 mm² | - J-H(St)H 4x2x0,8 mm² |  |  | m | 110 |  | 0
| - J-H(St)H 6x2x0,8 mm² | - J-H(St)H 6x2x0,8 mm² |  |  | m | 100 |  | 0
| - J-H(St)H 10x2x0,8 mm² | - J-H(St)H 10x2x0,8 mm² |  |  | m | 180 |  | 0
| - J-H(St)H 20x2x0,8 mm² | - J-H(St)H 20x2x0,8 mm² |  |  | m | 510 |  | 0
11.4 | Dobava in polaganje na kabelske police oz. uvlečenje v inštalacijske cevi, vključno z označevalnimi ploščicami, razvodnicami ter drobnim in spojnim materialom: | Supply and installation on cable racks or insertion into conduit pipes, including marker plates, conduit boxes, small and jointing materials:
| -F/FTP-Category 6A, 4x2x23 AWG, brezhalogenski, kot na primer: Leviton | -F/FTP-Category 6A, 4x2x23 AWG, halogen-free, such as Leviton |  |  | m | 150 |  | 0
| NAPRAVE ZA VODENJE IN NADZOR | COMMAND AND CONTROL EQUIPMENT | [5 empty] | 0

## 3.3.12_Ozemljitve
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.3 | ELEKTRO DELA | ELECTRICAL WORKS
3.3.12 | OZEMLJITVE IN IZENAČITVE POTENCIALOV | EARTHING AND EQUIPOTENTIAL BONDING |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
12 | OZEMLJITVE IN IZENAČITVE POTENCIALOV | EARTHING AND EQUIPOTENTIAL BONDING
12.1 | Izvedbo ozemljitev v TP ter obročev za izenačevanje potencialov v prostorih TP, komplet s pritrdilnim in spojnim priborom in pomožnim materialom: | Installation of earthing systems in the TP and equipotential bonding rings in the TP premises, complete with fixing and bonding fittings and auxiliary materials:
a. | - Rf valjanec 30x3,5 mm | - Rf roller 30x3,5 mm | m | 110 |  | 0
12.2 | Dobava in polaganje: Vodnik za izenačevanje potenciala, deloma položene na police, deloma uvlečen v zaščitne cevi vključno z označevalnimi ploščicami, odziv na ogenj vsaj Cca s1 d2 a1. Kabli brez halogena. N2XH-J, rumeno/zelena. | Supply and installation: Potential equalisation conductor, partly laid on shelves, partly enclosed in protective tubes including marker plates, reaction to fire at least Cca s1 d2 a1. N2XH-J, yellow/green.
a. | - 16 mm2 | - 16 mm2 | m | 50 |  | 0
b. | - 35 mm2 | - 35 mm2 | m | 50 |  | 0
c. | - 70 mm2 | - 70 mm2 | m | 65 |  | 0
d. | - 95 mm2 | - 95 mm2 | m | 30 |  | 0
e. | - 120 mm2 | - 120 mm2 | m | 10 |  | 0
12.3 | Križna sponka: Rf 30x3,5 mm/H07V-K 16 mm2, Rf 30x3,5 mm/H07V-K 35 mm2, Rf 30x3,5 mm/H07V-K 70 mm2, Rf 30x3,5 mm/H07V-K 95 mm2, Rf 30x3,5 mm/FeZn 25x4 mm, Rf 30x3,5 mm/Rf 30x3,5 mm | Cross clamp: Rf 30x3,5 mm/H07V-K 16 mm2, Rf 30x3,5 mm/H07V-K 35 mm2, Rf 30x3,5 mm/H07V-K 70 mm2, Rf 30x3,5 mm/H07V-K 95 mm2, Rf 30x3,5 mm/FeZn 25x4 mm, Rf 30x3,5 mm/Rf 30x3,5 mm | kos | 130 |  | 0
12.4 | Križna sponka: FeZn 25x4 mm/FeZn 25x4 mm | Cross clamp: FeZn 25x4 mm/FeZn 25x4 mm | kos | 20 |  | 0
12.5 | Križna sponka: kovinskih mas ter nosilnih in drugih kovinskih konstrukcij, rešetk za prezračevanje, kabelskih polic, ipd. za vijake M6-M12 | Cross clamp: for metal masses and load-bearing and other metal structures, ventilation grilles, cable racks, etc. for M6-M12 screws | kos | 40 |  | 0
12.6 | Križna sponka: električne razdelilnike | Cross-clamp: electrical distributors | kos | 55 |  | 0
12.7 | Drobni montažni in pritrdilni material: vijaki M12, M10, M8, M6 s podložkami in maticami, kabelski čevlji, nosilci Rf valjanca, PN cevi s pritrdilnim materialom, ipd. - ocenjeno | Small mounting and fixing material: screws M12, M10, M8, M6 with washers and nuts, cable shoes, Rf roller brackets, PN pipes with fixing material, etc. - estimated | kpl | 1 |  | 0
| OZEMLJITVE IN IZENAČITVE POTENCIALOV | EARTHING AND EQUIPOTENTIAL BONDING |  |  |  | 0

## 3.3.13_Obrtniška dela
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.3 | ELEKTRO DELA | ELECTRICAL WORKS
3.3.13 | GRADBENO - OBRATNIŠKA DELA V TP | CONSTRUCTION AND PLANT WORKS IN TP |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
13 | GRADBENO - OBRATNIŠKA DELA V TP | CONSTRUCTION AND PLANT WORKS IN TP
13.1 | Izdelava tesnjenja prehodov kablov in kabelskih inštalacij skozi požarne sektorje, ki ga z ustreznimi materiali izvede izvajalec z licenco ter na koncu izda ustrezni certifikat (izvedba in uporabljen material v skladu s standardom DIN 4102, skladno s smernico SZPV 408, skladno s NPV (EI60) in po navodilih proizvajalca), približno: f 100 mm. OPOMBA: tesnenje mora biti takšnega tipa, ki omogoča naknadno vstavljanje kablov. Kot na primer: Hilti | Sealing of cable and cable installation penetrations through fire sectors, carried out by a licensed contractor using suitable materials and finally certified (execution and material used in accordance with DIN 4102, in accordance with SZPV 408, in accordance with NPV (EI60) and in accordance with the manufacturer's instructions), approx.: f 100 mm. NOTE: The sealing shall be of a type to allow subsequent insertion of cables. Like Hilti | kpl | 10 |  | 0
13.2 | Izdelava tesnjenja prehodov kablov in kabelskih inštalacij skozi požarne sektorje, ki ga z ustreznimi materiali izvede izvajalec z licenco ter na koncu izda ustrezni certifikat (izvedba in uporabljen material v skladu s standardom DIN 4102, skladno s smernico SZPV 408, skladno s NPV (EI90) in po navodilih proizvajalca), približno: 0,7 m2. OPOMBA: tesnenje mora biti takšnega tipa, ki omogoča naknadno vstavljanje kablov. Kot na primer: Hilti | Sealing of cable and cable installation penetrations through fire sectors, carried out by a licensed contractor using suitable materials and finally certified (execution and material used in accordance with DIN 4102, in accordance with SZPV 408, in accordance with NPV (EI90) and in accordance with the manufacturer's instructions), approx. 0.7 m2. NOTE: The sealing shall be of a type to allow subsequent insertion of cables. Like Hilti | kpl | 1 |  | 0
13.3 | Izdelava tesnjenja prehodov kablov in kabelskih inštalacij skozi požarne sektorje, ki ga z ustreznimi materiali izvede izvajalec z licenco ter na koncu izda ustrezni certifikat (izvedba in uporabljen material v skladu s standardom DIN 4102, skladno s smernico SZPV 408, skladno s NPV (EI90) in po navodilih proizvajalca), približno: 0,2 m2. OPOMBA: tesnenje mora biti takšnega tipa, ki omogoča naknadno vstavljanje kablov. Kot na primer: Hilti | Sealing of cable and cable installation penetrations through fire sectors, carried out by a licensed contractor using suitable materials and finally certified (execution and material used in accordance with DIN 4102, in accordance with SZPV 408, in accordance with NPV (EI90) and in accordance with the manufacturer's instructions), approx.: 0.2 m2. NOTE: The sealing shall be of a type to allow subsequent insertion of cables. Like Hilti | kpl | 9 |  | 0
13.4 | Izdelava odprtin 500x200 mm v stenah debeline 400 mm. | Making 500x200 mm openings in 400 mm thick walls. | kos | 1 |  | 0
13.5 | Izdelava odprtin 600x200 mm v stenah debeline 400 mm. | Making 600x200 mm openings in 400 mm thick walls. | kos | 1 |  | 0
| GRADBENO - OBRATNIŠKA DELA V TP | CONSTRUCTION AND PLANT WORKS IN TP |  |  |  | 0

## 3.3.14_Ostalo
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.3 | ELEKTRO DELA | ELECTRICAL WORKS
3.3.14 | OSTALO | OTHER |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
14 | OSTALO | OTHER
14.1 | Priprava podlog za izdelavo PID projekta. Vnos sprememb, do katerih pride med izvedbo, v en izvod PZI projekta. | Preparation of the bases for the PID project. Entry of changes occurring during implementation in a single copy of the PID project. | kpl | 1 |  | 0
14.2 | Testiranje signalov in ožičenja krmilnega in nadzornega sistema, z izdelavo IQ in OQ dokumentacije. | Signal and wiring testing of control and monitoring systems, with IQ and OQ documentation. | kpl | 1 |  | 0
14.3 | Meritve, preizkusi in spuščanje v pogon posameznih sklopov elektro opreme. | Measurement, testing and commissioning of individual electrical equipment assemblies. | kpl | 1 |  | 0
14.4 | Nastavitve zaščit NN odklopnikov. | Settings for LV circuit breaker protection. | kpl | 105 |  | 0
14.5 | Izdelava enopolne SN in NN sheme - kaširane na ploščo ali karton pod steklom. | Production of single-pole MV and LV schematics - laminated on board or cardboard under glass. | kpl | 1 |  | 0
14.6 | Parametriranje sistema in zagon merilne opreme (števci) ter opreme za daljinsko upravljanje. | System parameterisation and commissioning of metering equipment (meters) and remote control equipment. | kpl | 2 |  | 0
14.7 | Izvedba meritev parametrov omrežja za določitev velikosti kompenzacijske naprave z izdelavo poročila. Poročilo meritev predati v treh izvodih. | Carry out measurements of the network parameters to determine the size of the compensation device and produce a report. Submit the measurement report in triplicate. | kpl | 1 |  | 0
14.8 | Izvedba zagonskih in funkcionalnih preizkusov 20 kV naprav. | Carrying out commissioning and functional tests of 20 kV installations. | kpl | 1 |  | 0
14.9 | Izvedba zagonskih in funkcionalnih preizkusov 0,4 kV naprav. | Carrying out commissioning and functional tests of 0.4 kV installations. | kpl | 1 |  | 0
14.10 | Pozitivne ocene, atesti, certifikati in potrdila ustreznih inštitucij za dokazovanje primerne kakovosti vgrajenih naprav, napeljav, materialov in montažnih del (EIMV, IVD, ZAG, SIQ in podobno). | Positive evaluations, attestations, certificates and attestations of the relevant institutions to prove the adequate quality of the installed devices, installations, materials and assembly works (EIMV, IVD, ZAG, SIQ, etc.). | kpl | 1 |  | 0
14.11 | Pridobitev in predaja izjav o skladnosit CE. | Obtaining and handing over CE declarations of conformity. | kpl | 1 |  | 0
14.12 | Šolanje uporabnika. | User training. | ur | 60 |  | 0
14.13 | Izdelati je potrebno projektno dokumentacijo, kot je delavniška dokumentacija, interne vezalne sheme sistemov, ipd. z upoštevanjem potrjene opreme in vso drugo dokumentacijo. | Project documentation such as workshop documentation, internal system wiring diagrams, etc. must be produced, taking into account the approved equipment and all other documentation. | kpl | 1 |  | 0
14.14 | Navodila za obratovanje in vzdrževanje. Izdelana natančna obratovalna navodila glede posameznih stikalnih manipulacij in komunikacij za zagotavljanje rezervnega napajanja in ponovne vzpostavitve normalnega napajanja. | Operating and maintenance instructions. Detailed operating instructions on individual switching manipulations and communications to ensure back-up power and restoration of normal power supply. | kpl | 1 |  | 0
14.15 | Pridobitev elektroenergetskega soglasja za priključitev objekta na elektroenergetsko omrežje | Obtaining electricity consent to connect a building to the electricity grid | kpl | 1 |  | 0
14.16 | Zagotovitev prisotnosti nadzora pristojnega elektrodistribucijskega podjetja v času izvajanja del. | Ensuring that the competent electricity distribution company is present during the works. | ur | 60 |  | 0
14.17 | Pomožna oprema: | Auxiliary equipment: | kpl | 1 |  | 0
| - opozorilne table - nazivne table - ročica za ozemljitveni ločilnik - prenosna garnitura za ozemljitve - komplet protipožarnega orodja - zaščitne čelade - garnitura predpisov in varnostnih tabel - komplet orodja za ročno posluževanje naprav 20kV - kompleti ključev - montaža plošča za pribor - ročni gasilnik - ročna svetilka z akumulatorjem ter polnilcem za zidno montažo | - warning signs - nominal tables - grounding disconnector lever - portable earthing set - fire-fighting tool kit - safety helmets - a set of regulations and safety signs - 20kV manual tool kit - sets of keys - mounting plate for accessories - hand-held fire extinguisher - handheld lamp with battery and wall-mounted charger
14.18 | Razna nepredvidena dela, ki se obračunajo po urah s potrditvijo nadzornika v gradbenem dnevniku. | Miscellaneous unforeseen work, billed by the hour with the supervisor's approval in the construction logbook. | kpl | 1 |  | 0
| OSTALO | OTHER |  |  |  | 0