## 0_Naslovnica
OPOZORILO! Vsi prevodi v angleščino so strojno izdelani in zgolj informativne narave. V primeru kakršnekoli nejasnosti ali dvoma izključno velja izvirno besedilo v slovenščini. WARNING! All translations into English have been produced by machine translation and are provided for informational purposes only. In the event of any ambiguity or uncertainty, the original Slovenian text shall prevail exclusively.
| / | / | [5 empty] | /
| Sprem./Rev.: | Opis spremembe/Description of Changes: | [5 empty] | Datum/Date: | Podpis/Signature:
| Investitor/Investor: |  |  |  |  | Gradnja/Facility
|  |  | Univerza v Ljubljani Kongresni trg 12 1000 Ljubljana, Slovenija |  |  | Fakulteta za strojništvo/Faculty of Mechanical Engineering
| Projektant/Design Engineer: |  |  |  |  | Del objekta/sistem/Building/System:
|  |  | IBE, svetovanje, projektiranje in inženiring Ljubljana, Slovenija |  |  | STAVBA FAKULTETE/FACULTY BUILDING
| Projektant/Design Engineer: |  |  |  |  | Vrsta načrta/Documentation:
3 NAČRT S PODROČJA ELEKTROTEHNIKE/ DOC. IN THE FIELD OF ELECTRICAL ENGINEERING
|  | Ime in priimek/Name and Surname: |  |  | Id. št./Id. No: | Vsebina risbe (dokumenta)/Document Title:
| Vodja proj./ Des. Manager: | Boštjan Vuga, univ. dipl. inž. arh., grad. dip. (AA) |  |  | ZAPS 0035 PA PPN | PR. POPIS ELEKTRO DEL/BOQ OF ELECTRICAL WORKS 3/4 NN razvod/LV Electrical Distribution
| Poobl. strok./ Cert. Profess.: | Robert Bobovnik, dipl.inž.el. |  |  | IZS E-2380
| Poobl. strok./ Cert. Profess.: |  |  |  |  | Št. proj./ Proj. No.: | 362-19 |  | Vrsta dokument./ Document. Type: | DZR
| Izdelal/ Creator: | Aleksandra Proeva, dipl.inž.el. |  |  |  | Klas. ozn./ Class. No.: | -- |  | Stran/ Page: | 1/*
| Datum/ Date: | maj/May 2026 |  | Merilo/ Scale: | / | Ident. ozn./ Id. No: | JULFS--6E9122P

## 0_Osebe
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
POOBLAŠČENI STROKOVNJAKI, ODGOVORNI ZA IZDELAVO PROJEKTANTSKEGA POPISA:
Id. št. ZAPS/IZS | Pooblaščeni strokovnjak | Strokovno področje
IZS E-2380 | Robert Bobovnik, dipl. inž. el. | Električne inštalacije
SODELAVCI PRI IZDELAVI PROJEKTANTSKEGA POPISA:
/ | Aleksandra Proeva, dipl. inž. el. | Električne inštalacije
/ | Janez Merhar, el. teh. | Električne inštalacije
CERTIFIED EXPERTS RESPONSIBLE FOR ELABORATING THE BILL OF QUANTITIES:
Id. No ZAPS/IZS | Certified Expert | Area of Expertise
IZS E-2380 | Robert Bobovnik, dipl. inž. el. | Electrical installations
COLABORATORS IN THE ELABORATING THE BILL OF QUANTITIES:
/ | Aleksandra Proeva, dipl. inž. el. | Electrical installations
/ | Janez Merhar, el. teh. | Electrical installations

## 0.1_Uvod-STP
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
0.1 | SPLOŠNI TEHNIČNI POGOJI | GENERAL TECHNICAL CONDITIONS
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic operator with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
0.1.1 | Izvajalec se obveže, da bo upošteval veljavno zakonodajo, ki ureja graditev objektov v Republiki Sloveniji, vključno s povezanimi podzakonskimi akti, predpisi, tehničnimi smernicami, standardi, pravili stroke in dobro gradbeno prakso. Prav tako mora izvajalec upoštevati vse zahteve izdanega integralnega gradbenega dovoljenja in vsa dela izvesti skladno s projektno dokumentacijo ter ostalimi pogoji, objavljenimi v razpisni dokumentaciji. | The Contractor undertakes to comply with the applicable legislation governing the construction of buildings in the Republic of Slovenia, including related by-laws, regulations, technical guidelines, standards, professional rules and good construction practice. The Contractor shall also comply with all the requirements of the integral building permit issued and shall carry out all works in accordance with the project documentation and other conditions published in the tender documentation.
0.1.2 | Dela lahko izvaja samo izvajalec, ki je registriran za opravljanje gradbene dejavnosti in ima za tovrstna dela ustrezno zavarovanje za škodo, certifikate, tehnično izobražen kader, sredstva ter je usposobljen za samostojno pripravo in izvedbo del. | The work may only be carried out by a contractor who is registered to carry out construction work and who has the appropriate insurance for such work, certificates, technically trained staff, resources and is qualified to prepare and carry out the work independently.
0.1.3 | Izvajalec odgovarja za kakovost izvedbe vseh del. | The Contractor shall be responsible for the quality of the execution of all works.
0.1.4 | Izvajalec nosi vso odgovornost za nesreče in škodo, ki nastane na objektu ali v okolici zaradi njegovega dela. | The Contractor shall bear all liability for accidents and damage to the installation or the surrounding area caused by his work.
0.1.5 | Pred oddajo ponudbe se je izvajalec dolžan seznaniti z območjem predvidenim za gradnjo in temu prilagoditi vsa potrebna dela, kar mora biti zajeto v ponudbi. V neposredni bližini predvidene gradnje se nahajajo stavbe, v katerih potekajo izobraževalni in raziskovalni procesi. Zato bo izvajalec moral izvajati kontrolo hrupa in kontrolo vibracij. Dela, ki so hrupna in dela, ki povzročajo vibracije bo izvajalec moral preprečiti oziroma jih izvesti na način, da povzročajo minimalne vplive. Tehnologijo rušenja, pilotiranja in tehnologijo izvedbe ostalih del bo izvajalec moral prilagoditi tako, da bo vpliv minimalen. Izvajalec mora preprečiti in zmanjšati emisije delcev iz gradbišča na najmanjšo možno mero. | Before submitting a tender, the contractor is obliged to familiarise himself with the area to be constructed and to adapt any necessary works accordingly, which must be included in the tender. In the immediate vicinity of the proposed construction, there are buildings in which educational and research processes take place. The contractor will therefore be required to carry out noise and vibration control. Noise and vibration works will have to be avoided or carried out in such a way as to minimise the impact. Demolition, piling and other works will have to be adapted to minimise the impact. The contractor must avoid and minimise the emission of particulates emitted from the construction site as far as is reasonably practicable.
0.1.6 | Izvajalec je pred oddajo ponudbe dolžan pregledati projektno dokumentacijo in ostale pogoje, ki so del razpisne dokumentacije V primeru morebitnih napak in neskladij je izvajalec dolžan na to opozoriti naročnika pred oddajo ponudbe. | The Contractor is obliged to review the project documentation and other conditions forming part of the tender documentation before submitting the tender In case of any errors or inconsistencies, the Contractor is obliged to bring these to the attention of the Contracting Authority before submitting the tender.
0.1.7 | Pred oddajo ponudbe je izvajalec dolžan preveriti ustreznost popisov del in količin v teh popisih ter njihovo skladnost z ostalimi dokumenti projektne dokumentacije, ki so del razpisne dokumentacije. Prav tako je izvajalec dolžan preveriti vse detajle in sheme. Vse izmere je potrebno preveriti po posameznih projektih oz. načrtih, ki sestavljajo razpisno dokumentacijo. V primeru ugotovljenih neskladij je v času priprave ponudbe obvezan o tem obvestiti naročnika. | Before submitting a tender, the Contractor shall check the adequacy of the inventories of works and quantities in these Bills of Quantities and their conformity with the other documents of the project documentation forming part of the tender documentation. The Contractor shall also check all details and diagrams. All measurements shall be checked against the individual projects or plans forming part of the tender documentation. In the event of any discrepancies, the Contractor shall inform the Contracting Authority at the time of preparing the tender.
0.1.8 | Pred oddajo ponudbe je izvajalec dolžan v tem popisu preveriti zmnožke in seštevke ter prenose le-teh v rekapitulacijo. Izvajalec se s pripravo ponudbe obvezuje, da je prebral vse celice in elemente celotnega popisa, vključno z vsemi postavkami in splošnimi navodili ali določili in je preveril pravilnost preračuna ter s tem zagotavlja ponudbeno vrednost. | Before submitting a tender, the Contractor is required to check the products and totals in this Bill of Quantities (BoQ) and their transfer to the recapitulation. The Contractor undertakes, by preparing a tender, to have read all the cells and elements of the complete BoQ, including all headings and general instructions or provisions, and to have checked the correctness of the conversion, thereby guaranteeing the value of the tender.
0.1.9 | Dela bo izvajalec moral izvajati po predloženi projektni dokumentaciji, detajlih in z upoštevanjem navodil in potrditev projektanta, nadzornika in investitorja. Vso potrebno delavniško dokumentacijo zagotovi izvajalec del v okviru ponujene cene. | The Contractor shall carry out the works in accordance with the submitted design documents, details and subject to the instructions and approvals of the Designer, the Supervisor and the Investor. All necessary workshop documentation shall be provided by the Contractor within the scope of the price quoted.
0.1.10 | Pred izvedbo posameznih del je izvajalec dolžan pregledati projektno dokumentacijo za izvedbo gradnje (PZI) in elaborate. Na morebitne napake v dokumentaciji ali neskladja med posameznimi načrti ali deli načrtov (popisi del, tehnična poročila, lokacijski in tehnični prikazi) izvajalec opozori nadzornika in projektanta, in se z njima pravočasno uskladi. | The Contractor shall review the Detailed Design documentation (PZI) and the studies before carrying out the individual works. The Contractor shall draw the attention of the Supervisor and the Designer to any errors in the documentation or discrepancies between the individual designs or parts of designs (BoQ, technical reports, location and technical drawings) and shall coordinate with them in good time.
0.1.11 | Tehnični opisi, prikazi, detajli, sheme ter ostali dokumenti v PZI dokumentaciji predstavljajo dodaten opis popisnih postavk gradbeno obrtniških in inštalacijskih del ter jih je potrebno dosledno upoštevati skupaj s popisom del. | The technical descriptions, illustrations, details, diagrams and other documents in the Detailed Design documentation (PZI) are additional descriptions of the BoQ inventory items of the building, construction and installation works and must be strictly followed together with the BoQ.
0.1.12 | Specifikacije in zahteve, navedene v popisu, se ne smejo upoštevati kot edine zahteve. Izvajalec je dolžan v ceni zajeti in dobaviti vse elemente opreme ter opraviti dela in storitve, ki niso eksplicitno navedeni, a so bistvenega pomena za funkcionalnost, skladnost s predpisi ter kontinuirano, zanesljivo in varno obratovanje opreme. | The specifications and requirements set out in the BoQ shall not be taken as the only requirements. The Contractor shall be obliged to include in the price and supply all items of equipment and to carry out works and services which are not expressly mentioned but which are essential for the functionality, regulatory compliance and continuous, reliable and safe operation of the equipment.
0.1.13 | Vsa dela morajo biti izvedena kvalitetno in iz materialov z zahtevanimi lastnostmi, izvedena skladno z veljavno zakonodajo in z upoštevanjem navodil za vgradnjo za izbrane materiale in opremo, s predložitvijo predpisanih izjav o lastnostih in/ali certifikatov. Vsi gradbeni proizvodi (GP) morajo biti označeni s CE oznako. | All work shall be of good quality and be executed with materials of the required characteristics, in accordance with the applicable legislation and in compliance with the installation instructions for the materials and equipment selected, and shall be accompanied by the prescribed declarations of performance and/or certificates. All construction products (GP) shall bear the CE marking.
0.1.14 | Za vsako opisano delo v popisu je potrebno upoštevati celotno potrebno delo, ves osnovni in pomožni material, prevoz materiala in orodja na objekt, notranje transporte, delovne in pomožne odre, zaključno čiščenje in odstranitev odpadkov po dovršenem delu. | For each work described in the inventory, the total work required, all basic and ancillary materials, the transport of materials and tools to the site, internal transports, working and ancillary scaffolding, final cleaning and the disposal of waste after the work has been completed must be taken into account.
0.1.15 | Vsa delovna sredstva, organizacija in koordinacija del, pripravljalna, spremljajoča in zaključna dela, potrebni montažni in tesnilni materiali ter podkonstrukcije so sestavni del posameznih postavk. | All labour, organisation and coordination of the works, preparatory, accompanying and finishing works, necessary prefabrication and sealing materials and substructures are part of the individual items.
0.1.16 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - načrt organizacije gradbišča s podrobnim terminskim planom in izvedba vseh pripravljalnih del, postavitev, organizacija, zaščita in prijava gradbišča, gradbiščnih objektov, ureditev začasnih deponij, tekoče vzdrževanje, skupaj s plačilom splošnih stroškov pristojbin in davkov upravnih organov, pridobivanju raznih dovoljenj in soglasij za izvedbo, ograditev gradbišča in postavitev gradbene table in prometne signalizacije, zagotavljanje ustrezne varnosti na gradbišču, tekoče vzdrževanje in končna odstranitev gradbišča; - zagotovitev potrebnih začasnih površin za transportne poti in gradnjo izven območja gradbišča s plačilom stroškov za sanacijo in vzpostavitev okoliških zemljišč in objektov v prvotno stanje (soglasja, odškodnine, itd.); - začasni odvoz, deponiranje in vračanje izkopanega materiala, ki ga ne bo možno deponirati na gradbišču; - odvoz in zagotovitev odstranjevanja odpadnega gradbenega materiala skladno z zakonodajo na področju ravnanja z odpadki (odvoz na urejene deponije s plačilom komunalnih prispevkov in taks itd.); - oteženi izkop v mokrem terenu, izkop v vodi, odvod meteorne vode iz gradbene jame in vode, ki se izceja iz bočnih strani izkopov; - ustrezno varovanje izkopa gradbene jame za objekt in ostalih manjših posameznih izkopov za izvedbo komunalne infrastrukture brez posegov na sosednja zemljišča; - ustrezno varovanje obstoječih objektov, infrastrukture in okolice v času gradnje ter dokumentiranje vseh morebitnih škodnih dogodkov; - pripravljalna, spremljajoča in zaključna dela (zakoličbe, zagotovitev potrebnih komunalnih priključkov za potrebe izvajanja gradnje, izvedba začasnih inštalacij, označevanje podzemnih vodov, postavljanje in vzdrževanje zakoličbenih profilov, izvedba in označevanje novih in starih križanj ter morebitna zaščita križanj komunalnih vodov, geodetski posnetki in izdajanje vmesnih posnetkov izvedene infrastrukture naročniku, izdelava zbirnih kart, itd.), v kolikor ni to drugače določeno; - pridobivanje soglasij in izvedba morebitnih zapor na vseh cestah s plačilom stroškov, nadomestil in pristojbin; - zagotovitev oz. postavitev in končna odstranitev po zaključku gradnje začasnih skladišč in začasnega pisarniškega kontejnerskega objekta vključno z opremo za dve delovni mesti in za skupne operativne sestanke vel. ca. 40 m2 za potrebe naročnika, s tekočim vzdrževanjem in čiščenjem. | The following must also be included or taken into account in the uniform prices for individual items: - a construction site organisation plan with a detailed timetable and the execution of all preparatory works, the setting-up, organisation, protection and registration of the construction site, site facilities, the arrangement of temporary storage facilities, ongoing maintenance, including the payment of general costs of fees and taxes of the administrative authorities, the obtaining of various permits and consents for the execution, the fencing of the site and the erection of construction signs and traffic signals, the provision of adequate security on the site, ongoing maintenance and the final dismantling of the construction site; - provision of the necessary temporary areas for transport routes and off-site construction, with costs for restoration and reinstatement of surrounding land and buildings (consents, compensation, etc.); - temporary removal, storage and return of excavated material that cannot be stored on site; - removing and disposing of waste building materials in accordance with waste management legislation (removal to regulated landfill sites with payment of municipal fees and charges, etc.); - difficult excavation in wet ground, excavation in water, drainage of rainwater from the construction pit and water draining from the sides of excavations; - adequate protection of the excavation of the construction pit for the building and other small individual excavations for the implementation of the utility infrastructure without encroaching on neighbouring land; - adequate protection of existing facilities, infrastructure and the surrounding area during construction, and documentation of any damage incidents; - preparatory, accompanying and finishing works (stake-out, provision of the necessary utility connections for the needs of construction, execution of temporary installations, marking of underground lines, installation and maintenance of stake-out profiles, execution and marking of new and old crossings and possible protection of crossings of utility lines, geodetic surveys and issuing of intermediate images of the completed infrastructure to the client, production of summary maps, etc.), unless otherwise specified; - obtaining consents and implementing any road closures, with costs, compensation and fees; - provision or erection and final removal on completion of construction of temporary storage and temporary office container building including equipment for two workstations and for joint operational meetings of approx. 40 m2 for the needs of the client, with ongoing maintenance and cleaning.
0.1.17 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - izdelava montažne tehnične dokumentacije, detajlov izvedbe in vse druge potrebne delavniške dokumentacije (s področja arhitekture, gradbeništva, elektrotehnike, strojništva in zunanje ter krajinske ureditve) ter pridobitev obvezne potrditve s strani projektanta, nadzornika in investitorja; - odprava vseh vrst inštalacijskih kolizij z izvajanjem potrebnih premikov inštalacij in njihovim usklajevanjem na mestu montaže, vse v obsegu, ki ne vpliva na projektirano rešitev ali tip inštalacij oz. opreme; - zagotavljanje kompletnosti elektro-instalacijskih sistemov s področja avtomatike za doseganje njihove popolne funkcionalnosti delovanja; - stroški za nadzor in koordinacijo izvedbe vseh elektro napeljav, ki so predmet končne instalacije proizvoda (senčila, vrata, okna,…); - izdelava montažnih skic in detajlov za izvedbo v dogovoru z vodjo gradnje in nadzornikom; - izdelava in predstavitev vzorcev v ustrezni velikosti za potrditev projektanta, nadzornika in investitorja; - zagotavljanje varnosti in zdravja pri delu, zlasti izvajanje vseh del, ki izhajajo in ukrepov, ki izhajajo iz določil veljavnih predpisov varstva pri delu in zahtev Varnostnega načrta;- stroški garancij, ki jih mora izvajalec predložiti naročniku. | The following must also be included or taken into account in the uniform prices for individual items: - preparation of prefabricated technical documentation, construction details and all other necessary workshop documentation (architectural, civil, electrical, mechanical, exterior and landscaping) and obtaining the mandatory approval of the designer, the supervisor and the investor; - elimination of all types of installation conflicts by carrying out the necessary relocation of installations and their coordination at the installation site, all to the extent that it does not affect the design solution or the type of installation or equipment; - ensuring the completeness of electrical installation systems in the automation sector to achieve their full operational functionality; - the cost of supervising and coordinating the installation of all the electrical installations that are the subject of the final installation of the product (blinds, doors, windows, etc.); - preparation of erection drawings and details for implementation in agreement with the construction manager and supervisor; - production and presentation of samples in appropriate sizes for the approval of the designer, the supervisor and the investor; - ensuring health and safety at work, in particular the implementation of all the works arising from and the measures resulting from the provisions of the applicable occupational safety regulations and the requirements of the Safety Plan; - the cost of the guarantees to be provided by the contractor to the client.
0.1.18 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - strošek vodje del glavnega izvajalca, ki bo izvajal tudi koordinacijo s podizvajalci in z drugimi izvajalci, ki jih bo izbral naročnik in bo opravljal delo vodje gradbišča; - koordinacija del z ostalimi izvajalci oz. podizvajalci del, projektantom, nadzornikom in investitorjem pri medsebojnem usklajevanju organizacije gradbišča in časovnega načrta del ter pri usklajevanju izdelave plana montaže, potrjenih s strani vseh udeležencev gradnje; - stroški koordinacije, sodelovanja in usklajevanja z dobavitelji tehnološke, laboratorijske, eksperimentalne in vse ostale pohištvene ter multimedijske opreme ter z vsemi ostalimi dobavitelji oz. podizvajalci na objektu; - stroški izdelave situacij; - stroški zavarovanja objekta v času izvedbe del in delavcev ter materiala na gradbišču v času izvajanja del, od začetka del do pridobitve uporabnega dovoljenja za objekt. Zavarovanje mora biti sklenjeno pri ustrezni zavarovalni družbi najmanj v višini pogodbene vrednosti ali v zakonsko predpisani vrednosti (v kolikor zavarovanje v višini pogodbene vrednosti presega zakonsko dovoljeno), za ves čas trajanja izvedbe del do uspešne primopredaje objekta; - preizkušanje kvalitete materiala, ki se vgrajuje in dokazovanje kvalitete s certifikati oz. tehničnimi soglasji; - izvedba vseh zahtevanih testov in preizkusov (npr. tlačni preizkusi, termografski pregledi, meritve elektromagnetnega sevanja, hrupa, itd.), poskusnega obratovanja celotnega objekta s poudarkom na vseh inštalacijah ter izvajanje predpisanega monitoringa v skladu s Poročilom o vplivih na okolje (pred gradnjo, med gradnjo in po končani gradnji); - izdelava izkaza požarne varnosti, vključno s sprotnim spremljanjem gradnje in izvajanjem požarnovarnostnih zahtev ter izdelava Požarnega reda z obveznimi prilogami; - izdelava Izkaza zaščite pred hrupom v stavbah; - izdelava Izkaza energijskih lastnosti stavbe in energetske izkaznice; - sodelovanje z izvajalci gradbenega in projektantskega nadzora in investitorjem za izvedbo tehničnega pregleda in priprava primopredaje, ki mora vsebovati vso zahtevano dokumentacijo, predvsem pa: izjave o skladnosti, požarni izkaz in ostale izkaze ter obvezne tabele, dokazilo o zanesljivosti objekta (DZO), certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo in vzdrževanje ter vse ostale dokumente v skladu s predpisi in pogodbenimi določili. | The following must also be included or taken into account in the uniform prices of the individual items: - the cost of a works manager for the main contractor, who will also coordinate with subcontractors and other contractors selected by the client and act as site manager; - coordination of the works with other contractors or subcontractors, the designer, the supervisor and the investor in coordinating the organisation of the construction site and the timetable for the works, and in coordinating the production of an installation plan approved by all the participants in the construction; - the costs of coordination, cooperation and coordination with suppliers of technological, laboratory, experimental and all other furniture and multimedia equipment, as well as with all other suppliers or subcontractors on the site; - the cost of drawing up situations; - the cost of insuring the building during the execution of the works and the workers and materials on site during the execution of the works, from the start of the works until the building has been licensed for occupation. The insurance must be taken out with a suitable insurance company for at least the contract value or the legal value (if the insurance for the contract value exceeds the legal value), for the entire duration of the works until the successful handover of the building; - testing the quality of the material to be installed and proving it with certificates or technical approvals; - carrying out all required tests and trials (e.g. pressure tests, thermographic inspections, electromagnetic radiation measurements, noise measurements, etc.), trial operation of the entire building, with emphasis on all installations, and carrying out the required monitoring in accordance with the Environmental Impact Assessment Report (before, during and after construction); - preparation of a fire safety statement, including ongoing monitoring of construction and implementation of fire safety requirements, and preparation of a Fire Safety Order with mandatory annexes; - preparation of a Noise Protection Statement for buildings; - preparation of the Building Energy Performance Report and Energy Performance Certificate; - cooperation with the construction and design supervision contractors and the investor to carry out the technical inspection and prepare the handover, which must include all the required documentation, in particular: declarations of conformity, fire and other statements and mandatory tables, proof of reliability of the building (DZO), certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use and maintenance, and all other documents in accordance with the regulations and the contractual provisions.
0.1.19 | V enotnih cenah posameznih postavk, ki se nanašajo na opremo in posamezne sisteme, mora biti zajeto oz. upoštevano tudi naslednje: - dobava oz. transport, - stroški za vse delovne stroje za dvigovanje bremen in delovne košare za dostope do delovišč; - morebitni stroški povzročeni upravljavcem GJI, ki bi nastali v zvezi s predmetno gradnjo; - montaža, vključno s pomožnim montažnim materialom (vezni, tesnilni in pritrdilni material, sidra, nosilni profili, podkonstrukcije in podobno) in navodili proizvajalca, - odprava vseh kolizij sistemov s stenami in med sistemi, - izvedba vseh potrebnih tesnjenj, - priključitev in nastavitve, vključno z morebitnim kalibriranjem, - zagon, testiranje in meritve, vključno s poročili, - šolanje uporabnikov oz. vzdrževalnega osebja za uporabo in vzdrževanje sistemov, - navodila za obratovanje in vzdrževanje, - vsi potrebni certifikati, izjave o skladnosti oz. potrdila ter - vsa druga pomožna dela in material, da se zagotovi funkcionalnost posamezne postavke popisa. | The following must also be included or taken into account in the uniform prices for individual items relating to equipment and individual systems: - delivery/transport, - the cost of all lifting machines and work baskets for access to work sites; - any costs incurred to the operators of utility infrastructure (GJI) in connection with the subject construction; - installation, including ancillary installation materials (bonding, sealing and fixing materials, anchors, support profiles, substructures, etc.) and manufacturer's instructions, - eliminating all system-to-wall and system-to-system collisions, - all necessary sealing work, - connection and set-up, including calibration if necessary, - commissioning, testing and measurements, including reports, - training users or maintenance staff in the use and maintenance of the systems, - operating and maintenance instructions, - any necessary certificates, declarations of conformity or attestations; and - all other ancillary works and materials to ensure the functionality of each inventory item.
0.1.20 | Vsi odri morajo biti upoštevani v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All scaffolding must be included in the uniform prices of the items listed, except where specifically mentioned.
0.1.21 | Vsi delovni in pomožni odri, lestve in ostala potrebna pomožna sredstva, kot tudi čiščenje vseh elementov po končanih delih, mora biti upoštevano v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All working and auxiliary scaffolding, ladders and other necessary ancillaries, as well as the cleaning of all elements after completion of the works, shall be included in the uniform prices of the items listed, except those specifically mentioned.
0.1.22 | Delavniško dokumentacijo za vse nosilne jeklene konstrukcije in podkonstrukcije izdela izvajalec, strošek izdelave delavniške dokumentacije se upošteva v ponujenih cenah in se ne obračuna posebej. | The cost of the shop drawings for all steelwork and substructures shall be included in the prices quoted and shall not be charged separately.
0.1.23 | V enotnih cenah postavk mora biti vključeno tudi vgrajevanje vseh instalacijskih razvodov v opaže armirano betonskih elementov in izdelava prehodov inštalacij ter dodatno izrezovanje utorov in prebojev v kamnite, zidane ali armirano-betonske stene, ponovno demontiranje in montiranje vseh vrst montažnih sten, vsa dodatna dela za zagotavljanje primernih križanj med posameznimi instalacijskimi vodi, izdelava vseh vrst ojačitev konstrukcij in podobna dela, ki zagotavljajo kakovostno vgradnjo vseh vrst instalacijskih vodov in niso posebej navedena v popisu GOI del. V ponudbi morajo biti upoštevana vsa drobna strojna in elektro instalacijska dela in transporti. | The installation of all installation ducts in the formwork of reinforced concrete elements and the construction of installation penetrations, as well as the additional cutting of grooves and penetrations in stone, masonry or reinforced concrete walls, the reassembly and reinstallation of all types of prefabricated walls, all additional work to ensure adequate crossings between individual installation ducts, the construction of all types of structural reinforcement and similar work to ensure the quality installation of all types of installation ducts and not specifically mentioned in the BoQ of the Construction, installation and finishing works (GOI) shall also be included in the uniform prices of the items. The tender shall take into account all minor mechanical and electrical installation work and transport.
0.1.24 | Vsi kovinski elementi in konstrukcije, ki bi lahko bili izpostavljeni atmosferskim in ostalim korozijskim vplivom, morajo biti ustrezno protikorozijsko zaščiteni. | All metallic elements and structures that could be exposed to atmospheric and other corrosive influences must be adequately protected against corrosion.
0.1.25 | Za vse večje jeklene dele se skladno s predpisi, izdelajo ustrezne ozemljitve, nevidno pritrjene in speljane na splošno ozemljitev objekta. | For all major steel parts, appropriate earth connections shall be made in accordance with the regulations, invisibly attached and connected to the general earth of the building.
0.1.26 | Za vse vidne elemente in serijske elemente je obvezna predhodna uskladitev obdelav, barv in materialov s projektantom na podlagi dostavljenih vzorcev v ustrezni velikosti. Obvezna je preveritev dejanskih mer na licu mesta in posledična prilagoditev elementov in njihove montaže. | For all visible elements and serial elements, it is mandatory to coordinate the finishes, colours and materials with the designer beforehand on the basis of the supplied samples in the appropriate size. It is mandatory to check the actual dimensions on site and to adjust the elements and their installation accordingly.
0.1.27 | Dimenzije obrtniških izdelkov in količine je potrebno pred naročanjem preveriti na objektu. Potrebna je uskladitev vseh elementov (kljuke, okovje, detajlne konstrukcije in obdelave, itd.) s projektantom, nadzornikom in investitorjem. Izvajalec je dolžan pred izdelavo predložiti projektantu v potrditev ustrezne delavniške načrte in detajle. | The dimensions of the workmanship and quantities must be checked on site before ordering. All elements (hooks, fittings, detailed construction and finishes, etc.) must be coordinated with the designer, the supervisor and the investor. The contractor is obliged to submit the relevant workshop plans and details to the designer for approval before manufacture.
0.1.28 | V posameznih postavkah popisa so navedeni proizvajalci in/ali tipi posameznih sistemov, materialov ali opreme, s čimer so zgolj natančno opredeljene zahtevane tehnične lastnosti. Izvajalec del lahko ponudi nadomesten sistem, material ali opremo drugega proizvajalca in tipa, pri čemer morajo biti tehnične lastnosti ponujenega sistema, materiala ali opreme enakovredne ali boljše od opredeljenih v popisu, dimenzijsko pa ne smejo presegati projektiranih dimenzij. Vse funkcijske in tehnične karakteristike nadomestnih sistemov, materialov ali opreme mora izvajalec dokazati z ustrezno dokumentacijo. Vse morebitne posledice zaradi spremembe sistemov, materialov ali opreme vključno z morebitnimi spremembami oz. dopolnitvami BIM modelov in projektne dokumentacije, stroškovno in časovno bremenijo izvajalca. | The individual items of the Inventory shall specify the manufacturers and/or types of the individual systems, materials or equipment, thereby merely specifying the required technical characteristics. The Contractor may offer a substitute system, material or equipment of a different manufacturer and type, provided that the technical characteristics of the offered system, material or equipment shall be equivalent to or better than those specified in the BoQ, and shall not exceed the design dimensions. All functional and technical characteristics of the substitute systems, materials or equipment shall be demonstrated by the Contractor with appropriate documentation. Any consequences resulting from changes to systems, materials or equipment, including any changes or additions to the BIM models and project documentation, shall be borne by the Contractor in terms of cost and time.
0.1.29 | Vsako zamenjavo, uporabo in končni izbor nadomestnih sistemov, materialov, proizvodov in opreme morajo obvezno in pravočasno (pred dobavo in vgradnjo) pisno potrditi projektant (vseh sodelujočih strok), nadzornik in investitor. | Any replacement, use and final selection of alternative systems, materials, products and equipment must be approved in writing by the designer (of all disciplines involved), the supervisor and the investor in a timely manner (prior to delivery and installation).
0.1.30 | Izvajalec mora v ponudbeno ceno vključiti tudi: - ves čas gradnje sprotno beleženje sprememb oz. odstopanj od PZI dokumentacije, vključno z izdelavo tekstualnega opisa sprememb, - pripravo podlog na nivoju PZI, ki so potrebne za posodobitev oz. uskladitev BIM modela z izvedenim stanjem (LOD 500) in izdelavo projektne dokumentacije izvedenih del (PID), - mesečno predajanje potrjenih sprememb opreme in materiala, ki vplivajo na BIM model, v formatu IFC, - vzdrževanje in uporabljanje pri izvedbi zadnje veljavne revizije PZI dokumentacije, vključno z dopolnitvami PZI načrtov, ki so nastali zaradi sprememb med gradnjo. | The contractor must also include in the tender price: - keeping a record of changes or deviations from the construction documentation (PZI) throughout construction, including a textual description of the changes, - preparation of the Detailed Design (PZI) level documents required to update or align the BIM model with the as-built condition (LOD 500) and the preparation of the as-built project documentation for the works (PID), - monthly submission of approved equipment and material changes affecting the BIM model in IFC format, - maintenance and use in the execution of the last valid revision of the construction documentation (PZI), including additions to the construction design documentation (PZI) resulting from changes during construction.

## 0.2_Uvod-DGNB
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
0.2 | SPLOŠNI TEHNIČNI POGOJI ZA PODROČJE DGNB CERTIFICIRANJA | GENERAL TECHNICAL CONDITIONS FOR DGNB CERTIFICATION
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic entity with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
| Splošni pogoji za področje DGNB certificiranja predstavljajo dopolnilo splošnim tehničnim pogojem in ne odpravljajo drugih obveznosti in odgovornosti, ki jih ima izvajalec v skladu s predpisi in pogodbo. | The General Conditions for DGNB Certification are complementary to the General Technical Conditions and do not exclude other obligations and responsibilities that the Contractor has under the Regulations and the Contract.
0.2.1 | Izvajalec mora v svojih ponudbah upoštevati, da se bo objekt certificiral v skladu z zahtevami DGNB sistema certificiranja trajnostne gradnje, ter pravočasno (vsaj 60 dni pred vgradnjo posameznega produkta) dostaviti vso ustrezno dokumentacijo za vse v ponudbi zajete materiale, elemente in opremo. Zahtevana je uporaba materialov, elementov ali opreme, ki so okolju in ljudem prijazni, energetsko učinkoviti in obenem ustrezajo zahtevam DGNB sistema. Zahtevan nivo certifikata je: ZLATI CERTIFIKAT | The Contractor shall take into account in its tenders that the building will be certified in accordance with the requirements of the DGNB Sustainable Building Certification Scheme and shall deliver all relevant documentation for all materials, elements and equipment included in the tender in a timely manner (at least 60 days before the installation of each product). The use of materials, elements or equipment that are environmentally and human friendly, energy efficient and at the same time meet the requirements of the DGNB system is required. The required level of certification is: GOLD CERTIFICATE
0.2.2 | Podrobnejši opis DGNB sistema in navodila za posamezne kriterije so dostopna v dokumentu"DGNB Criteria Set New Construction Buildings, Version 2020 International", ki je na voljo na DGNB spletni strani https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria | A more detailed description of the DGNB system and guidance on the individual criteria is available in the document "DGNB Criteria Set New Construction Buildings, Version 2020 International", available on the DGNB website https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria
0.2.3 | Izvajalec mora v svojih ponudbah upoštevati, da je potrebno skladno z določili DGNB certifikacijskega sistema, pravočasno (pred pričetkom gradnje) dostaviti vso ustrezno dokumentacijo, za vse v ponudbi zajete materiale, elemente in opremo (tehnični list, varnostni list, izjava o lastnostih, tehnična navodila za ravnanje, servisiranje, vzdrževanje,...) v slovenskem jeziku. Vgradnja kakršnihkoli materialov, elementov ali opreme, se izvede zgolj na podlagi predhodne preveritve posredovane dokumentacije in obenem potrditve s strani nadzornika. | The Contractor must take into account in its tenders that, in accordance with the provisions of the DGNB certification system, all relevant documentation for all materials, elements and equipment included in the tender (technical data sheet, safety data sheet, declaration of properties, technical instructions for handling, servicing, maintenance,...) must be delivered on time (prior to the start of construction) in the Slovene language (in accordance with the provisions of the DGNB certification system). The installation of any materials, elements or equipment shall be subject to prior checking of the submitted documentation and, at the same time, to the approval of the Supervisor.
0.2.4 | Izbrani materiali, elementi, naprave, sistemi in oprema morajo prispevati k večji trajnosti stavbe v smeri zagotavljanja energetske učinkovitosti, ekonomičnega in enostavnega vzdrževanja ter čiščenja, dolge življenjske dobe, uporabe okolju prijaznih materialov ipd. | The materials, elements, appliances, systems and equipment chosen must contribute to the sustainability of the building in terms of energy efficiency, economic and easy maintenance and cleaning, long lifetime, use of environmentally friendly materials, etc.
0.2.5 | Predloženi dokumenti za vse uporabljene materiale, elemente in opremo morajo izpolnjevati zahteve najmanj kakovostne stopnje QS3 (zaželeno QS4), iz dokumenta: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001) | The documents submitted for all materials, components and equipment used shall meet the requirements of at least quality level QS3 (preferably QS4) of the document DGNB Quality Grades for Materials, Components and Equipment (JULFS--7X9001)
0.2.6 | V kolikor izbrani materiali oz. elementi, navedeni v posameznih postavkah, ne ustrezajo vsaj kakovostni stopnji QS3 iz seznama: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), je izvajalec dolžan na to opozoriti projektanta, nadzor in investitorja ter podati predlog ustreznega materiala oz. elementa. | If the selected materials or elements listed in the individual items do not meet at least quality level QS3 of the list of DGNB quality classes for materials, elements and equipment (JULFS--7X9001), the Contractor shall draw this to the attention of the Designer, the Supervisor and the Investor, and shall make a proposal for a suitable material or element.
0.2.7 | Izvajalec lahko v svoji ponudbi predlaga alternativne produkte in rešitve glede na predvidene s projektom, pod pogojem, da le-te prav tako izpolnjujejo vse navedene zahteve. Pri morebitnih predlaganih alternativnih produktih oz. rešitvah je potrebno upoštevati najmanj enake ali boljše lastnosti v smislu življenjske dobe, obstojnosti, ter enostavnosti in stroška čiščenja ter vzdrževanja v primerjavi s projektom predpisanimi rešitvami. Za alternativne rešitve izvajalec pridobi soglasje projektanta, nadzornika in investitorja pred pričetkom gradnje. | The Contractor may propose alternative products and solutions to those envisaged by the project in its tender, provided that they also meet all the requirements set out above. Any alternative products or solutions proposed shall have at least the same or better characteristics in terms of service life, durability, and ease and cost of cleaning and maintenance compared to the solutions envisaged by the project. For alternative solutions, the contractor shall obtain the agreement of the designer, the supervisor and the investor before starting construction.
0.2.8 | Izvajalec med gradnjo dnevno beleži vsa eventualna odstopanja od PZI projektne dokumentacije ter podatke pravočasno posreduje naročniku, nadzoru in projektantu. Potrjene spremembe vnese v podlage za izdelavo PID in posodobitev BIM modelov. | During construction, the Contractor shall record on a daily basis any deviations from the Detailed Design documentation (PZI) and shall provide the information to the Client, Supervision and the Designer in a timely manner. Confirmed changes shall be entered into the basis for the As-built documentation (PID) and BIM model updates.
0.2.9 | Izvajalec med gradnjo sproti izpolnjuje Seznam vseh konstrukcijskih sestav s pripadajočimi vgrajenimi gradbenimi materiali in dokumentira naslednje podatke o vgrajenih materialih (v slovenskem jeziku): - Varnostni list - Tehnični list - Izjavo o lastnostih (če je relevantno) - Izkazovanje morebiti obstoječega okoljskega certifikata (Tip I - okoljski znak ali Tip III - okoljska produktna deklaracija /EPD) - Izjavo proizvajalca ali dobavitelja, da produkt ustreza zahtevam ENV1.2 - Tehnična navodila za ravnanje, servisiranje, vzdrževanje oziroma ostale, z zakonom predpisane dokumente in dokumentacijo. | During construction, the Contractor shall keep a List of all structural assemblies with their associated construction materials and document the following information on the materials installed (in Slovene language): - Safety Data Sheet - Technical Data Sheet - Declaration of performance (if applicable) - Demonstration of any existing environmental certification (Type I - Ecolabel or Type III - Environmental Product Declaration /EPD) - A declaration by the manufacturer or supplier that the product complies with the requirements of ENV1.2 - Technical instructions for handling, servicing, maintenance or other documents and documentation required by law.
0.2.10 | Za vse vgrajene bistvene tehnične sisteme mora izvajalec zagotoviti obstoj pooblaščenega servisa, ki deluje na območju Republike Slovenije, da ima investitor možnost skleniti ustrezno pogodbo o vzdrževanju. Med bistvene tehnične sisteme sodijo npr.: sistemi ogrevanja in hlajenja, priprava tehnoloških medijev, prezračevanje in klimatizacija, sistemi detekcije in gašenja požara, sistemi tehničnega varovanja, BMS in CNS sistemi upravljanja stavbe, razsvetljava, komunikacijski in WI-FI sistemi,... | For all installed essential technical systems, the contractor must ensure the existence of an authorised service centre operating in the territory of the Republic of Slovenia, so that the investor has the possibility of concluding an appropriate maintenance contract. The essential technical systems include, for example: heating and cooling systems, technological media preparation, ventilation and air conditioning, fire detection and extinguishing systems, technical security systems, BMS and CNS building management systems, lighting, communication and WI-FI systems,...
0.2.11 | Zaželeno je, da imajo uporabljeni elementi in materiali okoljsko oznako Tip I. (kot npr. ENCODE, BLUE ANGEL, ipd...). | It is preferable that the elements and materials used have a Type I environmental label (such as ENCODE, BLUE ANGEL, etc...).
0.2.12 | Izvajalec bo za elemente iz lesa moral dokazovati izvor z navedbo izvorne države in tipa lesa, FSC / PEFC certifikat z dodatnim pripadajočim potrdilom Chain of custody-trgovski certifikat dobavitelja - ta se dokazuje z dobavnicami, računi ali enakovredno. Za izdelke iz naravnega kamna iz EU držav je potrebna deklaracija, da je izvor in procesiranje teh izdelkov v celoti v EU državah. Za izdelke iz naravnega kamna, ki prihajajo iz držav izven EU, je potrebno predložiti dokazilo o izpolnjevanju ILO konvencije 182, ki vključuje neodvisna inšpekcijska poročila. | For wood elements, the contractor will be required to provide proof of origin, indicating the country of origin and the type of wood, FSC/PEFC certification with an additional Chain of Custody certificate - the supplier's trade certificate - this shall be evidenced by delivery notes, invoices or equivalent. For natural stone products from EU countries, a declaration that the sourcing and processing of these products is entirely in EU countries is required. For natural stone products from non-EU countries, proof of compliance with ILO Convention 182, including independent inspection reports, is required.
0.2.13 | Izobraževanje udeležencev pri gradnji Izvajalec je dolžan vse udeležence pri gradnji podrobneje seznaniti tudi z relevantnimi koncepti, študijami, elaborati, ki opredelujejo trajnostni način gradnje za naslednja področja: - zaščita pred hrupom (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)) - zaščita pred prašenjem - zaščita tal in podzemne vode (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)), Analiza tveganja za onesnaženje vodnega telesa podzemne vode št. 0346-023/2023, maj 2023 (Geološko projektiranje d.o.o.)) - ravnanje z gradbenimi odpadki (Načrt gospodarjenja z gradbenimi odpadki) Izobraževanja se izvajajo skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.1 1.2, 2.2, 3.2 in 4.2 Training for the parties implementing the construction work | Training of construction participants The contractor is also obliged to inform all construction participants in detail about relevant concepts, studies, elaborations defining sustainable construction methods for the following areas: - noise protection (Environmental Impact Assessment Report No 100123-11523, dated 11.5.2023, supplemented on 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.)) - dust protection - protection of soil and groundwater (Environmental Impact Assessment Report No. 100123-11523, dated 11.5.2023, supplemented 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.), Risk analysis for contamination of the groundwater No. 0346-023/2023, May 2023 (Geološko projektiranje d.o.o.)) - construction waste management (Construction Waste Management Plan) The training shall be carried out in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.1 1.2, 2.2, 3.2 and 4.2 Training for the parties implementing the construction work
0.2.14 | Navodila za obratovanje in vzdrževanje objekta Izvajalec pripravi Navodila za obratovanje in vzdrževanje objekta skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilih: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual | Instructions for the operation and maintenance of the facility The Contractor shall prepare the Operation and Maintenance Instructions for the Facility in accordance with the applicable Slovenian legislation and the DGNB System Instructions specified in the Criteria: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual
0.2.15 | Meritve kontrole kakovosti gradnje Izvajalec mora upoštevati, da se bodo po koncu gradnje izvedle naslednje meritve: - meritve zrakotesnosti - meritve s termokamero (termografija) - meritve akustike - meritve zvočne zaščite ovoja stavbe - meritve zvočne zaščite ločilnih elementov med posameznimi prostori različnih namembnosti - meritve udarnega zvoka - meritve vlažnosti vgrajenih elementov, pred vgradnjo finalnih tlakov - test odvoda dima in toplote Meritve morajo opraviti ustrezno usposobljeni preskusni organi ali strokovnjaki ter rezultate oceniti in primerjati z zahtevami. Obseg opravljenih meritev mora biti sorazmeren z velikostjo zgradbe in mora ustrezno odražati cilj preverjanja kakovosti zgradbe. Smiselno je, da izvajalec del tekom gradnje za sprotno kontrolo kakovosti vgrajenih materialov, elementov in opreme, sam izvaja meritve. Končne meritve (ob primopredaji) izvede tretja oseba kot neodvisna potrditev doseganja zahtev. Meritve se izvajajo skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 2. Quality control measurements | Construction quality control measurements The contractor must take into account that the following measurements will be carried out after completion of the construction: - airtightness measurements - thermal camera measurements (thermography) - acoustics measurements - measurements of the sound insulation of the building envelope - measurements of the sound insulation of the separating elements between different rooms of different uses - impact sound measurements - moisture measurements of the installed elements, prior to the installation of the final flooring - smoke and heat extraction test The measurements shall be carried out by suitably qualified test bodies or experts and the results evaluated and compared with the requirements. The extent of the measurements carried out shall be proportionate to the size of the building and shall adequately reflect the objective of the building quality verification. It is reasonable for the contractor to carry out his own measurements during construction to check the quality of the materials, elements and equipment installed. Final measurements (at handover) are carried out by a third party as an independent confirmation of compliance with the requirements. The measurements shall be carried out in accordance with the applicable Slovenian legislation and the DGNB system instructions specified in the benchmark: PRO 2.2 2. Quality control measurements
0.2.16 | Zagotavljanje kakovosti za uporabljene gradbene proizvode Izvajalec mora zagotavljati izvajanje primerjav med definiranim in dejansko uporabljenim materialom, elementom ali opremo skladno seznamom: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), vključno z dokazno dokumentacijo ugotovitev primerjav ter skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 3.1 Quality assurance for the used construction products | Quality assurance for the construction products used The Contractor shall ensure that comparisons are made between the defined and the actual material, element or equipment used in accordance with the list: DGNB Quality Grades of Installed Materials, Elements and Equipment (JULFS--7X9001), including supporting documentation of the findings of the comparisons, and in accordance with the DGNB system instructions defined in the Criterion: PRO 2.2 3.1 Quality assurance for the used construction products
0.2.17 | Zaščita pred vlago Izvajalec predloži dokumentacijo, ki dokazuje, da je bil izveden program prezračevanja, prilagojen stavbi, s čimer se zagotovi pogoje, da so vgrajeni gradbeni elementi ustrezno suhi, skladno z navodili DGNB opredeljenimi v merilu: PRO 2.2 4.1 Mould prevention | Protection against moisture The Contractor shall provide documentation demonstrating that a building-specific ventilation programme has been implemented to ensure that the building elements installed are adequately dry, in accordance with the DGNB guidelines specified in the criteria: PRO 2.2 4.1 Mould prevention
0.2.18 | Preizkusi delovanja sistemov Izvajalec sodeluje pri izvedbi predhodnega in končnega preizkusa delovanja vseh bistvenih tehničnih komponent stavbe in pripravi ustrezne dokazne dokumentacije ter pri usposabljanju vzdrževalcev/upravljalcev stavbe, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators | System performance tests The Contractor shall be involved in the performance of the preliminary and final performance tests of all essential technical components of the building and the preparation of the relevant supporting documentation, as well as in the training of the maintenance/management staff of the building, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators
0.2.19 | Poročilo o zagonu objekta Izvajalec sodeluje pri pripravi končnega poročila o zagonu objekta, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 5.1 Creation of a detailed final report | Commissioning report The Contractor shall be involved in the preparation of the final commissioning report, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 5.1 Creation of a detailed final report
0.2.20 | Koncept celovitega delovanja sistemov v stavbi Izvajalec sodeluje pri procesu implementiranja stalnega nadzora in nastavitev delovanja stavbe ter usposabljanju vzdrževalcev/upravljalcev stavbe. Navedeno se izvede v skladu z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 6.1 Creation and handover of an integral operating concept | The concept of integrated building systems The contractor is involved in the process of implementing the building's continuous monitoring and settings and training the building's maintenance/management staff. This shall be done in accordance with the DGNB system instructions defined in the benchmark: PRO 2.3 6.1 Creation and handover of an integral operating concept
0.2.21 | Prilagoditev nastavitev sistemov po začetni fazi uporabe objekta Izvajalec sodeluje pri ponovnem pregledu delovanja vseh bistvenih tehničnih sistemov ter eventualni ponovni prilagoditvi teh sistemov s strani strokovnjaka oz. (neodvisne) tretje osebe. Postopek se izvede po približno 10–14 mesecih po zaključku gradnje, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 7.1 Readjustment of the system following initial operating phase | Adjusting system settings after the initial phase of use of the building The Contractor shall be involved in the re-examination of the functioning of all essential technical systems and the possible re-adjustment of these systems by an expert or (independent) third party. The procedure shall be carried out approximately 10-14 months after completion of construction, in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.3 7.1 Readjustment of the system following initial operating phase

## 3.4.0_Rekapitulacija
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
| REKAPITULACIJA STROŠKOV ELEKTRO DEL | COST SUMMARY OF ELECTRICAL WORKS
| 3 NAČRT S PODROČJA ELEKTROTEHNIKE | 3 DOCUMENTATION IN THE FIELD OF ELECTRICAL ENGINEERING
| 3/4 NN razvod | 3/4 LV Electrical Distribution
3.4 | ELEKTRO DELA | ELECTRICAL WORKS
3.4.1 | RAZDELILNIKI | DISTRIBUTORS | 0
3.4.2 | KABLI, POLICE IN TALNI RAZVOD | CABLES, SHELVES AND FLOOR DISTRIBUTION | 0
3.4.3 | OSTALO | OTHER | 0
0
0 | NEPREDVIDENA DELA | UNFORSEEN WORKS | 0
| SKUPAJ ELEKTRO DELA | TOTAL ELECTRICAL WORKS | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT

## 3.4.1_Razdelilniki
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.4 | ELEKTRO DELA | ELECTRICAL WORKS
3.4.1 | RAZDELILNIKI | DISTRIBUTORS | [5 empty] | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description |  |  | EM | Količina | Cena/EM | Cena
1 | RAZDELILNIKI | DISTRIBUTORS
1.1 | Dobava in montaža razdelilnika +NN_K1_AP1_R iz jeklene pločevine v barvi RAL 7035, skupnih dimenzij 1200x2000x400mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 200mm, dvokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT SFN, tip: NSYSM2012402DP, Schneider. | Supply and installation of distribution box +NN_K1_AP1_R made of steel sheet in RAL 7035 colour, overall dimensions 1200x2000x400mm (WxHxD), including mounting plate, base V = 200mm, double-leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. As for example PanelSeT SFN cabinet, type: NSYSM2012402DP, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=630 A, 3P za montažo na montažno ploščo; kot naprimer tip: C633630S, Schneider | - main disconnecting switch In=630 A, 3P for mounting on a mounting plate; e.g. type: C633630S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV432598T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV432598T, Schneider | kos | 1
| - dvopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84204, Schneider | - 4 A double-pole circuit-breaker with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84204, Schneider | kos | 1
| - podnapetostna sprožna enota, 220 do 240 V AC, kot naprimer Acti9 - iMNx tip: A9A26969, Schneider | - 220 to 240 V AC undervoltage trigger unit, e.g. Acti9 - iMNx type: A9A26969, Schneider | kos | 12
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 6 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173221, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 6 A with C characteristic, 30 mA, type AC, as for example: 002173221, ETI | kos | 12
| - diferenčni tokovni odklopnik (RCCB), 4P, 40 A, 30mA, tip AC, tip B-EV kot naprimer Acti 9 iID tip: A9Z51440, Schneider | - differential circuit breaker (RCCB), 4P, 40 A, 30mA, type AC, type B-EV as for example Acti 9 iID type: A9Z51440, Schneider | kos | 12
| - varovalčni ločilnik 3P, 125 A, za varovalko 22 x 58 mm - 3 x varovalka gG 100 A, kot naprimer: A9GSB392 + DF2FN100, Schneider | - fuse isolator 3P, 125 A, for fuse 22 x 58 mm - 3 x fuse gG 100 A, as for example: A9GSB392 + DF2FN100, Schneider | kos | 1
| - varovalčni ločilnik 3P, 50 A, za varovalko 14 x 51 mm - 3 x varovalka gG 40 A, kot naprimer: A9GSB350 + DF2EN40, Schneider | - fuse isolator 3P, 50 A, for fuse 14 x 51 mm - 3 x fuse gG 40 A, as for example: A9GSB350 + DF2EN40, Schneider | kos | 12
| - varovalčni ločilnik 3P, 250 mA, z varovlačnim vložkom 3x250 mA, kot naprimer: VAROV_5x20, Schneider | - fuse disconnector 3P, 250 mA, with 3x250 mA fuse cartridge, e.g. VAROV_5x20, Schneider | kos | 1
| - varovalčni ločilnik 2P, 25 A, za varovalko 10,3 x 38 mm - varovalka gG 25 A, kot naprimer: A9N15651, Schneider | - fuse disconnector 2P, 25 A, for fuse 10,3 x 38 mm - fuse gG 25 A, as for example: A9N15651, Schneider | kos | 2
| - varovalčni ločilnik 2P, 10 A, za varovalko 8,5 x 31,5 mm - 2 x varovalka gG 2 A, kot naprimer: A9N15650 + DF2BN0200, Schneider | - fuse disconnector 2P, 10 A, for fuse 8,5 x 31,5 mm - 2 x fuse gG 2 A, as for example: A9N15650 + DF2BN0200, Schneider | kos | 5
| - varovalčni ločilnik 1P, 10 A, za varovalko 8,5 x 31,5 mm - varovalka gG 6 A, kot naprimer: A9N15635 + DF2BN0600, Schneider | - fuse disconnector 1P, 10 A, for fuse 8,5 x 31,5 mm - fuse gG 6 A, as for example: A9N15635 + DF2BN0600, Schneider | kos | 2
| - varovalčni ločilnik 1P, 10 A, za varovalko 8,5 x 31,5 mm - varovalka gG 4 A, kot naprimer: A9N15635 + DF2BN0400, Schneider | - fuse disconnector 1P, 10 A, for fuse 8,5 x 31,5 mm - fuse gG 4 A, as for example: A9N15635 + DF2BN0400, Schneider | kos | 4
| - varovalčni ločilnik 1P, 10 A, za varovalko 8,5 x 31,5 mm - varovalka gG 2 A, kot naprimer: A9N15635 + DF2BN0200, Schneider | - fuse disconnector 1P, 10 A, for fuse 8,5 x 31,5 mm - fuse gG 2 A, as for example: A9N15635 + DF2BN0200, Schneider | kos | 1
| - nastavljiv napajalnik 100-240 V AC, 1-fazni, 120W, izhodna napetost 24 V DC, kot naprimer: ABLS1A24050, Schneider | - adjustable power supply 100-240 V AC, 1-phase, 120W, output voltage 24 V DC, e.g. ABLS1A24050, Schneider | kos | 1
| - grelec 20 W, 120 do 240 V, IP20, kot naprimer: 06030.0-00, Stego | - heater 20 W, 120 to 240 V, IP20, as for example: 06030.0-00, Stego | kos | 3
| - termostat za regulacija grelnikov NC, 5 A, 240 V AC, IP20, kot naprimer: 01160.0-01, Stego | - thermostat for NC heater control, 5 A, 240 V AC, IP20, as for example: 01160.0-01, Stego | kos | 2
| - tokovni merilni transformator z nosilcem DIN, za kable in zbiralke 250/5 A, Class 0,5, 6 VA, kot naprimer: METSECT5MA025, Schneider | - current measuring transformer with DIN-rail, for cables and busbars 250/5 A, Class 0,5, 6 VA, e.g. METSECT5MA025, Schneider | kos | 3
| - merilnik energije - CT - RS485, 3P+N, 5 A, za aktivna, reaktivna, navidezna energija, večtarifni, Modbus 1DI+1DO, kot naprimer Acti 9 iEM3000 tip: A9MEM3255, Schneider | - energy meter - CT - RS485, 3P+N, 5 A, for active, reactive, virtual energy, multi-tariff, Modbus 1DI+1DO, like for example Acti 9 iEM3000 type: A9MEM3255, Schneider | kos | 1
| - Vmesnik Gateway RS485 / Ethernet, kot naprimer Link150 tip: EGX150, Schneider | - Gateway RS485/Ethernet interface, such as Link150 type: EGX150, Schneider | kos | 1
| - Ethernet neupravljalno stikalo TCP/IP, 10/100BASE-TX - 6x vhodov - za priključitev bakrenih mrežnih kablov, 100BASE-FX - 2x vhoda za priključitev optičnih kablov, napajanje 12 do 24 V DC kot naprimer tip: MCSESU083F2CU0, Schneider | - Ethernet unmanaged switch TCP/IP, 10/100BASE-TX - 6x inputs - for connection of copper network cables, 100BASE-FX - 2x inputs for connection of fibre optic cables, power supply 12 to 24 V DC as for example type: MCSESU083F2CU0, Schneider | kos | 4
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - 250V, 16A, DIN rail mounting socket, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.2 | Dobava in montaža razdelilnika +NN_K1_AP2_R iz jeklene pločevine v barvi RAL 7035, skupnih dimenzij 1200x2000x400mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 200mm, dvokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT SFN, tip: NSYSM2012402DP, Schneider. | Supply and installation of the switchboard +NN_K1_AP2_R made of steel sheet in RAL 7035 colour, overall dimensions 1200x2000x400mm (WxHxD), including mounting plate, base V = 200mm, double-leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. As for example PanelSeT SFN cabinet, type: NSYSM2012402DP, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=630 A, 3P za montažo na montažno ploščo; kot naprimer tip: C633630S, Schneider | - main disconnecting switch In=630 A, 3P for mounting on a mounting plate; e.g. type: C633630S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV432598T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV432598T, Schneider | kos | 1
| - dvopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84204, Schneider | - 4 A double-pole circuit-breaker with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84204, Schneider | kos | 1
| - podnapetostna sprožna enota, 220 do 240 V AC, kot naprimer Acti9 - iMNx tip: A9A26969, Schneider | - 220 to 240 V AC undervoltage trigger unit, such as Acti9 - iMNx type: A9A26969, Schneider | kos | 4
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 6 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173221, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 6 A with C characteristic, 30 mA, type AC, as for example: 002173221, ETI | kos | 4
| - diferenčni tokovni odklopnik (RCCB), 4P, 40 A, 30mA, tip AC, tip B-EV kot naprimer Acti 9 iID tip: A9Z51440, Schneider | - differential circuit breaker (RCCB), 4P, 40 A, 30mA, type AC, type B-EV as for example Acti 9 iID type: A9Z51440, Schneider | kos | 4
| - varovalčni ločilnik 3P, 125 A, za varovalko 22 x 58 mm - 3 x varovalka gG 100 A, kot naprimer: A9GSB392 + DF2FN100, Schneider | - fuse isolator 3P, 125 A, for fuse 22 x 58 mm - 3 x fuse gG 100 A, as for example: A9GSB392 + DF2FN100, Schneider | kos | 1
| - varovalčni ločilnik 3P, 50 A, za varovalko 14 x 51 mm - 3 x varovalka gG 40 A, kot naprimer: A9GSB350 + DF2EN40, Schneider | - fuse isolator 3P, 50 A, for fuse 14 x 51 mm - 3 x fuse gG 40 A, as for example: A9GSB350 + DF2EN40, Schneider | kos | 12
| - varovalčni ločilnik 3P, 250 mA, z varovlačnim vložkom 3x250 mA, kot naprimer: VAROV_5x20, Schneider | - fuse disconnector 3P, 250 mA, with 3x250 mA fuse cartridge, e.g. VAROV_5x20, Schneider | kos | 1
| - varovalčni ločilnik 2P, 25 A, za varovalko 10,3 x 38 mm - varovalka gG 25 A, kot naprimer: A9N15651, Schneider | - fuse disconnector 2P, 25 A, for fuse 10,3 x 38 mm - fuse gG 25 A, as for example: A9N15651, Schneider | kos | 2
| - varovalčni ločilnik 2P, 10 A, za varovalko 8,5 x 31,5 mm - 2 x varovalka gG 2 A, kot naprimer: A9N15650 + DF2BN0200, Schneider | - fuse disconnector 2P, 10 A, for fuse 8,5 x 31,5 mm - 2 x fuse gG 2 A, as for example: A9N15650 + DF2BN0200, Schneider | kos | 3
| - varovalčni ločilnik 1P, 10 A, za varovalko 8,5 x 31,5 mm - varovalka gG 6 A, kot naprimer: A9N15635 + DF2BN0600, Schneider | - fuse disconnector 1P, 10 A, for fuse 8,5 x 31,5 mm - fuse gG 6 A, as for example: A9N15635 + DF2BN0600, Schneider | kos | 2
| - varovalčni ločilnik 1P, 10 A, za varovalko 8,5 x 31,5 mm - varovalka gG 4 A, kot naprimer: A9N15635 + DF2BN0400, Schneider | - fuse disconnector 1P, 10 A, for fuse 8,5 x 31,5 mm - fuse gG 4 A, as for example: A9N15635 + DF2BN0400, Schneider | kos | 4
| - varovalčni ločilnik 1P, 10 A, za varovalko 8,5 x 31,5 mm - varovalka gG 2 A, kot naprimer: A9N15635 + DF2BN0200, Schneider | - fuse disconnector 1P, 10 A, for fuse 8,5 x 31,5 mm - fuse gG 2 A, as for example: A9N15635 + DF2BN0200, Schneider | kos | 1
| - nastavljiv napajalnik 100-240 V AC, 1-fazni, 120W, izhodna napetost 24 V DC, kot naprimer: ABLS1A24050, Schneider | - adjustable power supply 100-240 V AC, 1-phase, 120W, output voltage 24 V DC, e.g. ABLS1A24050, Schneider | kos | 1
| - grelec 20 W, 120 do 240 V, IP20, kot naprimer: 06030.0-00, Stego | - heater 20 W, 120 to 240 V, IP20, as for example: 06030.0-00, Stego | kos | 3
| - termostat za regulacija grelnikov NC, 5 A, 240 V AC, IP20, kot naprimer: 01160.0-01, Stego | - thermostat for NC heater control, 5 A, 240 V AC, IP20, as for example: 01160.0-01, Stego | kos | 2
| - tokovni merilni transformator z nosilcem DIN, za kable in zbiralke 250/5 A, Class 0,5, 6 VA, kot naprimer: METSECT5MA025, Schneider | - current measuring transformer with DIN-rail, for cables and busbars 250/5 A, Class 0,5, 6 VA, e.g. METSECT5MA025, Schneider | kos | 3
| - merilnik energije - CT - RS485, 3P+N, 5 A, za aktivna, reaktivna, navidezna energija, večtarifni, Modbus 1DI+1DO, kot naprimer Acti 9 iEM3000 tip: A9MEM3255, Schneider | - energy meter - CT - RS485, 3P+N, 5 A, for active, reactive, virtual energy, multi-tariff, Modbus 1DI+1DO, like for example Acti 9 iEM3000 type: A9MEM3255, Schneider | kos | 1
| - Vmesnik Gateway RS485 / Ethernet, kot naprimer Link150 tip: EGX150, Schneider | - Gateway RS485/Ethernet interface, such as Link150 type: EGX150, Schneider | kos | 1
| - Ethernet neupravljalno stikalo TCP/IP, 10/100BASE-TX - 6x vhodov - za priključitev bakrenih mrežnih kablov, 100BASE-FX - 2x vhoda za priključitev optičnih kablov, napajanje 12 do 24 V DC kot naprimer tip: MCSESU083F2CU0, Schneider | - Ethernet unmanaged switch TCP/IP, 10/100BASE-TX - 6x inputs - for connection of copper network cables, 100BASE-FX - 2x inputs for connection of fibre optic cables, power supply 12 to 24 V DC as for example type: MCSESU083F2CU0, Schneider | kos | 2
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - 250V, 16A, DIN rail mounting socket, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.3 | Dobava in montaža razdelilnika +NN_K1_AP3_R iz jeklene pločevine v barvi RAL 7035, skupnih dimenzij 1200x2000x400mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 200mm, dvokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT SFN, tip: NSYSM2012402DP, Schneider. | Supply and installation of distribution box +NN_K1_AP3_R made of steel sheet in RAL 7035 colour, overall dimensions 1200x2000x400mm (WxHxD), including mounting plate, base V = 200mm, double-leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. As for example PanelSeT SFN cabinet, type: NSYSM2012402DP, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=630 A, 3P za montažo na montažno ploščo; kot naprimer tip: C633630S, Schneider | - main disconnecting switch In=630 A, 3P for mounting on a mounting plate; e.g. type: C633630S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV432598T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV432598T, Schneider | kos | 1
| - dvopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84204, Schneider | - 4 A double-pole circuit-breaker with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84204, Schneider | kos | 1
| - podnapetostna sprožna enota, 220 do 240 V AC, kot naprimer Acti9 - iMNx tip: A9A26969, Schneider | - 220 to 240 V AC undervoltage trigger unit, such as Acti9 - iMNx type: A9A26969, Schneider | kos | 14
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 6 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173221, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 6 A with C characteristic, 30 mA, type AC, as for example: 002173221, ETI | kos | 14
| - diferenčni tokovni odklopnik (RCCB), 4P, 40 A, 30mA, tip AC, tip B-EV kot naprimer Acti 9 iID tip: A9Z51440, Schneider | - differential circuit breaker (RCCB), 4P, 40 A, 30mA, type AC, type B-EV as for example Acti 9 iID type: A9Z51440, Schneider | kos | 14
| - varovalčni ločilnik 3P, 50 A, za varovalko 14 x 51 mm - 3 x varovalka gG 40 A, kot naprimer: A9GSB350 + DF2EN40, Schneider | - fuse isolator 3P, 50 A, for fuse 14 x 51 mm - 3 x fuse gG 40 A, as for example: A9GSB350 + DF2EN40, Schneider | kos | 12
| - varovalčni ločilnik 3P, 250 mA, z varovlačnim vložkom 3x250 mA, kot naprimer: VAROV_5x20, Schneider | - fuse disconnector 3P, 250 mA, with 3x250 mA fuse cartridge, e.g. VAROV_5x20, Schneider | kos | 1
| - varovalčni ločilnik 2P, 25 A, za varovalko 10,3 x 38 mm - varovalka gG 25 A, kot naprimer: A9N15651, Schneider | - fuse disconnector 2P, 25 A, for fuse 10,3 x 38 mm - fuse gG 25 A, as for example: A9N15651, Schneider | kos | 2
| - varovalčni ločilnik 2P, 10 A, za varovalko 8,5 x 31,5 mm - 2 x varovalka gG 2 A, kot naprimer: A9N15650 + DF2BN0200, Schneider | - fuse disconnector 2P, 10 A, for fuse 8,5 x 31,5 mm - 2 x fuse gG 2 A, as for example: A9N15650 + DF2BN0200, Schneider | kos | 5
| - varovalčni ločilnik 1P, 10 A, za varovalko 8,5 x 31,5 mm - varovalka gG 6 A, kot naprimer: A9N15635 + DF2BN0600, Schneider | - fuse disconnector 1P, 10 A, for fuse 8,5 x 31,5 mm - fuse gG 6 A, as for example: A9N15635 + DF2BN0600, Schneider | kos | 2
| - varovalčni ločilnik 1P, 10 A, za varovalko 8,5 x 31,5 mm - varovalka gG 4 A, kot naprimer: A9N15635 + DF2BN0400, Schneider | - fuse disconnector 1P, 10 A, for fuse 8,5 x 31,5 mm - fuse gG 4 A, as for example: A9N15635 + DF2BN0400, Schneider | kos | 4
| - varovalčni ločilnik 1P, 10 A, za varovalko 8,5 x 31,5 mm - varovalka gG 2 A, kot naprimer: A9N15635 + DF2BN0200, Schneider | - fuse disconnector 1P, 10 A, for fuse 8,5 x 31,5 mm - fuse gG 2 A, as for example: A9N15635 + DF2BN0200, Schneider | kos | 1
| - nastavljiv napajalnik 100-240 V AC, 1-fazni, 120W, izhodna napetost 24 V DC, kot naprimer: ABLS1A24050, Schneider | - adjustable power supply 100-240 V AC, 1-phase, 120W, output voltage 24 V DC, e.g. ABLS1A24050, Schneider | kos | 1
| - grelec 20 W, 120 do 240 V, IP20, kot naprimer: 06030.0-00, Stego | - heater 20 W, 120 to 240 V, IP20, as for example: 06030.0-00, Stego | kos | 3
| - termostat za regulacija grelnikov NC, 5 A, 240 V AC, IP20, kot naprimer: 01160.0-01, Stego | - thermostat for NC heater control, 5 A, 240 V AC, IP20, as for example: 01160.0-01, Stego | kos | 2
| - tokovni merilni transformator z nosilcem DIN, za kable in zbiralke 250/5 A, Class 0,5, 6 VA, kot naprimer: METSECT5MA025, Schneider | - current measuring transformer with DIN-rail, for cables and busbars 250/5 A, Class 0,5, 6 VA, e.g. METSECT5MA025, Schneider | kos | 3
| - merilnik energije - CT - RS485, 3P+N, 5 A, za aktivna, reaktivna, navidezna energija, večtarifni, Modbus 1DI+1DO, kot naprimer Acti 9 iEM3000 tip: A9MEM3255, Schneider | - energy meter - CT - RS485, 3P+N, 5 A, for active, reactive, virtual energy, multi-tariff, Modbus 1DI+1DO, like for example Acti 9 iEM3000 type: A9MEM3255, Schneider | kos | 1
| - Vmesnik Gateway RS485 / Ethernet, kot naprimer Link150 tip: EGX150, Schneider | - Gateway RS485/Ethernet interface, such as Link150 type: EGX150, Schneider | kos | 1
| - Ethernet neupravljalno stikalo TCP/IP, 10/100BASE-TX - 6x vhodov - za priključitev bakrenih mrežnih kablov, 100BASE-FX - 2x vhoda za priključitev optičnih kablov, napajanje 12 do 24 V DC kot naprimer tip: MCSESU083F2CU0, Schneider | - Ethernet unmanaged switch TCP/IP, 10/100BASE-TX - 6x inputs - for connection of copper network cables, 100BASE-FX - 2x inputs for connection of fibre optic cables, power supply 12 to 24 V DC as for example type: MCSESU083F2CU0, Schneider | kos | 4
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.4 | Dobava in montaža razdelilnika +BMS_K1_AP_R iz jeklene pločevine v barvi RAL 7035, dimenzij 600x600x300mm (ŠxVxG), skupaj z montažno ploščo, enokrilna vrata, odpiranje vrat 120°, TN-S, IP66, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT SFN, tip: NSYCRN66300, Schneider. | Supply and installation of +BMS_K1_AP_R switchboard made of steel sheet in RAL 7035, dimensions 600x600x300mm (WxHxD), with mounting plate, single leaf door, door opening 120°, TN-S, IP66, IK10. Cable entry from above. As for example PanelSeT SFN cabinet, type: NSYCRN66300, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40500 | - surge arrester 1P+N, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40500 | kos | 1
| - glavno ločilno stikalo In=40 A, 1P+N za montažo na DIN letev, kot naprimer tip: A9S70640, Schneider | - main disconnecting switch In=40 A, 1P+N for DIN rail mounting, e.g. type: A9S70640, Schneider | kos | 1
| - vrtljiva ročica za krmiljenje glavnega ločilnega stikala + adapterski mehanizem; kot naprimer tip: A9A27006 + A9A27008, Schneider | - rotary lever for controlling the main disconnecting switch + adapter mechanism; as for example type: A9A27006 + A9A27008, Schneider | kos | 1
| - dvopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84204, Schneider | - 4 A double-pole circuit-breaker with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84204, Schneider | kos | 1
| - varovalčni ločilnik 2P, 10 A, za varovalko 8,5 x 31,5 mm - 2 x varovalka gG 2 A, kot naprimer: A9N15650 + DF2BN0200, Schneider | - fuse disconnector 2P, 10 A, for fuse 8,5 x 31,5 mm - 2 x fuse gG 2 A, as for example: A9N15650 + DF2BN0200, Schneider | kos | 2
| - varovalčni ločilnik 1P, 10 A, za varovalko 8,5 x 31,5 mm - varovalka gG 6 A, kot naprimer: A9N15635 + DF2BN0600, Schneider | - fuse disconnector 1P, 10 A, for fuse 8,5 x 31,5 mm - fuse gG 6 A, as for example: A9N15635 + DF2BN0600, Schneider | kos | 2
| - varovalčni ločilnik 1P, 10 A, za varovalko 8,5 x 31,5 mm - varovalka gG 4 A, kot naprimer: A9N15635 + DF2BN0400, Schneider | - fuse disconnector 1P, 10 A, for fuse 8,5 x 31,5 mm - fuse gG 4 A, as for example: A9N15635 + DF2BN0400, Schneider | kos | 1
| - varovalčni ločilnik 1P, 10 A, za varovalko 8,5 x 31,5 mm - varovalka gG 2 A, kot naprimer: A9N15635 + DF2BN0200, Schneider | - fuse disconnector 1P, 10 A, for fuse 8,5 x 31,5 mm - fuse gG 2 A, as for example: A9N15635 + DF2BN0200, Schneider | kos | 2
| - nastavljiv napajalnik 100-240 V AC, 1-fazni, 120W, izhodna napetost 24 V DC, kot naprimer: ABLS1A24050, Schneider | - adjustable power supply 100-240 V AC, 1-phase, 120W, output voltage 24 V DC, e.g. ABLS1A24050, Schneider | kos | 1
| - grelec 20 W, 120 do 240 V, IP20, kot naprimer: 06030.0-00, Stego | - heater 20 W, 120 to 240 V, IP20, as for example: 06030.0-00, Stego | kos | 3
| - termostat za regulacija grelnikov NC, 5 A, 240 V AC, IP20, kot naprimer: 01160.0-01, Stego | - thermostat for NC heater control, 5 A, 240 V AC, IP20, as for example: 01160.0-01, Stego | kos | 2
| -krmilnik polnilnih postaj, 100 napajalne postaje, dinamično upravljanje polnjenja, kot naprimer EcoStruxure EV Charging Expert tip: HMIBSCEA53D1EDL, Schneider | -charging station controller, 100 charging stations, dynamic charging management, e.g. EcoStruxure EV Charging Expert type: HMIBSCEA53D1EDL, Schneider | kos | 1
| - Ethernet neupravljalno stikalo TCP/IP, 10/100BASE-TX - 6x vhodov - za priključitev bakrenih mrežnih kablov, 100BASE-FX - 2x vhoda za priključitev optičnih kablov, napajanje 12 do 24 V DC kot naprimer tip: MCSESU083F2CU0, Schneider | - Ethernet unmanaged switch TCP/IP, 10/100BASE-TX - 6x inputs - for connection of copper network cables, 100BASE-FX - 2x inputs for connection of fibre optic cables, power supply 12 to 24 V DC as for example type: MCSESU083F2CU0, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 1
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.5 | Dobava in montaža razdelilnika iz jeklene pločevine v barvi RAL 7035, dimenzij 800x2000x400mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 200mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Omara je setavljena iz dveh polj in sicer NN polje in DEA polje. Polja sta medsebojno ločena s kovinsko pregrado. Kot naprimer omara Spacial CRN RAL7035, tip: NSYSM20840P, Schneider. | Supply and installation of a switchboard made of sheet steel in RAL 7035, dimensions 800x2000x400mm (WxHxD), including mounting plate, base V = 200mm, single leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. The cabinet is made up of two bays, the LV bay and the DEA bay. The two bays are separated by a metal barrier. For example, Spacial CRN RAL7035, type: NSYSM20840P, Schneider. |  |  | kpl | 1 |  | 0
| V NN polje omare z oznako +NN_K1_1_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the LV box of the cabinet marked +NN_K1_1_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=160 A, 3P za montažo na montažno ploščo; kot naprimer tip: C163160S, Schneider | - main disconnecting switch In=160 A, 3P for mounting on a mounting plate; e.g. type: C163160S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer Galaxy VS, tip: LV429338T, Schneider | - rotatable extension arm for controlling the main disconnecting switch; as for example Galaxy VS, type: LV429338T, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 50 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84350, Schneider | - three-pole circuit breaker 50 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84350, Schneider | kos | 6
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 18
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 3
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 3P+N, 16 A s C karakteristiko, 30 mA, tip A, kot naprimer: 002174924, ETI | - combined protection switch with overcurrent protection (CPS), 3P+N, 16 A with C characteristic, 30 mA, type A, as for example: 002174924, ETI | kos | 3
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 16
| - napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, kot naprimer RM17-U tip: RM17UB310, Schneider | - voltage control relay, range 183 to 528 V AC, 1 C/O, e.g. RM17-U type: RM17UB310, Schneider | kos | 1
| - miniaturni vtični elektromehanski rele, 6 A, 230 V AC (4x CO preklopni kontakt), kot naprimer Harmony tip: RXM4AB1P7PVS, Schneider | - miniature plug-in electromechanical relay, 6 A, 230 V AC (4x CO switching contact), such as Harmony type: RXM4AB1P7PVS, Schneider | kos | 1
| - varovalčni ločilnik 2P, 25 A, za varovalko 10,3 x 38 mm - varovalka gG 1 A, kot naprimer: A9N15651, Schneider | - fuse disconnector 2P, 25 A, for fuse 10,3 x 38 mm - fuse gG 1 A, as for example: A9N15651, Schneider | kos | 1
| - motorski odklopnik 3P, 4-6,3 A, termomagnetna zaščita, kot naprimer TeSys GV2 tip: GV2P10, Schneider | - motor circuit breaker 3P, 4-6.3 A, thermomagnetic protection, e.g. TeSys GV2 type: GV2P10, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
| V DEA polje omare z oznako +DEA_K1_1_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the DEA box of the cabinet marked +DEA_K1_1_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=40 A, 3P za montažo na montažno ploščo; kot naprimer tip: A9S65340, Schneider | - main disconnecting switch In=40 A, 3P for mounting on a mounting plate; e.g. type: A9S65340, Schneider | kos | 1
| - vrtljiva ročica za krmiljenje glavnega ločilnega stikala + adapterski mehanizem; kot naprimer tip: A9A27006 + A9A27008, Schneider | - rotary lever for controlling the main disconnecting switch + adapter mechanism; as for example type: A9A27006 + A9A27008, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 17
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 2
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.6 | Dobava in montaža razdelilnika iz jeklene pločevine v barvi RAL 7035, dimenzij 800x2000x400mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 200mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Omara je setavljena iz dveh polj in sicer NN polje in DEA polje. Polja sta medsebojno ločena s kovinsko pregrado. Kot naprimer omara Spacial CRN RAL7035, tip: NSYSM20840P, Schneider. | Supply and installation of a switchboard made of sheet steel in RAL 7035, dimensions 800x2000x400mm (WxHxD), including mounting plate, base V = 200mm, single leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. The cabinet is made up of two bays, the LV bay and the DEA bay. The two bays are separated by a metal barrier. For example, Spacial CRN RAL7035, type: NSYSM20840P, Schneider. |  |  | kpl | 1 |  | 0
| V NN polje omare z oznako +NN_K1_2_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the LV box of the cabinet marked +NN_K1_2_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=160 A, 3P za montažo na montažno ploščo; kot naprimer tip: C163160S, Schneider | - main disconnecting switch In=160 A, 3P for mounting on a mounting plate; e.g. type: C163160S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer Galaxy VS, tip: LV429338T, Schneider | - rotatable extension arm for controlling the main disconnecting switch; as for example Galaxy VS, type: LV429338T, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 50 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84350, Schneider | - three-pole circuit breaker 50 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84350, Schneider | kos | 5
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 16
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 3
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 3P+N, 16 A s C karakteristiko, 30 mA, tip A, kot naprimer: 002174924, ETI | - combined protection switch with overcurrent protection (CPS), 3P+N, 16 A with C characteristic, 30 mA, type A, as for example: 002174924, ETI | kos | 3
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 12
| - napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, kot naprimer RM17-U tip: RM17UB310, Schneider | - voltage control relay, range 183 to 528 V AC, 1 C/O, e.g. RM17-U type: RM17UB310, Schneider | kos | 1
| - miniaturni vtični elektromehanski rele, 6 A, 230 V AC (4x CO preklopni kontakt), kot naprimer Harmony tip: RXM4AB1P7PVS, Schneider | - miniature plug-in electromechanical relay, 6 A, 230 V AC (4x CO switching contact), such as Harmony type: RXM4AB1P7PVS, Schneider | kos | 1
| - varovalčni ločilnik 2P, 25 A, za varovalko 10,3 x 38 mm - varovalka gG 1 A, kot naprimer: A9N15651, Schneider | - fuse disconnector 2P, 25 A, for fuse 10,3 x 38 mm - fuse gG 1 A, as for example: A9N15651, Schneider | kos | 1
| - motorski odklopnik 3P, 4-6,3 A, termomagnetna zaščita, kot naprimer TeSys GV2 tip: GV2P10, Schneider | - motor circuit breaker 3P, 4-6.3 A, thermomagnetic protection, e.g. TeSys GV2 type: GV2P10, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - 250V, 16A, DIN rail mounting socket, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
| V DEA polje omare z oznako +DEA_K1_2_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the DEA box of the cabinet marked +DEA_K1_2_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=40 A, 3P za montažo na montažno ploščo; kot naprimer tip: A9S65340, Schneider | - main disconnecting switch In=40 A, 3P for mounting on a mounting plate; e.g. type: A9S65340, Schneider | kos | 1
| - vrtljiva ročica za krmiljenje glavnega ločilnega stikala + adapterski mehanizem; kot naprimer tip: A9A27006 + A9A27008, Schneider | - rotary lever for controlling the main disconnecting switch + adapter mechanism; as for example type: A9A27006 + A9A27008, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 14
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 2
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.7 | Dobava in montaža razdelilnika +NN_P1_1_R (sestavljen iz dveh polj) iz jeklene pločevine v barvi RAL 7035, skupnih dimenzij 1600x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT SFN, tip: NSYSFN221060P + NSYSFN22660P, Schneider. | Supply and installation of a distribution box +NN_P1_1_R (consisting of two boxes) made of steel sheet in RAL 7035 colour, overall dimensions 1600x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. As for example PanelSeT SFN cabinet, type: NSYSFN221060P + NSYSFN22660P, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=160 A, 3P za montažo na montažno ploščo; kot naprimer tip: C163160S, Schneider | - main disconnecting switch In=160 A, 3P for mounting on a mounting plate; e.g. type: C163160S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer Galaxy VS, tip: LV429338T, Schneider | - rotatable extension arm for controlling the main disconnecting switch; as for example Galaxy VS, type: LV429338T, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 7
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 8
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 3
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 10 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173222, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 10 A with C characteristic, 30mA, type AC, as for example: 002173222, ETI | kos | 5
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 39
| - napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, kot naprimer RM17-U tip: RM17UB310, Schneider | - voltage control relay, range 183 to 528 V AC, 1 C/O, e.g. RM17-U type: RM17UB310, Schneider | kos | 1
| - miniaturni vtični elektromehanski rele, 6 A, 230 V AC (4x CO preklopni kontakt), kot naprimer Harmony tip: RXM4AB1P7PVS, Schneider | - miniature plug-in electromechanical relay, 6 A, 230 V AC (4x CO switching contact), such as Harmony type: RXM4AB1P7PVS, Schneider | kos | 2
| - varovalčni ločilnik 2P, 25 A, za varovalko 10,3 x 38 mm - varovalka gG 1 A, kot naprimer: A9N15651, Schneider | - fuse disconnector 2P, 25 A, for fuse 10,3 x 38 mm - fuse gG 1 A, as for example: A9N15651, Schneider | kos | 1
| - motorski odklopnik 3P, 4-6,3 A, termomagnetna zaščita, kot naprimer TeSys GV2 tip: GV2P10, Schneider | - motor circuit breaker 3P, 4-6.3 A, thermomagnetic protection, e.g. TeSys GV2 type: GV2P10, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.8 | Dobava in montaža razdelilnika +NN_P1_2_R (sestavljen iz dveh polj) iz jeklene pločevine v barvi RAL 7035, skupnih dimenzij 1600x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT SFN, tip: NSYSFN221060P + NSYSFN22660P, Schneider. | Supply and installation of a distribution box +NN_P1_2_R (consisting of two boxes) made of steel sheet in RAL 7035 colour, overall dimensions 1600x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. As for example PanelSeT SFN cabinet, type: NSYSFN221060P + NSYSFN22660P, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=160 A, 3P za montažo na montažno ploščo; kot naprimer tip: C163160S, Schneider | - main disconnecting switch In=160 A, 3P for mounting on a mounting plate; e.g. type: C163160S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer Galaxy VS, tip: LV429338T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example Galaxy VS, type: LV429338T, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 8
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 11
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 3
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 10 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173222, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 10 A with C characteristic, 30mA, type AC, as for example: 002173222, ETI | kos | 5
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 36
| - napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, kot naprimer RM17-U tip: RM17UB310, Schneider | - voltage control relay, range 183 to 528 V AC, 1 C/O, e.g. RM17-U type: RM17UB310, Schneider | kos | 1
| - miniaturni vtični elektromehanski rele, 6 A, 230 V AC (4x CO preklopni kontakt), kot naprimer Harmony tip: RXM4AB1P7PVS, Schneider | - miniature plug-in electromechanical relay, 6 A, 230 V AC (4x CO switching contact), such as Harmony type: RXM4AB1P7PVS, Schneider | kos | 2
| - varovalčni ločilnik 2P, 25 A, za varovalko 10,3 x 38 mm - varovalka gG 1 A, kot naprimer: A9N15651, Schneider | - fuse disconnector 2P, 25 A, for fuse 10,3 x 38 mm - fuse gG 1 A, as for example: A9N15651, Schneider | kos | 1
| - motorski odklopnik 3P, 4-6,3 A, termomagnetna zaščita, kot naprimer TeSys GV2 tip: GV2P10, Schneider | - motor circuit breaker 3P, 4-6.3 A, thermomagnetic protection, e.g. TeSys GV2 type: GV2P10, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - 250V, 16A, DIN rail mounting socket, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.9 | Dobava in montaža razdelilnika +NN_P1_3_R (sestavljen iz treh polj) iz jeklene pločevine v barvi RAL 7035, skupnih dimenzij 3000x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT SFN, tip: 3 x NSYSFN221060P, Schneider. | Supply and installation of a distribution box +NN_P1_3_R (consisting of three boxes) made of steel sheet in RAL 7035, overall dimensions 3000x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single-leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. As for example PanelSeT SFN cabinet, type: 3 x NSYSFN221060P, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=400 A, 3P za montažo na montažno ploščo; kot naprimer tip: C403400S, Schneider | - main disconnecting switch In=400 A, 3P for mounting on a mounting plate; e.g. type: C403400S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV432598T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV432598T, Schneider | kos | 1
| - energijski senzor, 160 A 3P/3P+N položaj zgoraj/spodaj, kot naprimer PowerTag Flex tip: A9MEM1580, Schneider | - energy sensor, 160 A 3P/3P+N top/bottom position, e.g. PowerTag Flex type: A9MEM1580, Schneider | kos | 6
| - energijski senzor, 63 A 3P+N položaj zgoraj/spodaj, kot naprimer PowerTag Flex tip: A9MEM1570, Schneider | - energy sensor, 63 A 3P+N top/bottom position, e.g. PowerTag Flex type: A9MEM1570, Schneider | kos | 7
| - kompaktni odklopnik na diferenčni tok 4P, 160 A, 415 V, tip AC, 25 kA, kot naprimer ComPacT NSX, tip: C16B44V160, Schneider | - compact circuit breaker 4P, differential current, 160 A, 415 V, type AC, 25 kA, e.g. ComPacT NSX, type: C16B44V160, Schneider | kos | 1
| - kompaktni odklopnik na diferenčni tok 4P, 100 A, 415 V, tip AC, 25 kA, kot naprimer ComPacT NSX, tip: C10B44V100, Schneider | - compact circuit breaker 4P, differential current, 100 A, 415 V, type AC, 25 kA, e.g. ComPacT NSX, type: C10B44V100, Schneider | kos | 5
| - kompaktni odklopnik na diferenčni tok 4P, 40 A, 415 V, tip AC, 25 kA, kot naprimer ComPacT NSX, tip: C10B44V040, Schneider | - compact circuit breaker 4P, differential current, 40 A, 415 V, type AC, 25 kA, e.g. ComPacT NSX, type: C10B44V040, Schneider | kos | 6
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 20 kA, kot naprimer Acti 9 iC60L, tip: A9F94440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 20 kA, such as Acti 9 iC60L, type: A9F94440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 32 A, s C karakteristiko, 20 kA, kot naprimer Acti 9 iC60L, tip: A9F94332, Schneider | - three-pole 32 A circuit-breaker with C characteristic, 20 kA, such as Acti 9 iC60L, type: A9F94332, Schneider | kos | 2
| - tripolni inštalacijski odklopnik 20 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L, tip: A9F94320, Schneider | - three-pole circuit breaker 20 A, with C characteristic, 25 kA, e.g. Acti 9 iC60L, type: A9F94320, Schneider | kos | 11
| - tripolni inštalacijski odklopnik 16 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L, tip: A9F94316, Schneider | - three-pole circuit breaker 16 A, with C characteristic, 25 kA, e.g. Acti 9 iC60L, type: A9F94316, Schneider | kos | 46
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L, tip: A9F94304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 25 kA, e.g. Acti 9 iC60L, type: A9F94304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L tip: A9F94116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 25 kA, e.g. Acti 9 iC60L type: A9F94116, Schneider | kos | 136
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L tip: A9F94110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 25 kA, such as Acti 9 iC60L type: A9F94110, Schneider | kos | 12
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L tip: A9F94106, Schneider | - single-pole circuit-breaker 6 A, with C characteristic, 25 kA, such as Acti 9 iC60L type: A9F94106, Schneider | kos | 3
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 10 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173222, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 10 A with C characteristic, 30mA, type AC, as for example: 002173222, ETI | kos | 2
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPS), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 20
| - kontaktor, 4P (4NO), 200 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1D115004P7 + LADN11, Schneider | - contactor, 4P (4NO), 200 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, such as TeSys Deca, type: LC1D115004P7 + LADN11, Schneider | kos | 1
| - kontaktor, 4P (4NO), 80 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1DT80AP7 + LADN11, Schneider | - contactor, 4P (4NO), 80 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, like for example TeSys Deca, type: LC1DT80AP7 + LADN11, Schneider | kos | 1
| - kontaktor, 4P (4NO), 60 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1DT60AP7 + LADN11, Schneider | - contactor, 4P (4NO), 60 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, like for example TeSys Deca, type: LC1DT60AP7 + LADN11, Schneider | kos | 6
| - kontaktor, 4P (4NO), 40 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1DT40P7 + LADN11, Schneider | - contactor, 4P (4NO), 40 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, such as TeSys Deca, type: LC1DT40P7 + LADN11, Schneider | kos | 4
| - univerzalni wifi, koncentrator Modbus prehod 110-240 V AC/DC, kot naprimer tip: PAS600T, Schneider | - universal wifi, Modbus gateway concentrator 110-240 V AC/DC, e.g. type: PAS600T, Schneider | kos | 1
| - napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, kot naprimer RM17-U tip: RM17UB310, Schneider | - voltage control relay, range 183 to 528 V AC, 1 C/O, e.g. RM17-U type: RM17UB310, Schneider | kos | 1
| - miniaturni vtični elektromehanski rele, 6 A, 230 V AC (4x CO preklopni kontakt), kot naprimer Harmony tip: RXM4AB1P7PVS, Schneider | - miniature plug-in electromechanical relay, 6 A, 230 V AC (4x CO switching contact), such as Harmony type: RXM4AB1P7PVS, Schneider | kos | 10
| - ohišje za varovalčno ločilno stikalo 3P, 100 A, + 3 x talilni vložek gG 50 A, NH000, kot naprimer: LV480800, Schneider | - enclosure for fused isolating switch 3P, 100 A, + 3 x fusing insert gG 50 A, NH000, as for example: LV480800, Schneider | kos | 1
| - varovalčni ločilnik 2P, 25 A, za varovalko 10,3 x 38 mm - varovalka gG 1 A, kot naprimer: A9N15651, Schneider | - fuse disconnector 2P, 25 A, for fuse 10,3 x 38 mm - fuse gG 1 A, as for example: A9N15651, Schneider | kos | 1
| - ločilno stikalo 2P, 20 A, 415 V, kot naprimer Acti 9 iSW tip: A9S60220, Schneider | - disconnecting switch 2P, 20 A, 415 V, e.g. Acti 9 iSW type: A9S60220, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - 250V, 16A, DIN rail mounting socket, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.10 | Dobava in montaža razdelilnika +NN_P1_4_R (sestavljen iz treh polj) iz jeklene pločevine v barvi RAL 7035, skupnih dimenzij 3200x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna ozeroma dvokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT SFN, tip: 2 x NSYSFN221060P + NSYSFN2212602DP, Schneider. | Supply and installation of a distribution box +NN_P1_4_R (consisting of three boxes) made of steel sheet in RAL 7035 colour, overall dimensions 3200x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single or double wing door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. As for example PanelSeT SFN cabinet, type: 2 x NSYSFN221060P + NSYSFN2212602DP, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=630 A, 3P za montažo na montažno ploščo; kot naprimer tip: C633630S, Schneider | - main disconnecting switch In=630 A, 3P for mounting on a mounting plate; e.g. type: C633630S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV432600T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV432600T, Schneider | kos | 1
| - energijski senzor, 250 A 3P+N položaj spodaj, kot naprimer PowerTag M250 tip: LV434021, Schneider | - energy sensor, 250 A 3P+N position below, e.g. PowerTag M250 type: LV434021, Schneider | kos | 1
| - energijski senzor, 160 A 3P/3P+N položaj zgoraj/spodaj, kot naprimer PowerTag Flex tip: A9MEM1580, Schneider | - energy sensor, 160 A 3P/3P+N top/bottom position, e.g. PowerTag Flex type: A9MEM1580, Schneider | kos | 8
| - energijski senzor, 63 A 3P+N položaj zgoraj/spodaj, kot naprimer PowerTag Flex tip: A9MEM1570, Schneider | - energy sensor, 63 A 3P+N top/bottom position, e.g. PowerTag Flex type: A9MEM1570, Schneider | kos | 1
| - kompaktni odklopnik na diferenčni tok 4P, 250 A, 415 V, tip AC, 25 kA, kot naprimer ComPacT NSX, tip: C25B44V250, Schneider | - compact circuit breaker 4P, differential current, 250 A, 415 V, type AC, 25 kA, e.g. ComPacT NSX, type: C25B44V250, Schneider | kos | 1
| - kompaktni odklopnik na diferenčni tok 4P, 160 A, 415 V, tip AC, 25 kA, kot naprimer ComPacT NSX, tip: C16B44V160, Schneider | - compact circuit breaker 4P, differential current, 160 A, 415 V, type AC, 25 kA, e.g. ComPacT NSX, type: C16B44V160, Schneider | kos | 1
| - kompaktni odklopnik na diferenčni tok 4P, 100 A, 415 V, tip AC, 25 kA, kot naprimer ComPacT NSX, tip: C10B44V100, Schneider | - compact circuit breaker 4P, differential current, 100 A, 415 V, type AC, 25 kA, e.g. ComPacT NSX, type: C10B44V100, Schneider | kos | 7
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 20 kA, kot naprimer Acti 9 iC60L, tip: A9F94440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 20 kA, such as Acti 9 iC60L, type: A9F94440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 63 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60L, tip: A9F94363, Schneider | - three-pole circuit breaker 63 A, with C characteristic, 15 kA, such as Acti 9 iC60L, type: A9F94363, Schneider | kos | 3
| - tripolni inštalacijski odklopnik 40 A, s C karakteristiko, 20 kA, kot naprimer Acti 9 iC60L, tip: A9F94340, Schneider | - three-pole circuit breaker 40 A, with C characteristic, 20 kA, such as Acti 9 iC60L, type: A9F94340, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 32 A, s C karakteristiko, 20 kA, kot naprimer Acti 9 iC60L, tip: A9F94332, Schneider | - 32 A three-pole circuit-breaker with C characteristic, 20 kA, such as Acti 9 iC60L, type: A9F94332, Schneider | kos | 30
| - tripolni inštalacijski odklopnik 16 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L, tip: A9F94316, Schneider | - three-pole circuit breaker 16 A, with C characteristic, 25 kA, e.g. Acti 9 iC60L, type: A9F94316, Schneider | kos | 37
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L, tip: A9F94304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 25 kA, such as Acti 9 iC60L, type: A9F94304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L tip: A9F94116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 25 kA, e.g. Acti 9 iC60L type: A9F94116, Schneider | kos | 65
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L tip: A9F94110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 25 kA, such as Acti 9 iC60L type: A9F94110, Schneider | kos | 12
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L tip: A9F94106, Schneider | - single-pole circuit-breaker 6 A, with C characteristic, 25 kA, such as Acti 9 iC60L type: A9F94106, Schneider | kos | 3
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 10 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173222, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 10 A with C characteristic, 30 mA, type AC, as for example: 002173222, ETI | kos | 2
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 11
| - kontaktor, 4P (4NO), 200 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1D115004P7 + LADN11, Schneider | - contactor, 4P (4NO), 200 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, such as TeSys Deca, type: LC1D115004P7 + LADN11, Schneider | kos | 1
| - kontaktor, 4P (4NO), 125 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1D80004P7 + LADN11, Schneider | - contactor, 4P (4NO), 125 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. TeSys Deca, type: LC1D80004P7 + LADN11, Schneider | kos | 6
| - kontaktor, 4P (4NO), 80 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1DT80AP7 + LADN11, Schneider | - contactor, 4P (4NO), 80 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, such as TeSys Deca, type: LC1DT80AP7 + LADN11, Schneider | kos | 2
| - univerzalni wifi, koncentrator Modbus prehod 110-240 V AC/DC, kot naprimer tip: PAS600T, Schneider | - universal wifi, Modbus gateway concentrator 110-240 V AC/DC, e.g. type: PAS600T, Schneider | kos | 1
| - napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, kot naprimer RM17-U tip: RM17UB310, Schneider | - voltage control relay, range 183 to 528 V AC, 1 C/O, e.g. RM17-U type: RM17UB310, Schneider | kos | 1
| - miniaturni vtični elektromehanski rele, 6 A, 230 V AC (4x CO preklopni kontakt), kot naprimer Harmony tip: RXM4AB1P7PVS, Schneider | - miniature plug-in electromechanical relay, 6 A, 230 V AC (4x CO switching contact), such as Harmony type: RXM4AB1P7PVS, Schneider | kos | 3
| - varovalčni ločilnik 3P, 125 A, za varovalko 22 x 58 mm - varovalka gG 80 A, kot naprimer: A9GSB392 + DF2FN80, Schneider | - fuse disconnector 3P, 125 A, for fuse 22 x 58 mm - fuse gG 80 A, as for example: A9GSB392 + DF2FN80, Schneider | kos | 1
| - ohišje za varovalčno ločilno stikalo 3P, 100 A, + 3 x talilni vložek gG 50 A, NH000, kot naprimer: LV480800, Schneider | - enclosure for fused isolating switch 3P, 100 A, + 3 x fusing insert gG 50 A, NH000, as for example: LV480800, Schneider | kos | 1
| - varovalčni ločilnik 2P, 25 A, za varovalko 10,3 x 38 mm - varovalka gG 1 A, kot naprimer: A9N15651, Schneider | - fuse disconnector 2P, 25 A, for fuse 10,3 x 38 mm - fuse gG 1 A, as for example: A9N15651, Schneider | kos | 1
| - ločilno stikalo 2P, 20 A, 415 V, kot naprimer Acti 9 iSW tip: A9S60220, Schneider | - disconnecting switch 2P, 20 A, 415 V, e.g. Acti 9 iSW type: A9S60220, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - 250V, 16A, DIN rail mounting socket, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.11 | Dobava in montaža razdelilnika +NN_P1_5_R (sestavljen iz treh polj) iz jeklene pločevine v barvi RAL 7035, skupnih dimenzij 3200x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna ozeroma dvokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT SFN, tip: 2 x NSYSFN221060P + NSYSFN2212602DP, Schneider. | Supply and installation of a distribution box +NN_P1_5_R (consisting of three boxes) made of steel sheet in RAL 7035 colour, overall dimensions 3200x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single or double wing door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. As for example PanelSeT SFN cabinet, type: 2 x NSYSFN221060P + NSYSFN2212602DP, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=400 A, 3P za montažo na montažno ploščo; kot naprimer tip: C403400S, Schneider | - main disconnecting switch In=400 A, 3P for mounting on a mounting plate; e.g. type: C403400S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV432598T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV432598T, Schneider | kos | 1
| - energijski senzor, 160 A 3P/3P+N položaj zgoraj/spodaj, kot naprimer PowerTag Flex tip: A9MEM1580, Schneider | - energy sensor, 160 A 3P/3P+N top/bottom position, e.g. PowerTag Flex type: A9MEM1580, Schneider | kos | 6
| - energijski senzor, 63 A 3P+N položaj zgoraj/spodaj, kot naprimer PowerTag Flex tip: A9MEM1570, Schneider | - energy sensor, 63 A 3P+N top/bottom position, e.g. PowerTag Flex type: A9MEM1570, Schneider | kos | 4
| - kompaktni odklopnik na diferenčni tok 4P, 160 A, 415 V, tip AC, 25 kA, kot naprimer ComPacT NSX, tip: C16B44V160, Schneider | - compact circuit breaker 4P, differential current, 160 A, 415 V, type AC, 25 kA, e.g. ComPacT NSX, type: C16B44V160, Schneider | kos | 1
| - kompaktni odklopnik na diferenčni tok 4P, 100 A, 415 V, tip AC, 25 kA, kot naprimer ComPacT NSX, tip: C10B44V100, Schneider | - compact circuit breaker 4P, differential current, 100 A, 415 V, type AC, 25 kA, e.g. ComPacT NSX, type: C10B44V100, Schneider | kos | 5
| - kompaktni odklopnik na diferenčni tok 4P, 40 A, 415 V, tip AC, 25 kA, kot naprimer ComPacT NSX, tip: C10B44V040, Schneider | - compact circuit breaker 4P, differential current, 40 A, 415 V, type AC, 25 kA, e.g. ComPacT NSX, type: C10B44V040, Schneider | kos | 3
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 20 kA, kot naprimer Acti 9 iC60L, tip: A9F94440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 20 kA, such as Acti 9 iC60L, type: A9F94440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 63 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60L, tip: A9F94363, Schneider | - three-pole circuit breaker 63 A, with C characteristic, 15 kA, such as Acti 9 iC60L, type: A9F94363, Schneider | kos | 2
| - tripolni inštalacijski odklopnik 50 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60L, tip: A9F94350, Schneider | - three-pole circuit breaker 50 A, with C characteristic, 15 kA, e.g. Acti 9 iC60L, type: A9F94350, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 40 A, s C karakteristiko, 20 kA, kot naprimer Acti 9 iC60L, tip: A9F94340, Schneider | - three-pole circuit breaker 40 A, with C characteristic, 20 kA, such as Acti 9 iC60L, type: A9F94340, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 32 A, s C karakteristiko, 20 kA, kot naprimer Acti 9 iC60L, tip: A9F94332, Schneider | - three-pole 32 A circuit-breaker with C characteristic, 20 kA, such as Acti 9 iC60L, type: A9F94332, Schneider | kos | 12
| - tripolni inštalacijski odklopnik 20 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L, tip: A9F94320, Schneider | - three-pole circuit breaker 20 A, with C characteristic, 25 kA, e.g. Acti 9 iC60L, type: A9F94320, Schneider | kos | 22
| - tripolni inštalacijski odklopnik 16 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L, tip: A9F94316, Schneider | - three-pole circuit breaker 16 A, with C characteristic, 25 kA, e.g. Acti 9 iC60L, type: A9F94316, Schneider | kos | 31
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L, tip: A9F94304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 25 kA, e.g. Acti 9 iC60L, type: A9F94304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L tip: A9F94116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 25 kA, e.g. Acti 9 iC60L type: A9F94116, Schneider | kos | 71
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L tip: A9F94110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 25 kA, such as Acti 9 iC60L type: A9F94110, Schneider | kos | 11
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L tip: A9F94106, Schneider | - single-pole circuit-breaker 6 A, with C characteristic, 25 kA, such as Acti 9 iC60L type: A9F94106, Schneider | kos | 3
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPS), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 7
| - kontaktor, 4P (4NO), 200 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1D115004P7 + LADN11, Schneider | - contactor, 4P (4NO), 200 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, such as TeSys Deca, type: LC1D115004P7 + LADN11, Schneider | kos | 1
| - kontaktor, 4P (4NO), 80 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1DT80AP7 + LADN11, Schneider | - contactor, 4P (4NO), 80 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, like for example TeSys Deca, type: LC1DT80AP7 + LADN11, Schneider | kos | 4
| - kontaktor, 4P (4NO), 60 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1DT60AP7 + LADN11, Schneider | - contactor, 4P (4NO), 60 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, such as TeSys Deca, type: LC1DT60AP7 + LADN11, Schneider | kos | 1
| - kontaktor, 4P (4NO), 40 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1DT40P7 + LADN11, Schneider | - contactor, 4P (4NO), 40 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, such as TeSys Deca, type: LC1DT40P7 + LADN11, Schneider | kos | 3
| - univerzalni wifi, koncentrator Modbus prehod 110-240 V AC/DC, kot naprimer tip: PAS600T, Schneider | - universal wifi, Modbus gateway concentrator 110-240 V AC/DC, e.g. type: PAS600T, Schneider | kos | 1
| - napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, kot naprimer RM17-U tip: RM17UB310, Schneider | - voltage control relay, range 183 to 528 V AC, 1 C/O, e.g. RM17-U type: RM17UB310, Schneider | kos | 1
| - miniaturni vtični elektromehanski rele, 6 A, 230 V AC (4x CO preklopni kontakt), kot naprimer Harmony tip: RXM4AB1P7PVS, Schneider | - miniature plug-in electromechanical relay, 6 A, 230 V AC (4x CO switching contact), such as Harmony type: RXM4AB1P7PVS, Schneider | kos | 5
| - ohišje za varovalčno ločilno stikalo 3P, 100 A, + 3 x talilni vložek gG 32 A, NH000, kot naprimer: LV480800, Schneider | - enclosure for fused isolating switch 3P, 100 A, + 3 x fusing insert gG 32 A, NH000, as for example: LV480800, Schneider | kos | 1
| - varovalčni ločilnik 2P, 25 A, za varovalko 10,3 x 38 mm - varovalka gG 1 A, kot naprimer: A9N15651, Schneider | - fuse disconnector 2P, 25 A, for fuse 10,3 x 38 mm - fuse gG 1 A, as for example: A9N15651, Schneider | kos | 1
| - ločilno stikalo 2P, 20 A, 415 V, kot naprimer Acti 9 iSW tip: A9S60220, Schneider | - disconnecting switch 2P, 20 A, 415 V, e.g. Acti 9 iSW type: A9S60220, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - 250V, 16A, DIN rail mounting socket, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.12 | Dobava in montaža razdelilnika +NN_P1_6_R (sestavljen iz sedmih polj) iz jeklene pločevine v barvi RAL 9001, skupnih dimenzij 4400x2000x465mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-C, IP30, IK10. Uvod kablov od zgoraj. Kot naprimer omara tip: Prisma P, Schneider. | Supply and installation of a distribution box +NN_P1_6_R (consisting of seven boxes) made of sheet steel in RAL 9001, overall dimensions 4400x2000x465mm (WxHxD), including mounting plate, base V = 100mm, single leaf door, door opening 120°, TN-C, IP30, IK10. Cable entry from above. As for example cabinet type: Prisma P, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=1250 A, 3P za montažo na montažno ploščo; kot naprimer tip: 31348, Schneider | - main disconnecting switch In=1250 A, 3P for mounting on a mounting plate; as for example type: 31348, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer INS/INV, tip: 31289, Schneider | - rotatable extension arm for control of the main isolating switch; as for example INS/INV, type: 31289, Schneider | kos | 1
| - energijski senzor, 630 A 3P+N položaj spodaj, kot naprimer PowerTag M630 tip: LV434023, Schneider | - energy sensor, 630 A 3P+N position below, e.g. PowerTag M630 type: LV434023, Schneider | kos | 2
| - energijski senzor, 250 A 3P+N položaj spodaj, kot naprimer PowerTag M250 tip: LV434021, Schneider | - energy sensor, 250 A 3P+N position below, e.g. PowerTag M250 type: LV434021, Schneider | kos | 2
| - energijski senzor, 63 A 3P+N položaj zgoraj/spodaj, kot naprimer PowerTag Flex tip: A9MEM1570, Schneider | - energy sensor, 63 A 3P+N top/bottom position, e.g. PowerTag Flex type: A9MEM1570, Schneider | kos | 4
| - kompaktni odklopnik 4P, 630 A, 415 V, tip AC, 36 kA in pomožni kontakt 1 NO/NC kot naprimer ComPacT NSX, tip: C63F42D630 + 29450, Schneider | - compact circuit breaker 4P, 630 A, 415 V, type AC, 36 kA and auxiliary contact 1 NO/NC as for example ComPacT NSX, type: C63F42D630 + 29450, Schneider | kos | 1
| - kompaktni odklopnik 4P, 250 A, 415 V, tip AC, 36 kA in pomožni kontakt 1 NO/NC kot naprimer ComPacT NSX, tip: C40F42D250 + 29450, Schneider | - compact circuit breaker 4P, 250 A, 415 V, type AC, 36 kA and auxiliary contact 1 NO/NC as for example ComPacT NSX, type: C40F42D250 + 29450, Schneider | kos | 1
| - kompaktni odklopnik na diferenčni tok 4P, 630 A, 415 V, tip AC, 36 kA, kot naprimer ComPacT NSX, tip: C63F42D630 + LV432465, Schneider | - compact circuit breaker 4P, differential current, 630 A, 415 V, type AC, 36 kA, as for example ComPacT NSX, type: C63F42D630 + LV432465, Schneider | kos | 1
| - kompaktni odklopnik na diferenčni tok 4P, 250 A, 415 V, tip AC, 36 kA, kot naprimer ComPacT NSX, tip: C25F44V250, Schneider | - compact circuit breaker 4P, differential current, 250 A, 415 V, type AC, 36 kA, e.g. ComPacT NSX, type: C25F44V250, Schneider | kos | 1
| - štiripolni miniaturni odklopnik 63 A, s C karakteristiko, 36 kA, kot naprimer Acti 9 NG125, tip: 18739, Schneider | - four-pole miniature circuit-breaker 63 A, with C characteristic, 36 kA, such as for example Acti 9 NG125, type: 18739, Schneider | kos | 1
| - dodatna naprava diferenčnega toka 63 A, 4P, tip A, 30 mA, kot naprimer Vigi NG125, tip: 19015, Schneider | - additional differential current device 63 A, 4P, type A, 30 mA, such as Vigi NG125, type: 19015, Schneider | kos | 3
| - štiripolni miniaturni odklopnik 50 A, s C karakteristiko, 36 kA, kot naprimer Acti 9 NG125, tip: 18738, Schneider | - four-pole miniature circuit-breaker 50 A, with C characteristic, 36 kA, such as for example Acti 9 NG125, type: 18738, Schneider | kos | 1
| - štiripolni miniaturni odklopnik 40 A, s C karakteristiko, 36 kA, kot naprimer Acti 9 NG125, tip: 18737, Schneider | - four-pole miniature circuit-breaker 40 A, with C characteristic, 36 kA, such as for example Acti 9 NG125, type: 18737, Schneider | kos | 2
| - tripolni inštalacijski odklopnik 63 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60L, tip: A9F94363, Schneider | - three-pole circuit breaker 63 A, with C characteristic, 15 kA, such as Acti 9 iC60L, type: A9F94363, Schneider | kos | 3
| - tripolni inštalacijski odklopnik 40 A, s C karakteristiko, 20 kA, kot naprimer Acti 9 iC60L, tip: A9F94340, Schneider | - three-pole circuit breaker 40 A, with C characteristic, 20 kA, such as Acti 9 iC60L, type: A9F94340, Schneider | kos | 3
| - tripolni inštalacijski odklopnik 32 A, s C karakteristiko, 20 kA, kot naprimer Acti 9 iC60L, tip: A9F94332, Schneider | - three-pole 32 A circuit-breaker with C characteristic, 20 kA, such as Acti 9 iC60L, type: A9F94332, Schneider | kos | 37
| - tripolni inštalacijski odklopnik 25 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L, tip: A9F94325, Schneider | - three-pole installation circuit-breaker 25 A, with C characteristic, 25 kA, as for example Acti 9 iC60L, type: A9F94325, Schneider | kos | 3
| - tripolni inštalacijski odklopnik 16 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L, tip: A9F94316, Schneider | - three-pole circuit breaker 16 A, with C characteristic, 25 kA, e.g. Acti 9 iC60L, type: A9F94316, Schneider | kos | 33
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L tip: A9F94116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 25 kA, e.g. Acti 9 iC60L type: A9F94116, Schneider | kos | 42
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L tip: A9F94110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 25 kA, such as Acti 9 iC60L type: A9F94110, Schneider | kos | 11
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 8
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 3P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002174924, ETI | - combined protection switch with overcurrent protection (CPC), 3P+N, 16 A with C characteristic, 30mA, type AC, as for example: 002174924, ETI | kos | 2
| - kontaktor, 4P (4NO), 700 A, tuljava 100 do 250 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Giga, tip: LC1G5004KUEN + LAG8N113P, Schneider | - contactor, 4P (4NO), 700 A, coil 100 to 250 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. TeSys Giga, type: LC1G5004KUEN + LAG8N113P, Schneider | kos | 2
| - kontaktor, 4P (4NO), 200 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1D115004P7 + LADN11, Schneider | - contactor, 4P (4NO), 200 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, such as TeSys Deca, type: LC1D115004P7 + LADN11, Schneider | kos | 2
| - kontaktor, 4P (4NO), 80 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1DT80AP7 + LADN11, Schneider | - contactor, 4P (4NO), 80 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, such as TeSys Deca, type: LC1DT80AP7 + LADN11, Schneider | kos | 1
| - kontaktor, 4P (4NO), 60 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1DT60AP7 + LADN11, Schneider | - contactor, 4P (4NO), 60 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, such as TeSys Deca, type: LC1DT60AP7 + LADN11, Schneider | kos | 2
| - univerzalni wifi, koncentrator Modbus prehod 110-240 V AC/DC, kot naprimer tip: PAS600T, Schneider | - universal wifi, Modbus gateway concentrator 110-240 V AC/DC, e.g. type: PAS600T, Schneider | kos | 2
| - napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, kot naprimer RM17-U tip: RM17UB310, Schneider | - voltage control relay, range 183 to 528 V AC, 1 C/O, e.g. RM17-U type: RM17UB310, Schneider | kos | 1
| - ohišje za varovalčno ločilno stikalo 3P, 250 A, + 3 x talilni vložek gG 250 A, NH01, kot naprimer: LV480804, Schneider | - housing for fuse disconnector switch 3P, 250 A, + 3 x fusing insert gG 250 A, NH01, as for example: LV480804, Schneider | kos | 3
| - ohišje za varovalčno ločilno stikalo 3P, 100 A, + 3 x talilni vložek gG 100 A, NH000, kot naprimer: LV480800, Schneider | - enclosure for fused isolating switch 3P, 100 A, + 3 x fusing insert gG 100 A, NH000, as for example: LV480800, Schneider | kos | 1
| - ohišje za varovalčno ločilno stikalo 3P, 100 A, + 3 x talilni vložek gG 80 A, NH000, kot naprimer: LV480800, Schneider | - enclosure for fused isolating switch 3P, 100 A, + 3 x fusing insert gG 80 A, NH000, as for example: LV480800, Schneider | kos | 4
| - ohišje za varovalčno ločilno stikalo 3P, 100 A, + 3 x talilni vložek gG 63 A, NH000, kot naprimer: LV480800, Schneider | - enclosure for fused isolating switch 3P, 100 A, + 3 x fusing insert gG 63 A, NH000, as for example: LV480800, Schneider | kos | 4
| - ohišje za varovalčno ločilno stikalo 3P, 100 A, + 3 x talilni vložek gG 50 A, NH000, kot naprimer: LV480800, Schneider | - enclosure for fused isolating switch 3P, 100 A, + 3 x fusing insert gG 50 A, NH000, as for example: LV480800, Schneider | kos | 1
| - miniaturni vtični elektromehanski rele, 6 A, 230 V AC (4x CO preklopni kontakt), kot naprimer Harmony tip: RXM4AB1P7PVS, Schneider | - miniature plug-in electromechanical relay, 6 A, 230 V AC (4x CO switching contact), such as Harmony type: RXM4AB1P7PVS, Schneider | kos | 3
| - varovalčni ločilnik 3P, 25 A, za varovalko 10,3 x 38 mm - varovalka gG 4 A, kot naprimer: A9N15656 + DF2CN04, Schneider | - fuse disconnector 3P, 25 A, for fuse 10,3 x 38 mm - fuse gG 4 A, as for example: A9N15656 + DF2CN04, Schneider | kos | 1
| - varovalčni ločilnik 2P, 25 A, za varovalko 10,3 x 38 mm - varovalka gG 1 A, kot naprimer: A9N15651, Schneider | - fuse disconnector 2P, 25 A, for fuse 10,3 x 38 mm - fuse gG 1 A, as for example: A9N15651, Schneider | kos | 1
| - varovalčni ločilnik 1P, 10 A, za varovalko 8,5 x 31,5 mm - varovalka gG 6 A, kot naprimer: A9N15635 + DF2BN0600, Schneider | - fuse disconnector 1P, 10 A, for fuse 8,5 x 31,5 mm - fuse gG 6 A, as for example: A9N15635 + DF2BN0600, Schneider | kos | 3
| - ločilno stikalo 2P, 20 A, 415 V, kot naprimer Acti 9 iSW tip: A9S60220, Schneider | - disconnecting switch 2P, 20 A, 415 V, e.g. Acti 9 iSW type: A9S60220, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - 250V, 16A, DIN rail mounting socket, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.13 | Dobava in montaža razdelilnika +NN_P1_6_R_LICEM (sestavljen iz treh polj) iz jeklene pločevine v barvi RAL 7035, skupnih dimenzij 2600x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna ozeroma dvokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT SFN, tip: NSYSFN221060P + 2 x NSYSFN22860P, Schneider. | Supply and installation of a distribution box +NN_P1_6_R_LICEM (consisting of three boxes) made of steel sheet in RAL 7035 colour, overall dimensions 2600x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single or double wing door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. As for example PanelSeT SFN cabinet, type: NSYSFN221060P + 2 x NSYSFN22860P, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=400 A, 3P za montažo na montažno ploščo; kot naprimer tip: C403400S, Schneider | - main disconnecting switch In=400 A, 3P for mounting on a mounting plate; e.g. type: C403400S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV432598T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV432598T, Schneider | kos | 1
| - energijski senzor, 160 A 3P/3P+N položaj zgoraj/spodaj, kot naprimer PowerTag Flex tip: A9MEM1580, Schneider | - energy sensor, 160 A 3P/3P+N top/bottom position, e.g. PowerTag Flex type: A9MEM1580, Schneider | kos | 6
| - kompaktni odklopnik na diferenčni tok 4P, 100 A, 415 V, tip AC, 25 kA, kot naprimer ComPacT NSX, tip: C10B44V100, Schneider | - compact circuit breaker 4P, differential current, 100 A, 415 V, type AC, 25 kA, e.g. ComPacT NSX, type: C10B44V100, Schneider | kos | 6
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 20 kA, kot naprimer Acti 9 iC60L, tip: A9F94440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 20 kA, such as Acti 9 iC60L, type: A9F94440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 32 A, s C karakteristiko, 20 kA, kot naprimer Acti 9 iC60L, tip: A9F94332, Schneider | - three-pole 32 A circuit-breaker with C characteristic, 20 kA, such as Acti 9 iC60L, type: A9F94332, Schneider | kos | 4
| - tripolni inštalacijski odklopnik 16 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L, tip: A9F94316, Schneider | - three-pole circuit breaker 16 A, with C characteristic, 25 kA, e.g. Acti 9 iC60L, type: A9F94316, Schneider | kos | 38
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L, tip: A9F94304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 25 kA, e.g. Acti 9 iC60L, type: A9F94304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L tip: A9F94116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 25 kA, such as Acti 9 iC60L type: A9F94116, Schneider | kos | 33
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L tip: A9F94106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 25 kA, such as Acti 9 iC60L type: A9F94106, Schneider | kos | 3
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kontaktor, 4P (4NO), 120 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1D80004P7 + LADN11, Schneider | - contactor, 4P (4NO), 120 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, such as TeSys Deca, type: LC1D80004P7 + LADN11, Schneider | kos | 2
| - kontaktor, 4P (4NO), 80 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1DT80AP7 + LADN11, Schneider | - contactor, 4P (4NO), 80 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, such as TeSys Deca, type: LC1DT80AP7 + LADN11, Schneider | kos | 2
| - kontaktor, 4P (4NO), 60 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1DT60AP7 + LADN11, Schneider | - contactor, 4P (4NO), 60 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, such as TeSys Deca, type: LC1DT60AP7 + LADN11, Schneider | kos | 2
| - miniaturni vtični elektromehanski rele, 6 A, 230 V AC (4x CO preklopni kontakt), kot naprimer Harmony tip: RXM4AB1P7PVS, Schneider | - miniature plug-in electromechanical relay, 6 A, 230 V AC (4x CO switching contact), such as Harmony type: RXM4AB1P7PVS, Schneider | kos | 2
| - univerzalni wifi, koncentrator Modbus prehod 110-240 V AC/DC, kot naprimer tip: PAS600T, Schneider | - universal wifi, Modbus gateway concentrator 110-240 V AC/DC, e.g. type: PAS600T, Schneider | kos | 1
| - ločilno stikalo 2P, 20 A, 415 V, kot naprimer Acti 9 iSW tip: A9S60220, Schneider | - disconnecting switch 2P, 20 A, 415 V, e.g. Acti 9 iSW type: A9S60220, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.14 | Dobava in montaža razdelilnika +NN_P1_6_R_LICEM_300_1 iz jeklene pločevine v barvi RAL 7035, dimenzij 800x1000x400mm (ŠxVxG), skupaj z montažno ploščo, enokrilna vrata, odpiranje vrat 120°, TN-S, IP66, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT CRN, tip: NSYCRN108400, Schneider. | Supply and installation of distribution box +NN_P1_6_R_LICEM_300_1 made of steel sheet in RAL 7035, dimensions 800x1000x400mm (WxHxD), with mounting plate, single leaf door, door opening 120°, TN-S, IP66, IK10. Cable entry from above. As for example PanelSeT CRN cabinet, type: NSYCRN108400, Schneider. |  |  | kpl | 1 |  | 0
| - glavno ločilno stikalo In=630 A, 4P za montažo na montažno ploščo; kot naprimer tip: C634630S, Schneider | - main disconnecting switch In=630 A, 4P for mounting on a mounting plate; e.g. type: C634630S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV432598T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV432598T, Schneider | kos | 1
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.15 | Dobava in montaža razdelilnika +NN_P1_6_R_LICEM_300_2 iz jeklene pločevine v barvi RAL 7035, dimenzij 800x1000x400mm (ŠxVxG), skupaj z montažno ploščo, enokrilna vrata, odpiranje vrat 120°, TN-S, IP66, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT CRN, tip: NSYCRN108400, Schneider. | Supply and installation of distribution box +NN_P1_6_R_LICEM_300_2 made of steel sheet in RAL 7035, dimensions 800x1000x400mm (WxHxD), with mounting plate, single leaf door, door opening 120°, TN-S, IP66, IK10. Cable entry from above. As for example PanelSeT CRN cabinet, type: NSYCRN108400, Schneider. |  |  | kpl | 1 |  | 0
| - glavno ločilno stikalo In=630 A, 4P za montažo na montažno ploščo; kot naprimer tip: C634630S, Schneider | - main disconnecting switch In=630 A, 4P for mounting on a mounting plate; e.g. type: C634630S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV432598T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV432598T, Schneider | kos | 1
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.16 | Dobava in montaža razdelilnika +NN_N1_1_R (sestavljen iz dveh polj) iz jeklene pločevine v barvi RAL 7035, skupnih dimenzij 1600x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT SFN, tip: NSYSFN221060P + NSYSFN22660P, Schneider. | Supply and installation of a distribution box +NN_N1_1_R (consisting of two boxes) made of steel sheet in RAL 7035 colour, overall dimensions 1600x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single-leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. As for example PanelSeT SFN cabinet, type: NSYSFN221060P + NSYSFN22660P, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=160 A, 3P za montažo na montažno ploščo; kot naprimer tip: C163160S, Schneider | - main disconnecting switch In=160 A, 3P for mounting on a mounting plate; e.g. type: C163160S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer Galaxy VS, tip: LV429338T, Schneider | - rotatable extension arm for controlling the main disconnecting switch; as for example Galaxy VS, type: LV429338T, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 23
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 3
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 10 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173222, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 10 A with C characteristic, 30 mA, type AC, as for example: 002173222, ETI | kos | 3
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, such as for example: 002173224, ETI | kos | 50
| - napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, kot naprimer RM17-U tip: RM17UB310, Schneider | - voltage control relay, range 183 to 528 V AC, 1 C/O, e.g. RM17-U type: RM17UB310, Schneider | kos | 1
| - miniaturni vtični elektromehanski rele, 6 A, 230 V AC (4x CO preklopni kontakt), kot naprimer Harmony tip: RXM4AB1P7PVS, Schneider | - miniature plug-in electromechanical relay, 6 A, 230 V AC (4x CO switching contact), such as Harmony type: RXM4AB1P7PVS, Schneider | kos | 1
| - varovalčni ločilnik 2P, 25 A, za varovalko 10,3 x 38 mm - varovalka gG 1 A, kot naprimer: A9N15651, Schneider | - fuse disconnector 2P, 25 A, for fuse 10,3 x 38 mm - fuse gG 1 A, as for example: A9N15651, Schneider | kos | 1
| - motorski odklopnik 3P, 4-6,3 A, termomagnetna zaščita, kot naprimer TeSys GV2 tip: GV2P10, Schneider | - motor circuit breaker 3P, 4-6.3 A, thermomagnetic protection, e.g. TeSys GV2 type: GV2P10, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - 250V, 16A, DIN rail mounting socket, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.17 | Dobava in montaža razdelilnika +NN_N1_2_R (sestavljen iz dveh polj) iz jeklene pločevine v barvi RAL 7035, skupnih dimenzij 1600x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT SFN, tip: NSYSFN221060P + NSYSFN22660P, Schneider. | Supply and installation of a distribution box +NN_N1_2_R (consisting of two boxes) made of steel sheet in RAL 7035 colour, overall dimensions 1600x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. As for example PanelSeT SFN cabinet, type: NSYSFN221060P + NSYSFN22660P, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=160 A, 3P za montažo na montažno ploščo; kot naprimer tip: C163160S, Schneider | - main disconnecting switch In=160 A, 3P for mounting on a mounting plate; e.g. type: C163160S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer Galaxy VS, tip: LV429338T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example Galaxy VS, type: LV429338T, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 2
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 22
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 3
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 10 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173222, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 10 A with C characteristic, 30mA, type AC, as for example: 002173222, ETI | kos | 3
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 59
| - napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, kot naprimer RM17-U tip: RM17UB310, Schneider | - voltage control relay, range 183 to 528 V AC, 1 C/O, e.g. RM17-U type: RM17UB310, Schneider | kos | 1
| - miniaturni vtični elektromehanski rele, 6 A, 230 V AC (4x CO preklopni kontakt), kot naprimer Harmony tip: RXM4AB1P7PVS, Schneider | - miniature plug-in electromechanical relay, 6 A, 230 V AC (4x CO switching contact), such as Harmony type: RXM4AB1P7PVS, Schneider | kos | 1
| - varovalčni ločilnik 2P, 25 A, za varovalko 10,3 x 38 mm - varovalka gG 1 A, kot naprimer: A9N15651, Schneider | - fuse disconnector 2P, 25 A, for fuse 10,3 x 38 mm - fuse gG 1 A, as for example: A9N15651, Schneider | kos | 1
| - motorski odklopnik 3P, 4-6,3 A, termomagnetna zaščita, kot naprimer TeSys GV2 tip: GV2P10, Schneider | - motor circuit breaker 3P, 4-6.3 A, thermomagnetic protection, e.g. TeSys GV2 type: GV2P10, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.18 | Dobava in montaža razdelilnika +NN_N1_3_R (sestavljen iz treh polj) iz jeklene pločevine v barvi RAL 7035, skupnih dimenzij 3200x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna ozeroma dvokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT SFN, tip: 2 x NSYSFN221060P + NSYSFN2212602DP, Schneider. | Supply and installation of a distribution box +NN_N1_3_R (consisting of three boxes) made of steel sheet in RAL 7035 colour, overall dimensions 3200x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single or double wing door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. As for example PanelSeT SFN cabinet, type: 2 x NSYSFN221060P + NSYSFN2212602DP, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=250 A, 3P za montažo na montažno ploščo; kot naprimer tip: C253250S, Schneider | - main disconnecting switch In=250 A, 3P for mounting on a mounting plate; e.g. type: C253250S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV429338T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV429338T, Schneider | kos | 1
| - energijski senzor, 160 A 3P/3P+N položaj zgoraj/spodaj, kot naprimer PowerTag Flex tip: A9MEM1580, Schneider | - energy sensor, 160 A 3P/3P+N top/bottom position, e.g. PowerTag Flex type: A9MEM1580, Schneider | kos | 3
| - energijski senzor, 63 A 3P+N položaj zgoraj/spodaj, kot naprimer PowerTag Flex tip: A9MEM1570, Schneider | - energy sensor, 63 A 3P+N top/bottom position, e.g. PowerTag Flex type: A9MEM1570, Schneider | kos | 2
| - kompaktni odklopnik 3P, 160 A, 415 V, tip AC, 25 kA, in pomožni kontakt 1 NO/NC kot naprimer ComPacT NSX, tip: C16B3TM160 + 29450, Schneider | - compact circuit breaker 3P, 160 A, 415 V, type AC, 25 kA, and auxiliary contact 1 NO/NC as for example ComPacT NSX, type: C16B3TM160 + 29450, Schneider | kos | 1
| - kompaktni odklopnik na diferenčni tok 4P, 100 A, 415 V, tip AC, 25 kA, kot naprimer ComPacT NSX, tip: C10B44V100, Schneider | - compact circuit breaker 4P, differential current, 100 A, 415 V, type AC, 25 kA, e.g. ComPacT NSX, type: C10B44V100, Schneider | kos | 2
| - kompaktni odklopnik na diferenčni tok 4P, 40 A, 415 V, tip AC, 25 kA, kot naprimer ComPacT NSX, tip: C10B44V040, Schneider | - compact circuit breaker 4P, differential current, 40 A, 415 V, type AC, 25 kA, e.g. ComPacT NSX, type: C10B44V040, Schneider | kos | 2
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 32 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84332, Schneider | - 32 A three-pole circuit-breaker with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84332, Schneider | kos | 6
| - tripolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84316, Schneider | - three-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84316, Schneider | kos | 2
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 37
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 15
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 3
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 10 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173222, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 10 A with C characteristic, 30mA, type AC, such as for example: 002173222, ETI | kos | 4
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 83
| - kontaktor, 4P (4NO), 80 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1DT80AP7 + LADN11, Schneider | - contactor, 4P (4NO), 80 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, such as TeSys Deca, type: LC1DT80AP7 + LADN11, Schneider | kos | 2
| - kontaktor, 4P (4NO), 40 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1DT40P7 + LADN11, Schneider | - contactor, 4P (4NO), 40 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, such as TeSys Deca, type: LC1DT40P7 + LADN11, Schneider | kos | 2
| - univerzalni wifi, koncentrator Modbus prehod 110-240 V AC/DC, kot naprimer tip: PAS600T, Schneider | - universal wifi, Modbus gateway concentrator 110-240 V AC/DC, e.g. type: PAS600T, Schneider | kos | 1
| - napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, kot naprimer RM17-U tip: RM17UB310, Schneider | - voltage control relay, range 183 to 528 V AC, 1 C/O, e.g. RM17-U type: RM17UB310, Schneider | kos | 1
| - miniaturni vtični elektromehanski rele, 6 A, 230 V AC (4x CO preklopni kontakt), kot naprimer Harmony tip: RXM4AB1P7PVS, Schneider | - miniature plug-in electromechanical relay, 6 A, 230 V AC (4x CO switching contact), such as Harmony type: RXM4AB1P7PVS, Schneider | kos | 2
| - varovalčni ločilnik 2P, 25 A, za varovalko 10,3 x 38 mm - varovalka gG 1 A, kot naprimer: A9N15651, Schneider | - fuse disconnector 2P, 25 A, for fuse 10,3 x 38 mm - fuse gG 1 A, as for example: A9N15651, Schneider | kos | 1
| - ločilno stikalo 2P, 20 A, 415 V, kot naprimer Acti 9 iSW tip: A9S60220, Schneider | - disconnecting switch 2P, 20 A, 415 V, e.g. Acti 9 iSW type: A9S60220, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - 250V, 16A, DIN rail mounting socket, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.19 | Dobava in montaža razdelilnika +NN_N1_4_R (sestavljen iz treh polj) iz jeklene pločevine v barvi RAL 7035, skupnih dimenzij 3200x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna ozeroma dvokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT SFN, tip: 2 x NSYSFN221060P + NSYSFN2212602DP, Schneider. | Supply and installation of a distribution box +NN_N1_4_R (consisting of three boxes) made of steel sheet in RAL 7035 colour, overall dimensions 3200x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single or double wing door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. As for example PanelSeT SFN cabinet, type: 2 x NSYSFN221060P + NSYSFN2212602DP, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=250 A, 3P za montažo na montažno ploščo; kot naprimer tip: C253250S, Schneider | - main disconnecting switch In=250 A, 3P for mounting on a mounting plate; e.g. type: C253250S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV429338T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV429338T, Schneider | kos | 1
| - energijski senzor, 160 A 3P/3P+N položaj zgoraj/spodaj, kot naprimer PowerTag Flex tip: A9MEM1580, Schneider | - energy sensor, 160 A 3P/3P+N top/bottom position, e.g. PowerTag Flex type: A9MEM1580, Schneider | kos | 2
| - energijski senzor, 63 A 3P+N položaj zgoraj/spodaj, kot naprimer PowerTag Flex tip: A9MEM1570, Schneider | - energy sensor, 63 A 3P+N top/bottom position, e.g. PowerTag Flex type: A9MEM1570, Schneider | kos | 3
| - kompaktni odklopnik na diferenčni tok 4P, 100 A, 415 V, tip AC, 25 kA, kot naprimer ComPacT NSX, tip: C10B44V100, Schneider | - compact circuit breaker 4P, differential current, 100 A, 415 V, type AC, 25 kA, e.g. ComPacT NSX, type: C10B44V100, Schneider | kos | 2
| - kompaktni odklopnik na diferenčni tok 4P, 40 A, 415 V, tip AC, 25 kA, kot naprimer ComPacT NSX, tip: C10B44V040, Schneider | - compact circuit breaker 4P, differential current, 40 A, 415 V, type AC, 25 kA, e.g. ComPacT NSX, type: C10B44V040, Schneider | kos | 2
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 32 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84332, Schneider | - 32 A three-pole circuit-breaker with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84332, Schneider | kos | 3
| - tripolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84316, Schneider | - three-pole 16 A circuit breaker with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84316, Schneider | kos | 14
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 34
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 15
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 3
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 10 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173222, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 10 A with C characteristic, 30 mA, type AC, as for example: 002173222, ETI | kos | 3
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 75
| - kontaktor, 4P (4NO), 60 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1DT60AP7 + LADN11, Schneider | - contactor, 4P (4NO), 60 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, such as TeSys Deca, type: LC1DT60AP7 + LADN11, Schneider | kos | 2
| - kontaktor, 4P (4NO), 40 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1DT40P7 + LADN11, Schneider | - contactor, 4P (4NO), 40 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, such as TeSys Deca, type: LC1DT40P7 + LADN11, Schneider | kos | 2
| - univerzalni wifi, koncentrator Modbus prehod 110-240 V AC/DC, kot naprimer tip: PAS600T, Schneider | - universal wifi, Modbus gateway concentrator 110-240 V AC/DC, e.g. type: PAS600T, Schneider | kos | 1
| - napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, kot naprimer RM17-U tip: RM17UB310, Schneider | - voltage control relay, range 183 to 528 V AC, 1 C/O, e.g. RM17-U type: RM17UB310, Schneider | kos | 1
| - miniaturni vtični elektromehanski rele, 6 A, 230 V AC (4x CO preklopni kontakt), kot naprimer Harmony tip: RXM4AB1P7PVS, Schneider | - miniature plug-in electromechanical relay, 6 A, 230 V AC (4x CO switching contact), such as Harmony type: RXM4AB1P7PVS, Schneider | kos | 5
| - ohišje za varovalčno ločilno stikalo 3P, 160 A, + 3 x talilni vložek gG 160 A, NH00, kot naprimer: LV480801, Schneider | - enclosure for fused isolating switch 3P, 160 A, + 3 x fusing insert gG 160 A, NH00, as for example: LV480801, Schneider | kos | 1
| - varovalčni ločilnik 2P, 25 A, za varovalko 10,3 x 38 mm - varovalka gG 1 A, kot naprimer: A9N15651, Schneider | - fuse disconnector 2P, 25 A, for fuse 10,3 x 38 mm - fuse gG 1 A, as for example: A9N15651, Schneider | kos | 1
| - ločilno stikalo 2P, 20 A, 415 V, kot naprimer Acti 9 iSW tip: A9S60220, Schneider | - disconnecting switch 2P, 20 A, 415 V, e.g. Acti 9 iSW type: A9S60220, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.20 | Dobava in montaža razdelilnika +NN_N1_5_R (sestavljen iz dveh polj) iz jeklene pločevine v barvi RAL 7035, skupnih dimenzij 1600x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna ozeroma dvokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT SFN, tip: NSYSFN221060P + NSYSFN22660P, Schneider. | Supply and installation of a distribution box +NN_N1_5_R (consisting of two boxes) made of steel sheet in RAL 7035, overall dimensions 1600x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single or double wing door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. As for example PanelSeT SFN cabinet, type: NSYSFN221060P + NSYSFN22660P, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=100 A, 3P za montažo na montažno ploščo; kot naprimer tip: C103100S, Schneider | - main disconnecting switch In=100 A, 3P for mounting on a mounting plate; e.g. type: C103100S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer Galaxy VS, tip: LV429338T, Schneider | - rotatable extension arm for controlling the main disconnecting switch; as for example Galaxy VS, type: LV429338T, Schneider | kos | 1
| - energijski senzor, 63 A 3P+N položaj zgoraj/spodaj, kot naprimer PowerTag Flex tip: A9MEM1570, Schneider | - energy sensor, 63 A 3P+N top/bottom position, e.g. PowerTag Flex type: A9MEM1570, Schneider | kos | 1
| - kompaktni odklopnik na diferenčni tok 4P, 40 A, 415 V, tip AC, 25 kA, kot naprimer ComPacT NSX, tip: C10B44V040, Schneider | - compact circuit breaker 4P, differential current, 40 A, 415 V, type AC, 25 kA, e.g. ComPacT NSX, type: C10B44V040, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84316, Schneider | - three-pole 16 A circuit breaker with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84316, Schneider | kos | 2
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 7
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 9
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 3
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPS), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 36
| - kontaktor, 4P (4NO), 40 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1DT40P7 + LADN11, Schneider | - contactor, 4P (4NO), 40 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, such as TeSys Deca, type: LC1DT40P7 + LADN11, Schneider | kos | 1
| - univerzalni wifi, koncentrator Modbus prehod 110-240 V AC/DC, kot naprimer tip: PAS600T, Schneider | - universal wifi, Modbus gateway concentrator 110-240 V AC/DC, e.g. type: PAS600T, Schneider | kos | 1
| - napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, kot naprimer RM17-U tip: RM17UB310, Schneider | - voltage control relay, range 183 to 528 V AC, 1 C/O, e.g. RM17-U type: RM17UB310, Schneider | kos | 1
| - miniaturni vtični elektromehanski rele, 6 A, 230 V AC (4x CO preklopni kontakt), kot naprimer Harmony tip: RXM4AB1P7PVS, Schneider | - miniature plug-in electromechanical relay, 6 A, 230 V AC (4x CO switching contact), such as Harmony type: RXM4AB1P7PVS, Schneider | kos | 2
| - varovalčni ločilnik 2P, 25 A, za varovalko 10,3 x 38 mm - varovalka gG 1 A, kot naprimer: A9N15651, Schneider | - fuse disconnector 2P, 25 A, for fuse 10,3 x 38 mm - fuse gG 1 A, as for example: A9N15651, Schneider | kos | 1
| - ločilno stikalo 2P, 20 A, 415 V, kot naprimer Acti 9 iSW tip: A9S60220, Schneider | - disconnecting switch 2P, 20 A, 415 V, e.g. Acti 9 iSW type: A9S60220, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - 250V, 16A, DIN rail mounting socket, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.21 | Dobava in montaža razdelilnika +NN_N1_6_R (sestavljen iz dveh polj) iz jeklene pločevine v barvi RAL 7035, skupnih dimenzij 2000x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna ozeroma dvokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT SFN, tip: 2 x NSYSFN221060P, Schneider. | Supply and installation of a distribution box +NN_N1_6_R (consisting of two boxes) made of steel sheet in RAL 7035 colour, overall dimensions 2000x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single or double wing door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. As for example PanelSeT SFN cabinet, type: 2 x NSYSFN221060P, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=160 A, 3P za montažo na montažno ploščo; kot naprimer tip: C163160S, Schneider | - main disconnecting switch In=160 A, 3P for mounting on a mounting plate; e.g. type: C163160S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer Galaxy VS, tip: LV429338T, Schneider | - rotatable extension arm for controlling the main isolating switch; as for example Galaxy VS, type: LV429338T, Schneider | kos | 1
| - energijski senzor, 160 A 3P/3P+N položaj zgoraj/spodaj, kot naprimer PowerTag Flex tip: A9MEM1580, Schneider | - energy sensor, 160 A 3P/3P+N top/bottom position, e.g. PowerTag Flex type: A9MEM1580, Schneider | kos | 1
| - energijski senzor, 63 A 3P+N položaj zgoraj/spodaj, kot naprimer PowerTag Flex tip: A9MEM1570, Schneider | - energy sensor, 63 A 3P+N top/bottom position, e.g. PowerTag Flex type: A9MEM1570, Schneider | kos | 2
| - kompaktni odklopnik na diferenčni tok 4P, 40 A, 415 V, tip AC, 25 kA, kot naprimer ComPacT NSX, tip: C10B44V040, Schneider | - compact circuit breaker 4P, differential current, 40 A, 415 V, type AC, 25 kA, e.g. ComPacT NSX, type: C10B44V040, Schneider | kos | 2
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 20 kA, kot naprimer Acti 9 iC60L, tip: A9F94440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 20 kA, such as Acti 9 iC60L, type: A9F94440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 16 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L, tip: A9F94316, Schneider | - three-pole circuit breaker 16 A, with C characteristic, 25 kA, e.g. Acti 9 iC60L, type: A9F94316, Schneider | kos | 7
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L, tip: A9F94304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 25 kA, e.g. Acti 9 iC60L, type: A9F94304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L tip: A9F94116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 25 kA, e.g. Acti 9 iC60L type: A9F94116, Schneider | kos | 17
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L tip: A9F94110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 25 kA, such as Acti 9 iC60L type: A9F94110, Schneider | kos | 9
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L tip: A9F94106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 25 kA, such as Acti 9 iC60L type: A9F94106, Schneider | kos | 3
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 47
| - kontaktor, 4P (4NO), 40 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1DT40P7 + LADN11, Schneider | - contactor, 4P (4NO), 40 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, such as TeSys Deca, type: LC1DT40P7 + LADN11, Schneider | kos | 2
| - univerzalni wifi, koncentrator Modbus prehod 110-240 V AC/DC, kot naprimer tip: PAS600T, Schneider | - universal wifi, Modbus gateway concentrator 110-240 V AC/DC, e.g. type: PAS600T, Schneider | kos | 1
| - napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, kot naprimer RM17-U tip: RM17UB310, Schneider | - voltage control relay, range 183 to 528 V AC, 1 C/O, e.g. RM17-U type: RM17UB310, Schneider | kos | 1
| - miniaturni vtični elektromehanski rele, 6 A, 230 V AC (4x CO preklopni kontakt), kot naprimer Harmony tip: RXM4AB1P7PVS, Schneider | - miniature plug-in electromechanical relay, 6 A, 230 V AC (4x CO switching contact), such as Harmony type: RXM4AB1P7PVS, Schneider | kos | 3
| - ohišje za varovalčno ločilno stikalo 3P, 100 A, + 3 x talilni vložek gG 100 A, NH000, kot naprimer: LV480800, Schneider | - enclosure for fused isolating switch 3P, 100 A, + 3 x fusing insert gG 100 A, NH000, as for example: LV480800, Schneider | kos | 1
| - varovalčni ločilnik 2P, 25 A, za varovalko 10,3 x 38 mm - varovalka gG 1 A, kot naprimer: A9N15651, Schneider | - fuse disconnector 2P, 25 A, for fuse 10,3 x 38 mm - fuse gG 1 A, as for example: A9N15651, Schneider | kos | 1
| - ločilno stikalo 2P, 20 A, 415 V, kot naprimer Acti 9 iSW tip: A9S60220, Schneider | - disconnecting switch 2P, 20 A, 415 V, e.g. Acti 9 iSW type: A9S60220, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.22 | Dobava in montaža razdelilnika +NN_N2_1_R (sestavljen iz treh polj) iz jeklene pločevine v barvi RAL 7035, skupnih dimenzij 2800x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT SFN, tip: 2 x NSYSFN221060P + NSYSFN22860P, Schneider. | Supply and installation of a distribution box +NN_N2_1_R (consisting of three boxes) made of steel sheet in RAL 7035, overall dimensions 2800x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single-leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. As for example PanelSeT SFN cabinet, type: 2 x NSYSFN221060P + NSYSFN22860P, Schneider.Material: 2 x NSYSFN221060P + NSYSFN22860P. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=250 A, 3P za montažo na montažno ploščo; kot naprimer tip: C253250S, Schneider | - main disconnecting switch In=250 A, 3P for mounting on a mounting plate; e.g. type: C253250S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV429338T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV429338T, Schneider | kos | 1
| - energijski senzor, 160 A 3P/3P+N položaj zgoraj/spodaj, kot naprimer PowerTag Flex tip: A9MEM1580, Schneider | - energy sensor, 160 A 3P/3P+N top/bottom position, e.g. PowerTag Flex type: A9MEM1580, Schneider | kos | 1
| - energijski senzor, 63 A 3P+N položaj zgoraj/spodaj, kot naprimer PowerTag Flex tip: A9MEM1570, Schneider | - energy sensor, 63 A 3P+N top/bottom position, e.g. PowerTag Flex type: A9MEM1570, Schneider | kos | 8
| - kompaktni odklopnik 3P, 160 A, 415 V, tip AC, 25 kA, in pomožni kontakt 1 NO/NC kot naprimer ComPacT NSX, tip: C16B3TM160 + 29450, Schneider | - compact circuit breaker 3P, 160 A, 415 V, type AC, 25 kA, and auxiliary contact 1 NO/NC as for example ComPacT NSX, type: C16B3TM160 + 29450, Schneider | kos | 1
| - kompaktni odklopnik na diferenčni tok 4P, 40 A, 415 V, tip AC, 25 kA, kot naprimer ComPacT NSX, tip: C10B44V040, Schneider | - compact circuit breaker 4P, differential current, 40 A, 415 V, type AC, 25 kA, e.g. ComPacT NSX, type: C10B44V040, Schneider | kos | 8
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84316, Schneider | - three-pole 16 A circuit breaker with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84316, Schneider | kos | 14
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 52
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 11
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 3
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 10 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173222, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 10 A with C characteristic, 30 mA, type AC, as for example: 002173222, ETI | kos | 2
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPS), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 61
| - kontaktor, 4P (4NO), 40 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1DT40P7 + LADN11, Schneider | - contactor, 4P (4NO), 40 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, such as TeSys Deca, type: LC1DT40P7 + LADN11, Schneider | kos | 8
| - univerzalni wifi, koncentrator Modbus prehod 110-240 V AC/DC, kot naprimer tip: PAS600T, Schneider | - universal wifi, Modbus gateway concentrator 110-240 V AC/DC, e.g. type: PAS600T, Schneider | kos | 1
| - napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, kot naprimer RM17-U tip: RM17UB310, Schneider | - voltage control relay, range 183 to 528 V AC, 1 C/O, e.g. RM17-U type: RM17UB310, Schneider | kos | 1
| - miniaturni vtični elektromehanski rele, 6 A, 230 V AC (4x CO preklopni kontakt), kot naprimer Harmony tip: RXM4AB1P7PVS, Schneider | - miniature plug-in electromechanical relay, 6 A, 230 V AC (4x CO switching contact), such as Harmony type: RXM4AB1P7PVS, Schneider | kos | 6
| - varovalčni ločilnik 2P, 25 A, za varovalko 10,3 x 38 mm - varovalka gG 1 A, kot naprimer: A9N15651, Schneider | - fuse disconnector 2P, 25 A, for fuse 10,3 x 38 mm - fuse gG 1 A, as for example: A9N15651, Schneider | kos | 1
| - ločilno stikalo 2P, 20 A, 415 V, kot naprimer Acti 9 iSW tip: A9S60220, Schneider | - disconnecting switch 2P, 20 A, 415 V, e.g. Acti 9 iSW type: A9S60220, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.23 | Dobava in montaža razdelilnika +NN_N2_2_R (sestavljen iz treh polj) iz jeklene pločevine v barvi RAL 7035, skupnih dimenzij 2800x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT SFN, tip: 2 x NSYSFN221060P + NSYSFN22860P, Schneider. | Supply and installation of a distribution box +NN_N2_2_R (consisting of three boxes) made of steel sheet in RAL 7035, overall dimensions 2800x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single-leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. As for example PanelSeT SFN cabinet, type: 2 x NSYSFN221060P + NSYSFN22860P, Schneider.Material: 2 x NSYSFN221060P + NSYSFN22860P. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=250 A, 3P za montažo na montažno ploščo; kot naprimer tip: C253250S, Schneider | - main disconnecting switch In=250 A, 3P for mounting on a mounting plate; e.g. type: C253250S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV429338T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV429338T, Schneider | kos | 1
| - energijski senzor, 160 A 3P/3P+N položaj zgoraj/spodaj, kot naprimer PowerTag Flex tip: A9MEM1580, Schneider | - energy sensor, 160 A 3P/3P+N top/bottom position, e.g. PowerTag Flex type: A9MEM1580, Schneider | kos | 3
| - energijski senzor, 63 A 3P+N položaj zgoraj/spodaj, kot naprimer PowerTag Flex tip: A9MEM1570, Schneider | - energy sensor, 63 A 3P+N top/bottom position, e.g. PowerTag Flex type: A9MEM1570, Schneider | kos | 4
| - kompaktni odklopnik 3P, 160 A, 415 V, tip AC, 25 kA, in pomožni kontakt 1 NO/NC kot naprimer ComPacT NSX, tip: C16B3TM160 + 29450, Schneider | - compact circuit breaker 3P, 160 A, 415 V, type AC, 25 kA, and auxiliary contact 1 NO/NC as for example ComPacT NSX, type: C16B3TM160 + 29450, Schneider | kos | 1
| - kompaktni odklopnik na diferenčni tok 4P, 100 A, 415 V, tip AC, 25 kA, kot naprimer ComPacT NSX, tip: C10B44V100, Schneider | - compact circuit breaker 4P, differential current, 100 A, 415 V, type AC, 25 kA, e.g. ComPacT NSX, type: C10B44V100, Schneider | kos | 2
| - kompaktni odklopnik na diferenčni tok 4P, 40 A, 415 V, tip AC, 25 kA, kot naprimer ComPacT NSX, tip: C10B44V040, Schneider | - compact circuit breaker 4P, differential current, 40 A, 415 V, type AC, 25 kA, e.g. ComPacT NSX, type: C10B44V040, Schneider | kos | 4
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 32 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84332, Schneider | - 32 A three-pole circuit-breaker with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84332, Schneider | kos | 3
| - tripolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84316, Schneider | - three-pole 16 A circuit breaker with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84316, Schneider | kos | 14
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 49
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 11
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 3
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 10 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173222, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 10 A with C characteristic, 30mA, type AC, as for example: 002173222, ETI | kos | 2
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 57
| - kontaktor, 4P (4NO), 125 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1D80004P7 + LADN11, Schneider | - contactor, 4P (4NO), 125 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, such as TeSys Deca, type: LC1D80004P7 + LADN11, Schneider | kos | 1
| - kontaktor, 4P (4NO), 60 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1DT60AP7 + LADN11, Schneider | - contactor, 4P (4NO), 60 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, like for example TeSys Deca, type: LC1DT60AP7 + LADN11, Schneider | kos | 1
| - kontaktor, 4P (4NO), 40 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1DT40P7 + LADN11, Schneider | - contactor, 4P (4NO), 40 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, such as TeSys Deca, type: LC1DT40P7 + LADN11, Schneider | kos | 4
| - univerzalni wifi, koncentrator Modbus prehod 110-240 V AC/DC, kot naprimer tip: PAS600T, Schneider | - universal wifi, Modbus gateway concentrator 110-240 V AC/DC, e.g. type: PAS600T, Schneider | kos | 1
| - napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, kot naprimer RM17-U tip: RM17UB310, Schneider | - voltage control relay, range 183 to 528 V AC, 1 C/O, e.g. RM17-U type: RM17UB310, Schneider | kos | 1
| - miniaturni vtični elektromehanski rele, 6 A, 230 V AC (4x CO preklopni kontakt), kot naprimer Harmony tip: RXM4AB1P7PVS, Schneider | - miniature plug-in electromechanical relay, 6 A, 230 V AC (4x CO switching contact), such as Harmony type: RXM4AB1P7PVS, Schneider | kos | 2
| - varovalčni ločilnik 2P, 25 A, za varovalko 10,3 x 38 mm - varovalka gG 1 A, kot naprimer: A9N15651, Schneider | - fuse disconnector 2P, 25 A, for fuse 10,3 x 38 mm - fuse gG 1 A, as for example: A9N15651, Schneider | kos | 1
| - ločilno stikalo 2P, 20 A, 415 V, kot naprimer Acti 9 iSW tip: A9S60220, Schneider | - disconnecting switch 2P, 20 A, 415 V, e.g. Acti 9 iSW type: A9S60220, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.24 | Dobava in montaža razdelilnika +NN_N2_3_R (sestavljen iz treh polj) iz jeklene pločevine v barvi RAL 7035, skupnih dimenzij 3000x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT SFN, tip: 3 x NSYSFN221060P, Schneider. | Supply and installation of a distribution box +NN_N2_3_R (consisting of three boxes) made of steel sheet in RAL 7035 colour, overall dimensions 3000x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. As for example PanelSeT SFN cabinet, type: 3 x NSYSFN221060P, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=250 A, 3P za montažo na montažno ploščo; kot naprimer tip: C253250S, Schneider | - main disconnecting switch In=250 A, 3P for mounting on a mounting plate; e.g. type: C253250S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV429338T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV429338T, Schneider | kos | 1
| - energijski senzor, 160 A 3P/3P+N položaj zgoraj/spodaj, kot naprimer PowerTag Flex tip: A9MEM1580, Schneider | - energy sensor, 160 A 3P/3P+N top/bottom position, e.g. PowerTag Flex type: A9MEM1580, Schneider | kos | 6
| - energijski senzor, 63 A 3P+N položaj zgoraj/spodaj, kot naprimer PowerTag Flex tip: A9MEM1570, Schneider | - energy sensor, 63 A 3P+N top/bottom position, e.g. PowerTag Flex type: A9MEM1570, Schneider | kos | 2
| - kompaktni odklopnik 3P, 160 A, 415 V, tip AC, 25 kA, in pomožni kontakt 1 NO/NC kot naprimer ComPacT NSX, tip: C16B3TM160 + 29450, Schneider | - compact circuit breaker 3P, 160 A, 415 V, type AC, 25 kA, and auxiliary contact 1 NO/NC as for example ComPacT NSX, type: C16B3TM160 + 29450, Schneider | kos | 1
| - kompaktni odklopnik na diferenčni tok 4P, 100 A, 415 V, tip AC, 25 kA, kot naprimer ComPacT NSX, tip: C10B44V100, Schneider | - compact circuit breaker 4P, differential current, 100 A, 415 V, type AC, 25 kA, e.g. ComPacT NSX, type: C10B44V100, Schneider | kos | 5
| - kompaktni odklopnik na diferenčni tok 4P, 40 A, 415 V, tip AC, 25 kA, kot naprimer ComPacT NSX, tip: C10B44V040, Schneider | - compact circuit breaker 4P, differential current, 40 A, 415 V, type AC, 25 kA, e.g. ComPacT NSX, type: C10B44V040, Schneider | kos | 2
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 32 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84332, Schneider | - 32 A three-pole circuit-breaker with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84332, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 20 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84320, Schneider | - three-pole circuit breaker 20 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84320, Schneider | kos | 10
| - tripolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84316, Schneider | - three-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84316, Schneider | kos | 21
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 54
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 13
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 3
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 10 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173222, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 10 A with C characteristic, 30 mA, type AC, as for example: 002173222, ETI | kos | 3
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 69
| - kontaktor, 4P (4NO), 80 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1DT80AP7 + LADN11, Schneider | - contactor, 4P (4NO), 80 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, such as TeSys Deca, type: LC1DT80AP7 + LADN11, Schneider | kos | 2
| - kontaktor, 4P (4NO), 60 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1DT60AP7 + LADN11, Schneider | - contactor, 4P (4NO), 60 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, such as TeSys Deca, type: LC1DT60AP7 + LADN11, Schneider | kos | 3
| - kontaktor, 4P (4NO), 40 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1DT40P7 + LADN11, Schneider | - contactor, 4P (4NO), 40 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, such as TeSys Deca, type: LC1DT40P7 + LADN11, Schneider | kos | 2
| - univerzalni wifi, koncentrator Modbus prehod 110-240 V AC/DC, kot naprimer tip: PAS600T, Schneider | - universal wifi, Modbus gateway concentrator 110-240 V AC/DC, e.g. type: PAS600T, Schneider | kos | 1
| - napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, kot naprimer RM17-U tip: RM17UB310, Schneider | - voltage control relay, range 183 to 528 V AC, 1 C/O, e.g. RM17-U type: RM17UB310, Schneider | kos | 1
| - miniaturni vtični elektromehanski rele, 6 A, 230 V AC (4x CO preklopni kontakt), kot naprimer Harmony tip: RXM4AB1P7PVS, Schneider | - miniature plug-in electromechanical relay, 6 A, 230 V AC (4x CO switching contact), such as Harmony type: RXM4AB1P7PVS, Schneider | kos | 7
| - varovalčni ločilnik 2P, 25 A, za varovalko 10,3 x 38 mm - varovalka gG 1 A, kot naprimer: A9N15651, Schneider | - fuse disconnector 2P, 25 A, for fuse 10,3 x 38 mm - fuse gG 1 A, as for example: A9N15651, Schneider | kos | 1
| - ločilno stikalo 2P, 20 A, 415 V, kot naprimer Acti 9 iSW tip: A9S60220, Schneider | - disconnecting switch 2P, 20 A, 415 V, e.g. Acti 9 iSW type: A9S60220, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.25 | Dobava in montaža razdelilnika +NN_N2_4_R (sestavljen iz treh polj) iz jeklene pločevine v barvi RAL 7035, skupnih dimenzij 3400x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna ozeroma dvokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT SFN, tip: NSYSFN221060P + 2 x NSYSFN2212602DP, Schneider. | Supply and installation of a distribution box +NN_N2_4_R (consisting of three boxes) made of steel sheet in RAL 7035, overall dimensions 3400x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single or double wing door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. As for example PanelSeT SFN cabinet, type: NSYSFN221060P + 2 x NSYSFN2212602DP, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=400 A, 3P za montažo na montažno ploščo; kot naprimer tip: C403400S, Schneider | - main disconnecting switch In=400 A, 3P for mounting on a mounting plate; e.g. type: C403400S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV432598T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV432598T, Schneider | kos | 1
| - energijski senzor, 160 A 3P/3P+N položaj zgoraj/spodaj, kot naprimer PowerTag Flex tip: A9MEM1580, Schneider | - energy sensor, 160 A 3P/3P+N top/bottom position, e.g. PowerTag Flex type: A9MEM1580, Schneider | kos | 5
| - energijski senzor, 63 A 3P+N položaj zgoraj/spodaj, kot naprimer PowerTag Flex tip: A9MEM1570, Schneider | - energy sensor, 63 A 3P+N top/bottom position, e.g. PowerTag Flex type: A9MEM1570, Schneider | kos | 5
| - kompaktni odklopnik na diferenčni tok 4P, 160 A, 415 V, tip AC, 25 kA, kot naprimer ComPacT NSX, tip: C16B44V160, Schneider | - compact circuit breaker 4P, differential current, 160 A, 415 V, type AC, 25 kA, e.g. ComPacT NSX, type: C16B44V160, Schneider | kos | 1
| - kompaktni odklopnik na diferenčni tok 4P, 100 A, 415 V, tip AC, 25 kA, kot naprimer ComPacT NSX, tip: C10B44V100, Schneider | - compact circuit breaker 4P, differential current, 100 A, 415 V, type AC, 25 kA, e.g. ComPacT NSX, type: C10B44V100, Schneider | kos | 3
| - kompaktni odklopnik na diferenčni tok 4P, 40 A, 415 V, tip AC, 25 kA, kot naprimer ComPacT NSX, tip: C10B44V040, Schneider | - compact circuit breaker 4P, differential current, 40 A, 415 V, type AC, 25 kA, e.g. ComPacT NSX, type: C10B44V040, Schneider | kos | 5
| - štiripolni miniaturni odklopnik 40 A, s C karakteristiko, 50 kA, kot naprimer Acti 9 NG125, tip: 18737, Schneider | - four-pole miniature circuit-breaker 40 A, with C characteristic, 50 kA, such as for example Acti 9 NG125, type: 18737, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 40 A, s C karakteristiko, 20 kA, kot naprimer Acti 9 iC60L, tip: A9F94332, Schneider | - three-pole circuit breaker 40 A, with C characteristic, 20 kA, such as Acti 9 iC60L, type: A9F94332, Schneider | kos | 9
| - tripolni inštalacijski odklopnik 20 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L, tip: A9F94320, Schneider | - three-pole circuit breaker 20 A, with C characteristic, 25 kA, e.g. Acti 9 iC60L, type: A9F94320, Schneider | kos | 4
| - tripolni inštalacijski odklopnik 16 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L, tip: A9F94316, Schneider | - three-pole circuit breaker 16 A, with C characteristic, 25 kA, e.g. Acti 9 iC60L, type: A9F94316, Schneider | kos | 37
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L, tip: A9F94304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 25 kA, e.g. Acti 9 iC60L, type: A9F94304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L tip: A9F94116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 25 kA, e.g. Acti 9 iC60L type: A9F94116, Schneider | kos | 73
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L tip: A9F94110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 25 kA, such as Acti 9 iC60L type: A9F94110, Schneider | kos | 15
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 25 kA, kot naprimer Acti 9 iC60L tip: A9F94106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 25 kA, such as Acti 9 iC60L type: A9F94106, Schneider | kos | 3
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 10 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173222, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 10 A with C characteristic, 30mA, type AC, as for example: 002173222, ETI | kos | 3
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 76
| - ohišje za varovalčno ločilno stikalo 3P, 160 A, + 3 x talilni vložek gG 160 A, NH00, kot naprimer: LV480801, Schneider | - enclosure for fused isolating switch 3P, 160 A, + 3 x fusing insert gG 160 A, NH00, as for example: LV480801, Schneider | kos | 1
| - kontaktor, 4P (4NO), 200 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1D115004P7 + LADN11, Schneider | - contactor, 4P (4NO), 200 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, such as TeSys Deca, type: LC1D115004P7 + LADN11, Schneider | kos | 1
| - kontaktor, 4P (4NO), 80 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1DT80AP7 + LADN11, Schneider | - contactor, 4P (4NO), 80 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, like for example TeSys Deca, type: LC1DT80AP7 + LADN11, Schneider | kos | 1
| - kontaktor, 4P (4NO), 60 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1DT60AP7 + LADN11, Schneider | - contactor, 4P (4NO), 60 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, like for example TeSys Deca, type: LC1DT60AP7 + LADN11, Schneider | kos | 5
| - kontaktor, 4P (4NO), 40 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer TeSys Deca, tip: LC1DT40P7 + LADN11, Schneider | - contactor, 4P (4NO), 40 A, coil 230 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, such as TeSys Deca, type: LC1DT40P7 + LADN11, Schneider | kos | 2
| - univerzalni wifi, koncentrator Modbus prehod 110-240 V AC/DC, kot naprimer tip: PAS600T, Schneider | - universal wifi, Modbus gateway concentrator 110-240 V AC/DC, e.g. type: PAS600T, Schneider | kos | 1
| - napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, kot naprimer RM17-U tip: RM17UB310, Schneider | - voltage control relay, range 183 to 528 V AC, 1 C/O, e.g. RM17-U type: RM17UB310, Schneider | kos | 1
| - miniaturni vtični elektromehanski rele, 6 A, 230 V AC (4x CO preklopni kontakt), kot naprimer Harmony tip: RXM4AB1P7PVS, Schneider | - miniature plug-in electromechanical relay, 6 A, 230 V AC (4x CO switching contact), such as Harmony type: RXM4AB1P7PVS, Schneider | kos | 9
| - varovalčni ločilnik 2P, 25 A, za varovalko 10,3 x 38 mm - varovalka gG 1 A, kot naprimer: A9N15651, Schneider | - fuse disconnector 2P, 25 A, for fuse 10,3 x 38 mm - fuse gG 1 A, as for example: A9N15651, Schneider | kos | 1
| - ločilno stikalo 2P, 20 A, 415 V, kot naprimer Acti 9 iSW tip: A9S60220, Schneider | - disconnecting switch 2P, 20 A, 415 V, e.g. Acti 9 iSW type: A9S60220, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - 250V, 16A, DIN rail mounting socket, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.26 | Dobava in montaža razdelilnika +NN_N3_1_R (sestavljen iz dveh polj) iz jeklene pločevine v barvi RAL 7035, skupnih dimenzij 1600x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT SFN, tip: NSYSFN221060P + NSYSFN22660P, Schneider. | Supply and installation of a distribution box +NN_N3_1_R (consisting of two boxes) made of steel sheet in RAL 7035 colour, overall dimensions 1600x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. As for example PanelSeT SFN cabinet, type: NSYSFN221060P + NSYSFN22660P, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=100 A, 3P za montažo na montažno ploščo; kot naprimer tip: C103100S, Schneider | - main disconnecting switch In=100 A, 3P for mounting on a mounting plate; e.g. type: C103100S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer Galaxy VS, tip: LV429338T, Schneider | - rotatable extension arm for controlling the main isolating switch; as for example Galaxy VS, type: LV429338T, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 11
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 3
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 10 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173222, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 10 A with C characteristic, 30mA, type AC, as for example: 002173222, ETI | kos | 4
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 25
| - napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, kot naprimer RM17-U tip: RM17UB310, Schneider | - voltage control relay, range 183 to 528 V AC, 1 C/O, e.g. RM17-U type: RM17UB310, Schneider | kos | 1
| - miniaturni vtični elektromehanski rele, 6 A, 230 V AC (4x CO preklopni kontakt), kot naprimer Harmony tip: RXM4AB1P7PVS, Schneider | - miniature plug-in electromechanical relay, 6 A, 230 V AC (4x CO switching contact), such as Harmony type: RXM4AB1P7PVS, Schneider | kos | 1
| - varovalčni ločilnik 2P, 25 A, za varovalko 10,3 x 38 mm - varovalka gG 1 A, kot naprimer: A9N15651, Schneider | - fuse disconnector 2P, 25 A, for fuse 10,3 x 38 mm - fuse gG 1 A, as for example: A9N15651, Schneider | kos | 1
| - motorski odklopnik 3P, 4-6,3 A, termomagnetna zaščita, kot naprimer TeSys GV2 tip: GV2P10, Schneider | - motor circuit breaker 3P, 4-6.3 A, thermomagnetic protection, e.g. TeSys GV2 type: GV2P10, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.27 | Dobava in montaža razdelilnika +NN_N3_2_R (sestavljen iz dveh polj) iz jeklene pločevine v barvi RAL 7035, skupnih dimenzij 1600x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT SFN, tip: NSYSFN221060P + NSYSFN22660P, Schneider. | Supply and installation of a distribution box +NN_N3_2_R (consisting of two boxes) made of steel sheet in RAL 7035 colour, overall dimensions 1600x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single-leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. As for example PanelSeT SFN cabinet, type: NSYSFN221060P + NSYSFN22660P, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=160 A, 3P za montažo na montažno ploščo; kot naprimer tip: C163160S, Schneider | - main disconnecting switch In=160 A, 3P for mounting on a mounting plate; e.g. type: C163160S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer Galaxy VS, tip: LV429338T, Schneider | - rotatable extension arm for controlling the main disconnecting switch; as for example Galaxy VS, type: LV429338T, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 2
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 10
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 3
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 10 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173222, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 10 A with C characteristic, 30 mA, type AC, as for example: 002173222, ETI | kos | 5
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 38
| - napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, kot naprimer RM17-U tip: RM17UB310, Schneider | - voltage control relay, range 183 to 528 V AC, 1 C/O, e.g. RM17-U type: RM17UB310, Schneider | kos | 1
| - miniaturni vtični elektromehanski rele, 6 A, 230 V AC (4x CO preklopni kontakt), kot naprimer Harmony tip: RXM4AB1P7PVS, Schneider | - miniature plug-in electromechanical relay, 6 A, 230 V AC (4x CO switching contact), such as Harmony type: RXM4AB1P7PVS, Schneider | kos | 1
| - varovalčni ločilnik 2P, 25 A, za varovalko 10,3 x 38 mm - varovalka gG 1 A, kot naprimer: A9N15651, Schneider | - fuse disconnector 2P, 25 A, for fuse 10,3 x 38 mm - fuse gG 1 A, as for example: A9N15651, Schneider | kos | 1
| - motorski odklopnik 3P, 4-6,3 A, termomagnetna zaščita, kot naprimer TeSys GV2 tip: GV2P10, Schneider | - motor circuit breaker 3P, 4-6.3 A, thermomagnetic protection, e.g. TeSys GV2 type: GV2P10, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.28 | Dobava in montaža razdelilnika +NN_N3_3_R iz jeklene pločevine v barvi RAL 7035, skupnih dimenzij 1200x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT SFN, tip: NSYSFN2212602DP, Schneider. | Supply and installation of distribution box +NN_N3_3_R made of steel sheet in RAL 7035 colour, overall dimensions 1200x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. As for example PanelSeT SFN cabinet, type: NSYSFN2212602DP, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=250 A, 3P za montažo na montažno ploščo; kot naprimer tip: C253250S, Schneider | - main disconnecting switch In=250 A, 3P for mounting on a mounting plate; e.g. type: C253250S, Schneider | kos | 1
| - kompaktni odklopnik 3P, 63 A, 415 V, tip AC, 25 kA, kot naprimer ComPacT NSX, tip: C10B3TM063, Schneider | - compact circuit breaker 3P, 63 A, 415 V, type AC, 25 kA, e.g. ComPacT NSX, type: C10B3TM063, Schneider | kos | 1
| - kompaktni odklopnik 3P, 50 A, 415 V, tip AC, 25 kA, kot naprimer ComPacT NSX, tip: C10B3TM050, Schneider | - compact circuit breaker 3P, 50 A, 415 V, type AC, 25 kA, e.g. ComPacT NSX, type: C10B3TM050, Schneider | kos | 1
| - kompaktni odklopnik 3P, 32 A, 415 V, tip AC, 25 kA, kot naprimer ComPacT NSX, tip: C10B3TM032, Schneider | - compact circuit breaker 3P, 32 A, 415 V, type AC, 25 kA, e.g. ComPacT NSX, type: C10B3TM032, Schneider | kos | 3
| - kompaktni odklopnik 3P, 25 A, 415 V, tip AC, 25 kA, kot naprimer ComPacT NSX, tip: C10B3TM025, Schneider | - compact circuit breaker 3P, 25 A, 415 V, type AC, 25 kA, e.g. ComPacT NSX, type: C10B3TM025, Schneider | kos | 5
| - kompaktni odklopnik 3P, 16 A, 415 V, tip AC, 25 kA, kot naprimer ComPacT NSX, tip: C10B3TM016, Schneider | - compact circuit breaker 3P, 16 A, 415 V, type AC, 25 kA, e.g. ComPacT NSX, type: C10B3TM016, Schneider | kos | 2
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84310, Schneider | - three-pole installation circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84310, Schneider | kos | 2
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 7
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 3
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 10 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173222, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 10 A with C characteristic, 30 mA, type AC, as for example: 002173222, ETI | kos | 5
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, such as for example: 002173224, ETI | kos | 63
| - varovalčni ločilnik 2P, 25 A, za varovalko 10,3 x 38 mm - varovalka gG 1 A, kot naprimer: A9N15651, Schneider | - fuse disconnector 2P, 25 A, for fuse 10,3 x 38 mm - fuse gG 1 A, as for example: A9N15651, Schneider | kos | 1
| - napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, kot naprimer RM17-U tip: RM17UB310, Schneider | - voltage control relay, range 183 to 528 V AC, 1 C/O, e.g. RM17-U type: RM17UB310, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.29 | Dobava in montaža razdelilnika +NN_N3_4_R (sestavljen iz dveh polj) iz jeklene pločevine v barvi RAL 7035, skupnih dimenzij 1600x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT SFN, tip: NSYSFN221060P + NSYSFN22660P, Schneider. | Supply and installation of a distribution box +NN_N3_4_R (consisting of two boxes) made of steel sheet in RAL 7035 colour, overall dimensions 1600x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. As for example PanelSeT SFN cabinet, type: NSYSFN221060P + NSYSFN22660P, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=160 A, 3P za montažo na montažno ploščo; kot naprimer tip: C163160S, Schneider | - main disconnecting switch In=160 A, 3P for mounting on a mounting plate; e.g. type: C163160S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer Galaxy VS, tip: LV429338T, Schneider | - rotatable extension arm for controlling the main isolating switch; as for example Galaxy VS, type: LV429338T, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84316, Schneider | - three-pole 16 A circuit breaker with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84316, Schneider | kos | 2
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 8
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 3
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 10 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173222, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 10 A with C characteristic, 30mA, type AC, such as for example: 002173222, ETI | kos | 5
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 49
| - napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, kot naprimer RM17-U tip: RM17UB310, Schneider | - voltage control relay, range 183 to 528 V AC, 1 C/O, e.g. RM17-U type: RM17UB310, Schneider | kos | 1
| - miniaturni vtični elektromehanski rele, 6 A, 230 V AC (4x CO preklopni kontakt), kot naprimer Harmony tip: RXM4AB1P7PVS, Schneider | - miniature plug-in electromechanical relay, 6 A, 230 V AC (4x CO switching contact), such as Harmony type: RXM4AB1P7PVS, Schneider | kos | 1
| - varovalčni ločilnik 2P, 25 A, za varovalko 10,3 x 38 mm - varovalka gG 1 A, kot naprimer: A9N15651, Schneider | - fuse disconnector 2P, 25 A, for fuse 10,3 x 38 mm - fuse gG 1 A, as for example: A9N15651, Schneider | kos | 1
| - motorski odklopnik 3P, 4-6,3 A, termomagnetna zaščita, kot naprimer TeSys GV2 tip: GV2P10, Schneider | - motor circuit breaker 3P, 4-6.3 A, thermomagnetic protection, e.g. TeSys GV2 type: GV2P10, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - 250V, 16A, DIN rail mounting socket, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.30 | Dobava in montaža razdelilnika iz jeklene pločevine v barvi RAL 7035, dimenzij 800x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Omara je setavljena iz dveh polj in sicer UPS polje in DEA polje. Polja sta medsebojno ločena s kovinsko pregrado. Kot naprimer omara PanelSeT SFN, tip: NSYSFN22860P, Schneider. | Supply and installation of a switchboard made of steel sheet in RAL 7035, dimensions 800x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. The cabinet is assembled from two fields, namely UPS field and DEA field. The fields are separated by a metal barrier. As for example PanelSeT SFN cabinet, type: NSYSFN22860P, Schneider. |  |  | kpl | 1 |  | 0
| V UPS polje omare z oznako +UPS_P1_1_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the UPS box of the cabinet marked +UPS_P1_1_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=100 A, 4P za montažo na montažno ploščo; kot naprimer tip: C104100S, Schneider | - main disconnecting switch In=100 A, 4P for mounting on a mounting plate; e.g. type: C104100S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV429340T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV429340T, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 9
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 3
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
| V DEA polje omare z oznako +DEA_P1_1_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the DEA box of the cabinet marked +DEA_P1_1_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=40 A, 4P za montažo na montažno ploščo; kot naprimer tip: A9S65440, Schneider | - main disconnecting switch In=40 A, 4P for mounting on a mounting plate; e.g. type: A9S65440, Schneider | kos | 1
| - vrtljiva ročica za krmiljenje glavnega ločilnega stikala + adapterski mehanizem; kot naprimer tip: A9A27006 + A9A27008, Schneider | - rotary lever for controlling the main disconnecting switch + adapter mechanism; as for example type: A9A27006 + A9A27008, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 3
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 9
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 2
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.31 | Dobava in montaža razdelilnika iz jeklene pločevine v barvi RAL 7035, dimenzij 800x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Omara je setavljena iz dveh polj in sicer UPS polje in DEA polje. Polja sta medsebojno ločena s kovinsko pregrado. Kot naprimer omara PanelSeT SFN, tip: NSYSFN22860P, Schneider. | Supply and installation of a switchboard made of steel sheet in RAL 7035, dimensions 800x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. The cabinet is assembled from two fields, namely UPS field and DEA field. The fields are separated by a metal barrier. As for example PanelSeT SFN cabinet, type: NSYSFN22860P, Schneider. |  |  | kpl | 1 |  | 0
| V UPS polje omare z oznako +UPS_P1_2_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the UPS box of the cabinet marked +UPS_P1_2_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=100 A, 4P za montažo na montažno ploščo; kot naprimer tip: C104100S, Schneider | - main disconnecting switch In=100 A, 4P for mounting on a mounting plate; e.g. type: C104100S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV429340T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV429340T, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 9
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 3
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
| V DEA polje omare z oznako +DEA_P1_2_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the DEA box of the cabinet marked +DEA_P1_2_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=40 A, 4P za montažo na montažno ploščo; kot naprimer tip: A9S65440, Schneider | - main disconnecting switch In=40 A, 4P for mounting on a mounting plate; e.g. type: A9S65440, Schneider | kos | 1
| - vrtljiva ročica za krmiljenje glavnega ločilnega stikala + adapterski mehanizem; kot naprimer tip: A9A27006 + A9A27008, Schneider | - rotary lever for controlling the main disconnecting switch + adapter mechanism; as for example type: A9A27006 + A9A27008, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 5
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 12
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 2
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.32 | Dobava in montaža razdelilnika iz jeklene pločevine v barvi RAL 7035, dimenzij 1000x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Omara je setavljena iz dveh polj in sicer UPS polje in DEA polje. Polja sta medsebojno ločena s kovinsko pregrado. Kot naprimer omara PanelSeT SFN, tip: NSYSFN221060P, Schneider. | Supply and installation of a switchboard made of steel sheet in RAL 7035, dimensions 1000x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. The cabinet is assembled from two boxes, namely the UPS box and the DEA box. The two boxes are separated by a metal barrier. As for example PanelSeT SFN cabinet, type: NSYSFN221060P, Schneider. |  |  | kpl | 1 |  | 0
| V UPS polje omare z oznako +UPS_P1_3_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the UPS box of the cabinet marked +UPS_P1_3_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=100 A, 4P za montažo na montažno ploščo; kot naprimer tip: C104100S, Schneider | - main disconnecting switch In=100 A, 4P for mounting on a mounting plate; e.g. type: C104100S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV429340T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV429340T, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 24
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 6
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 3P+N, 25 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002174926, ETI | - combined protection switch with overcurrent protection (CPC), 3P+N, 25 A with C characteristic, 30mA, type AC, such as for example: 002174926, ETI | kos | 3
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, such as for example: 002173224, ETI | kos | 6
| - kontaktor, 4P (4NO), 25 A, tuljava 220 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20834 + A9C15914, Schneider | - contactor, 4P (4NO), 25 A, coil 220 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20834 + A9C15914, Schneider | kos | 3
| - kontaktor, 2P (2NO), 25 A, tuljava 230 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20732 + A9C15914, Schneider | - contactor, 2P (2NO), 25 A, coil 230 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20732 + A9C15914, Schneider | kos | 6
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
| V DEA polje omare z oznako +DEA_P1_3_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the DEA box of the cabinet marked +DEA_P1_3_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=100 A, 4P za montažo na montažno ploščo; kot naprimer tip: C104100S, Schneider | - main disconnecting switch In=100 A, 4P for mounting on a mounting plate; e.g. type: C104100S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV429340T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV429340T, Schneider | kos | 1
| - dodatna naprava diferenčnega toka 63 A, 4P, tip A, 30 mA, kot naprimer Vigi iC60, tip: A9V61463, Schneider | - additional differential current device 63 A, 4P, type A, 30 mA, such as Vigi iC60, type: A9V61463, Schneider | kos | 2
| - štiripolni inštalacijski odklopnik 50 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84450, Schneider | - four-pole circuit breaker 50 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84450, Schneider | kos | 2
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 32 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84332, Schneider | - 32 A three-pole circuit-breaker with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84332, Schneider | kos | 2
| - tripolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84316, Schneider | - three-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84316, Schneider | kos | 5
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 12
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 2
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 1
| - kontaktor, 4P (4NO), 63 A, tuljava 220 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20864 + A9C15914, Schneider | - contactor, 4P (4NO), 63 A, coil 220 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20864 + A9C15914, Schneider | kos | 2
| - kontaktor, 2P (2NO), 25 A, tuljava 230 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20732 + A9C15914, Schneider | - contactor, 2P (2NO), 25 A, coil 230 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20732 + A9C15914, Schneider | kos | 1
| - ločilno stikalo 2P, 20 A, 415 V, kot naprimer Acti 9 iSW tip: A9S60220, Schneider | - disconnecting switch 2P, 20 A, 415 V, e.g. Acti 9 iSW type: A9S60220, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.33 | Dobava in montaža razdelilnika iz jeklene pločevine v barvi RAL 7035, dimenzij 800x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Omara je setavljena iz dveh polj in sicer UPS polje in DEA polje. Polja sta medsebojno ločena s kovinsko pregrado. Kot naprimer omara PanelSeT SFN, tip: NSYSFN22860P, Schneider. | Supply and installation of a switchboard made of steel sheet in RAL 7035, dimensions 800x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. The cabinet is assembled from two boxes, namely the UPS box and the DEA box. The two boxes are separated from each other by a metal barrier. As for example PanelSeT SFN cabinet, type: NSYSFN22860P, Schneider. |  |  | kpl | 1 |  | 0
| V UPS polje omare z oznako +UPS_P1_4_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the UPS box of the cabinet marked +UPS_P1_4_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=100 A, 4P za montažo na montažno ploščo; kot naprimer tip: C104100S, Schneider | - main disconnecting switch In=100 A, 4P for mounting on a mounting plate; e.g. type: C104100S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV429340T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV429340T, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 17
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 6
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 3P+N, 25 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002174926, ETI | - combined protection switch with overcurrent protection (CPS), 3P+N, 25 A with C characteristic, 30mA, type AC, as for example: 002174926, ETI | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 1
| - kontaktor, 4P (4NO), 25 A, tuljava 220 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20834 + A9C15914, Schneider | - contactor, 4P (4NO), 25 A, coil 220 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20834 + A9C15914, Schneider | kos | 1
| - kontaktor, 2P (2NO), 25 A, tuljava 230 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20732 + A9C15914, Schneider | - contactor, 2P (2NO), 25 A, coil 230 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20732 + A9C15914, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - 250V, 16A, DIN rail mounting socket, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
| V DEA polje omare z oznako +DEA_P1_4_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the DEA box of the cabinet marked +DEA_P1_4_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=40 A, 4P za montažo na montažno ploščo; kot naprimer tip: A9S65440, Schneider | - main disconnecting switch In=40 A, 4P for mounting on a mounting plate; e.g. type: A9S65440, Schneider | kos | 1
| - vrtljiva ročica za krmiljenje glavnega ločilnega stikala + adapterski mehanizem; kot naprimer tip: A9A27006 + A9A27008, Schneider | - rotary lever for controlling the main disconnecting switch + adapter mechanism; as for example type: A9A27006 + A9A27008, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 2
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 9
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 2
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 1
| - kontaktor, 2P (2NO), 25 A, tuljava 230 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20732 + A9C15914, Schneider | - contactor, 2P (2NO), 25 A, coil 230 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20732 + A9C15914, Schneider | kos | 1
| - ločilno stikalo 2P, 20 A, 415 V, kot naprimer Acti 9 iSW tip: A9S60220, Schneider | - disconnecting switch 2P, 20 A, 415 V, e.g. Acti 9 iSW type: A9S60220, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.34 | Dobava in montaža razdelilnika iz jeklene pločevine v barvi RAL 7035, dimenzij 800x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Omara je setavljena iz dveh polj in sicer UPS polje in DEA polje. Polja sta medsebojno ločena s kovinsko pregrado. Kot naprimer omara PanelSeT SFN, tip: NSYSFN22860P, Schneider. | Supply and installation of a switchboard made of steel sheet in RAL 7035, dimensions 800x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. The cabinet is assembled from two boxes, namely the UPS box and the DEA box. The two boxes are separated from each other by a metal barrier. As for example PanelSeT SFN cabinet, type: NSYSFN22860P, Schneider. |  |  | kpl | 1 |  | 0
| V UPS polje omare z oznako +UPS_P1_5_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the UPS box of the cabinet marked +UPS_P1_5_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=40 A, 4P za montažo na montažno ploščo; kot naprimer tip: A9S65440, Schneider | - main disconnecting switch In=40 A, 4P for mounting on a mounting plate; e.g. type: A9S65440, Schneider | kos | 1
| - vrtljiva ročica za krmiljenje glavnega ločilnega stikala + adapterski mehanizem; kot naprimer tip: A9A27006 + A9A27008, Schneider | - rotary lever for controlling the main disconnecting switch + adapter mechanism; as for example type: A9A27006 + A9A27008, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 14
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 6
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 3P+N, 25 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002174926, ETI | - combined protection switch with overcurrent protection (CPS), 3P+N, 25 A with C characteristic, 30mA, type AC, as for example: 002174926, ETI | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 3
| - kontaktor, 4P (4NO), 25 A, tuljava 220 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20834 + A9C15914, Schneider | - contactor, 4P (4NO), 25 A, coil 220 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20834 + A9C15914, Schneider | kos | 1
| - kontaktor, 2P (2NO), 25 A, tuljava 230 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20732 + A9C15914, Schneider | - contactor, 2P (2NO), 25 A, coil 230 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20732 + A9C15914, Schneider | kos | 3
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - 250V, 16A, DIN rail mounting socket, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
| V DEA polje omare z oznako +DEA_P1_5_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the DEA box of the cabinet marked +DEA_P1_5_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=100 A, 4P za montažo na montažno ploščo; kot naprimer tip: C104100S, Schneider | - main disconnecting switch In=100 A, 4P for mounting on a mounting plate; e.g. type: C104100S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV429340T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV429340T, Schneider | kos | 1
| - dodatna naprava diferenčnega toka 63 A, 4P, tip A, 30 mA, kot naprimer Vigi iC60, tip: A9V61463, Schneider | - additional differential current device 63 A, 4P, type A, 30 mA, such as Vigi iC60, type: A9V61463, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 2
| - tripolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84316, Schneider | - three-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84316, Schneider | kos | 7
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 10
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 2
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 1
| - kontaktor, 4P (4NO), 63 A, tuljava 220 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20864 + A9C15914, Schneider | - contactor, 4P (4NO), 63 A, coil 220 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20864 + A9C15914, Schneider | kos | 1
| - kontaktor, 2P (2NO), 25 A, tuljava 230 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20732 + A9C15914, Schneider | - contactor, 2P (2NO), 25 A, coil 230 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20732 + A9C15914, Schneider | kos | 1
| - ločilno stikalo 2P, 20 A, 415 V, kot naprimer Acti 9 iSW tip: A9S60220, Schneider | - disconnecting switch 2P, 20 A, 415 V, e.g. Acti 9 iSW type: A9S60220, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.35 | Dobava in montaža razdelilnika iz jeklene pločevine v barvi RAL 7035, dimenzij 800x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Omara je setavljena iz dveh polj in sicer UPS polje in DEA polje. Polja sta medsebojno ločena s kovinsko pregrado. Kot naprimer omara PanelSeT SFN, tip: NSYSFN22860P, Schneider. | Supply and installation of a switchboard made of steel sheet in RAL 7035, dimensions 800x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. The cabinet is assembled from two boxes, namely the UPS box and the DEA box. The two boxes are separated from each other by a metal barrier. As for example PanelSeT SFN cabinet, type: NSYSFN22860P, Schneider. |  |  | kpl | 1 |  | 0
| V UPS polje omare z oznako +UPS_P1_6_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the UPS box of the cabinet marked +UPS_P1_6_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=40 A, 4P za montažo na montažno ploščo; kot naprimer tip: A9S65440, Schneider | - main disconnecting switch In=40 A, 4P for mounting on a mounting plate; e.g. type: A9S65440, Schneider | kos | 1
| - vrtljiva ročica za krmiljenje glavnega ločilnega stikala + adapterski mehanizem; kot naprimer tip: A9A27006 + A9A27008, Schneider | - rotary lever for controlling the main disconnecting switch + adapter mechanism; as for example type: A9A27006 + A9A27008, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 14
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 7
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 3P+N, 25 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002174926, ETI | - combined protection switch with overcurrent protection (CPC), 3P+N, 25 A with C characteristic, 30mA, type AC, as for example: 002174926, ETI | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 1
| - kontaktor, 4P (4NO), 25 A, tuljava 220 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20834 + A9C15914, Schneider | - contactor, 4P (4NO), 25 A, coil 220 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20834 + A9C15914, Schneider | kos | 1
| - kontaktor, 2P (2NO), 25 A, tuljava 230 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20732 + A9C15914, Schneider | - contactor, 2P (2NO), 25 A, coil 230 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20732 + A9C15914, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - 250V, 16A, DIN rail mounting socket, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
| V DEA polje omare z oznako +DEA_P1_6_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the DEA box of the cabinet marked +DEA_P1_6_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=100 A, 4P za montažo na montažno ploščo; kot naprimer tip: C104100S, Schneider | - main disconnecting switch In=100 A, 4P for mounting on a mounting plate; e.g. type: C104100S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV429340T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV429340T, Schneider | kos | 1
| - dodatna naprava diferenčnega toka 63 A, 4P, tip A, 30 mA, kot naprimer Vigi iC60, tip: A9V61463, Schneider | - additional differential current device 63 A, 4P, type A, 30 mA, such as Vigi iC60, type: A9V61463, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 2
| - tripolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84316, Schneider | - three-pole 16 A circuit breaker with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84316, Schneider | kos | 3
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 9
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 2
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kontaktor, 4P (4NO), 63 A, tuljava 220 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20864 + A9C15914, Schneider | - contactor, 4P (4NO), 63 A, coil 220 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20864 + A9C15914, Schneider | kos | 1
| - ločilno stikalo 2P, 20 A, 415 V, kot naprimer Acti 9 iSW tip: A9S60220, Schneider | - disconnecting switch 2P, 20 A, 415 V, e.g. Acti 9 iSW type: A9S60220, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.36 | Dobava in montaža stenskega razdelilnika +NN_P1_6_R_LICEM iz jeklene pločevine v barvi RAL 7035, dimenzij 600x800x250mm (ŠxVxG), skupaj z montažno ploščo, enokrilna vrata, odpiranje vrat 120°, TN-S, IP66, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT SFN, tip: NSYCRN86250, Schneider. | Supply and installation of wall-mounted distribution box +NN_P1_6_R_LICEM made of steel sheet in RAL 7035, dimensions 600x800x250mm (WxHxD), with mounting plate, single leaf door, door opening 120°, TN-S, IP66, IK10. Cable entry from above. As for example PanelSeT SFN cabinet, type: NSYCRN86250, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=40 A, 4P za montažo na montažno ploščo; kot naprimer tip: A9S65440, Schneider | - main disconnecting switch In=40 A, 4P for mounting on a mounting plate; e.g. type: A9S65440, Schneider | kos | 1
| - vrtljiva ročica za krmiljenje glavnega ločilnega stikala + adapterski mehanizem; kot naprimer tip: A9A27006 + A9A27008, Schneider | - rotary lever for controlling the main disconnecting switch + adapter mechanism; as for example type: A9A27006 + A9A27008, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 4
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 6
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 3P+N, 25 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002174926, ETI | - combined protection switch with overcurrent protection (CPS), 3P+N, 25 A with C characteristic, 30mA, type AC, as for example: 002174926, ETI | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 1
| - kontaktor, 4P (4NO), 25 A, tuljava 220 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20834 + A9C15914, Schneider | - contactor, 4P (4NO), 25 A, coil 220 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20834 + A9C15914, Schneider | kos | 1
| - kontaktor, 2P (2NO), 25 A, tuljava 230 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20732 + A9C15914, Schneider | - contactor, 2P (2NO), 25 A, coil 230 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20732 + A9C15914, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.37 | Dobava in montaža razdelilnika iz jeklene pločevine v barvi RAL 7035, dimenzij 800x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Omara je setavljena iz dveh polj in sicer UPS polje in DEA polje. Polja sta medsebojno ločena s kovinsko pregrado. Kot naprimer omara PanelSeT SFN, tip: NSYSFN22860P, Schneider. | Supply and installation of a switchboard made of steel sheet in RAL 7035, dimensions 800x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. The cabinet is assembled from two fields, namely UPS field and DEA field. The fields are separated by a metal barrier. As for example PanelSeT SFN cabinet, type: NSYSFN22860P, Schneider. |  |  | kpl | 1 |  | 0
| V UPS polje omare z oznako +UPS_N1_1_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the UPS box of the cabinet marked +UPS_N1_1_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=100 A, 4P za montažo na montažno ploščo; kot naprimer tip: C104100S, Schneider | - main disconnecting switch In=100 A, 4P for mounting on a mounting plate; e.g. type: C104100S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV429340T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV429340T, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 8
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 3
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
| V DEA polje omare z oznako +DEA_N1_1_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the DEA box of the cabinet marked +DEA_N1_1_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=40 A, 4P za montažo na montažno ploščo; kot naprimer tip: A9S65440, Schneider | - main disconnecting switch In=40 A, 4P for mounting on a mounting plate; e.g. type: A9S65440, Schneider | kos | 1
| - vrtljiva ročica za krmiljenje glavnega ločilnega stikala + adapterski mehanizem; kot naprimer tip: A9A27006 + A9A27008, Schneider | - rotary lever for controlling the main disconnecting switch + adapter mechanism; as for example type: A9A27006 + A9A27008, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 2
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 18
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 2
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.38 | Dobava in montaža razdelilnika iz jeklene pločevine v barvi RAL 7035, dimenzij 800x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Omara je setavljena iz dveh polj in sicer UPS polje in DEA polje. Polja sta medsebojno ločena s kovinsko pregrado. Kot naprimer omara PanelSeT SFN, tip: NSYSFN22860P, Schneider. | Supply and installation of a switchboard made of steel sheet in RAL 7035, dimensions 800x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. The cabinet is assembled from two fields, namely UPS field and DEA field. The fields are separated by a metal barrier. As for example PanelSeT SFN cabinet, type: NSYSFN22860P, Schneider. |  |  | kpl | 1 |  | 0
| V UPS polje omare z oznako +UPS_N1_2_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the UPS box of the cabinet marked +UPS_N1_2_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=100 A, 4P za montažo na montažno ploščo; kot naprimer tip: C104100S, Schneider | - main disconnecting switch In=100 A, 4P for mounting on a mounting plate; e.g. type: C104100S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV429340T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV429340T, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 8
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 3
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
| V DEA polje omare z oznako +DEA_N1_2_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the DEA box of the cabinet marked +DEA_N1_2_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=40 A, 4P za montažo na montažno ploščo; kot naprimer tip: A9S65440, Schneider | - main disconnecting switch In=40 A, 4P for mounting on a mounting plate; e.g. type: A9S65440, Schneider | kos | 1
| - vrtljiva ročica za krmiljenje glavnega ločilnega stikala + adapterski mehanizem; kot naprimer tip: A9A27006 + A9A27008, Schneider | - rotary lever for controlling the main disconnecting switch + adapter mechanism; as for example type: A9A27006 + A9A27008, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 16
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 2
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.39 | Dobava in montaža razdelilnika iz jeklene pločevine v barvi RAL 7035, dimenzij 800x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Omara je setavljena iz dveh polj in sicer UPS polje in DEA polje. Polja sta medsebojno ločena s kovinsko pregrado. Kot naprimer omara PanelSeT SFN, tip: NSYSFN22860P, Schneider. | Supply and installation of a switchboard made of steel sheet in RAL 7035, dimensions 800x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. The cabinet is assembled from two fields, namely UPS field and DEA field. The fields are separated by a metal barrier. As for example PanelSeT SFN cabinet, type: NSYSFN22860P, Schneider. |  |  | kpl | 1 |  | 0
| V UPS polje omare z oznako +UPS_N1_3_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the UPS box of the cabinet marked +UPS_N1_3_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=100 A, 4P za montažo na montažno ploščo; kot naprimer tip: C104100S, Schneider | - main disconnecting switch In=100 A, 4P for mounting on a mounting plate; e.g. type: C104100S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV429340T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV429340T, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 8
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84100, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84100, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 6
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 1
| - kontaktor, 2P (2NO), 25 A, tuljava 230 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20732 + A9C15914, Schneider | - contactor, 2P (2NO), 25 A, coil 230 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20732 + A9C15914, Schneider | kos | 6
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - 250V, 16A, DIN rail mounting socket, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
| V DEA polje omare z oznako +DEA_N1_3_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the DEA box of the cabinet marked +DEA_N1_3_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=100 A, 4P za montažo na montažno ploščo; kot naprimer tip: C104100S, Schneider | - main disconnecting switch In=100 A, 4P for mounting on a mounting plate; e.g. type: C104100S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV429340T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV429340T, Schneider | kos | 1
| - dodatna naprava diferenčnega toka 63 A, 4P, tip A, 30 mA, kot naprimer Vigi iC60, tip: A9V61463, Schneider | - additional differential current device 63 A, 4P, type A, 30 mA, such as Vigi iC60, type: A9V61463, Schneider | kos | 2
| - štiripolni inštalacijski odklopnik 50 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84450, Schneider | - four-pole circuit breaker 50 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84450, Schneider | kos | 2
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 32 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84332, Schneider | - 32 A three-pole circuit-breaker with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84332, Schneider | kos | 2
| - tripolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84316, Schneider | - three-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84316, Schneider | kos | 5
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 12
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 2
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, such as for example: 002173224, ETI | kos | 1
| - kontaktor, 4P (4NO), 63 A, tuljava 220 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20864 + A9C15914, Schneider | - contactor, 4P (4NO), 63 A, coil 220 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20864 + A9C15914, Schneider | kos | 2
| - kontaktor, 2P (2NO), 25 A, tuljava 230 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20732 + A9C15914, Schneider | - contactor, 2P (2NO), 25 A, coil 230 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20732 + A9C15914, Schneider | kos | 1
| - ločilno stikalo 2P, 20 A, 415 V, kot naprimer Acti 9 iSW tip: A9S60220, Schneider | - disconnecting switch 2P, 20 A, 415 V, e.g. Acti 9 iSW type: A9S60220, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.40 | Dobava in montaža razdelilnika iz jeklene pločevine v barvi RAL 7035, dimenzij 800x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Omara je setavljena iz dveh polj in sicer UPS polje in DEA polje. Polja sta medsebojno ločena s kovinsko pregrado. Kot naprimer omara PanelSeT SFN, tip: NSYSFN22860P, Schneider. | Supply and installation of a switchboard made of steel sheet in RAL 7035, dimensions 800x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. The cabinet is assembled from two fields, namely UPS field and DEA field. The fields are separated by a metal barrier. As for example PanelSeT SFN cabinet, type: NSYSFN22860P, Schneider. |  |  | kpl | 1 |  | 0
| V UPS polje omare z oznako +UPS_N1_4_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the UPS box of the cabinet marked +UPS_N1_4_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=100 A, 4P za montažo na montažno ploščo; kot naprimer tip: C104100S, Schneider | - main disconnecting switch In=100 A, 4P for mounting on a mounting plate; e.g. type: C104100S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV429340T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV429340T, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 18
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 6
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 3P+N, 25 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002174926, ETI | - combined protection switch with overcurrent protection (CPS), 3P+N, 25 A with C characteristic, 30mA, type AC, as for example: 002174926, ETI | kos | 2
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPS), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 1
| - kontaktor, 4P (4NO), 25 A, tuljava 220 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20834 + A9C15914, Schneider | - contactor, 4P (4NO), 25 A, coil 220 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20834 + A9C15914, Schneider | kos | 2
| - kontaktor, 2P (2NO), 25 A, tuljava 230 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20732 + A9C15914, Schneider | - contactor, 2P (2NO), 25 A, coil 230 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20732 + A9C15914, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
| V DEA polje omare z oznako +DEA_N1_4_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the DEA box of the cabinet marked +DEA_N1_4_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=40 A, 4P za montažo na montažno ploščo; kot naprimer tip: A9S65440, Schneider | - main disconnecting switch In=40 A, 4P for mounting on a mounting plate; e.g. type: A9S65440, Schneider | kos | 1
| - vrtljiva ročica za krmiljenje glavnega ločilnega stikala + adapterski mehanizem; kot naprimer tip: A9A27006 + A9A27008, Schneider | - rotary lever for controlling the main disconnecting switch + adapter mechanism; as for example type: A9A27006 + A9A27008, Schneider | kos | 1
| - dodatna naprava diferenčnega toka 25 A, 4P, tip A, 30 mA, kot naprimer Vigi iC60, tip: A9V51425, Schneider | - additional differential current device 25 A, 4P, type A, 30 mA, such as Vigi iC60, type: A9V51425, Schneider | kos | 3
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 25 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84425, Schneider | - four-pole installation circuit-breaker 25 A, with C characteristic, 15 kA, such as for example Acti 9 iC60H, type: A9F84425, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 7
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 8
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 2
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 1
| - kontaktor, 4P (4NO), 25 A, tuljava 220 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20834 + A9C15914, Schneider | - contactor, 4P (4NO), 25 A, coil 220 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20834 + A9C15914, Schneider | kos | 1
| - ločilno stikalo 2P, 20 A, 415 V, kot naprimer Acti 9 iSW tip: A9S60220, Schneider | - disconnecting switch 2P, 20 A, 415 V, e.g. Acti 9 iSW type: A9S60220, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.41 | Dobava in montaža razdelilnika iz jeklene pločevine v barvi RAL 7035, dimenzij 800x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Omara je setavljena iz dveh polj in sicer UPS polje in DEA polje. Polja sta medsebojno ločena s kovinsko pregrado. Kot naprimer omara PanelSeT SFN, tip: NSYSFN22860P, Schneider. | Supply and installation of a switchboard made of steel sheet in RAL 7035, dimensions 800x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. The cabinet is assembled from two fields, namely UPS field and DEA field. The fields are separated by a metal barrier. As for example PanelSeT SFN cabinet, type: NSYSFN22860P, Schneider. |  |  | kpl | 1 |  | 0
| V UPS polje omare z oznako +UPS_N1_5_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the UPS box of the cabinet marked +UPS_N1_5_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=40 A, 4P za montažo na montažno ploščo; kot naprimer tip: A9S65440, Schneider | - main disconnecting switch In=40 A, 4P for mounting on a mounting plate; e.g. type: A9S65440, Schneider | kos | 1
| - vrtljiva ročica za krmiljenje glavnega ločilnega stikala + adapterski mehanizem; kot naprimer tip: A9A27006 + A9A27008, Schneider | - rotary lever for controlling the main disconnecting switch + adapter mechanism; as for example type: A9A27006 + A9A27008, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 8
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 6
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPS), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 1
| - kontaktor, 2P (2NO), 25 A, tuljava 230 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20732 + A9C15914, Schneider | - contactor, 2P (2NO), 25 A, coil 230 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20732 + A9C15914, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - 250V, 16A, DIN rail mounting socket, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
| V DEA polje omare z oznako +DEA_N1_5_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the DEA box of the cabinet marked +DEA_N1_5_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=100 A, 4P za montažo na montažno ploščo; kot naprimer tip: C104100S, Schneider | - main disconnecting switch In=100 A, 4P for mounting on a mounting plate; e.g. type: C104100S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV429340T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV429340T, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 8
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 2
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.42 | Dobava in montaža razdelilnika iz jeklene pločevine v barvi RAL 7035, dimenzij 800x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Omara je setavljena iz dveh polj in sicer UPS polje in DEA polje. Polja sta medsebojno ločena s kovinsko pregrado. Kot naprimer omara PanelSeT SFN, tip: NSYSFN22860P, Schneider. | Supply and installation of a switchboard made of steel sheet in RAL 7035, dimensions 800x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. The cabinet is assembled from two fields, namely UPS field and DEA field. The fields are separated by a metal barrier. As for example PanelSeT SFN cabinet, type: NSYSFN22860P, Schneider. |  |  | kpl | 1 |  | 0
| V UPS polje omare z oznako +UPS_N1_6_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the UPS box of the cabinet marked +UPS_N1_6_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=40 A, 4P za montažo na montažno ploščo; kot naprimer tip: A9S65440, Schneider | - main disconnecting switch In=40 A, 4P for mounting on a mounting plate; e.g. type: A9S65440, Schneider | kos | 1
| - vrtljiva ročica za krmiljenje glavnega ločilnega stikala + adapterski mehanizem; kot naprimer tip: A9A27006 + A9A27008, Schneider | - rotary lever for controlling the main disconnecting switch + adapter mechanism; as for example type: A9A27006 + A9A27008, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 8
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 6
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 2
| - kontaktor, 2P (2NO), 25 A, tuljava 230 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20732 + A9C15914, Schneider | - contactor, 2P (2NO), 25 A, coil 230 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20732 + A9C15914, Schneider | kos | 2
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - 250V, 16A, DIN rail mounting socket, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
| V DEA polje omare z oznako +DEA_N1_6_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the DEA box of the cabinet marked +DEA_N1_6_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=100 A, 4P za montažo na montažno ploščo; kot naprimer tip: C104100S, Schneider | - main disconnecting switch In=100 A, 4P for mounting on a mounting plate; e.g. type: C104100S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV429340T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV429340T, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 8
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 2
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.43 | Dobava in montaža razdelilnika iz jeklene pločevine v barvi RAL 7035, dimenzij 800x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Omara je setavljena iz dveh polj in sicer UPS polje in DEA polje. Polja sta medsebojno ločena s kovinsko pregrado. Kot naprimer omara PanelSeT SFN, tip: NSYSFN22860P, Schneider. | Supply and installation of a switchboard made of steel sheet in RAL 7035, dimensions 800x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. The cabinet is assembled from two fields, namely UPS field and DEA field. The fields are separated by a metal barrier. As for example PanelSeT SFN cabinet, type: NSYSFN22860P, Schneider. |  |  | kpl | 1 |  | 0
| V UPS polje omare z oznako +UPS_N2_1_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the UPS box of the cabinet marked +UPS_N2_1_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=100 A, 4P za montažo na montažno ploščo; kot naprimer tip: C104100S, Schneider | - main disconnecting switch In=100 A, 4P for mounting on a mounting plate; e.g. type: C104100S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV429340T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV429340T, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84316, Schneider | - three-pole 16 A circuit breaker with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84316, Schneider | kos | 3
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 31
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 6
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 3P+N, 25 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002174926, ETI | - combined protection switch with overcurrent protection (CPS), 3P+N, 25 A with C characteristic, 30mA, type AC, as for example: 002174926, ETI | kos | 4
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPC), 1P+N, 16 A with C characteristic, 30 mA, type AC, such as for example: 002173224, ETI | kos | 1
| - kontaktor, 4P (4NO), 25 A, tuljava 220 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20834 + A9C15914, Schneider | - contactor, 4P (4NO), 25 A, coil 220 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20834 + A9C15914, Schneider | kos | 4
| - kontaktor, 2P (2NO), 25 A, tuljava 230 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20732 + A9C15914, Schneider | - contactor, 2P (2NO), 25 A, coil 230 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20732 + A9C15914, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - 250V, 16A, DIN rail mounting socket, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
| V DEA polje omare z oznako +DEA_N2_1_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the DEA box of the cabinet marked +DEA_N2_1_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=40 A, 4P za montažo na montažno ploščo; kot naprimer tip: A9S65440, Schneider | - main disconnecting switch In=40 A, 4P for mounting on a mounting plate; e.g. type: A9S65440, Schneider | kos | 1
| - vrtljiva ročica za krmiljenje glavnega ločilnega stikala + adapterski mehanizem; kot naprimer tip: A9A27006 + A9A27008, Schneider | - rotary lever for controlling the main disconnecting switch + adapter mechanism; as for example type: A9A27006 + A9A27008, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 2
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 10
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 2
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 3P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002174924, ETI | - combined protection switch with overcurrent protection (CPC), 3P+N, 16 A with C characteristic, 30mA, type AC, as for example: 002174924, ETI | kos | 1
| - kontaktor, 4P (4NO), 25 A, tuljava 220 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20834 + A9C15914, Schneider | - contactor, 4P (4NO), 25 A, coil 220 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20834 + A9C15914, Schneider | kos | 1
| - ločilno stikalo 2P, 20 A, 415 V, kot naprimer Acti 9 iSW tip: A9S60220, Schneider | - disconnecting switch 2P, 20 A, 415 V, e.g. Acti 9 iSW type: A9S60220, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.44 | Dobava in montaža razdelilnika iz jeklene pločevine v barvi RAL 7035, dimenzij 800x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Omara je setavljena iz dveh polj in sicer UPS polje in DEA polje. Polja sta medsebojno ločena s kovinsko pregrado. Kot naprimer omara PanelSeT SFN, tip: NSYSFN22860P, Schneider. | Supply and installation of a switchboard made of steel sheet in RAL 7035, dimensions 800x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. The cabinet is assembled from two boxes, namely the UPS box and the DEA box. The two boxes are separated from each other by a metal barrier. As for example PanelSeT SFN cabinet, type: NSYSFN22860P, Schneider. |  |  | kpl | 1 |  | 0
| V UPS polje omare z oznako +UPS_N2_2_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the UPS box of the cabinet marked +UPS_N2_2_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=40 A, 4P za montažo na montažno ploščo; kot naprimer tip: A9S65440, Schneider | - main disconnecting switch In=40 A, 4P for mounting on a mounting plate; e.g. type: A9S65440, Schneider | kos | 1
| - vrtljiva ročica za krmiljenje glavnega ločilnega stikala + adapterski mehanizem; kot naprimer tip: A9A27006 + A9A27008, Schneider | - rotary lever for controlling the main disconnecting switch + adapter mechanism; as for example type: A9A27006 + A9A27008, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 14
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 6
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 3P+N, 25 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002174926, ETI | - combined protection switch with overcurrent protection (CPS), 3P+N, 25 A with C characteristic, 30mA, type AC, as for example: 002174926, ETI | kos | 1
| - kontaktor, 4P (4NO), 25 A, tuljava 220 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20834 + A9C15914, Schneider | - contactor, 4P (4NO), 25 A, coil 220 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20834 + A9C15914, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
| V DEA polje omare z oznako +DEA_N2_2_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the DEA box of the cabinet marked +DEA_N2_2_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=100 A, 4P za montažo na montažno ploščo; kot naprimer tip: C104100S, Schneider | - main disconnecting switch In=100 A, 4P for mounting on a mounting plate; e.g. type: C104100S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV429340T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV429340T, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 12
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 2
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.45 | Dobava in montaža razdelilnika iz jeklene pločevine v barvi RAL 7035, dimenzij 800x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Omara je setavljena iz dveh polj in sicer UPS polje in DEA polje. Polja sta medsebojno ločena s kovinsko pregrado. Kot naprimer omara PanelSeT SFN, tip: NSYSFN22860P, Schneider. | Supply and installation of a switchboard made of steel sheet in RAL 7035, dimensions 800x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. The cabinet is assembled from two fields, namely UPS field and DEA field. The fields are separated by a metal barrier. As for example PanelSeT SFN cabinet, type: NSYSFN22860P, Schneider. |  |  | kpl | 1 |  | 0
| V UPS polje omare z oznako +UPS_N2_3_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the UPS box of the cabinet marked +UPS_N2_3_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=100 A, 4P za montažo na montažno ploščo; kot naprimer tip: C104100S, Schneider | - main disconnecting switch In=100 A, 4P for mounting on a mounting plate; e.g. type: C104100S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV429340T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV429340T, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84316, Schneider | - three-pole 16 A circuit breaker with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84316, Schneider | kos | 3
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 32
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 6
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 3P+N, 25 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002174926, ETI | - combined protection switch with overcurrent protection (CPS), 3P+N, 25 A with C characteristic, 30mA, type AC, as for example: 002174926, ETI | kos | 5
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPS), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 1
| - kontaktor, 4P (4NO), 25 A, tuljava 220 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20834 + A9C15914, Schneider | - contactor, 4P (4NO), 25 A, coil 220 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20834 + A9C15914, Schneider | kos | 5
| - kontaktor, 2P (2NO), 25 A, tuljava 230 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20732 + A9C15914, Schneider | - contactor, 2P (2NO), 25 A, coil 230 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20732 + A9C15914, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
| V DEA polje omare z oznako +DEA_N2_3_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the DEA box of the cabinet marked +DEA_N2_3_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=100 A, 4P za montažo na montažno ploščo; kot naprimer tip: C104100S, Schneider | - main disconnecting switch In=100 A, 4P for mounting on a mounting plate; e.g. type: C104100S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV429340T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV429340T, Schneider | kos | 1
| - dodatna naprava diferenčnega toka 63 A, 4P, tip A, 30 mA, kot naprimer Vigi iC60, tip: A9V61463, Schneider | - additional differential current device 63 A, 4P, type A, 30 mA, such as Vigi iC60, type: A9V61463, Schneider | kos | 2
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 3
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 10
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 10
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 2
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kontaktor, 4P (4NO), 63 A, tuljava 220 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20864 + A9C15914, Schneider | - contactor, 4P (4NO), 63 A, coil 220 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20864 + A9C15914, Schneider | kos | 2
| - ločilno stikalo 2P, 20 A, 415 V, kot naprimer Acti 9 iSW tip: A9S60220, Schneider | - disconnecting switch 2P, 20 A, 415 V, e.g. Acti 9 iSW type: A9S60220, Schneider | kos | 1
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.46 | Dobava in montaža razdelilnika iz jeklene pločevine v barvi RAL 7035, dimenzij 800x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Omara je setavljena iz dveh polj in sicer UPS polje in DEA polje. Polja sta medsebojno ločena s kovinsko pregrado. Kot naprimer omara PanelSeT SFN, tip: NSYSFN22860P, Schneider. | Supply and installation of a switchboard made of steel sheet in RAL 7035, dimensions 800x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. The cabinet is assembled from two fields, namely UPS field and DEA field. The fields are separated by a metal barrier. As for example PanelSeT SFN cabinet, type: NSYSFN22860P, Schneider. |  |  | kpl | 1 |  | 0
| V UPS polje omare z oznako +UPS_N2_4_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the UPS box of the cabinet marked +UPS_N2_4_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=100 A, 4P za montažo na montažno ploščo; kot naprimer tip: C104100S, Schneider | - main disconnecting switch In=100 A, 4P for mounting on a mounting plate; e.g. type: C104100S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV429340T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV429340T, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 26
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 6
| - enopolni inštalacijski odklopnik 2 A, s D karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F85102, Schneider | - single-pole circuit breaker 2 A, with D characteristic, 15 kA, such as Acti 9 iC60H type: A9F85102, Schneider | kos | 1
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 3P+N, 25 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002174926, ETI | - combined protection switch with overcurrent protection (CPS), 3P+N, 25 A with C characteristic, 30mA, type AC, as for example: 002174926, ETI | kos | 3
| - kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip AC, kot naprimer: 002173224, ETI | - combined protection switch with overcurrent protection (CPS), 1P+N, 16 A with C characteristic, 30 mA, type AC, as for example: 002173224, ETI | kos | 5
| - kontaktor, 4P (4NO), 25 A, tuljava 220 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20834 + A9C15914, Schneider | - contactor, 4P (4NO), 25 A, coil 220 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20834 + A9C15914, Schneider | kos | 3
| - kontaktor, 2P (2NO), 25 A, tuljava 230 do 240 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, kot naprimer Acti9 iCT, tip: A9C20732 + A9C15914, Schneider | - contactor, 2P (2NO), 25 A, coil 230 to 240 V AC, 50Hz and auxiliary contact block 1 NO + 1 NC, e.g. Acti9 iCT, type: A9C20732 + A9C15914, Schneider | kos | 5
| - napetostni transformator 230 do 400 V, kot naprimer: ABL6TS25U, Schneider | - voltage transformer 230 to 400 V, e.g. ABL6TS25U, Schneider | kos | 1
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
| V DEA polje omare z oznako +DEA_N2_4_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the DEA box of the cabinet marked +DEA_N2_4_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=40 A, 4P za montažo na montažno ploščo; kot naprimer tip: A9S65440, Schneider | - main disconnecting switch In=40 A, 4P for mounting on a mounting plate; e.g. type: A9S65440, Schneider | kos | 1
| - vrtljiva ročica za krmiljenje glavnega ločilnega stikala + adapterski mehanizem; kot naprimer tip: A9A27006 + A9A27008, Schneider | - rotary lever for controlling the main disconnecting switch + adapter mechanism; as for example type: A9A27006 + A9A27008, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 3
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 12
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 2
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.47 | Dobava in montaža razdelilnika iz jeklene pločevine v barvi RAL 7035, dimenzij 800x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Omara je setavljena iz dveh polj in sicer UPS polje in DEA polje. Polja sta medsebojno ločena s kovinsko pregrado. Kot naprimer omara PanelSeT SFN, tip: NSYSFN22860P, Schneider. | Supply and installation of a switchboard made of steel sheet in RAL 7035, dimensions 800x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. The cabinet is assembled from two fields, namely UPS field and DEA field. The fields are separated by a metal barrier. As for example PanelSeT SFN cabinet, type: NSYSFN22860P, Schneider. |  |  | kpl | 1 |  | 0
| V UPS polje omare z oznako +UPS_N3_1_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the UPS box of the cabinet marked +UPS_N3_1_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=100 A, 4P za montažo na montažno ploščo; kot naprimer tip: C104100S, Schneider | - main disconnecting switch In=100 A, 4P for mounting on a mounting plate; e.g. type: C104100S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV429340T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV429340T, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 9
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 3
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
| V DEA polje omare z oznako +DEA_N3_1_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the DEA box of the cabinet marked +DEA_N3_1_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=40 A, 4P za montažo na montažno ploščo; kot naprimer tip: A9S65440, Schneider | - main disconnecting switch In=40 A, 4P for mounting on a mounting plate; e.g. type: A9S65440, Schneider | kos | 1
| - vrtljiva ročica za krmiljenje glavnega ločilnega stikala + adapterski mehanizem; kot naprimer tip: A9A27006 + A9A27008, Schneider | - rotary lever for controlling the main disconnecting switch + adapter mechanism; as for example type: A9A27006 + A9A27008, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 2
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 10
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 2
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.48 | Dobava in montaža razdelilnika iz jeklene pločevine v barvi RAL 7035, dimenzij 800x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Omara je setavljena iz dveh polj in sicer UPS polje in DEA polje. Polja sta medsebojno ločena s kovinsko pregrado. Kot naprimer omara PanelSeT SFN, tip: NSYSFN22860P, Schneider. | Supply and installation of a switchboard made of steel sheet in RAL 7035, dimensions 800x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. The cabinet is assembled from two fields, namely UPS field and DEA field. The fields are separated by a metal barrier. As for example PanelSeT SFN cabinet, type: NSYSFN22860P, Schneider. |  |  | kpl | 1 |  | 0
| V UPS polje omare z oznako +UPS_N3_2_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the UPS box of the cabinet marked +UPS_N3_2_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=40 A, 4P za montažo na montažno ploščo; kot naprimer tip: A9S65440, Schneider | - main disconnecting switch In=40 A, 4P for mounting on a mounting plate; e.g. type: A9S65440, Schneider | kos | 1
| - vrtljiva ročica za krmiljenje glavnega ločilnega stikala + adapterski mehanizem; kot naprimer tip: A9A27006 + A9A27008, Schneider | - rotary lever for controlling the main disconnecting switch + adapter mechanism; as for example type: A9A27006 + A9A27008, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 9
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 3
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
| V DEA polje omare z oznako +DEA_N3_2_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the DEA box of the cabinet marked +DEA_N3_2_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=100 A, 4P za montažo na montažno ploščo; kot naprimer tip: C104100S, Schneider | - main disconnecting switch In=100 A, 4P for mounting on a mounting plate; e.g. type: C104100S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV429340T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV429340T, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 63 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F94363, Schneider | - three-pole circuit breaker 63 A, with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F94363, Schneider | kos | 2
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 8
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 2
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.49 | Dobava in montaža razdelilnika iz jeklene pločevine v barvi RAL 7035, dimenzij 800x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Omara je setavljena iz dveh polj in sicer UPS polje in DEA polje. Polja sta medsebojno ločena s kovinsko pregrado. Kot naprimer omara PanelSeT SFN, tip: NSYSFN22860P, Schneider. | Supply and installation of a switchboard made of steel sheet in RAL 7035, dimensions 800x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. The cabinet is assembled from two fields, namely UPS field and DEA field. The fields are separated by a metal barrier. As for example PanelSeT SFN cabinet, type: NSYSFN22860P, Schneider. |  |  | kpl | 1 |  | 0
| V UPS polje omare z oznako +UPS_N3_3_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the UPS box of the cabinet marked +UPS_N3_3_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=100 A, 4P za montažo na montažno ploščo; kot naprimer tip: C104100S, Schneider | - main disconnecting switch In=100 A, 4P for mounting on a mounting plate; e.g. type: C104100S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV429340T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV429340T, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 9
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 3
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
| V DEA polje omare z oznako +DEA_N3_3_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the DEA box of the cabinet marked +DEA_N3_3_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=100 A, 4P za montažo na montažno ploščo; kot naprimer tip: C104100S, Schneider | - main disconnecting switch In=100 A, 4P for mounting on a mounting plate; e.g. type: C104100S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV429340T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV429340T, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 8
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 2
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.50 | Dobava in montaža razdelilnika iz jeklene pločevine v barvi RAL 7035, dimenzij 800x2200x600mm (ŠxVxG), skupaj z montažno ploščo, podstavek V = 100mm, enokrilna vrata, odpiranje vrat 120°, TN-S, IP55, IK10. Uvod kablov od zgoraj. Omara je setavljena iz dveh polj in sicer UPS polje in DEA polje. Polja sta medsebojno ločena s kovinsko pregrado. Kot naprimer omara PanelSeT SFN, tip: NSYSFN22860P, Schneider. | Supply and installation of a switchboard made of steel sheet in RAL 7035, dimensions 800x2200x600mm (WxHxD), including mounting plate, base V = 100mm, single leaf door, door opening 120°, TN-S, IP55, IK10. Cable entry from above. The cabinet is assembled from two boxes, namely the UPS box and the DEA box. The two boxes are separated from each other by a metal barrier. As for example PanelSeT SFN cabinet, type: NSYSFN22860P, Schneider. |  |  | kpl | 1 |  | 0
| V UPS polje omare z oznako +UPS_N3_4_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the UPS box of the cabinet marked +UPS_N3_4_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=100 A, 4P za montažo na montažno ploščo; kot naprimer tip: C104100S, Schneider | - main disconnecting switch In=100 A, 4P for mounting on a mounting plate; e.g. type: C104100S, Schneider | kos | 1
| - vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala; kot naprimer ComPacT NSX, tip: LV429340T, Schneider | - rotatable extension arm for control of the main isolating switch; as for example ComPacT NSX, type: LV429340T, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 9
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 3
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
| V DEA polje omare z oznako +DEA_N3_4_R se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in the DEA box of the cabinet marked +DEA_N3_4_R:
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=40 A, 4P za montažo na montažno ploščo; kot naprimer tip: A9S65440, Schneider | - main disconnecting switch In=40 A, 4P for mounting on a mounting plate; e.g. type: A9S65440, Schneider | kos | 1
| - vrtljiva ročica za krmiljenje glavnega ločilnega stikala + adapterski mehanizem; kot naprimer tip: A9A27006 + A9A27008, Schneider | - rotary lever for controlling the main disconnecting switch + adapter mechanism; as for example type: A9A27006 + A9A27008, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84116, Schneider | - single-pole circuit breaker 16 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H type: A9F84116, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84110, Schneider | - single-pole circuit breaker 10 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84110, Schneider | kos | 8
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 2
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.51 | Dobava in montaža razdelilnika +NN_P1_6_MN1 iz jeklene pločevine v barvi RAL 7035, dimenzij 600x1000x250mm (ŠxVxG), skupaj z montažno ploščo, enokrilna vrata, odpiranje vrat 120°, TN-S, IP66, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT SFN, tip: NSYCRN106250, Schneider. | Supply and installation of distribution box +NN_P1_6_MN1 made of steel sheet in RAL 7035, dimensions 600x1000x250mm (WxHxD), with mounting plate, single leaf door, door opening 120°, TN-S, IP66, IK10. Cable entry from above. As for example PanelSeT SFN cabinet, type: NSYCRN106250, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=40 A, 4P za montažo na montažno ploščo; kot naprimer tip: A9S65440, Schneider | - main disconnecting switch In=40 A, 4P for mounting on a mounting plate; e.g. type: A9S65440, Schneider | kos | 1
| - vrtljiva ročica za krmiljenje glavnega ločilnega stikala + adapterski mehanizem; kot naprimer tip: A9A27006 + A9A27008, Schneider | - rotary lever for controlling the main disconnecting switch + adapter mechanism; as for example type: A9A27006 + A9A27008, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 7
| - dvopolni inštalacijski odklopnik 10 A, s C karakteristiko, kot naprimer Acti 9 C60H-DC, tip: A9N61528, Schneider | - 10 A double-pole circuit-breaker with C characteristic, such as Acti 9 C60H-DC, type: A9N61528, Schneider | kos | 4
| - dvopolni inštalacijski odklopnik 4 A, s C karakteristiko, kot naprimer Acti 9 C60H-DC, tip: A9N61524, Schneider | - 4 A double-pole circuit-breaker with C characteristic, such as Acti 9 C60H-DC, type: A9N61524, Schneider | kos | 9
| - napajalnik, nazivna napetost 120/230 V AC, izhodna napetost 24 V DC, izhodni tok 5 A, kot naprimer tip: 6EP1333-2BA20, Siemens | - power supply, rated voltage 120/230 V AC, output voltage 24 V DC, output current 5 A, such as type: 6EP1333-2BA20, Siemens | kos | 1
| - nastavljiva kratkostična zaščita, 3A-10A, 24 V DC, kot naprimer tip: 6EP1961-2BA21, Siemens | - adjustable short-circuit protection, 3A-10A, 24 V DC, as for example type: 6EP1961-2BA21, Siemens | kos | 1
| - napajalnik, nazivna napetost 100/240 V AC, izhodna napetost 12 V DC, izhodni tok 8,3 A, kot naprimer tip: 2902997, Phoenix contact | - power supply, rated voltage 100/240 V AC, output voltage 12 V DC, output current 8.3 A, as for example type: 2902997, Phoenix contact | kos | 1
| - napajalnik, nazivna napetost 100/240 V AC, izhodna napetost 9 V DC, izhodni tok 5 A | - power supply, rated voltage 100/240 V AC, output voltage 9 V DC, output current 5 A | kos | 1
| - napajalnik, nazivna napetost 100/240 V AC, izhodna napetost 5 V DC, izhodni tok 8 A, kot naprimer tip: 2904375, Phoenix contact | - power supply, rated voltage 100/240 V AC, output voltage 5 V DC, output current 8 A, as for example type: 2904375, Phoenix contact | kos | 1
| - ločilno stikalo za montažo na vrata razdelilnika, 12A, kot naprimer TeSys VARIO, tip: VBF02, Schneider | - isolating switch for mounting on the distributor door, 12A, e.g TeSys VARIO, type: VBF02, Schneider | kos | 4
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - vijačni konektorji za malo napetost (24, 12, 9, 5 VDC). Koplet z montažnim materialom za namestitev na vrata razdelilnega sestava. OPOMBA: tip in število konektorjev se uskladi z naročnikom. | - screw connectors for low voltage (24, 12, 9, 5 VDC). Bath with mounting material for mounting on the door of the distribution assembly. NOTE: The type and number of connectors shall be coordinated with the customer. | kos | 60
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.52 | Dobava in montaža razdelilnika +NN_P1_6_MN2 iz jeklene pločevine v barvi RAL 7035, dimenzij 600x1000x250mm (ŠxVxG), skupaj z montažno ploščo, enokrilna vrata, odpiranje vrat 120°, TN-S, IP66, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT SFN, tip: NSYCRN106250, Schneider. | Supply and installation of distribution box +NN_P1_6_MN2 made of steel sheet in RAL 7035, dimensions 600x1000x250mm (WxHxD), with mounting plate, single leaf door, door opening 120°, TN-S, IP66, IK10. Cable entry from above. As for example PanelSeT SFN cabinet, type: NSYCRN106250, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=40 A, 4P za montažo na montažno ploščo; kot naprimer tip: A9S65440, Schneider | - main disconnecting switch In=40 A, 4P for mounting on a mounting plate; e.g. type: A9S65440, Schneider | kos | 1
| - vrtljiva ročica za krmiljenje glavnega ločilnega stikala + adapterski mehanizem; kot naprimer tip: A9A27006 + A9A27008, Schneider | - rotary lever for controlling the main disconnecting switch + adapter mechanism; as for example type: A9A27006 + A9A27008, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 7
| - dvopolni inštalacijski odklopnik 10 A, s C karakteristiko, kot naprimer Acti 9 C60H-DC, tip: A9N61528, Schneider | - 10 A double-pole circuit-breaker with C characteristic, e.g. Acti 9 C60H-DC, type: A9N61528, Schneider | kos | 4
| - dvopolni inštalacijski odklopnik 4 A, s C karakteristiko, kot naprimer Acti 9 C60H-DC, tip: A9N61524, Schneider | - 4 A double-pole circuit-breaker with C characteristic, such as Acti 9 C60H-DC, type: A9N61524, Schneider | kos | 9
| - napajalnik, nazivna napetost 120/230 V AC, izhodna napetost 24 V DC, izhodni tok 5 A, kot naprimer tip: 6EP1333-2BA20, Siemens | - power supply, rated voltage 120/230 V AC, output voltage 24 V DC, output current 5 A, such as for example type: 6EP1333-2BA20, Siemens | kos | 1
| - nastavljiva kratkostična zaščita, 3A-10A, 24 V DC, kot naprimer tip: 6EP1961-2BA21, Siemens | - adjustable short-circuit protection, 3A-10A, 24 V DC, as for example type: 6EP1961-2BA21, Siemens | kos | 1
| - napajalnik, nazivna napetost 100/240 V AC, izhodna napetost 12 V DC, izhodni tok 8,3 A, kot naprimer tip: 2902997, Phoenix contact | - power supply, rated voltage 100/240 V AC, output voltage 12 V DC, output current 8.3 A, as for example type: 2902997, Phoenix contact | kos | 1
| - napajalnik, nazivna napetost 100/240 V AC, izhodna napetost 9 V DC, izhodni tok 5 A | - power supply, rated voltage 100/240 V AC, output voltage 9 V DC, output current 5 A | kos | 1
| - napajalnik, nazivna napetost 100/240 V AC, izhodna napetost 5 V DC, izhodni tok 8 A, kot naprimer tip: 2904375, Phoenix contact | - power supply, rated voltage 100/240 V AC, output voltage 5 V DC, output current 8 A, as for example type: 2904375, Phoenix contact | kos | 1
| - ločilno stikalo za montažo na vrata razdelilnika, 12A, kot naprimer TeSys VARIO, tip: VBF02, Schneider | - isolating switch for mounting on the distributor door, 12A, e.g TeSys VARIO, type: VBF02, Schneider | kos | 4
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - 250V, 16A, DIN rail mounting socket, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - vijačni konektorji za malo napetost (24, 12, 9, 5 VDC). Koplet z montažnim materialom za namestitev na vrata razdelilnega sestava. OPOMBA: tip in število konektorjev se uskladi z naročnikom. | - screw connectors for low voltage (24, 12, 9, 5 VDC). Bath with mounting material for mounting on the door of the distribution assembly. NOTE: The type and number of connectors shall be coordinated with the customer. | kos | 60
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.53 | Dobava in montaža razdelilnika +NN_P1_6_MN3 iz jeklene pločevine v barvi RAL 7035, dimenzij 600x1000x250mm (ŠxVxG), skupaj z montažno ploščo, enokrilna vrata, odpiranje vrat 120°, TN-S, IP66, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT SFN, tip: NSYCRN106250, Schneider. | Supply and installation of distribution box +NN_P1_6_MN3 made of steel sheet in RAL 7035, dimensions 600x1000x250mm (WxHxD), with mounting plate, single leaf door, door opening 120°, TN-S, IP66, IK10. Cable entry from above. As for example PanelSeT SFN cabinet, type: NSYCRN106250, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=40 A, 4P za montažo na montažno ploščo; kot naprimer tip: A9S65440, Schneider | - main disconnecting switch In=40 A, 4P for mounting on a mounting plate; e.g. type: A9S65440, Schneider | kos | 1
| - vrtljiva ročica za krmiljenje glavnega ločilnega stikala + adapterski mehanizem; kot naprimer tip: A9A27006 + A9A27008, Schneider | - rotary lever for controlling the main disconnecting switch + adapter mechanism; as for example type: A9A27006 + A9A27008, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 7
| - dvopolni inštalacijski odklopnik 10 A, s C karakteristiko, kot naprimer Acti 9 C60H-DC, tip: A9N61528, Schneider | - 10 A double-pole circuit-breaker with C characteristic, such as Acti 9 C60H-DC, type: A9N61528, Schneider | kos | 4
| - dvopolni inštalacijski odklopnik 4 A, s C karakteristiko, kot naprimer Acti 9 C60H-DC, tip: A9N61524, Schneider | - 4 A double-pole circuit-breaker with C characteristic, such as Acti 9 C60H-DC, type: A9N61524, Schneider | kos | 9
| - napajalnik, nazivna napetost 120/230 V AC, izhodna napetost 24 V DC, izhodni tok 5 A, kot naprimer tip: 6EP1333-2BA20, Siemens | - power supply, rated voltage 120/230 V AC, output voltage 24 V DC, output current 5 A, such as type: 6EP1333-2BA20, Siemens | kos | 1
| - nastavljiva kratkostična zaščita, 3A-10A, 24 V DC, kot naprimer tip: 6EP1961-2BA21, Siemens | - adjustable short-circuit protection, 3A-10A, 24 V DC, as for example type: 6EP1961-2BA21, Siemens | kos | 1
| - napajalnik, nazivna napetost 100/240 V AC, izhodna napetost 12 V DC, izhodni tok 8,3 A, kot naprimer tip: 2902997, Phoenix contact | - power supply, rated voltage 100/240 V AC, output voltage 12 V DC, output current 8.3 A, as for example type: 2902997, Phoenix contact | kos | 1
| - napajalnik, nazivna napetost 100/240 V AC, izhodna napetost 9 V DC, izhodni tok 5 A | - power supply, rated voltage 100/240 V AC, output voltage 9 V DC, output current 5 A | kos | 1
| - napajalnik, nazivna napetost 100/240 V AC, izhodna napetost 5 V DC, izhodni tok 8 A, kot naprimer tip: 2904375, Phoenix contact | - power supply, rated voltage 100/240 V AC, output voltage 5 V DC, output current 8 A, as for example type: 2904375, Phoenix contact | kos | 1
| - ločilno stikalo za montažo na vrata razdelilnika, 12A, kot naprimer TeSys VARIO, tip: VBF02, Schneider | - isolating switch for mounting on the distributor door, 12A, e.g TeSys VARIO, type: VBF02, Schneider | kos | 4
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - 250V, 16A, DIN rail mounting socket, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - vijačni konektorji za malo napetost (24, 12, 9, 5 VDC). Koplet z montažnim materialom za namestitev na vrata razdelilnega sestava. OPOMBA: tip in število konektorjev se uskladi z naročnikom. | - screw connectors for low voltage (24, 12, 9, 5 VDC). Bath with mounting material for mounting on the door of the distribution assembly. NOTE: The type and number of connectors shall be coordinated with the customer. | kos | 60
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
1.54 | Dobava in montaža razdelilnika +NN_P1_6_MN4 iz jeklene pločevine v barvi RAL 7035, dimenzij 600x1000x250mm (ŠxVxG), skupaj z montažno ploščo, enokrilna vrata, odpiranje vrat 120°, TN-S, IP66, IK10. Uvod kablov od zgoraj. Kot naprimer omara PanelSeT SFN, tip: NSYCRN106250, Schneider. | Supply and installation of distribution box +NN_P1_6_MN4 made of steel sheet in RAL 7035, dimensions 600x1000x250mm (WxHxD), with mounting plate, single leaf door, door opening 120°, TN-S, IP66, IK10. Cable entry from above. As for example PanelSeT SFN cabinet, type: NSYCRN106250, Schneider. |  |  | kpl | 1 |  | 0
| - prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II; kot naprimer Schneider, tip: A9L40601 | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II; as for example Schneider, type: A9L40601 | kos | 1
| - glavno ločilno stikalo In=40 A, 4P za montažo na montažno ploščo; kot naprimer tip: A9S65440, Schneider | - main disconnecting switch In=40 A, 4P for mounting on a mounting plate; e.g. type: A9S65440, Schneider | kos | 1
| - vrtljiva ročica za krmiljenje glavnega ločilnega stikala + adapterski mehanizem; kot naprimer tip: A9A27006 + A9A27008, Schneider | - rotary lever for controlling the main disconnecting switch + adapter mechanism; as for example type: A9A27006 + A9A27008, Schneider | kos | 1
| - štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84440, Schneider | - 40 A four-pole circuit-breaker with C characteristic, 15 kA, such as Acti 9 iC60H, type: A9F84440, Schneider | kos | 1
| - tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H, tip: A9F84304, Schneider | - 3-pole circuit breaker 4 A, with C characteristic, 15 kA, e.g. Acti 9 iC60H, type: A9F84304, Schneider | kos | 1
| - enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, kot naprimer Acti 9 iC60H tip: A9F84106, Schneider | - single-pole circuit breaker 6 A, with C characteristic, 15 kA, such as Acti 9 iC60H type: A9F84106, Schneider | kos | 7
| - dvopolni inštalacijski odklopnik 10 A, s C karakteristiko, kot naprimer Acti 9 C60H-DC, tip: A9N61528, Schneider | - 10 A double-pole circuit-breaker with C characteristic, such as Acti 9 C60H-DC, type: A9N61528, Schneider | kos | 4
| - dvopolni inštalacijski odklopnik 4 A, s C karakteristiko, kot naprimer Acti 9 C60H-DC, tip: A9N61524, Schneider | - 4 A double-pole circuit-breaker with C characteristic, such as Acti 9 C60H-DC, type: A9N61524, Schneider | kos | 9
| - napajalnik, nazivna napetost 120/230 V AC, izhodna napetost 24 V DC, izhodni tok 5 A, kot naprimer tip: 6EP1333-2BA20, Siemens | - power supply, rated voltage 120/230 V AC, output voltage 24 V DC, output current 5 A, such as type: 6EP1333-2BA20, Siemens | kos | 1
| - nastavljiva kratkostična zaščita, 3A-10A, 24 V DC, kot naprimer tip: 6EP1961-2BA21, Siemens | - adjustable short-circuit protection, 3A-10A, 24 V DC, as for example type: 6EP1961-2BA21, Siemens | kos | 1
| - napajalnik, nazivna napetost 100/240 V AC, izhodna napetost 12 V DC, izhodni tok 8,3 A, kot naprimer tip: 2902997, Phoenix contact | - power supply, rated voltage 100/240 V AC, output voltage 12 V DC, output current 8.3 A, as for example type: 2902997, Phoenix contact | kos | 1
| - napajalnik, nazivna napetost 100/240 V AC, izhodna napetost 9 V DC, izhodni tok 5 A | - power supply, rated voltage 100/240 V AC, output voltage 9 V DC, output current 5 A | kos | 1
| - napajalnik, nazivna napetost 100/240 V AC, izhodna napetost 5 V DC, izhodni tok 8 A, kot naprimer tip: 2904375, Phoenix contact | - power supply, rated voltage 100/240 V AC, output voltage 5 V DC, output current 8 A, as for example type: 2904375, Phoenix contact | kos | 1
| - ločilno stikalo za montažo na vrata razdelilnika, 12A, kot naprimer TeSys VARIO, tip: VBF02, Schneider | - isolating switch for mounting on the distributor door, 12A, e.g TeSys VARIO, type: VBF02, Schneider | kos | 4
| - končno stikalo za LED luč 230V 1A, kot naprimer: 2500460, RITTAL | - limit switch for LED light 230V 1A, as for example: 2500460, RITTAL | kos | 1
| - luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, kot naprimer 2500200 RITTAL | - led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, as for example 2500200 RITTAL | kos | 1
| - priključni kabel za LED svetilko OR 3000mm, kot naprimer 2500400 RITTAL | - connecting cable for LED luminaire OR 3000mm, like for example 2500400 RITTAL | kos | 1
| - vgradna vtičnica 250V, 16A, za montažo na DIN letev, kot naprimer: 2506120, RITTAL | - recessed socket 250V, 16A, for DIN rail mounting, e.g. 2506120, RITTAL | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 3
| - vijačni konektorji za malo napetost (24, 12, 9, 5 VDC). Koplet z montažnim materialom za namestitev na vrata razdelilnega sestava. OPOMBA: tip in število konektorjev se uskladi z naročnikom. | - screw connectors for low voltage (24, 12, 9, 5 VDC). Bath with mounting material for mounting on the door of the distribution assembly. NOTE: The type and number of connectors shall be coordinated with the customer. | kos | 60
| - spojni, drobni in vezni material, N zbiralka, PE zbiralka, izolacijski materiali, označitveni material... | - jointing, fines and bonding materials, N busbar, PE busbar, insulation materials, marking materials, etc. | kpl | 1
| RAZDELILNIKI | DISTRIBUTORS | [5 empty] | 0

## 3.4.2_Kabli
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.4 | ELEKTRO DELA | ELECTRICAL WORKS
3.4.2 | KABLI, POLICE IN TALNI RAZVOD | CABLES, SHELVES AND FLOOR DISTRIBUTION | [5 empty] | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description |  |  | EM | Količina | Cena/EM | Cena
2 | KABLI, POLICE IN TALNI RAZVOD | CABLES, SHELVES AND FLOOR DISTRIBUTION
2.1 | Dobava in polaganje: Kabel za razsvetljavo in malo moč, deloma položene na plice, deloma uvlečen v zaščitne cevi vključno z označevalnimi ploščicami, odziv na ogenj vsaj Cca s1 d2 a1. Kabli brez halogena. | Supply and installation: Lighting and low-power cable, partly laid on tanks, partly trapped in protective tubes including marker plates, reaction to fire at least Cca s1 d2 a1. Cables without halogen.
| - N2XH-O 2x1,5mm2 | - N2XH-O 2x1,5mm2 |  |  | m | 1440 |  | 0
| - N2XH-J 3x1,5mm2 | - N2XH-J 3x1,5mm2 |  |  | m | 7000 |  | 0
| - N2XH-J 3x2,5mm2 | - N2XH-J 3x2,5mm2 |  |  | m | 67900 |  | 0
| - N2XH-J 5x1,5mm2 | - N2XH-J 5x1,5mm2 |  |  | m | 31000 |  | 0
| - N2XH-J 5x2,5mm2 | - N2XH-J 5x2,5mm2 |  |  | m | 15900 |  | 0
| - N2XH-J 5x4mm2 | - N2XH-J 5x4mm2 |  |  | m | 4700 |  | 0
| - N2XH-J 5x6mm2 | - N2XH-J 5x6mm2 |  |  | m | 2640 |  | 0
| - N2XH-J 5x10mm2 | - N2XH-J 5x10mm2 |  |  | m | 1400 |  | 0
| - N2XH-J 5x16mm2 | - N2XH-J 5x16mm2 |  |  | m | 640 |  | 0
| - N2XH-J 5x25mm2 | - N2XH-J 5x25mm2 |  |  | m | 1400 |  | 0
| - N2XH-J 1x25mm2 | - N2XH-J 1x25mm2 |  |  | m | 350 |  | 0
| - N2XH-J 4x35mm2 | - N2XH-J 4x35mm2 |  |  | m | 280 |  | 0
| - N2XH-J 4x50mm2 | - N2XH-J 4x50mm2 |  |  | m | 70 |  | 0
| - N2XH-J 5x35mm2 | - N2XH-J 5x35mm2 |  |  | m | 186 |  | 0
| - N2XH-O 4x1,5mm2 | - N2XH-O 4x1,5mm2 |  |  | m | 35 |  | 0
| - N2XH-O 7x1,5mm2 | - N2XH-O 7x1,5mm2 |  |  | m | 20 |  | 0
| - N2XH-J 10x1,5mm2 | - N2XH-J 10x1,5mm2 |  |  | m | 10 |  | 0
| - N2XH-J 19x1,5mm2 | - N2XH-J 19x1,5mm2 |  |  | m | 30 |  | 0
| - Ethernet kabel Cat.6A FRNC 4x2x23AWG | - Ethernet cable Cat.6A FRNC 4x2x23AWG |  |  | m | 1450 |  | 0
2.2 | Dobava in polaganje: Požarno odporni kabel za varnostno razsvetljavo, položen na objemke, vključno z označevalnimi ploščicami, odziv na ogenj vsaj Cca s1 d2 a1. Kabli brez halogena. | Supply and installation: Fire-resistant safety lighting cable, laid on clamps, including marker plates, reaction to fire not less than Cca s1 d2 a1. Halogen-free cables.
| - NHXH-J FE180/E30 3x1,5mm2 | - NHXH-J FE180/E30 3x1,5mm2 |  |  | m | 320 |  | 0
| - NHXH-J FE180/E30 3x2,5mm2 | - NHXH-J FE180/E30 3x2,5mm2 |  |  | m | 700 |  | 0
2.3 | Dobava in montaža: Sistem ESM, BETAfixss, E30/E90, razmik med objemkami < 800mm. Ob montaži upoštevati navodila proizvajalca: | Supply and installation: ESM system, BETAfixss, E30/E90, clamp spacing < 800mm. Follow manufacturer's instructions for installation:
| - ESM 12 M6 (za kable premera 11,1-13,1 mm) enojna objemka | - ESM 12 M6 (for cables diameter 11,1-13,1 mm) single clamp |  |  | kos | 100 |  | 0
| - zidni vložek SNA 6x30 M6/4 | - wall insert SNA 6x30 M6/4 |  |  | kos | 100 |  | 0
2.4 | Dobava in montaža kabelske police, perforirane, hladno cinkane, komplet s pokrovi, tipskimi koleni, tipskimi konzolami, odcepnimi kosi, elementi za dvig in spust, fleksibilni nivojskimi elementi in ostalimi elementi za montažo in zaščito položenih kablov, kot naprimer Hermi | Supply and installation of cable racks, perforated, cold galvanised, complete with covers, type knees, type brackets, spur pieces, lifting and lowering elements, flexible leveling elements and other elements for the installation and protection of laid cables, such as Hermi
| - 50/60 | - 50/60 |  |  | m | 1250 |  | 0
| - 100/60 | - 100/60 |  |  | m | 8100 |  | 0
| - 200/60 | - 200/60 |  |  | m | 4200 |  | 0
| - 300/60 | - 300/60 |  |  | m | 1650 |  | 0
| - 400/60 | - 400/60 |  |  | m | 3400 |  | 0
| - 500/60 | - 500/60 |  |  | m | 50 |  | 0
2.5 | Dobava in montaža kabelske lestve, hladno cinkane, tipskimi koleni, tipskimi konzolami, odcepnimi kosi, elementi za dvig in spust, fleksibilni nivojskimi elementi in ostalimi elementi za montažo, pritrdilnim priborom za montažo, kot naprimer Hermi | Supply and installation of cable ladders, cold galvanised, type knees, type brackets, spur pieces, lifting and lowering elements, flexible leveling elements and other mounting elements, mounting fixtures, such as Hermi
| - 100/60 | - 100/60 |  |  | m | 25 |  | 0
| - 200/60 | - 200/60 |  |  | m | 70 |  | 0
| - 300/60 | - 300/60 |  |  | m | 50 |  | 0
| - 400/60 | - 400/60 |  |  | m | 950 |  | 0
| - 500/60 | - 500/60 |  |  | m | 20 |  | 0
2.6 | Dobava in montaža cevi PN toge in pregibne od fi=50 mm, kompet s koleni. | Supply and installation of PN rigid and flexible pipes from fi=50 mm, with elbows. |  |  | m | 100 |  | 0
2.7 | Dobava in monža zaščitnih INOX okrogle šivne cevi, fi=22x1.5 mm, za zaščito kablov komplet s pritrdilnim materialom. | Supply and installation of protective INOX round seamed tubes, fi=22x1.5 mm, for cable protection, complete with fixing material. |  |  | m | 150 |  | 0
2.8 | Dobava in monža zaščitnih INOX okrogle šivne cevi, fi=52x1.5 mm, za zaščito kablov komplet s pritrdilnim materialom. | Supply and installation of protective INOX round seamed tubes, fi=52x1.5 mm, for cable protection, complete with fixing material. |  |  | m | 150 |  | 0
2.9 | Dobava in montaža: Nadometni zidni kanal, dimenzije 170x72mm, komplet s priborom, kot naprimer AT 170/72mm, ELBA | Supply and installation: Overhead wall channel, dimensions 170x72mm, complete with accessories, e.g. AT 170/72mm, ELBA |  |  | m | 2030 |  | 0
| - s tipskimi pokrovi in prirobnicami za montažo elementov | - with standard covers and flanges for mounting the elements
| - s tipskimi elementi za spajanje, koleni, zaključnimi elementi, elementi za pritrditev kablov in kovinskimi pregradami | - with standard splice elements, elbows, terminations, cable fixings and metallic barriers
| - in drugim potrebnim drobnim tipskim priborom za montažo | - and other necessary small type accessories for installation
2.10 | Dobava in montaža: Vgradni zidni kanal, dimenzije 125x55mm, komplet s priborom, kot naprimer AT 125/55mm, ELBA | Supply and installation: Wall-mounted channel, dimensions 125x55mm, complete with accessories, e.g. AT 125/55mm, ELBA |  |  | m | 400 |  | 0
| - s tipskimi pokrovi in prirobnicami za montažo elementov | - with standard covers and flanges for mounting the elements
| - s tipskimi elementi za spajanje, koleni, zaključnimi elementi, elementi za pritrditev kablov in kovinskimi pregradami | - with standard splice elements, elbows, terminations, cable fixings and metallic barriers
| - in drugim potrebnim drobnim tipskim priborom za montažo | - and other necessary small type accessories for installation
2.11 | Dobava in montaža talne doze TD-6, 6M dimenzij 222x222x73mm. Globina za vgradnjo 80mm, IK08, IP20; kot naprimer GES4 Obo Bettermann. | Supply and installation of floor dock TD-6, 6M dimensions 222x222x73mm. Installation depth 80mm, IK08, IP20; as for example GES4 Obo Bettermann. |  |  | kpl | 397 |  | 0
| - kvadratno vgradno ohišje | - square recessed housing | 1 | kos
| - univerzalni nosilec 3M | - 3M universal holder | 2 | kos
| - vgradni element s pokrovom z zapahi | - installation element with lid with latches | 1 | kos
| - trojna vtičnica z zaščitnim kontaktom 16A, 220V, bela barva | - triple socket with protective contact 16A, 220V, white | 1 | kos
| - enojna vtičnica z zaščitnim kontaktom 16A, 220V, bela barva | - single socket with protective contact 16A, 220V, white | 1 | kos
| - nosilna plošča za 2 modula tip RM, 45x45mm | - support plate for 2 modules type RM, 45x45mm | 2 | kos
| - konektor UTP RJ45 | - rJ45 UTP connector | 4 | kos
2.12 | Dobava in montaža talne doze TD-12, 12M dimenzij 264x264x75mm. Globina za vgradnjo 83mm, IK08, IP20; kot naprimer GES9 Obo Bettermann. | Supply and installation of floor dock TD-12, 12M, dimensions 264x264x75mm. Installation depth 83mm, IK08, IP20; as for example GES9 Obo Bettermann. |  |  | kpl | 126 |  | 0
| - kvadratno vgradno ohišje | - square recessed housing | 1 | kos
| - univerzalni nosilec 4M | - 4M universal carrier | 3 | kos
| - vgradni element s pokrovom z zapahi | - installation element with lid with latches | 1 | kos
| - dvojna vtičnica z zaščitnim kontaktom 16A, 220V, bela barva | - double socket with protective contact 16A, 220V, white | 4 | kos
| - nosilna plošča za 2 modula tip RM, 45x45mm | - support plate for 2 modules type RM, 45x45mm | 4 | kos
| - konektor UTP RJ45 | - rJ45 UTP connector | 8 | kos
2.13 | Dobava in montaža talne doze TD-12a, 12M dimenzij 264x264x75mm. Globina za vgradnjo 83mm, IK08, IP20; kot naprimer GES9 Obo Bettermann. | Supply and installation of floor dock TD-12a, 12M dimensions 264x264x75mm. Installation depth 83mm, IK08, IP20; as for example GES9 Obo Bettermann. |  |  | kpl | 2 |  | 0
| - kvadratno vgradno ohišje | - square recessed housing | 1 | kos
| - univerzalni nosilec 4M | - 4M universal carrier | 3 | kos
| - vgradni element s pokrovom z zapahi | - installation element with lid with latches | 1 | kos
| - trojna vtičnica z zaščitnim kontaktom 16A, 220V, bela barva | - triple socket with protective contact 16A, 220V, white | 1 | kos
| - dvojna vtičnica z zaščitnim kontaktom 16A, 220V, bela barva | - double socket with protective contact 16A, 220V, white | 1 | kos
| - enojna vtičnica z zaščitnim kontaktom 16A, 220V, zelena barva | - single socket with protective contact 16A, 220V, green | 1 | kos
| - nosilna plošča za 2 modula tip RM, 45x45mm | - support plate for 2 modules type RM, 45x45mm | 1 | kos
| - konektor UTP RJ45 | - rJ45 UTP connector | 2 | kos
2.14 | Dobava in montaža talne doze TD-12b, 12M dimenzij 264x264x75mm. Globina za vgradnjo 83mm, IK08, IP20; kot naprimer GES9 Obo Bettermann. | Supply and installation of floor dock TD-12b, 12M dimensions 264x264x75mm. Installation depth 83mm, IK08, IP20; as for example GES9 Obo Bettermann. |  |  | kpl | 2 |  | 0
| - kvadratno vgradno ohišje | - square recessed housing | 1 | kos
| - univerzalni nosilec 4M | - 4M universal carrier | 3 | kos
| - vgradni element s pokrovom z zapahi | - installation element with lid with latches | 1 | kos
| - dvojna vtičnica z zaščitnim kontaktom 16A, 220V, bela barva | - double socket with protective contact 16A, 220V, white | 5 | kos
| - nosilna plošča za 2 modula tip RM, 45x45mm | - support plate for 2 modules type RM, 45x45mm | 2 | kos
| - konektor UTP RJ45 | - rJ45 UTP connector | 4 | kos
2.15 | Dobava in montaža talne doze TD-12c, 12M dimenzij 264x264x75mm. Globina za vgradnjo 83mm, IK08, IP20; kot naprimer GES9 Obo Bettermann. | Supply and installation of floor dock TD-12c, 12M dimensions 264x264x75mm. Installation depth 83mm, IK08, IP20; as for example GES9 Obo Bettermann. |  |  | kpl | 2 |  | 0
| - kvadratno vgradno ohišje | - square recessed housing | 1 | kos
| - univerzalni nosilec 4M | - 4M universal carrier | 3 | kos
| - vgradni element s pokrovom z zapahi | - installation element with lid with latches | 1 | kos
| - trojna vtičnica z zaščitnim kontaktom 16A, 220V, bela barva | - triple socket with protective contact 16A, 220V, white | 1 | kos
| - dvojna vtičnica z zaščitnim kontaktom 16A, 220V, zelena barva | - double socket with protective contact 16A, 220V, green | 2 | kos
| - nosilna plošča za 2 modula tip RM, 45x45mm | - support plate for 2 modules type RM, 45x45mm | 1 | kos
| - konektor UTP RJ45 | - rJ45 UTP connector | 2 | kos
2.16 | Dobava in montaža talne doze TD-12d, 12M dimenzij 264x264x75mm. Globina za vgradnjo 83mm, IK08, IP20; kot naprimer GES9 Obo Bettermann. | Supply and installation of floor dock TD-12d, 12M dimensions 264x264x75mm. Installation depth 83mm, IK08, IP20; as for example GES9 Obo Bettermann. |  |  | kpl | 7 |  | 0
| - kvadratno vgradno ohišje | - square recessed housing | 1 | kos
| - univerzalni nosilec 4M | - 4M universal carrier | 3 | kos
| - vgradni element s pokrovom z zapahi | - installation element with lid with latches | 1 | kos
| - dvojna vtičnica z zaščitnim kontaktom 16A, 220V, bela barva | - double socket with protective contact 16A, 220V, white | 4 | kos
| - nosilna plošča za 2 modula tip RM, 45x45mm | - support plate for 2 modules type RM, 45x45mm | 2 | kos
| - konektor UTP RJ45 | - rJ45 UTP connector | 4 | kos
2.17 | Dobava in montaža talne doze TD-12e, 12M dimenzij 264x264x75mm. Globina za vgradnjo 83mm, IK08, IP20; kot naprimer GES9 Obo Bettermann. | Supply and installation of floor dock TD-12e, 12M dimensions 264x264x75mm. Installation depth 83mm, IK08, IP20; as for example GES9 Obo Bettermann. |  |  | kpl | 2 |  | 0
| - kvadratno vgradno ohišje | - square recessed housing | 1 | kos
| - univerzalni nosilec 4M | - 4M universal carrier | 3 | kos
| - vgradni element s pokrovom z zapahi | - installation element with lid with latches | 1 | kos
| - dvojna vtičnica z zaščitnim kontaktom 16A, 220V, bela barva | - double socket with protective contact 16A, 220V, white | 4 | kos
| - dvojna vtičnica z zaščitnim kontaktom 16A, 220V, zelena barva | - double socket with protective contact 16A, 220V, green | 1 | kos
| - nosilna plošča za 2 modula tip RM, 45x45mm | - support plate for 2 modules type RM, 45x45mm | 2 | kos
| - konektor UTP RJ45 | - rJ45 UTP connector | 4 | kos
2.18 | Dobava in montaža talne doze, kvadratno vgradno ohišje za vgradnjo v estrih tleh v notranjih prostorih, dimenzij 210x205x75mm. Ohišje zaprto z montažnim pokrovom. Globina za vgradnjo 70mm; kot naprimer GES4 Obo Bettermann. | Supply and installation of floor dock, square recessed housing for installation in screeded floors in interior spaces, dimensions 210x205x75mm. Housing closed with mounting cover. Installation depth 70mm; as for example GES4 Obo Bettermann. |  |  | kos | 5 |  | 0
2.19 | Dobava in montaža talnega inštalacijskega kanala, z 2 komorama, višina kanala 38 mm, širina 190mm; kot naprimer Obo Bettermann. | Supply and installation of a floor installation duct, with 2 chambers, duct height 38 mm, width 190 mm; as for example Obo Bettermann. |  |  | m | 2500 |  | 0
2.20 | Dobava in montaža vertikalnega kolena, z 2 komorama, višina 38 mm, širina 190mm; kot naprimer Obo Bettermann. | Supply and installation of vertical elbow, with 2 chambers, height 38 mm, width 190 mm; as for example Obo Bettermann. |  |  | kos | 330 |  | 0
| KABLI, POLICE IN TALNI RAZVOD | CABLES, SHELVES AND FLOOR DISTRIBUTION | [5 empty] | 0

## 3.4.3_Ostalo
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.4 | ELEKTRO DELA | ELECTRICAL WORKS
3.4.3 | OSTALO | OTHER |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
3 | OSTALO | OTHER
3.1 | Priprava podlog za izdelavo PID projekta. Vnos sprememb, do katerih pride med izvedbo, v en izvod PZI projekta. | Preparation of the basis for the PID project. Entry of changes that occur during implementation in one copy of the PID project. | kpl | 1 |  | 0
3.2 | Izvedba meritev in funkcionalnega pregleda elektroinstalacij z izdelavo zapisnikov in poročil za celoten sistem v sestavi : | Carrying out measurements and functional inspection of the electrical installations, producing minutes and reports for the entire system as a whole: | kpl | 1 |  | 0
| - merjenje izolacijske upornosti | - insulation resistance measurement
| - funkcionalni preizkus | - functional test
| - nastavitev zaščit | - setting safeguards
3.3 | Pozitivne ocene, atesti, certifikati in potrdila ustreznih inštitucij za dokazovanje primerne kakovosti vgrajenih naprav, napeljav, materialov in montažnih del (EIMV, IVD, ZAG, SIQ in podobno). | Positive evaluations, attestations, certificates and attestations of the relevant institutions to prove the adequate quality of the installed devices, installations, materials and assembly works (EIMV, IVD, ZAG, SIQ, etc.). | kpl | 1 |  | 0
3.4 | Izdelava tesnjenja prehodov kablov in kabelskih inštalacij skozi požarne sektorje, ki ga z ustreznimi materiali izvede izvajalec z licenco ter na koncu izda ustrezni certifikat (izvedba in uporabljen material v skladu s standardom DIN 4102, skladno s smernico SZPV 408, skladno s NPV (EI90) in po navodilih proizvajalca), cca: Φ 110 mm, kot naprimer Protecta, za stene do debeline 400 mm OPOMBA: tesnenje mora biti takšnega tipa, ki omogoča naknadno vstavljanje kablov. | Sealing of cable and cable installation penetrations through fire sectors, carried out by a licensed contractor using appropriate materials and finally certified (execution and material used in accordance with DIN 4102, in accordance with SZPV 408, in accordance with NPV (EI90) and according to the manufacturer's instructions), approx.: Φ 110 mm, such as Protecta, for walls up to 400 mm thick NOTE: The sealing shall be of a type to allow subsequent insertion of cables. | kpl | 400 |  | 0
3.5 | Izdelava tesnjenja prehodov kablov in kabelskih inštalacij skozi požarne sektorje, ki ga z ustreznimi materiali izvede izvajalec z licenco ter na koncu izda ustrezni certifikat (izvedba in uporabljen material v skladu s standardom DIN 4102, skladno s smernico SZPV 408, skladno s NPV (EI90) in po navodilih proizvajalca), cca: fi 110 mm, kot naprimer Hilti, za stene debelejše od 400 mm OPOMBA: tesnenje mora biti takšnega tipa, ki omogoča naknadno vstavljanje kablov. | Sealing of cable and cable installation penetrations through fire sectors, carried out by a licensed contractor using appropriate materials and finally certified (execution and material used in accordance with DIN 4102, in accordance with SZPV 408, in accordance with NPV (EI90) and according to the manufacturer's instructions), approx.: fi 110 mm, such as Hilti, for walls thicker than 400 mm NOTE: The sealing shall be of a type to allow subsequent insertion of cables. | kpl | 50 |  | 0
3.6 | Izdelava tesnjenja prehodov kablov in kabelskih inštalacij skozi požarne sektorje, ki ga z ustreznimi materiali izvede izvajalec z licenco ter na koncu izda ustrezni certifikat (izvedba in uporabljen material v skladu s standardom DIN 4102, skladno s smernico SZPV 408, skladno s NPV (EI90) in po navodilih proizvajalca), cca: Φ 150 mm, kot naprimer Hilti, za stene debelejše od 400 mm OPOMBA: tesnenje mora biti takšnega tipa, ki omogoča naknadno vstavljanje kablov. | Sealing of cable and cable installation penetrations through fire sectors, carried out by a licensed contractor using appropriate materials and finally certified (execution and material used in accordance with DIN 4102, in accordance with SZPV 408, in accordance with NPV (EI90) and according to the manufacturer's instructions), approx.: Φ 150 mm, such as Hilti, for walls thicker than 400 mm NOTE: The sealing shall be of a type to allow subsequent insertion of cables. | kpl | 30 |  | 0
3.7 | Izdelava tesnjenja prehodov kablov in kabelskih inštalacij skozi požarne sektorje, ki ga z ustreznimi materiali izvede izvajalec z licenco ter na koncu izda ustrezni certifikat (izvedba in uporabljen material v skladu s standardom DIN 4102, skladno s smernico SZPV 408, skladno s NPV (EI90) in po navodilih proizvajalca), cca: 600 x 100 mm, kot naprimer Hilti OPOMBA: tesnenje mora biti takšnega tipa, ki omogoča naknadno vstavljanje kablov. | Sealing of cable and cable installation penetrations through fire sectors, carried out by a licensed contractor using appropriate materials and finally certified (execution and material used in accordance with DIN 4102, in accordance with SZPV 408, in accordance with NPV (EI90) and according to the manufacturer's instructions), approx.: 600 x 100 mm, such as Hilti NOTE: The sealing shall be of a type to allow subsequent insertion of cables. | kpl | 6 |  | 0
3.8 | Vrtanje odprtin v stenah in ploščah, do premera Φ 150 mm | Drilling of holes in walls and panels, up to a diameter of Φ 150 mm | kos | 750 |  | 0
3.9 | Izdelava tesnjenja horizontalnih prehodov kablov in kabelskih inštalacij skozi stene, do Φ 50 mm. | Sealing of horizontal passages for cables and cable installations through walls, up to Φ 50 mm. | kpl | 15 |  | 0
3.10 | Izdelava tesnjenja horizontalnih prehodov kablov in kabelskih inštalacij skozi stene, do Φ 110 mm. | Sealing of horizontal passages for cables and cable installations through walls, up to Φ 110 mm. | kpl | 700 |  | 0
3.11 | Izdelava tesnjenja horizontalnih prehodov kablov in kabelskih inštalacij skozi stene, do Φ 150 mm. | Sealing of horizontal passages for cables and cable installations through walls, up to Φ 150 mm. | kpl | 40 |  | 0
3.12 | Razna nepredvidena dela, ki se obračunajo po urah s potrditvijo nadzornika v gradbenem dnevniku. | Miscellaneous unforeseen work, billed by the hour with the supervisor's approval in the construction logbook. | ur | 24 |  | 0
| OSTALO | OTHER |  |  |  | 0