## 0_Naslovnica
OPOZORILO! Vsi prevodi v angleščino so strojno izdelani in zgolj informativne narave. V primeru kakršnekoli nejasnosti ali dvoma izključno velja izvirno besedilo v slovenščini. WARNING! All translations into English have been produced by machine translation and are provided for informational purposes only. In the event of any ambiguity or uncertainty, the original Slovenian text shall prevail exclusively.
| / | / | [5 empty] | /
| Sprem./Rev.: | Opis spremembe/Description of Changes: | [5 empty] | Datum/Date: | Podpis/Signature:
| Investitor/Investor: |  |  |  |  | Gradnja/Facility
|  |  | Univerza v Ljubljani Kongresni trg 12 1000 Ljubljana, Slovenija |  |  | Fakulteta za strojništvo/Faculty of Mechanical Engineering
| Projektant/Design Engineer: |  |  |  |  | Del objekta/sistem/Building/System:
|  |  | IBE, svetovanje, projektiranje in inženiring Ljubljana, Slovenija |  |  | STAVBA FAKULTETE/FACULTY BUILDING
| Projektant/Design Engineer: |  |  |  |  | Vrsta načrta/Documentation:
3 NAČRT S PODROČJA ELEKTROTEHNIKE/ DOC. IN THE FIELD OF ELECTRICAL ENGINEERING
|  | Ime in priimek/Name and Surname: |  |  | Id. št./Id. No: | Vsebina risbe (dokumenta)/Document Title:
| Vodja proj./ Des. Manager: | Boštjan Vuga, univ. dipl. inž. arh., grad. dip. (AA) |  |  | ZAPS 0035 PA PPN | PR. POPIS ELEKTRO DEL/BOQ OF ELECTRICAL WORKS 3/7 Razsvetljava/Lighting
| Poobl. strok./ Cert. Profess.: | Robert Bobovnik, dipl.inž.el. |  |  | IZS E-2380
| Poobl. strok./ Cert. Profess.: |  |  |  |  | Št. proj./ Proj. No.: | 362-19 |  | Vrsta dokument./ Document. Type: | DZR
| Izdelal/ Creator: | Aleksandra Proeva, dipl.inž.el. Enis Rokša, mag.inž.el. |  |  |  | Klas. ozn./ Class. No.: | -- |  | Stran/ Page: | 1/*
| Datum/ Date: | maj/May 2026 |  | Merilo/ Scale: | / | Ident. ozn./ Id. No: | JULFS--6E9322P

## 0_Osebe
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
POOBLAŠČENI STROKOVNJAKI, ODGOVORNI ZA IZDELAVO PROJEKTANTSKEGA POPISA:
Id. št. ZAPS/IZS | Pooblaščeni strokovnjak | Strokovno področje
IZS E-2380 | Robert Bobovnik, dipl. inž. el. | Električne inštalacije
SODELAVCI PRI IZDELAVI PROJEKTANTSKEGA POPISA:
/ | Aleksandra Proeva, dipl. inž. el. | Električne inštalacije
/ | Enis Rokša, mag. inž. el. | Električne inštalacije
CERTIFIED EXPERTS RESPONSIBLE FOR ELABORATING THE BILL OF QUANTITIES:
Id. No ZAPS/IZS | Certified Expert | Area of Expertise
IZS E-2380 | Robert Bobovnik, dipl. inž. el. | Electrical installations
COLABORATORS IN THE ELABORATING THE BILL OF QUANTITIES:
/ | Aleksandra Proeva, dipl. inž. el. | Electrical installations
/ | Enis Rokša, mag. inž. el. | Electrical installations

## 0.1_Uvod-STP
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
0.1 | SPLOŠNI TEHNIČNI POGOJI | GENERAL TECHNICAL CONDITIONS
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic operator with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
0.1.1 | Izvajalec se obveže, da bo upošteval veljavno zakonodajo, ki ureja graditev objektov v Republiki Sloveniji, vključno s povezanimi podzakonskimi akti, predpisi, tehničnimi smernicami, standardi, pravili stroke in dobro gradbeno prakso. Prav tako mora izvajalec upoštevati vse zahteve izdanega integralnega gradbenega dovoljenja in vsa dela izvesti skladno s projektno dokumentacijo ter ostalimi pogoji, objavljenimi v razpisni dokumentaciji. | The Contractor undertakes to comply with the applicable legislation governing the construction of buildings in the Republic of Slovenia, including related by-laws, regulations, technical guidelines, standards, professional rules and good construction practice. The Contractor shall also comply with all the requirements of the integral building permit issued and shall carry out all works in accordance with the project documentation and other conditions published in the tender documentation.
0.1.2 | Dela lahko izvaja samo izvajalec, ki je registriran za opravljanje gradbene dejavnosti in ima za tovrstna dela ustrezno zavarovanje za škodo, certifikate, tehnično izobražen kader, sredstva ter je usposobljen za samostojno pripravo in izvedbo del. | The work may only be carried out by a contractor who is registered to carry out construction work and who has the appropriate insurance for such work, certificates, technically trained staff, resources and is qualified to prepare and carry out the work independently.
0.1.3 | Izvajalec odgovarja za kakovost izvedbe vseh del. | The Contractor shall be responsible for the quality of the execution of all works.
0.1.4 | Izvajalec nosi vso odgovornost za nesreče in škodo, ki nastane na objektu ali v okolici zaradi njegovega dela. | The Contractor shall bear all liability for accidents and damage to the installation or the surrounding area caused by his work.
0.1.5 | Pred oddajo ponudbe se je izvajalec dolžan seznaniti z območjem predvidenim za gradnjo in temu prilagoditi vsa potrebna dela, kar mora biti zajeto v ponudbi. V neposredni bližini predvidene gradnje se nahajajo stavbe, v katerih potekajo izobraževalni in raziskovalni procesi. Zato bo izvajalec moral izvajati kontrolo hrupa in kontrolo vibracij. Dela, ki so hrupna in dela, ki povzročajo vibracije bo izvajalec moral preprečiti oziroma jih izvesti na način, da povzročajo minimalne vplive. Tehnologijo rušenja, pilotiranja in tehnologijo izvedbe ostalih del bo izvajalec moral prilagoditi tako, da bo vpliv minimalen. Izvajalec mora preprečiti in zmanjšati emisije delcev iz gradbišča na najmanjšo možno mero. | Before submitting a tender, the contractor is obliged to familiarise himself with the area to be constructed and to adapt any necessary works accordingly, which must be included in the tender. In the immediate vicinity of the proposed construction, there are buildings in which educational and research processes take place. The contractor will therefore be required to carry out noise and vibration control. Noise and vibration works will have to be avoided or carried out in such a way as to minimise the impact. Demolition, piling and other works will have to be adapted to minimise the impact. The contractor must avoid and minimise the emission of particulates emitted from the construction site as far as is reasonably practicable.
0.1.6 | Izvajalec je pred oddajo ponudbe dolžan pregledati projektno dokumentacijo in ostale pogoje, ki so del razpisne dokumentacije V primeru morebitnih napak in neskladij je izvajalec dolžan na to opozoriti naročnika pred oddajo ponudbe. | The Contractor is obliged to review the project documentation and other conditions forming part of the tender documentation before submitting the tender In case of any errors or inconsistencies, the Contractor is obliged to bring these to the attention of the Contracting Authority before submitting the tender.
0.1.7 | Pred oddajo ponudbe je izvajalec dolžan preveriti ustreznost popisov del in količin v teh popisih ter njihovo skladnost z ostalimi dokumenti projektne dokumentacije, ki so del razpisne dokumentacije. Prav tako je izvajalec dolžan preveriti vse detajle in sheme. Vse izmere je potrebno preveriti po posameznih projektih oz. načrtih, ki sestavljajo razpisno dokumentacijo. V primeru ugotovljenih neskladij je v času priprave ponudbe obvezan o tem obvestiti naročnika. | Before submitting a tender, the Contractor shall check the adequacy of the inventories of works and quantities in these Bills of Quantities and their conformity with the other documents of the project documentation forming part of the tender documentation. The Contractor shall also check all details and diagrams. All measurements shall be checked against the individual projects or plans forming part of the tender documentation. In the event of any discrepancies, the Contractor shall inform the Contracting Authority at the time of preparing the tender.
0.1.8 | Pred oddajo ponudbe je izvajalec dolžan v tem popisu preveriti zmnožke in seštevke ter prenose le-teh v rekapitulacijo. Izvajalec se s pripravo ponudbe obvezuje, da je prebral vse celice in elemente celotnega popisa, vključno z vsemi postavkami in splošnimi navodili ali določili in je preveril pravilnost preračuna ter s tem zagotavlja ponudbeno vrednost. | Before submitting a tender, the Contractor is required to check the products and totals in this Bill of Quantities (BoQ) and their transfer to the recapitulation. The Contractor undertakes, by preparing a tender, to have read all the cells and elements of the complete BoQ, including all headings and general instructions or provisions, and to have checked the correctness of the conversion, thereby guaranteeing the value of the tender.
0.1.9 | Dela bo izvajalec moral izvajati po predloženi projektni dokumentaciji, detajlih in z upoštevanjem navodil in potrditev projektanta, nadzornika in investitorja. Vso potrebno delavniško dokumentacijo zagotovi izvajalec del v okviru ponujene cene. | The Contractor shall carry out the works in accordance with the submitted design documents, details and subject to the instructions and approvals of the Designer, the Supervisor and the Investor. All necessary workshop documentation shall be provided by the Contractor within the scope of the price quoted.
0.1.10 | Pred izvedbo posameznih del je izvajalec dolžan pregledati projektno dokumentacijo za izvedbo gradnje (PZI) in elaborate. Na morebitne napake v dokumentaciji ali neskladja med posameznimi načrti ali deli načrtov (popisi del, tehnična poročila, lokacijski in tehnični prikazi) izvajalec opozori nadzornika in projektanta, in se z njima pravočasno uskladi. | The Contractor shall review the Detailed Design documentation (PZI) and the studies before carrying out the individual works. The Contractor shall draw the attention of the Supervisor and the Designer to any errors in the documentation or discrepancies between the individual designs or parts of designs (BoQ, technical reports, location and technical drawings) and shall coordinate with them in good time.
0.1.11 | Tehnični opisi, prikazi, detajli, sheme ter ostali dokumenti v PZI dokumentaciji predstavljajo dodaten opis popisnih postavk gradbeno obrtniških in inštalacijskih del ter jih je potrebno dosledno upoštevati skupaj s popisom del. | The technical descriptions, illustrations, details, diagrams and other documents in the Detailed Design documentation (PZI) are additional descriptions of the BoQ inventory items of the building, construction and installation works and must be strictly followed together with the BoQ.
0.1.12 | Specifikacije in zahteve, navedene v popisu, se ne smejo upoštevati kot edine zahteve. Izvajalec je dolžan v ceni zajeti in dobaviti vse elemente opreme ter opraviti dela in storitve, ki niso eksplicitno navedeni, a so bistvenega pomena za funkcionalnost, skladnost s predpisi ter kontinuirano, zanesljivo in varno obratovanje opreme. | The specifications and requirements set out in the BoQ shall not be taken as the only requirements. The Contractor shall be obliged to include in the price and supply all items of equipment and to carry out works and services which are not expressly mentioned but which are essential for the functionality, regulatory compliance and continuous, reliable and safe operation of the equipment.
0.1.13 | Vsa dela morajo biti izvedena kvalitetno in iz materialov z zahtevanimi lastnostmi, izvedena skladno z veljavno zakonodajo in z upoštevanjem navodil za vgradnjo za izbrane materiale in opremo, s predložitvijo predpisanih izjav o lastnostih in/ali certifikatov. Vsi gradbeni proizvodi (GP) morajo biti označeni s CE oznako. | All work shall be of good quality and be executed with materials of the required characteristics, in accordance with the applicable legislation and in compliance with the installation instructions for the materials and equipment selected, and shall be accompanied by the prescribed declarations of performance and/or certificates. All construction products (GP) shall bear the CE marking.
0.1.14 | Za vsako opisano delo v popisu je potrebno upoštevati celotno potrebno delo, ves osnovni in pomožni material, prevoz materiala in orodja na objekt, notranje transporte, delovne in pomožne odre, zaključno čiščenje in odstranitev odpadkov po dovršenem delu. | For each work described in the inventory, the total work required, all basic and ancillary materials, the transport of materials and tools to the site, internal transports, working and ancillary scaffolding, final cleaning and the disposal of waste after the work has been completed must be taken into account.
0.1.15 | Vsa delovna sredstva, organizacija in koordinacija del, pripravljalna, spremljajoča in zaključna dela, potrebni montažni in tesnilni materiali ter podkonstrukcije so sestavni del posameznih postavk. | All labour, organisation and coordination of the works, preparatory, accompanying and finishing works, necessary prefabrication and sealing materials and substructures are part of the individual items.
0.1.16 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - načrt organizacije gradbišča s podrobnim terminskim planom in izvedba vseh pripravljalnih del, postavitev, organizacija, zaščita in prijava gradbišča, gradbiščnih objektov, ureditev začasnih deponij, tekoče vzdrževanje, skupaj s plačilom splošnih stroškov pristojbin in davkov upravnih organov, pridobivanju raznih dovoljenj in soglasij za izvedbo, ograditev gradbišča in postavitev gradbene table in prometne signalizacije, zagotavljanje ustrezne varnosti na gradbišču, tekoče vzdrževanje in končna odstranitev gradbišča; - zagotovitev potrebnih začasnih površin za transportne poti in gradnjo izven območja gradbišča s plačilom stroškov za sanacijo in vzpostavitev okoliških zemljišč in objektov v prvotno stanje (soglasja, odškodnine, itd.); - začasni odvoz, deponiranje in vračanje izkopanega materiala, ki ga ne bo možno deponirati na gradbišču; - odvoz in zagotovitev odstranjevanja odpadnega gradbenega materiala skladno z zakonodajo na področju ravnanja z odpadki (odvoz na urejene deponije s plačilom komunalnih prispevkov in taks itd.); - oteženi izkop v mokrem terenu, izkop v vodi, odvod meteorne vode iz gradbene jame in vode, ki se izceja iz bočnih strani izkopov; - ustrezno varovanje izkopa gradbene jame za objekt in ostalih manjših posameznih izkopov za izvedbo komunalne infrastrukture brez posegov na sosednja zemljišča; - ustrezno varovanje obstoječih objektov, infrastrukture in okolice v času gradnje ter dokumentiranje vseh morebitnih škodnih dogodkov; - pripravljalna, spremljajoča in zaključna dela (zakoličbe, zagotovitev potrebnih komunalnih priključkov za potrebe izvajanja gradnje, izvedba začasnih inštalacij, označevanje podzemnih vodov, postavljanje in vzdrževanje zakoličbenih profilov, izvedba in označevanje novih in starih križanj ter morebitna zaščita križanj komunalnih vodov, geodetski posnetki in izdajanje vmesnih posnetkov izvedene infrastrukture naročniku, izdelava zbirnih kart, itd.), v kolikor ni to drugače določeno; - pridobivanje soglasij in izvedba morebitnih zapor na vseh cestah s plačilom stroškov, nadomestil in pristojbin; - zagotovitev oz. postavitev in končna odstranitev po zaključku gradnje začasnih skladišč in začasnega pisarniškega kontejnerskega objekta vključno z opremo za dve delovni mesti in za skupne operativne sestanke vel. ca. 40 m2 za potrebe naročnika, s tekočim vzdrževanjem in čiščenjem. | The following must also be included or taken into account in the uniform prices for individual items: - a construction site organisation plan with a detailed timetable and the execution of all preparatory works, the setting-up, organisation, protection and registration of the construction site, site facilities, the arrangement of temporary storage facilities, ongoing maintenance, including the payment of general costs of fees and taxes of the administrative authorities, the obtaining of various permits and consents for the execution, the fencing of the site and the erection of construction signs and traffic signals, the provision of adequate security on the site, ongoing maintenance and the final dismantling of the construction site; - provision of the necessary temporary areas for transport routes and off-site construction, with costs for restoration and reinstatement of surrounding land and buildings (consents, compensation, etc.); - temporary removal, storage and return of excavated material that cannot be stored on site; - removing and disposing of waste building materials in accordance with waste management legislation (removal to regulated landfill sites with payment of municipal fees and charges, etc.); - difficult excavation in wet ground, excavation in water, drainage of rainwater from the construction pit and water draining from the sides of excavations; - adequate protection of the excavation of the construction pit for the building and other small individual excavations for the implementation of the utility infrastructure without encroaching on neighbouring land; - adequate protection of existing facilities, infrastructure and the surrounding area during construction, and documentation of any damage incidents; - preparatory, accompanying and finishing works (stake-out, provision of the necessary utility connections for the needs of construction, execution of temporary installations, marking of underground lines, installation and maintenance of stake-out profiles, execution and marking of new and old crossings and possible protection of crossings of utility lines, geodetic surveys and issuing of intermediate images of the completed infrastructure to the client, production of summary maps, etc.), unless otherwise specified; - obtaining consents and implementing any road closures, with costs, compensation and fees; - provision or erection and final removal on completion of construction of temporary storage and temporary office container building including equipment for two workstations and for joint operational meetings of approx. 40 m2 for the needs of the client, with ongoing maintenance and cleaning.
0.1.17 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - izdelava montažne tehnične dokumentacije, detajlov izvedbe in vse druge potrebne delavniške dokumentacije (s področja arhitekture, gradbeništva, elektrotehnike, strojništva in zunanje ter krajinske ureditve) ter pridobitev obvezne potrditve s strani projektanta, nadzornika in investitorja; - odprava vseh vrst inštalacijskih kolizij z izvajanjem potrebnih premikov inštalacij in njihovim usklajevanjem na mestu montaže, vse v obsegu, ki ne vpliva na projektirano rešitev ali tip inštalacij oz. opreme; - zagotavljanje kompletnosti elektro-instalacijskih sistemov s področja avtomatike za doseganje njihove popolne funkcionalnosti delovanja; - stroški za nadzor in koordinacijo izvedbe vseh elektro napeljav, ki so predmet končne instalacije proizvoda (senčila, vrata, okna,…); - izdelava montažnih skic in detajlov za izvedbo v dogovoru z vodjo gradnje in nadzornikom; - izdelava in predstavitev vzorcev v ustrezni velikosti za potrditev projektanta, nadzornika in investitorja; - zagotavljanje varnosti in zdravja pri delu, zlasti izvajanje vseh del, ki izhajajo in ukrepov, ki izhajajo iz določil veljavnih predpisov varstva pri delu in zahtev Varnostnega načrta;- stroški garancij, ki jih mora izvajalec predložiti naročniku. | The following must also be included or taken into account in the uniform prices for individual items: - preparation of prefabricated technical documentation, construction details and all other necessary workshop documentation (architectural, civil, electrical, mechanical, exterior and landscaping) and obtaining the mandatory approval of the designer, the supervisor and the investor; - elimination of all types of installation conflicts by carrying out the necessary relocation of installations and their coordination at the installation site, all to the extent that it does not affect the design solution or the type of installation or equipment; - ensuring the completeness of electrical installation systems in the automation sector to achieve their full operational functionality; - the cost of supervising and coordinating the installation of all the electrical installations that are the subject of the final installation of the product (blinds, doors, windows, etc.); - preparation of erection drawings and details for implementation in agreement with the construction manager and supervisor; - production and presentation of samples in appropriate sizes for the approval of the designer, the supervisor and the investor; - ensuring health and safety at work, in particular the implementation of all the works arising from and the measures resulting from the provisions of the applicable occupational safety regulations and the requirements of the Safety Plan; - the cost of the guarantees to be provided by the contractor to the client.
0.1.18 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - strošek vodje del glavnega izvajalca, ki bo izvajal tudi koordinacijo s podizvajalci in z drugimi izvajalci, ki jih bo izbral naročnik in bo opravljal delo vodje gradbišča; - koordinacija del z ostalimi izvajalci oz. podizvajalci del, projektantom, nadzornikom in investitorjem pri medsebojnem usklajevanju organizacije gradbišča in časovnega načrta del ter pri usklajevanju izdelave plana montaže, potrjenih s strani vseh udeležencev gradnje; - stroški koordinacije, sodelovanja in usklajevanja z dobavitelji tehnološke, laboratorijske, eksperimentalne in vse ostale pohištvene ter multimedijske opreme ter z vsemi ostalimi dobavitelji oz. podizvajalci na objektu; - stroški izdelave situacij; - stroški zavarovanja objekta v času izvedbe del in delavcev ter materiala na gradbišču v času izvajanja del, od začetka del do pridobitve uporabnega dovoljenja za objekt. Zavarovanje mora biti sklenjeno pri ustrezni zavarovalni družbi najmanj v višini pogodbene vrednosti ali v zakonsko predpisani vrednosti (v kolikor zavarovanje v višini pogodbene vrednosti presega zakonsko dovoljeno), za ves čas trajanja izvedbe del do uspešne primopredaje objekta; - preizkušanje kvalitete materiala, ki se vgrajuje in dokazovanje kvalitete s certifikati oz. tehničnimi soglasji; - izvedba vseh zahtevanih testov in preizkusov (npr. tlačni preizkusi, termografski pregledi, meritve elektromagnetnega sevanja, hrupa, itd.), poskusnega obratovanja celotnega objekta s poudarkom na vseh inštalacijah ter izvajanje predpisanega monitoringa v skladu s Poročilom o vplivih na okolje (pred gradnjo, med gradnjo in po končani gradnji); - izdelava izkaza požarne varnosti, vključno s sprotnim spremljanjem gradnje in izvajanjem požarnovarnostnih zahtev ter izdelava Požarnega reda z obveznimi prilogami; - izdelava Izkaza zaščite pred hrupom v stavbah; - izdelava Izkaza energijskih lastnosti stavbe in energetske izkaznice; - sodelovanje z izvajalci gradbenega in projektantskega nadzora in investitorjem za izvedbo tehničnega pregleda in priprava primopredaje, ki mora vsebovati vso zahtevano dokumentacijo, predvsem pa: izjave o skladnosti, požarni izkaz in ostale izkaze ter obvezne tabele, dokazilo o zanesljivosti objekta (DZO), certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo in vzdrževanje ter vse ostale dokumente v skladu s predpisi in pogodbenimi določili. | The following must also be included or taken into account in the uniform prices of the individual items: - the cost of a works manager for the main contractor, who will also coordinate with subcontractors and other contractors selected by the client and act as site manager; - coordination of the works with other contractors or subcontractors, the designer, the supervisor and the investor in coordinating the organisation of the construction site and the timetable for the works, and in coordinating the production of an installation plan approved by all the participants in the construction; - the costs of coordination, cooperation and coordination with suppliers of technological, laboratory, experimental and all other furniture and multimedia equipment, as well as with all other suppliers or subcontractors on the site; - the cost of drawing up situations; - the cost of insuring the building during the execution of the works and the workers and materials on site during the execution of the works, from the start of the works until the building has been licensed for occupation. The insurance must be taken out with a suitable insurance company for at least the contract value or the legal value (if the insurance for the contract value exceeds the legal value), for the entire duration of the works until the successful handover of the building; - testing the quality of the material to be installed and proving it with certificates or technical approvals; - carrying out all required tests and trials (e.g. pressure tests, thermographic inspections, electromagnetic radiation measurements, noise measurements, etc.), trial operation of the entire building, with emphasis on all installations, and carrying out the required monitoring in accordance with the Environmental Impact Assessment Report (before, during and after construction); - preparation of a fire safety statement, including ongoing monitoring of construction and implementation of fire safety requirements, and preparation of a Fire Safety Order with mandatory annexes; - preparation of a Noise Protection Statement for buildings; - preparation of the Building Energy Performance Report and Energy Performance Certificate; - cooperation with the construction and design supervision contractors and the investor to carry out the technical inspection and prepare the handover, which must include all the required documentation, in particular: declarations of conformity, fire and other statements and mandatory tables, proof of reliability of the building (DZO), certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use and maintenance, and all other documents in accordance with the regulations and the contractual provisions.
0.1.19 | V enotnih cenah posameznih postavk, ki se nanašajo na opremo in posamezne sisteme, mora biti zajeto oz. upoštevano tudi naslednje: - dobava oz. transport, - stroški za vse delovne stroje za dvigovanje bremen in delovne košare za dostope do delovišč; - morebitni stroški povzročeni upravljavcem GJI, ki bi nastali v zvezi s predmetno gradnjo; - montaža, vključno s pomožnim montažnim materialom (vezni, tesnilni in pritrdilni material, sidra, nosilni profili, podkonstrukcije in podobno) in navodili proizvajalca, - odprava vseh kolizij sistemov s stenami in med sistemi, - izvedba vseh potrebnih tesnjenj, - priključitev in nastavitve, vključno z morebitnim kalibriranjem, - zagon, testiranje in meritve, vključno s poročili, - šolanje uporabnikov oz. vzdrževalnega osebja za uporabo in vzdrževanje sistemov, - navodila za obratovanje in vzdrževanje, - vsi potrebni certifikati, izjave o skladnosti oz. potrdila ter - vsa druga pomožna dela in material, da se zagotovi funkcionalnost posamezne postavke popisa. | The following must also be included or taken into account in the uniform prices for individual items relating to equipment and individual systems: - delivery/transport, - the cost of all lifting machines and work baskets for access to work sites; - any costs incurred to the operators of utility infrastructure (GJI) in connection with the subject construction; - installation, including ancillary installation materials (bonding, sealing and fixing materials, anchors, support profiles, substructures, etc.) and manufacturer's instructions, - eliminating all system-to-wall and system-to-system collisions, - all necessary sealing work, - connection and set-up, including calibration if necessary, - commissioning, testing and measurements, including reports, - training users or maintenance staff in the use and maintenance of the systems, - operating and maintenance instructions, - any necessary certificates, declarations of conformity or attestations; and - all other ancillary works and materials to ensure the functionality of each inventory item.
0.1.20 | Vsi odri morajo biti upoštevani v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All scaffolding must be included in the uniform prices of the items listed, except where specifically mentioned.
0.1.21 | Vsi delovni in pomožni odri, lestve in ostala potrebna pomožna sredstva, kot tudi čiščenje vseh elementov po končanih delih, mora biti upoštevano v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All working and auxiliary scaffolding, ladders and other necessary ancillaries, as well as the cleaning of all elements after completion of the works, shall be included in the uniform prices of the items listed, except those specifically mentioned.
0.1.22 | Delavniško dokumentacijo za vse nosilne jeklene konstrukcije in podkonstrukcije izdela izvajalec, strošek izdelave delavniške dokumentacije se upošteva v ponujenih cenah in se ne obračuna posebej. | The cost of the shop drawings for all steelwork and substructures shall be included in the prices quoted and shall not be charged separately.
0.1.23 | V enotnih cenah postavk mora biti vključeno tudi vgrajevanje vseh instalacijskih razvodov v opaže armirano betonskih elementov in izdelava prehodov inštalacij ter dodatno izrezovanje utorov in prebojev v kamnite, zidane ali armirano-betonske stene, ponovno demontiranje in montiranje vseh vrst montažnih sten, vsa dodatna dela za zagotavljanje primernih križanj med posameznimi instalacijskimi vodi, izdelava vseh vrst ojačitev konstrukcij in podobna dela, ki zagotavljajo kakovostno vgradnjo vseh vrst instalacijskih vodov in niso posebej navedena v popisu GOI del. V ponudbi morajo biti upoštevana vsa drobna strojna in elektro instalacijska dela in transporti. | The installation of all installation ducts in the formwork of reinforced concrete elements and the construction of installation penetrations, as well as the additional cutting of grooves and penetrations in stone, masonry or reinforced concrete walls, the reassembly and reinstallation of all types of prefabricated walls, all additional work to ensure adequate crossings between individual installation ducts, the construction of all types of structural reinforcement and similar work to ensure the quality installation of all types of installation ducts and not specifically mentioned in the BoQ of the Construction, installation and finishing works (GOI) shall also be included in the uniform prices of the items. The tender shall take into account all minor mechanical and electrical installation work and transport.
0.1.24 | Vsi kovinski elementi in konstrukcije, ki bi lahko bili izpostavljeni atmosferskim in ostalim korozijskim vplivom, morajo biti ustrezno protikorozijsko zaščiteni. | All metallic elements and structures that could be exposed to atmospheric and other corrosive influences must be adequately protected against corrosion.
0.1.25 | Za vse večje jeklene dele se skladno s predpisi, izdelajo ustrezne ozemljitve, nevidno pritrjene in speljane na splošno ozemljitev objekta. | For all major steel parts, appropriate earth connections shall be made in accordance with the regulations, invisibly attached and connected to the general earth of the building.
0.1.26 | Za vse vidne elemente in serijske elemente je obvezna predhodna uskladitev obdelav, barv in materialov s projektantom na podlagi dostavljenih vzorcev v ustrezni velikosti. Obvezna je preveritev dejanskih mer na licu mesta in posledična prilagoditev elementov in njihove montaže. | For all visible elements and serial elements, it is mandatory to coordinate the finishes, colours and materials with the designer beforehand on the basis of the supplied samples in the appropriate size. It is mandatory to check the actual dimensions on site and to adjust the elements and their installation accordingly.
0.1.27 | Dimenzije obrtniških izdelkov in količine je potrebno pred naročanjem preveriti na objektu. Potrebna je uskladitev vseh elementov (kljuke, okovje, detajlne konstrukcije in obdelave, itd.) s projektantom, nadzornikom in investitorjem. Izvajalec je dolžan pred izdelavo predložiti projektantu v potrditev ustrezne delavniške načrte in detajle. | The dimensions of the workmanship and quantities must be checked on site before ordering. All elements (hooks, fittings, detailed construction and finishes, etc.) must be coordinated with the designer, the supervisor and the investor. The contractor is obliged to submit the relevant workshop plans and details to the designer for approval before manufacture.
0.1.28 | V posameznih postavkah popisa so navedeni proizvajalci in/ali tipi posameznih sistemov, materialov ali opreme, s čimer so zgolj natančno opredeljene zahtevane tehnične lastnosti. Izvajalec del lahko ponudi nadomesten sistem, material ali opremo drugega proizvajalca in tipa, pri čemer morajo biti tehnične lastnosti ponujenega sistema, materiala ali opreme enakovredne ali boljše od opredeljenih v popisu, dimenzijsko pa ne smejo presegati projektiranih dimenzij. Vse funkcijske in tehnične karakteristike nadomestnih sistemov, materialov ali opreme mora izvajalec dokazati z ustrezno dokumentacijo. Vse morebitne posledice zaradi spremembe sistemov, materialov ali opreme vključno z morebitnimi spremembami oz. dopolnitvami BIM modelov in projektne dokumentacije, stroškovno in časovno bremenijo izvajalca. | The individual items of the Inventory shall specify the manufacturers and/or types of the individual systems, materials or equipment, thereby merely specifying the required technical characteristics. The Contractor may offer a substitute system, material or equipment of a different manufacturer and type, provided that the technical characteristics of the offered system, material or equipment shall be equivalent to or better than those specified in the BoQ, and shall not exceed the design dimensions. All functional and technical characteristics of the substitute systems, materials or equipment shall be demonstrated by the Contractor with appropriate documentation. Any consequences resulting from changes to systems, materials or equipment, including any changes or additions to the BIM models and project documentation, shall be borne by the Contractor in terms of cost and time.
0.1.29 | Vsako zamenjavo, uporabo in končni izbor nadomestnih sistemov, materialov, proizvodov in opreme morajo obvezno in pravočasno (pred dobavo in vgradnjo) pisno potrditi projektant (vseh sodelujočih strok), nadzornik in investitor. | Any replacement, use and final selection of alternative systems, materials, products and equipment must be approved in writing by the designer (of all disciplines involved), the supervisor and the investor in a timely manner (prior to delivery and installation).
0.1.30 | Izvajalec mora v ponudbeno ceno vključiti tudi: - ves čas gradnje sprotno beleženje sprememb oz. odstopanj od PZI dokumentacije, vključno z izdelavo tekstualnega opisa sprememb, - pripravo podlog na nivoju PZI, ki so potrebne za posodobitev oz. uskladitev BIM modela z izvedenim stanjem (LOD 500) in izdelavo projektne dokumentacije izvedenih del (PID), - mesečno predajanje potrjenih sprememb opreme in materiala, ki vplivajo na BIM model, v formatu IFC, - vzdrževanje in uporabljanje pri izvedbi zadnje veljavne revizije PZI dokumentacije, vključno z dopolnitvami PZI načrtov, ki so nastali zaradi sprememb med gradnjo. | The contractor must also include in the tender price: - keeping a record of changes or deviations from the construction documentation (PZI) throughout construction, including a textual description of the changes, - preparation of the Detailed Design (PZI) level documents required to update or align the BIM model with the as-built condition (LOD 500) and the preparation of the as-built project documentation for the works (PID), - monthly submission of approved equipment and material changes affecting the BIM model in IFC format, - maintenance and use in the execution of the last valid revision of the construction documentation (PZI), including additions to the construction design documentation (PZI) resulting from changes during construction.

## 0.2_Uvod-DGNB
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
0.2 | SPLOŠNI TEHNIČNI POGOJI ZA PODROČJE DGNB CERTIFICIRANJA | GENERAL TECHNICAL CONDITIONS FOR DGNB CERTIFICATION
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic entity with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
| Splošni pogoji za področje DGNB certificiranja predstavljajo dopolnilo splošnim tehničnim pogojem in ne odpravljajo drugih obveznosti in odgovornosti, ki jih ima izvajalec v skladu s predpisi in pogodbo. | The General Conditions for DGNB Certification are complementary to the General Technical Conditions and do not exclude other obligations and responsibilities that the Contractor has under the Regulations and the Contract.
0.2.1 | Izvajalec mora v svojih ponudbah upoštevati, da se bo objekt certificiral v skladu z zahtevami DGNB sistema certificiranja trajnostne gradnje, ter pravočasno (vsaj 60 dni pred vgradnjo posameznega produkta) dostaviti vso ustrezno dokumentacijo za vse v ponudbi zajete materiale, elemente in opremo. Zahtevana je uporaba materialov, elementov ali opreme, ki so okolju in ljudem prijazni, energetsko učinkoviti in obenem ustrezajo zahtevam DGNB sistema. Zahtevan nivo certifikata je: ZLATI CERTIFIKAT | The Contractor shall take into account in its tenders that the building will be certified in accordance with the requirements of the DGNB Sustainable Building Certification Scheme and shall deliver all relevant documentation for all materials, elements and equipment included in the tender in a timely manner (at least 60 days before the installation of each product). The use of materials, elements or equipment that are environmentally and human friendly, energy efficient and at the same time meet the requirements of the DGNB system is required. The required level of certification is: GOLD CERTIFICATE
0.2.2 | Podrobnejši opis DGNB sistema in navodila za posamezne kriterije so dostopna v dokumentu"DGNB Criteria Set New Construction Buildings, Version 2020 International", ki je na voljo na DGNB spletni strani https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria | A more detailed description of the DGNB system and guidance on the individual criteria is available in the document "DGNB Criteria Set New Construction Buildings, Version 2020 International", available on the DGNB website https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria
0.2.3 | Izvajalec mora v svojih ponudbah upoštevati, da je potrebno skladno z določili DGNB certifikacijskega sistema, pravočasno (pred pričetkom gradnje) dostaviti vso ustrezno dokumentacijo, za vse v ponudbi zajete materiale, elemente in opremo (tehnični list, varnostni list, izjava o lastnostih, tehnična navodila za ravnanje, servisiranje, vzdrževanje,...) v slovenskem jeziku. Vgradnja kakršnihkoli materialov, elementov ali opreme, se izvede zgolj na podlagi predhodne preveritve posredovane dokumentacije in obenem potrditve s strani nadzornika. | The Contractor must take into account in its tenders that, in accordance with the provisions of the DGNB certification system, all relevant documentation for all materials, elements and equipment included in the tender (technical data sheet, safety data sheet, declaration of properties, technical instructions for handling, servicing, maintenance,...) must be delivered on time (prior to the start of construction) in the Slovene language (in accordance with the provisions of the DGNB certification system). The installation of any materials, elements or equipment shall be subject to prior checking of the submitted documentation and, at the same time, to the approval of the Supervisor.
0.2.4 | Izbrani materiali, elementi, naprave, sistemi in oprema morajo prispevati k večji trajnosti stavbe v smeri zagotavljanja energetske učinkovitosti, ekonomičnega in enostavnega vzdrževanja ter čiščenja, dolge življenjske dobe, uporabe okolju prijaznih materialov ipd. | The materials, elements, appliances, systems and equipment chosen must contribute to the sustainability of the building in terms of energy efficiency, economic and easy maintenance and cleaning, long lifetime, use of environmentally friendly materials, etc.
0.2.5 | Predloženi dokumenti za vse uporabljene materiale, elemente in opremo morajo izpolnjevati zahteve najmanj kakovostne stopnje QS3 (zaželeno QS4), iz dokumenta: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001) | The documents submitted for all materials, components and equipment used shall meet the requirements of at least quality level QS3 (preferably QS4) of the document DGNB Quality Grades for Materials, Components and Equipment (JULFS--7X9001)
0.2.6 | V kolikor izbrani materiali oz. elementi, navedeni v posameznih postavkah, ne ustrezajo vsaj kakovostni stopnji QS3 iz seznama: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), je izvajalec dolžan na to opozoriti projektanta, nadzor in investitorja ter podati predlog ustreznega materiala oz. elementa. | If the selected materials or elements listed in the individual items do not meet at least quality level QS3 of the list of DGNB quality classes for materials, elements and equipment (JULFS--7X9001), the Contractor shall draw this to the attention of the Designer, the Supervisor and the Investor, and shall make a proposal for a suitable material or element.
0.2.7 | Izvajalec lahko v svoji ponudbi predlaga alternativne produkte in rešitve glede na predvidene s projektom, pod pogojem, da le-te prav tako izpolnjujejo vse navedene zahteve. Pri morebitnih predlaganih alternativnih produktih oz. rešitvah je potrebno upoštevati najmanj enake ali boljše lastnosti v smislu življenjske dobe, obstojnosti, ter enostavnosti in stroška čiščenja ter vzdrževanja v primerjavi s projektom predpisanimi rešitvami. Za alternativne rešitve izvajalec pridobi soglasje projektanta, nadzornika in investitorja pred pričetkom gradnje. | The Contractor may propose alternative products and solutions to those envisaged by the project in its tender, provided that they also meet all the requirements set out above. Any alternative products or solutions proposed shall have at least the same or better characteristics in terms of service life, durability, and ease and cost of cleaning and maintenance compared to the solutions envisaged by the project. For alternative solutions, the contractor shall obtain the agreement of the designer, the supervisor and the investor before starting construction.
0.2.8 | Izvajalec med gradnjo dnevno beleži vsa eventualna odstopanja od PZI projektne dokumentacije ter podatke pravočasno posreduje naročniku, nadzoru in projektantu. Potrjene spremembe vnese v podlage za izdelavo PID in posodobitev BIM modelov. | During construction, the Contractor shall record on a daily basis any deviations from the Detailed Design documentation (PZI) and shall provide the information to the Client, Supervision and the Designer in a timely manner. Confirmed changes shall be entered into the basis for the As-built documentation (PID) and BIM model updates.
0.2.9 | Izvajalec med gradnjo sproti izpolnjuje Seznam vseh konstrukcijskih sestav s pripadajočimi vgrajenimi gradbenimi materiali in dokumentira naslednje podatke o vgrajenih materialih (v slovenskem jeziku): - Varnostni list - Tehnični list - Izjavo o lastnostih (če je relevantno) - Izkazovanje morebiti obstoječega okoljskega certifikata (Tip I - okoljski znak ali Tip III - okoljska produktna deklaracija /EPD) - Izjavo proizvajalca ali dobavitelja, da produkt ustreza zahtevam ENV1.2 - Tehnična navodila za ravnanje, servisiranje, vzdrževanje oziroma ostale, z zakonom predpisane dokumente in dokumentacijo. | During construction, the Contractor shall keep a List of all structural assemblies with their associated construction materials and document the following information on the materials installed (in Slovene language): - Safety Data Sheet - Technical Data Sheet - Declaration of performance (if applicable) - Demonstration of any existing environmental certification (Type I - Ecolabel or Type III - Environmental Product Declaration /EPD) - A declaration by the manufacturer or supplier that the product complies with the requirements of ENV1.2 - Technical instructions for handling, servicing, maintenance or other documents and documentation required by law.
0.2.10 | Za vse vgrajene bistvene tehnične sisteme mora izvajalec zagotoviti obstoj pooblaščenega servisa, ki deluje na območju Republike Slovenije, da ima investitor možnost skleniti ustrezno pogodbo o vzdrževanju. Med bistvene tehnične sisteme sodijo npr.: sistemi ogrevanja in hlajenja, priprava tehnoloških medijev, prezračevanje in klimatizacija, sistemi detekcije in gašenja požara, sistemi tehničnega varovanja, BMS in CNS sistemi upravljanja stavbe, razsvetljava, komunikacijski in WI-FI sistemi,... | For all installed essential technical systems, the contractor must ensure the existence of an authorised service centre operating in the territory of the Republic of Slovenia, so that the investor has the possibility of concluding an appropriate maintenance contract. The essential technical systems include, for example: heating and cooling systems, technological media preparation, ventilation and air conditioning, fire detection and extinguishing systems, technical security systems, BMS and CNS building management systems, lighting, communication and WI-FI systems,...
0.2.11 | Zaželeno je, da imajo uporabljeni elementi in materiali okoljsko oznako Tip I. (kot npr. ENCODE, BLUE ANGEL, ipd...). | It is preferable that the elements and materials used have a Type I environmental label (such as ENCODE, BLUE ANGEL, etc...).
0.2.12 | Izvajalec bo za elemente iz lesa moral dokazovati izvor z navedbo izvorne države in tipa lesa, FSC / PEFC certifikat z dodatnim pripadajočim potrdilom Chain of custody-trgovski certifikat dobavitelja - ta se dokazuje z dobavnicami, računi ali enakovredno. Za izdelke iz naravnega kamna iz EU držav je potrebna deklaracija, da je izvor in procesiranje teh izdelkov v celoti v EU državah. Za izdelke iz naravnega kamna, ki prihajajo iz držav izven EU, je potrebno predložiti dokazilo o izpolnjevanju ILO konvencije 182, ki vključuje neodvisna inšpekcijska poročila. | For wood elements, the contractor will be required to provide proof of origin, indicating the country of origin and the type of wood, FSC/PEFC certification with an additional Chain of Custody certificate - the supplier's trade certificate - this shall be evidenced by delivery notes, invoices or equivalent. For natural stone products from EU countries, a declaration that the sourcing and processing of these products is entirely in EU countries is required. For natural stone products from non-EU countries, proof of compliance with ILO Convention 182, including independent inspection reports, is required.
0.2.13 | Izobraževanje udeležencev pri gradnji Izvajalec je dolžan vse udeležence pri gradnji podrobneje seznaniti tudi z relevantnimi koncepti, študijami, elaborati, ki opredelujejo trajnostni način gradnje za naslednja področja: - zaščita pred hrupom (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)) - zaščita pred prašenjem - zaščita tal in podzemne vode (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)), Analiza tveganja za onesnaženje vodnega telesa podzemne vode št. 0346-023/2023, maj 2023 (Geološko projektiranje d.o.o.)) - ravnanje z gradbenimi odpadki (Načrt gospodarjenja z gradbenimi odpadki) Izobraževanja se izvajajo skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.1 1.2, 2.2, 3.2 in 4.2 Training for the parties implementing the construction work | Training of construction participants The contractor is also obliged to inform all construction participants in detail about relevant concepts, studies, elaborations defining sustainable construction methods for the following areas: - noise protection (Environmental Impact Assessment Report No 100123-11523, dated 11.5.2023, supplemented on 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.)) - dust protection - protection of soil and groundwater (Environmental Impact Assessment Report No. 100123-11523, dated 11.5.2023, supplemented 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.), Risk analysis for contamination of the groundwater No. 0346-023/2023, May 2023 (Geološko projektiranje d.o.o.)) - construction waste management (Construction Waste Management Plan) The training shall be carried out in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.1 1.2, 2.2, 3.2 and 4.2 Training for the parties implementing the construction work
0.2.14 | Navodila za obratovanje in vzdrževanje objekta Izvajalec pripravi Navodila za obratovanje in vzdrževanje objekta skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilih: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual | Instructions for the operation and maintenance of the facility The Contractor shall prepare the Operation and Maintenance Instructions for the Facility in accordance with the applicable Slovenian legislation and the DGNB System Instructions specified in the Criteria: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual
0.2.15 | Meritve kontrole kakovosti gradnje Izvajalec mora upoštevati, da se bodo po koncu gradnje izvedle naslednje meritve: - meritve zrakotesnosti - meritve s termokamero (termografija) - meritve akustike - meritve zvočne zaščite ovoja stavbe - meritve zvočne zaščite ločilnih elementov med posameznimi prostori različnih namembnosti - meritve udarnega zvoka - meritve vlažnosti vgrajenih elementov, pred vgradnjo finalnih tlakov - test odvoda dima in toplote Meritve morajo opraviti ustrezno usposobljeni preskusni organi ali strokovnjaki ter rezultate oceniti in primerjati z zahtevami. Obseg opravljenih meritev mora biti sorazmeren z velikostjo zgradbe in mora ustrezno odražati cilj preverjanja kakovosti zgradbe. Smiselno je, da izvajalec del tekom gradnje za sprotno kontrolo kakovosti vgrajenih materialov, elementov in opreme, sam izvaja meritve. Končne meritve (ob primopredaji) izvede tretja oseba kot neodvisna potrditev doseganja zahtev. Meritve se izvajajo skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 2. Quality control measurements | Construction quality control measurements The contractor must take into account that the following measurements will be carried out after completion of the construction: - airtightness measurements - thermal camera measurements (thermography) - acoustics measurements - measurements of the sound insulation of the building envelope - measurements of the sound insulation of the separating elements between different rooms of different uses - impact sound measurements - moisture measurements of the installed elements, prior to the installation of the final flooring - smoke and heat extraction test The measurements shall be carried out by suitably qualified test bodies or experts and the results evaluated and compared with the requirements. The extent of the measurements carried out shall be proportionate to the size of the building and shall adequately reflect the objective of the building quality verification. It is reasonable for the contractor to carry out his own measurements during construction to check the quality of the materials, elements and equipment installed. Final measurements (at handover) are carried out by a third party as an independent confirmation of compliance with the requirements. The measurements shall be carried out in accordance with the applicable Slovenian legislation and the DGNB system instructions specified in the benchmark: PRO 2.2 2. Quality control measurements
0.2.16 | Zagotavljanje kakovosti za uporabljene gradbene proizvode Izvajalec mora zagotavljati izvajanje primerjav med definiranim in dejansko uporabljenim materialom, elementom ali opremo skladno seznamom: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), vključno z dokazno dokumentacijo ugotovitev primerjav ter skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 3.1 Quality assurance for the used construction products | Quality assurance for the construction products used The Contractor shall ensure that comparisons are made between the defined and the actual material, element or equipment used in accordance with the list: DGNB Quality Grades of Installed Materials, Elements and Equipment (JULFS--7X9001), including supporting documentation of the findings of the comparisons, and in accordance with the DGNB system instructions defined in the Criterion: PRO 2.2 3.1 Quality assurance for the used construction products
0.2.17 | Zaščita pred vlago Izvajalec predloži dokumentacijo, ki dokazuje, da je bil izveden program prezračevanja, prilagojen stavbi, s čimer se zagotovi pogoje, da so vgrajeni gradbeni elementi ustrezno suhi, skladno z navodili DGNB opredeljenimi v merilu: PRO 2.2 4.1 Mould prevention | Protection against moisture The Contractor shall provide documentation demonstrating that a building-specific ventilation programme has been implemented to ensure that the building elements installed are adequately dry, in accordance with the DGNB guidelines specified in the criteria: PRO 2.2 4.1 Mould prevention
0.2.18 | Preizkusi delovanja sistemov Izvajalec sodeluje pri izvedbi predhodnega in končnega preizkusa delovanja vseh bistvenih tehničnih komponent stavbe in pripravi ustrezne dokazne dokumentacije ter pri usposabljanju vzdrževalcev/upravljalcev stavbe, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators | System performance tests The Contractor shall be involved in the performance of the preliminary and final performance tests of all essential technical components of the building and the preparation of the relevant supporting documentation, as well as in the training of the maintenance/management staff of the building, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators
0.2.19 | Poročilo o zagonu objekta Izvajalec sodeluje pri pripravi končnega poročila o zagonu objekta, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 5.1 Creation of a detailed final report | Commissioning report The Contractor shall be involved in the preparation of the final commissioning report, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 5.1 Creation of a detailed final report
0.2.20 | Koncept celovitega delovanja sistemov v stavbi Izvajalec sodeluje pri procesu implementiranja stalnega nadzora in nastavitev delovanja stavbe ter usposabljanju vzdrževalcev/upravljalcev stavbe. Navedeno se izvede v skladu z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 6.1 Creation and handover of an integral operating concept | The concept of integrated building systems The contractor is involved in the process of implementing the building's continuous monitoring and settings and training the building's maintenance/management staff. This shall be done in accordance with the DGNB system instructions defined in the benchmark: PRO 2.3 6.1 Creation and handover of an integral operating concept
0.2.21 | Prilagoditev nastavitev sistemov po začetni fazi uporabe objekta Izvajalec sodeluje pri ponovnem pregledu delovanja vseh bistvenih tehničnih sistemov ter eventualni ponovni prilagoditvi teh sistemov s strani strokovnjaka oz. (neodvisne) tretje osebe. Postopek se izvede po približno 10–14 mesecih po zaključku gradnje, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 7.1 Readjustment of the system following initial operating phase | Adjusting system settings after the initial phase of use of the building The Contractor shall be involved in the re-examination of the functioning of all essential technical systems and the possible re-adjustment of these systems by an expert or (independent) third party. The procedure shall be carried out approximately 10-14 months after completion of construction, in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.3 7.1 Readjustment of the system following initial operating phase

## 3.7.0_Rekapitulacija
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
| REKAPITULACIJA STROŠKOV ELEKTRO DEL | COST SUMMARY OF ELECTRICAL WORKS
| 3 NAČRT S PODROČJA ELEKTROTEHNIKE | 3 DOCUMENTATION IN THE FIELD OF ELECTRICAL ENGINEERING
| 3/7 Razsvetljava | 3/7 Lighting
3.7 | ELEKTRO DELA | ELECTRICAL WORKS
3.7.1 | RAZSVETLJAVA | LIGHTING | 0
3.7.2 | ZASILNA RAZSVETLJAVA | EMERGENCY LIGHTING | 0
3.7.3 | OSTALO | OTHER | 0
0
0 | NEPREDVIDENA DELA | UNFORSEEN WORKS | 0
| SKUPAJ ELEKTRO DELA | TOTAL ELECTRICAL WORKS | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT

## 3.7.1_Razsvetljava
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.7 | ELEKTRO DELA | ELECTRICAL WORKS
3.7.1 | RAZSVETLJAVA | LIGHTING |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
1 | RAZSVETLJAVA | LIGHTING
1.1 | -S1 Dobava in montaža nadometne LED svetilke, 3800 lm, 25 W, 840, L1277 mm, DALI, IP66, optika polprosojna PC, ohišje PC, konektorski priklop(brez odpiranja), komplet z obešaljnim priborom za dolžino do 3m, kot naprimer 5700, Intra Lighting | -S1 Supply and installation of overhead LED luminaire, 3800 lm, 25 W, 840, L1277 mm, DALI, IP66, optics semi-transparent PC, housing PC, connector connection (without opening), complete with hanging accessories for lengths up to 3 m, such as for example 5700, Intra Lighting | kpl | 458 |  | 0
1.2 | -S3 Dobava in montaža nadometne LED svetilke, 7000 lm, 46 W, 840, L1573 mm, DALI, IP66, optika polprosojna PC, ohišje PC, konektorski priklop(brez odpiranja), komplet z obešaljnim priborom za dolžino do 3m, kot naprimer 5700, Intra Lighting | -S3 Supply and installation of overhead LED luminaire, 7000 lm, 46 W, 840, L1573 mm, DALI, IP66, optics semi-transparent PC, housing PC, connector connection (without opening), complete with hanging accessories for lengths up to 3 m, such as for example 5700, Intra Lighting | kpl | 203 |  | 0
1.3 | -S6 Dobava in montaža nadometne linijske LED svetilke, 4500 lm, 45 W, 840, L2525 mm, DALI, IP43, optika mikroprizmatika PMMA, Al ohišje, komplet z obešaljnim priborom za dolžino do 2m, kot naprimer Kalis S 55, Intra Lighting | -S6 Supply and installation of overhead linear LED luminaire, 4500 lm, 45 W, 840, L2525 mm, DALI, IP43, PMMA microprism optics, Al housing, complete with hanging accessories for lengths up to 2 m, e.g. Kalis S 55, Intra Lighting | kpl | 19 |  | 0
1.4 | -S6-A Dobava in montaža nadometne linijske LED svetilke, 3500 lm, 35 W, 840, L1965 mm, DALI, IP43, optika mikroprizmatika PMMA, Al ohišje, komplet z obešaljnim priborom za dolžino do 2m, kot naprimer Kalis S 55, Intra Lighting | -S6-A Supply and installation of overhead linear LED luminaire, 3500 lm, 35 W, 840, L1965 mm, DALI, IP43, PMMA microprism optics, Al housing, complete with hanging accessories for lengths up to 2 m, e.g. Kalis S 55, Intra Lighting | kpl | 4 |  | 0
1.5 | -S9 Dobava in montaža vgradne LED svetilke, 2750 lm, 27 W, 830, D720 mm, h=400mm, DALI, IP43, kot naprimer Pasaža, Intra Lighting | -S9 Supply and installation of recessed LED luminaire, 2750 lm, 27 W, 830, D720 mm, h=400mm, DALI, IP43, as for example Passage, Intra Lighting | kpl | 349 |  | 0
1.6 | -S9A Dobava in montaža vgradne LED svetilke, 2750 lm, 27 W, 830, D720 mm, h=200mm, DALI, IP43, kot naprimer Pasaža, Intra Lighting | -S9A Supply and installation of recessed LED luminaire, 2750 lm, 27 W, 830, D720 mm, h=200 mm, DALI, IP43, as for example Passage, Intra Lighting | kpl | 26 |  | 0
1.7 | -S10 Dobava in montaža nadometne linijske LED svetilke, 1900 lm, 21 W, 930, L845 mm, DALI, IP43, optika mikroprizmatika D22PMMA, Al ohišje, komplet z obešaljnim priborom za dolžino do 2m, kot naprimer Kalis C 55, Intra Lighting | -S10 Supply and installation of overhead linear LED luminaire, 1900 lm, 21 W, 930, L845 mm, DALI, IP43, optics microprismatics D22PMMA, Al housing, complete with hanging accessories for lengths up to 2 m, e.g. Kalis C 55, Intra Lighting | kpl | 32 |  | 0
1.8 | -S12 Dobava in montaža viseče LED svetilke, 13516 lm, 140 W, 940, DALI, IP20, optika mikroprizmatika PMMA, krivulja po shemi v načrtu, komplet z obešaljnim priborom za dolžino do 2m, kot naprimer Wave C/S-sestavljna iz elementov, Intra Lighting | -S12 Supply and installation of suspended LED luminaire, 13516 lm, 140 W, 940, DALI, IP20, optics PMMA microprismatics, curve according to scheme in plan, complete with hanging accessories for lengths of up to 2 m, such as Wave C/S-assembled from elements, Intra Lighting | kpl | 65 |  | 0
1.9 | -S15 Dobava in montaža nadometne LED svetilke, 8700 lm, 55 W, 840, L1163 mm, DALI, IP40, 10°PC-gladka, Al ohišje, komplet z obešaljnim priborom za dolžino do 2m, kot naprimer Sequal C, Intra Lighting | -S15 Supply and installation of overhead LED luminaire, 8700 lm, 55 W, 840, L1163 mm, DALI, IP40, 10°PC-smooth, Al housing, complete with hanging accessories for lengths up to 2 m, e.g. Sequal C, Intra Lighting | kpl | 727 |  | 0
1.10 | -S19 Dobava in montaža viseče LED svetilke, 1000 lm,10 W, 930, D310 mm, DALI, IP43, optika mikroprizmatika PMMA, Al ohišje, komplet z obešaljnim priborom za dolžino do 2m, kot naprimer LONA KLOBUK RV 300, Intra Lighting | -S19 Supply and installation of hanging LED luminaire, 1000 lm,10 W, 930, D310 mm, DALI, IP43, PMMA microprismatic optics, Al housing, complete with hanging accessories for lengths up to 2 m, e.g. LONA KLOBUK RV 300, Intra Lighting | kpl | 1325 |  | 0
1.11 | -S20 Dobava in montaža nadometne LED svetilke, 2500 lm, 32 W, 940, L1682 mm, DALI, IP43, namestitev med lamele - obešeno na njih - spodnji nivo svetilke izravnan s spodnjim nivojem lamel, dodati nosilček(monter), kot naprimer Intra Rylo Pro, Intra Lighting | -S20 Supply and installation of overhead LED luminaire, 2500 lm, 32 W, 940, L1682 mm, DALI, IP43, installation between slats - suspended from them - lower luminaire level with lower slat level, add bracket (installer), e.g. Intra Rylo Pro, Intra Lighting | kpl | 473 |  | 0
1.12 | -S21 Dobava in montaža nadometne LED svetilke, 2500 lm, 32 W, 940, L1962 mm, DALI, IP43, namestitev med lamele - obešeno na njih - spodnji nivo svetilke izravnan s spodnjim nivojem lamel, dodati nosilček(monter), kot naprimer Intra Rylo Pro, Intra Lighting | -S21 Supply and installation of overhead LED luminaire, 2500 lm, 32 W, 940, L1962 mm, DALI, IP43, installation between slats - suspended from them - lower luminaire level with lower slat level, add bracket (installer), e.g. Intra Rylo Pro, Intra Lighting | kpl | 200 |  | 0
1.13 | -S21-A Dobava in montaža nadometne LED svetilke, 2500 lm, 32 W, 940, L2242 mm, DALI, IP43, namestitev med lamele - obešeno na njih - spodnji nivo svetilke izravnan s spodnjim nivojem lamel, dodati nosilček(monter), kot naprimer Intra Rylo Pro, Intra Lighting | -S21-A Supply and installation of overhead LED luminaire, 2500 lm, 32 W, 940, L2242 mm, DALI, IP43, installation between slats - suspended from them - lower luminaire level with lower slat level, add bracket (installer), e.g. Intra Rylo Pro, Intra Lighting | kpl | 661 |  | 0
1.14 | -S23 Dobava in montaža nadometne LED svetilke, 640 lm, 6 W, 940, DALI, IP20, ohišje kovinsko, optika 62°,black , 100 x 100 x 100 mm + nosilec za obešanje na lamelnin strop po arhitekturi, spodnji nivo svetilke in lamele izravnana, kot naprimer Cub, Intra Lighting | -S23 Supply and installation of overhead LED luminaire, 640 lm, 6 W, 940, DALI, IP20, metal housing, optics 62°,black , 100 x 100 x 100 mm + bracket for hanging on architectural ceiling slats, lower luminaire level and slats levelled, e.g. Cub, Intra Lighting | kpl | 12 |  | 0
1.15 | -S26.1 Dobava in montaža viseče LED svetilke, krivulja po shemi v načrtu, 46847 lm, 490 W, 930, DALI, IP20, komplet z obešaljnim priborom za dolžino do 2m, kot naprimer Gyon Line C/S , Wave C/S, Intra Lighting | -S26.1 Supply and installation of LED pendant luminaire, curve according to diagram in plan, 46847 lm, 490 W, 930, DALI, IP20, complete with hanging accessories for lengths up to 2 m, e.g. Gyon Line C/S , Wave C/S, Intra Lighting | kpl | 1 |  | 0
1.16 | -S26.2 Dobava in montaža viseče LED svetilke, krivulja po shemi v načrtu, 45840 lm, 479 W, 930, DALI, IP20, komplet z obešaljnim priborom za dolžino do 2m, kot naprimer Gyon Line C/S , Wave C/S, Intra Lighting | -S26.2 Supply and installation of LED pendant luminaire, curve according to diagram in plan, 45840 lm, 479 W, 930, DALI, IP20, complete with hanging accessories for lengths up to 2 m, e.g. Gyon Line C/S , Wave C/S, Intra Lighting | kpl | 1 |  | 0
1.17 | -S26.3 Dobava in montaža viseče LED svetilke, krivulja po shemi v načrtu, 64574 lm, 673 W, 930, DALI, IP20, komplet z obešaljnim priborom za dolžino do 2m, kot naprimer Gyon Line C/S , Wave C/S, Intra Lighting | -S26.3 Supply and installation of LED pendant luminaire, curve as shown in plan, 64574 lm, 673 W, 930, DALI, IP20, complete with hanging accessories for lengths up to 2 m, e.g. Gyon Line C/S , Wave C/S, Intra Lighting | kpl | 1 |  | 0
1.18 | -S26.4 Dobava in montaža viseče LED svetilke, krivulja po shemi v načrtu, 46847 lm, 490 W, 930, DALI, IP20, komplet z obešaljnim priborom za dolžino do 2m, kot naprimer Gyon Line C/S , Wave C/S, Intra Lighting | -S26.4 Supply and installation of LED pendant luminaire, curve according to diagram in plan, 46847 lm, 490 W, 930, DALI, IP20, complete with hanging accessories for lengths up to 2 m, e.g. Gyon Line C/S , Wave C/S, Intra Lighting | kpl | 1 |  | 0
1.19 | -S26.5 Dobava in montaža viseče LED svetilke, krivulja po shemi v načrtu, 58491 lm, 613 W, 930, DALI, IP20, komplet z obešaljnim priborom za dolžino do 2m, kot naprimer Gyon Line C/S , Wave C/S, Intra Lighting | -S26.5 Supply and installation of LED pendant luminaire, curve according to diagram in plan, 58491 lm, 613 W, 930, DALI, IP20, complete with hanging accessories for lengths up to 2 m, e.g. Gyon Line C/S , Wave C/S, Intra Lighting | kpl | 1 |  | 0
1.20 | -S26.6 Dobava in montaža viseče LED svetilke, krivulja po shemi v načrtu, 23884 lm, 256 W, 930, DALI, IP20, komplet z obešaljnim priborom za dolžino do 2m, kot naprimer Gyon Line C/S , Wave C/S, Intra Lighting | -S26.6 Supply and installation of LED pendant luminaire, curve as shown in plan, 23884 lm, 256 W, 930, DALI, IP20, complete with hanging accessories for lengths up to 2 m, e.g. Gyon Line C/S , Wave C/S, Intra Lighting | kpl | 1 |  | 0
1.21 | -S26.7 Dobava in montaža viseče LED svetilke, krivulja po shemi v načrtu, 64574 lm, 673 W, 930, DALI, IP20, komplet z obešaljnim priborom za dolžino do 2m, kot naprimer Gyon Line C/S , Wave C/S, Intra Lighting | -S26.7 Supply and installation of LED pendant luminaire, curve as shown in plan, 64574 lm, 673 W, 930, DALI, IP20, complete with hanging accessories for lengths up to 2 m, e.g. Gyon Line C/S , Wave C/S, Intra Lighting | kpl | 1 |  | 0
1.22 | -S26.8 Dobava in montaža viseče LED svetilke, krivulja po shemi v načrtu, 46847 lm, 490 W, 930, DALI, IP20, komplet z obešaljnim priborom za dolžino do 2m, kot naprimer Gyon Line C/S , Wave C/S, Intra Lighting | -S26.8 Supply and installation of LED pendant luminaire, curve according to diagram in plan, 46847 lm, 490 W, 930, DALI, IP20, complete with hanging accessories for lengths up to 2 m, e.g. Gyon Line C/S , Wave C/S, Intra Lighting | kpl | 1 |  | 0
1.23 | -S26.9 Dobava in montaža viseče LED svetilke, krivulja po shemi v načrtu, 38388 lm, 397 W, 930, DALI, IP20, komplet z obešaljnim priborom za dolžino do 2m, kot naprimer Gyon Line C/S , Wave C/S, Intra Lighting | -S26.9 Supply and installation of LED pendant luminaire, curve as shown in plan, 38388 lm, 397 W, 930, DALI, IP20, complete with hanging accessories for lengths up to 2 m, e.g. Gyon Line C/S , Wave C/S, Intra Lighting | kpl | 1 |  | 0
1.24 | -S26.10 Dobava in montaža viseče LED svetilke, krivulja po shemi v načrtu, 46143 lm, 478 W, 930, DALI, IP20, komplet z obešaljnim priborom za dolžino do 2m, kot naprimer Gyon Line C/S , Wave C/S, Intra Lighting | -S26.10 Supply and installation of LED pendant luminaire, curve according to diagram in plan, 46143 lm, 478 W, 930, DALI, IP20, complete with hanging accessories for lengths up to 2 m, e.g. Gyon Line C/S , Wave C/S, Intra Lighting | kpl | 1 |  | 0
1.25 | -S27 Dobava in montaža nadometne LED svetilke, 3400 lm, 44 W, 930, 200x1200 mm, DALI, IP43, optika prizmatika PMMA, komplet z obešaljnim priborom za dolžino do 2m, kot naprimer 216, Intra Lighting | -S27 Supply and installation of overhead LED luminaire, 3400 lm, 44 W, 930, 200x1200 mm, DALI, IP43, PMMA prism optics, complete with hanging accessories for lengths up to 2 m, as for example 216, Intra Lighting | kpl | 61 |  | 0
1.26 | -S29 Dobava in montaža viseče LED svetilke, 6500 lm, 54 W, 930, L2249 mm, DALI, IP40, Al ohišje, komplet z obešaljnim priborom za dolžino do 2m, kot naprimer Trix C/S, Intra Lighting | -S29 Supply and installation of LED pendant luminaire, 6500 lm, 54 W, 930, L2249 mm, DALI, IP40, Al housing, complete with hanging accessories for lengths up to 2 m, e.g. Trix C/S, Intra Lighting | kpl | 28 |  | 0
1.27 | -S30 Dobava in montaža viseče LED svetilke v obliki križa, 3300 lm, 38 W, 930, 1,7 x 1,7 m, DALI, IP20, optika opalna PMMA 120°, Al ohišje, komplet z obešaljnim priborom za dolžino do 2m, kot naprimer Kalis 65 Line C/S X, Intra Lighting | -S30 Supply and installation of LED pendant luminaire in the shape of a cross, 3300 lm, 38 W, 930, 1.7 x 1.7 m, DALI, IP20, PMMA 120° opal optics, Al housing, complete with hanging accessories for lengths up to 2 m, e.g. Kalis 65 Line C/S X, Intra Lighting | kpl | 18 |  | 0
1.28 | -S31 Dobava in montaža nadometne linijske viseče LED svetilke v obliki kvadrata, min 10000 lm, max 140 W, 930, 4 x 4 m, DALI, IP20, optika opalna PMMA 120°, Al ohišje, komplet z obešaljnim priborom za dolžino do 2m, kot naprimer Kalis 65 Line C/S, Intra Lighting | -S31 Supply and installation of a square-shaped LED luminaire, min 10000 lm, max 140 W, 930, 4 x 4 m, DALI, IP20, opal PMMA 120° optics, Al housing, complete with hanging accessories for lengths up to 2 m, e.g. Kalis 65 Line C/S, Intra Lighting | kpl | 4 |  | 0
1.29 | -S33 Dobava in montaža nadometne linijske viseče LED svetilke v obliki kvadrata, min 8000 lm, max 120 W, 930, 2,6 x 2,6 m, DALI, IP20, optika opalna PMMA 120°, Al ohišje, komplet z obešaljnim priborom za dolžino do 2m, kot naprimer Kalis 65 Line C/S, Intra Lighting | -S33 Supply and installation of a square-shaped LED luminaire, min 8000 lm, max 120 W, 930, 2,6 x 2,6 m, DALI, IP20, optic PMMA 120°, Al housing, complete with hanging accessories for lengths up to 2 m, such as Kalis 65 Line C/S, Intra Lighting | kpl | 4 |  | 0
1.30 | -S34 Dobava in montaža nadometne linijske LED svetilke, 2000 lm, 20 W, 930, L1122 mm, DALI, IP20, optika opalna PMMA 120°, Al ohišje, namestitev med lamele - obešeno na njih - spodnji nivo svetilke izravnan s spodnjim nivojem lamel, dodati nosilček(monter), kot naprimer Kalis 65 Line C/S, Intra Lighting | -S34 Supply and installation of overhead linear LED luminaire, 2000 lm, 20 W, 930, L1122 mm, DALI, IP20, PMMA 120° optics, Al housing, installation between louvres - suspended from them - lower luminaire level with lower luminaire level, add bracket (installer), e.g. Kalis 65 Line C/S, Intra Lighting | kpl | 45 |  | 0
1.31 | -S36 Dobava in montaža nadometne linijske LED svetilke, 2800 lm, 29 W, 930, L2616 mm, DALI, IP20, optika mikroprizmatika PMMA, Al ohišje, namestitev med lamele - obešeno na njih - spodnji nivo svetilke izravnan s spodnjim nivojem lamel, dodati nosilček(monter), kot naprimer Kalis 65 Line C/S, Intra Lighting | -S36 Supply and installation of overhead linear LED luminaire, 2800 lm, 29 W, 930, L2616 mm, DALI, IP20, optics PMMA microprismatics, Al housing, installation between slats - suspended from them - lower luminaire level with lower slat level, add bracket (installer), e.g. Kalis 65 Line C/S, Intra Lighting | kpl | 2 |  | 0
1.32 | -S37 Dobava in montaža nadometne linijske LED svetilke, 3000 lm, 33 W, 930, L3085 mm, DALI, IP43, optika mikroprizmatika PMMA, Al ohišje, namestitev med lamele - obešeno na njih - spodnji nivo svetilke izravnan s spodnjim nivojem lamel, dodati nosilček(monter), kot naprimer Kalis 65 Line C/S, Intra Lighting | -S37 Supply and installation of overhead linear LED luminaire, 3000 lm, 33 W, 930, L3085 mm, DALI, IP43, PMMA microprism optics, Al housing, installation between slats - suspended from them - lower luminaire level with lower slat level, add bracket (installer), e.g. Kalis 65 Line C/S, Intra Lighting | kpl | 7 |  | 0
1.33 | -S39 Dobava in montaža nadometne linijske viseče LED svetilke v obliki elipse, 17932 lm, 193 W, 930, DALI, IP20, optika polopalna PC, Al ohišje, komplet z obešaljnim priborom za dolžino do 2m, kot naprimer Gyon Line C/S , Wave C/S, Intra Lighting | -S39 Supply and installation of an ellipse-shaped LED luminaire, 17932 lm, 193 W, 930, DALI, IP20, semi-flush PC optics, Al housing, complete with hanging accessories for lengths up to 2 m, e.g. Gyon Line C/S , Wave C/S, Intra Lighting | kpl | 1 |  | 0
1.34 | -S43 Dobava in montaža nadometne stropne LED svetilke, 1556 lm, 15,8 W, 930, 112x120 mm, DALI, IP65, optika 60° poglobljena dark, Al ohišje, kot naprimer Linelight Portik_Q, Intra Lighting | -S43 Supply and installation of ceiling-mounted LED luminaire, 1556 lm, 15,8 W, 930, 112x120 mm, DALI, IP65, optics 60° deep dark, Al housing, e.g. Linelight Portik_Q, Intra Lighting | kpl | 57 |  | 0
1.35 | -S45 Dobava in montaža nadometne stenske LED svetilke, 3400 lm, 39 W, 930, 516x70 mm, DALI, IP65, optika asimetrična, Al ohišje, kot naprimer FLOS DOOKU, Intra Lighting | -S45 Supply and installation of wall-mounted LED luminaire, 3400 lm, 39 W, 930, 516x70 mm, DALI, IP65, optics asymmetrical, Al housing, e.g. FLOS DOOKU, Intra Lighting | kpl | 5 |  | 0
1.36 | -S46 Dobava in montaža nadometne stropne LED svetilke, 4100 lm, 41 W, 835, L1685 mm, DALI, IP43, optika SOP polopalna PC, Al ohišje, kot naprimer Kalis C 55, Intra Lighting | -S46 Supply and installation of ceiling-mounted LED luminaire, 4100 lm, 41 W, 835, L1685 mm, DALI, IP43, optics SOP semi-flush PC, Al housing, e.g. Kalis C 55, Intra Lighting | kpl | 9 |  | 0
1.37 | -S47 Dobava in montaža nadometne stropne LED svetilke, 3400 lm, 34 W, 835, L1405 mm, DALI, IP43, optika SOP polopalna PC, Al ohišje, kot naprimer Kalis C 55, Intra Lighting | -S47 Supply and installation of ceiling-mounted LED luminaire, 3400 lm, 34 W, 835, L1405 mm, DALI, IP43, optics SOP semi-flush PC, Al housing, e.g. Kalis C 55, Intra Lighting | kpl | 84 |  | 0
1.38 | -S53 Dobava in montaža nadometne stropne LED svetilke, 798 lm, 7 W, 930, 75x75 mm, DALI, IP65, optika 60°, Al ohišje, kot naprimer Portik_Q, Intra Lighting | -S53 Supply and installation of ceiling-mounted LED luminaire, 798 lm, 7 W, 930, 75x75 mm, DALI, IP65, optics 60°, Al housing, such as Portik_Q, Intra Lighting | kpl | 18 |  | 0
1.39 | -S54 Dobava in montaža nadometne industrijske LED svetilke, 3800 lm, 31 W, 940, L1277 mm, DALI, IP66, optika polprosojna PC, ohišje PC, konektorski priklop, komplet z obešaljnim priborom za dolžino do 2m, kot naprimer 5700, Intra Lighting | -S54 Supply and installation of overhead industrial LED luminaire, 3800 lm, 31 W, 940, L1277 mm, DALI, IP66, optics semi-transparent PC, housing PC, connector connection, complete with hanging accessories for lengths up to 2 m, such as for example 5700, Intra Lighting | kpl | 28 |  | 0
1.40 | -S56 Dobava in montaža nadometne linijske LED svetilke, 1450 lm, 15 W, 930, L565 mm, barva hodnika, DALI, IP43, optika mikroprizmatika PMMA, Al ohišje, komplet z obešaljnim priborom za dolžino do 2m, kot naprimer Kalis C 55, Intra Lighting | -S56 Supply and installation of overhead linear LED luminaire, 1450 lm, 15 W, 930, L565 mm, corridor colour, DALI, IP43, PMMA microprism optics, Al housing, complete with hanging accessories for lengths up to 2 m, e.g. Kalis C 55, Intra Lighting | kpl | 1617 |  | 0
1.41 | -S57 Dobava in montaža nadometne linijske LED svetilke, 840 lm, 10 W, 930, L845 mm, barva hodnika, DALI, IP43, optika mikroprizmatika PMMA, Al ohišje, komplet z obešaljnim priborom za dolžino do 2m, kot naprimer Kalis C 55, Intra Lighting | -S57 Supply and installation of overhead linear LED luminaire, 840 lm, 10 W, 930, L845 mm, corridor colour, DALI, IP43, PMMA microprism optics, Al housing, complete with hanging accessories for lengths up to 2 m, e.g. Kalis C 55, Intra Lighting | kpl | 16 |  | 0
1.42 | -S57-A Dobava in montaža nadometne linijske LED svetilke, 840 lm, 10 W, 930, L845 mm, bela barva, DALI, IP43, optika mikroprizmatika PMMA, Al ohišje, komplet z obešaljnim priborom za dolžino do 2m, kot naprimer Kalis C 55, Intra Lighting | -S57-A Supply and installation of overhead linear LED luminaire, 840 lm, 10 W, 930, L845 mm, white, DALI, IP43, PMMA microprism optics, Al housing, complete with hanging accessories for lengths up to 2 m, e.g. Kalis C 55, Intra Lighting | kpl | 318 |  | 0
1.43 | -S57-B Dobava in montaža nadometne linijske LED svetilke, 1500 lm, 15 W, 930, L845 mm, bela barva, DALI, IP43, optika mikroprizmatika PMMA, Al ohišje, kot naprimer Kalis W 55, Intra Lighting | -S57-B Supply and installation of overhead linear LED luminaire, 1500 lm, 15 W, 930, L845 mm, white, DALI, IP43, PMMA microprism optics, Al housing, e.g. Kalis W 55, Intra Lighting | kpl | 2 |  | 0
1.44 | -S58 Dobava in montaža vgradne stenske asimetrične LED svetilke, 266 lm, 2,7 W, 840, L845 mm, IP44, optika poglobljena strogo asimetrična v tla 74°, inox ohišje, kot naprimer Linealight Quara_Q, Intra Lighting | -S58 Supply and installation of recessed wall-mounted asymmetrical LED luminaire, 266 lm, 2,7 W, 840, L845 mm, IP44, optics recessed strictly asymmetrical in the floor 74°, inox housing, e.g. Linealight Quara_Q, Intra Lighting | kpl | 70 |  | 0
1.45 | -S59 Dobava in montaža viseče LED svetilke, 874 lm, 12 W, 930, D132 mm, IP20, optika poglobljena dark 62°, ohišje Al, kot naprimer Zoe Z6, Intra Lighting | -S59 Supply and installation of LED pendant luminaire, 874 lm, 12 W, 930, D132 mm, IP20, optics recessed dark 62°, housing Al, e.g. Zoe Z6, Intra Lighting | kpl | 87 |  | 0
1.46 | -S61 Dobava in montaža viseče LED svetilke, 15200+15800 lm, 320 W, 930, D4900 mm, IP20, ohišje Al, kot naprimer Wave Round SDI, Intra Lighting | -S61 Supply and installation of LED pendant luminaire, 15200+15800 lm, 320 W, 930, L4900 mm, IP20, housing Al, as for example Wave Round SDI, Intra Lighting | kpl | 1 |  | 0
1.47 | -S62 Dobava in montaža viseče LED svetilke, 2350-1700 lm, 66 W, 930, D753 mm, IP20, ohišje Al, kot naprimer Rynk SDI, Intra Lighting | -S62 Supply and installation of LED pendant luminaire, 2350-1700 lm, 66 W, 930, D753 mm, IP20, Al housing, e.g. Rynk SDI, Intra Lighting | kpl | 15 |  | 0
1.48 | -S70 Dobava in montaža vgradne stropne 3700 lm, 27 W, 840, 597x597 mm, IP65, za čiste prostore, kot naprimer Alkon HMP, Intra Lighting | -S70 Supply and installation of recessed ceiling luminaire 3700 lm, 27 W, 840, 597x597 mm, IP65, for clean rooms, such as Alkon HMP, Intra Lighting | kpl | 99 |  | 0
1.49 | -S71 Dobava in montaža nadometne LED svetilke, 10000 lm, 67 W, 840, L770 mm, IP65, komplet z obešaljnim priborom za dolžino do 2m, kot naprimer Sequal 2M, Intra Lighting | -S71 Supply and installation of overhead LED luminaire, 10000 lm, 67 W, 840, L770 mm, IP65, complete with suspension fittings for lengths up to 2 m, e.g. Sequal 2M, Intra Lighting | kpl | 54 |  | 0
1.50 | -S72 Dobava in montaža nadometne LED svetilke, EX cona II, 2G Ex eb mb q IIC T4 Gb, 6020 lm, 40 W, 860, 1250x182x114 mm, IP66, kot naprimer nD866F 12L60, Schuch | -S72 Supply and installation of overhead LED luminaire, EX zone II, 2G Ex eb mb q IIC T4 Gb, 6020 lm, 40 W, 860, 1250x182x114 mm, IP66, as for example nD866F 12L60, Schuch | kpl | 4 |  | 0
1.51 | Dobava in montaža podometnega stikala DALI 2 za posamično krmiljenje do 64 svetilk 10 A, 250 V, možnost zatemnitve, kot naprimer JUNG | Supply and installation of a DALI 2 flush-mounted switch for individual control of up to 64 luminaires 10 A, 250 V, dimmable, e.g. JUNG | kos | 133 |  | 0
1.52 | Dobava in montaža nadometnega stikala, nadometno ohišje 2M + podometno stikalo DALI 2 za posamično krmiljenje do 64 svetilk 10 A, 250 V, možnost zatemnitve, kot naprimer JUNG | Supply and installation of an overhead switch, 2M overhead housing + DALI 2 underground switch for individual control of up to 64 luminaires 10 A, 250 V, dimmable, e.g. JUNG | kpl | 62 |  | 0
1.53 | Dobava in montaža nadometnega stikala, 16A, 250V, IP65, za montažo v cono 1 in cono 2 eksplozivne ogroženosti, 8040/A, II 2G Ex de IIC T6 Gb, kot naprimer Schuch | Supply and installation of an overhead switch, 16A, 250V, IP65, for installation in explosion hazard zone 1 and zone 2, 8040/A, II 2G Ex de IIC T6 Gb, as for example Schuch | kpl | 4 |  | 0
1.54 | Dobava in montaža senzorja prisotnosti DALI-2 ali KNX, z nastavljivo svetlobno občutljivostjo, 12V - 22,5 V, 10-1000 lx, kot zaznavanja 360°, domet 20 x 3 m, višina montaže 2,5-3,5 m, IP20, kot naprimer DUAL HF, Steinel ali Schneider | Supply and installation of DALI-2 or KNX occupancy sensor with adjustable light sensitivity, 12V - 22.5 V, 10-1000 lx, detection angle 360°, range 20 x 3 m, mounting height 2.5-3.5 m, IP20, such as DUAL HF, Steinel or Schneider | kpl | 136 |  | 0
1.55 | Dobava in montaža senzorja prisotnosti DALI-2 ali KNX, z nastavljivo svetlobno občutljivostjo, 30 V, 10-1000 lx, kot zaznavanja 360°, domet Φ12 m, višina montaže 2,5-4 m, IP20, kot naprimer HF 360-2, Steinel ali Schneider | Supply and installation of DALI-2 or KNX occupancy sensor, adjustable light sensitivity, 30 V, 10-1000 lx, detection angle 360°, range Φ12 m, mounting height 2.5-4 m, IP20, e.g. HF 360-2, Steinel or Schneider | kpl | 148 |  | 0
1.56 | Dobava in montaža senzorja prisotnosti DALI-2 ali KNX, z nastavljivo svetlobno občutljivostjo, 12V - 22,5 V, 2-1000 lx, kot zaznavanja 360°, domet Φ8 m, višina montaže 2-4 m, IP54, kot naprimer HF 3360, Steinel ali Schneider | Supply and installation of DALI-2 or KNX occupancy sensor with adjustable light sensitivity, 12V - 22.5 V, 2-1000 lx, detection angle 360°, range Φ8 m, mounting height 2-4 m, IP54, such as e.g. HF 3360, Steinel or Schneider | kpl | 118 |  | 0
1.57 | Dobava in montaža programabilnega kontrolera na dotik, 2xEthernet, WLAN, Bluethooth, senzor vlage in temperature, senzor osvetljenosti, IR senzor, 24 V DC, 3W, IP20; kot naprimer LOYTEC LPAD7-30G2 | Supply and installation of programmable touch controller, 2xEthernet, WLAN, Bluethooth, humidity and temperature sensor, light sensor, IR sensor, 24 V DC, 3W, IP20; such as LOYTEC LPAD7-30G2 | kpl | 418 |  | 0
| RAZSVETLJAVA | LIGHTING |  |  |  | 0

## 3.7.2_Zasilna Razsvetljava
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.7 | ELEKTRO DELA | ELECTRICAL WORKS
3.7.2 | ZASILNA RAZSVETLJAVA | EMERGENCY LIGHTING |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
2 | ZASILNA RAZSVETLJAVA | EMERGENCY LIGHTING
2.1 | Dobava in montaža Centralna enota SU 6 NET Naprava za centralno napajanje varnostne razsvetljave din-Sicherheitstechnik po DIN VDE 0108. Mikroprocesorska enota za nadzor. PLC tehnologija omogoča mešanje trajnega in pripravnega spoja na enem tokokrogu. Sistem omogoča avtomatsko adresiranje s centralnega mesta. Možnost dimanja vsake svetilke iz centralne enote. 6 izhodnih tokokrogov, izhodne napetosti 24V DC za priključitev din PLC 24 LED svetilk. Tekstovni prikazovalnik s statusnimi informacijami serijsko v slovenskem jeziku. Vključno z baterijsko omarico in baterijskim sistemom 24V. Mere VxŠxG 465 mm x 250 mm x 129 mm. Garancija na kompletni sistem 5 let ob rednih letnih pregledih s strani proizvajalca. Kot na primer: din-Sicherheitstechnik; SU 6 NET | Supply and installation Central unit SU 6 NET Central power supply unit for din-Sicherheitstechnik security lighting according to DIN VDE 0108. Microprocessor control unit. PLC technology allows mixing of permanent and standby junction on one circuit. The system allows automatic addressing from a central point. Possibility of dimming each luminaire from the central unit. 6 output circuits, output voltage 24V DC for connection of din PLC 24 LED luminaires. Text display with status information in English as standard. Including battery box and 24V battery system. Dimensions HxWxD 465 mm x 250 mm x 129 mm. 5 years warranty on complete system with regular annual inspections by the manufacturer. Such as: din-Sicherheitstechnik; SU 6 NET | kos | 11 |  | 0
2.2 | Dobava in montaža Centralna enota SU 6 NET Naprava za centralno napajanje varnostne razsvetljave din-Sicherheitstechnik po DIN VDE 0108. Mikroprocesorska enota za nadzor. PLC tehnologija omogoča mešanje trajnega in pripravnega spoja na enem tokokrogu. Sistem omogoča avtomatsko adresiranje s centralnega mesta. Možnost dimanja vsake svetilke iz centralne enote. 6 izhodnih tokokrogov, izhodne napetosti 24V DC za priključitev din PLC 24 LED svetilk. Tekstovni prikazovalnik s statusnimi informacijami serijsko v slovenskem jeziku. Vključno z baterijsko omarico in baterijskim sistemom 24V. Mere VxŠxG 465 mm x 250 mm x 129 mm. Garancija na kompletni sistem 5 let ob rednih letnih pregledih s strani proizvajalca. Kot na primer: din-Sicherheitstechnik; SU 6 NET | Supply and installation Central unit SU 6 NET Central power supply unit for din-Sicherheitstechnik security lighting according to DIN VDE 0108. Microprocessor control unit. PLC technology allows mixing of permanent and standby junction on one circuit. The system allows automatic addressing from a central point. Possibility of dimming each luminaire from the central unit. 6 output circuits, output voltage 24V DC for connection of din PLC 24 LED luminaires. Text display with status information in English as standard. Including battery box and 24V battery system. Dimensions HxWxD 465 mm x 250 mm x 129 mm. 5 years warranty on complete system with regular annual inspections by the manufacturer. Such as: din-Sicherheitstechnik; SU 6 NET | kos | 9 |  | 0
2.3 | Dobava in montaža SU P, dodatna baterijska omara kompletno z že ožičenim baterijskim setom ob povečani avtonomiji. Svinčene baterije v GEL tehnologiji, hermetično zaprte brez vzdrževanja, baterije morajo zagotavljati zahtevano avtonomijo za spodaj navedene svetilke + 30 % obvezne rezerve zaradi daljšega delovanja in zanesljivosti sistema. Mere VxŠxG 374 mm x 250 mm x 129 mm Tip: din-Sicherheitstechnik; SU P | Supply and installation of SU P, additional battery cabinet complete with already wired battery set with increased autonomy. Lead acid batteries in GEL technology, hermetically sealed without maintenance, batteries must provide the required autonomy for the lamps listed below + 30% mandatory reserve for longer operation and system reliability. Dimensions HxWxD 374 mm x 250 mm x 129 mm Type: din-Sicherheitstechnik; SU P | kos | 9 |  | 0
2.4 | Dobava in montaža SU-GSM, modul za brezžični nadzor posameznega centralnega napajalnika preko mobilne aplikacija. Omogoča daljinski (TCP) dostop do sistema brez dodatnih stroškov. Preko aplikacije mySU je možen pregled stanja sistema in morebitnih napak. Možen hkraten dostop do sistema preko več prenosnih naprav. Kot na primer: din-Sicherheitstechnik; SU-GSM | Supply and installation SU-GSM, a module for wireless control of a single central power supply via a mobile app. It allows remote (TCP) access to the system at no additional cost. The mySU app allows the overview of the system status and possible faults. Simultaneous access to the system via multiple portable devices is possible. Such as: din-Sicherheitstechnik; SU-GSM | kos | 20 |  | 0
2.5 | Dobava in montaža SU-CNS, modul za navezavo posameznega centralnega napajalnika na CNS ali požarno centralo. Kot na primer: din-Sicherheitstechnik; SU-CNS | Supply and installation SU-CNS, a module for connecting a single central power supply to a CNS or fire panel. Such as: din-Sicherheitstechnik; SU-CNS | kos | 1 |  | 0
2.6 | Dobava in montaža 3PH-1, 3 fazni kontrolnik napetosti. Enopolni preklopni breznapetostni izhod. Montira se v vse razdelilce, ki napajajo splošno razsvetljavo. Kot na primer: din-Sicherheitstechnik; 3PH-1 | Supply and installation of 3PH-1, 3 phase voltage controller. Single pole switching voltage-free output. To be installed in all distributors supplying general lighting. Such as: din-Sicherheitstechnik; 3PH-1 | kos | 20 |  | 0
2.7 | Dobava in montaža SU CONTROL Basic, namenska programska oprema za lažje programiranje in vizualizacijo sistema preko PC-ja ali tabličnega računalnika. Podpora za WIN, IOS, Android Kot na primer: din-Sicherheitstechnik; SU CONTROL Basic | Supply and installation of SU CONTROL Basic, dedicated software for easy programming and visualisation of the system via PC or tablet. Support for WIN, IOS, Android Such as: din-Sicherheitstechnik; SU CONTROL Basic | kos | 1 |  | 0
2.8 | Tlorisna vizualizacija | Floor visualisation | kos | 1 |  | 0
2.9 | Programiranje sistema, spuščanje v pogon in uvajanje operaterja, poimenovanje svetilk do 200 znakov. | System programming, commissioning and operator induction, lamp naming up to 200 characters. | kos | 4 |  | 0
2.10 | Garancija na kompletni sistem 5 let ob rednih letnih pregledih s strani proizvajalca. | 5 years warranty on the complete system, subject to regular annual inspections by the manufacturer. | kos | 10 |  | 0
2.11 | -Z11P Dobava in montaža: Dimabilna LED varnostna svetilka s prosojno kapo. Ohišje iz polikarbonata bele barve RAL 9003, difuzor iz prosojnega polikarbonata. Nadgradna, modularno sestavljena svetilka zaščite IP 65, mehanska zaščita IK 07. Dovoljeno temperaturno območje uporabe -15oC do +40oC. Dovoljena priključna napetost 24V DC (PLC24). Asimetrična optika za enakomerno osvetljevanje poti umika. Svetlobni vir: 15 x Mid-Power LED 3,4W; skupna svetilnost minimalno 540 lm. Hlajenje LED vira s posebno toplotno prevodno umetno maso za zanesljivo delovanje v trajnem spoju. Svetilka je adresabilna, z možnostjo mešanja trajnega in pripravnega spoja na istem tokokrogu. Set priključnih sponk za linijsko vezavo 2 x 3 x 2,5 mm2. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; Concept 2 SL3 PLC | -Z11P Dobava in montaža: Dimabilna LED varnostna svetilka s prosojno kapo. Ohišje iz polikarbonata bele barve RAL 9003, difuzor iz prosojnega polikarbonata. Nadgradna, modularno sestavljena svetilka zaščite IP 65, mehanska zaščita IK 07. Dovoljeno temperaturno območje uporabe -15oC do +40oC. Dovoljena priključna napetost 24V DC (PLC24). Asimetrična optika za enakomerno osvetljevanje poti umika. Svetlobni vir: 15 x Mid-Power LED 3,4W; skupna svetilnost minimalno 540 lm. Hlajenje LED vira s posebno toplotno prevodno umetno maso za zanesljivo delovanje v trajnem spoju. Svetilka je adresabilna, z možnostjo mešanja trajnega in pripravnega spoja na istem tokokrogu. Set priključnih sponk za linijsko vezavo 2 x 3 x 2,5 mm2. 50.000 hours warranty. Such as: din-Sicherheitstechnik; Concept 2 SL3 PLC | kos | 78 |  | 0
2.12 | Pribor za spuščeno montažo svetilk serije CONCEPT. Komplet dveh jeklenic maksimalne dolžine 3 m s sponkami. Tip: din-Sicherheitstechnik; Stahlseil-Abhängung verzinkt 3m | Accessories for the lowered mounting of CONCEPT series luminaires. Set of two steel tubes with a maximum length of 3 m with clips. Type: din-Sicherheitstechnik; Stahlseil-Abhängung verzinkt 3m | kos | 78 |  | 0
2.13 | Pribor za spuščeno montažo svetilk CONCEPT. Komplet dveh obročnih vijakov z maticama in tesnili za visečo montažo svetilke. Brez jeklenice ali verige. Tip: din-Sicherheitstechnik; Concept-BE | Accessories for the lowered mounting of CONCEPT luminaires. Set of two ring bolts with nuts and gaskets for the hanging mounting of the luminaire. Without steel chain or chain. Type: din-Sicherheitstechnik; Concept-BE | kos | 78 |  | 0
2.14 | -Z12N Dobava in montaža: LED svetilka za osvetljevanje evakuacijske poti, nadgradna izvedba, simetrična optika. Okroglo ohišje iz polikarbonata, barva bela, RAL 9003, možnost dobave v poljubni barvi po izboru arhitekta. Zaščita IP40. Dovoljeno temperaturno območje uporabe -15°C do +40°C. Dovoljena priključna napetost 24V DC +/-20%. Svetilka omogoča avtomatsko adresiranje ter mešano programiranje trajnega in pripravnega spoja na istem tokokrogu brez dodatnega kabliranja. Osvetlitev se dosega z visoko zmogljivo LED diodo moči 2W. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; STRING 2 eco spot AP2 DA R 4000K PLC | -Z12N Supply and installation: LED luminaire for evacuation path lighting, upgradeable version, symmetrical optics. Round polycarbonate housing, colour white, RAL 9003, can be supplied in any colour of the architect's choice. Protection IP40. Permissible temperature range -15°C to +40°C. Permissible connection voltage 24V DC +/-20%. The luminaire allows automatic addressing and mixed programming of the permanent and standby junction on the same circuit without any additional cabling. The illumination is provided by a high-performance LED with 2W output. 50.000 hours warranty. As for example: din-Sicherheitstechnik; STRING 2 eco spot AP2 DA R 4000K PLC | kos | 57 |  | 0
2.15 | -Z13N Dobava in montaža: LED svetilka za osvetljevanje evakuacijske poti, nadgradna izvedba, simetrična optika. Okroglo ohišje iz polikarbonata, barva bela, RAL 9003, možnost dobave v poljubni barvi po izboru arhitekta. Zaščita IP40. Dovoljeno temperaturno območje uporabe -15°C do +40°C. Dovoljena priključna napetost 24V DC +/-20%. Svetilka omogoča avtomatsko adresiranje ter mešano programiranje trajnega in pripravnega spoja na istem tokokrogu brez dodatnega kabliranja. Osvetlitev se dosega s tremi visoko zmogljivimi LED diodami moči 1W. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; STRING 2 power spot AP DA R 4000K PLC | -Z13N Supply and installation: LED luminaire for evacuation path lighting, upgradeable version, symmetrical optics. Round polycarbonate housing, colour white, RAL 9003, can be supplied in any colour of the architect's choice. Protection IP40. Permissible temperature range -15°C to +40°C. Permissible connection voltage 24V DC +/-20%. The luminaire allows automatic addressing and mixed programming of the permanent and standby junction on the same circuit without any additional cabling. The illumination is provided by three high-performance LEDs with a power of 1 W. 50.000 hours warranty. As for example: din-Sicherheitstechnik; STRING 2 power spot AP DA R 4000K PLC | kos | 31 |  | 0
2.16 | -Z14 Dobava in montaža: LED svetilka za osvetljevanje evakuacijske poti, vgradna izvedba, simetrična optika. Ohišje polikarbonat, barva bela, RAL 9003, možnost dobave v poljubni barvi po izboru arhitekta. Zaščita IP40. Dovoljeno temperaturno območje uporabe -15°C do +40°C. Dovoljena priključna napetost 24V DC +/-20%. Svetilka omogoča avtomatsko adresiranje ter mešano programiranje trajnega in pripravnega spoja na istem tokokrogu brez dodatnega kabliranja. Osvetlitev se dosega z visoko zmogljivo LED diodo moči 1W. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; STRING 2 eco spot AP DE 4000K PLC | -Z14 Supply and installation: LED luminaire for evacuation path illumination, recessed design, symmetrical optics. Polycarbonate housing, colour white, RAL 9003, can be supplied in any colour of the architect's choice. Protection IP40. Permissible temperature range -15°C to +40°C. Permissible connection voltage 24V DC +/-20%. The luminaire allows automatic addressing and mixed programming of the permanent and standby junction on the same circuit without any additional cabling. The illumination is achieved with a high performance 1W LED. 50.000 hours warranty. As for example: din-Sicherheitstechnik; STRING 2 eco spot AP DE 4000K PLC | kos | 9 |  | 0
2.17 | -Z14N Dobava in montaža: LED svetilka za osvetljevanje evakuacijske poti, nadgradna izvedba, simetrična optika. Okroglo ohišje iz polikarbonata, barva bela, RAL 9003, možnost dobave v poljubni barvi po izboru arhitekta. Zaščita IP40. Dovoljeno temperaturno območje uporabe -15°C do +40°C. Dovoljena priključna napetost 24V DC +/-20%. Svetilka omogoča avtomatsko adresiranje ter mešano programiranje trajnega in pripravnega spoja na istem tokokrogu brez dodatnega kabliranja. Osvetlitev se dosega z visoko zmogljivo LED diodo moči 1W. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; STRING 2 eco spot AP DA R 4000K PLC | -Z14N Supply and installation: LED luminaire for evacuation path lighting, upgradeable version, symmetrical optics. Round polycarbonate housing, colour white, RAL 9003, can be supplied in any colour of the architect's choice. Protection IP40. Permissible temperature range -15°C to +40°C. Permissible connection voltage 24V DC +/-20%. The luminaire allows automatic addressing and mixed programming of the permanent and standby junction on the same circuit without any additional cabling. The illumination is achieved with a high performance 1W LED. 50.000 hours warranty. As for example: din-Sicherheitstechnik; STRING 2 eco spot AP DA R 4000K PLC | kos | 25 |  | 0
2.18 | -Z16 Dobava in montaža: Dimabilna LED svetilka za osvetljevanje evakuacijske poti, vgradna izvedba, simetrična optika. Brez vidnega ohišja. Zaščita IP 40. Dovoljena priključna napetost 24 V DC +/- 25%. Dovoljeno temperaturno območje uporabe -15°C do +40°C. Svetilka omogoča avtomatsko adresiranje ter mešano programiranje trajnega in pripravnega spoja na istem tokokrogu brez dodatnega kabliranja. Osvetlitev se dosega z visoko zmogljivo LED diodo moči 1W. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; EyE 90 AP 4000K PLC | -Z16 Supply and installation: Dimmable LED luminaire for evacuation path illumination, recessed design, symmetrical optics. No visible housing. Protection IP 40. Permissible connection voltage 24 V DC +/- 25%. Permissible temperature range -15°C to +40°C. The luminaire allows automatic addressing and mixed programming of the permanent and standby junction on the same circuit without additional cabling. The illumination is achieved with a high performance 1W LED. 50.000 hours warranty. As for example: din-Sicherheitstechnik; EyE 90 AP 4000K PLC | kos | 298 |  | 0
2.19 | -Z16C Dobava in montaža: Dimabilna LED svetilka za osvetljevanje evakuacijske poti, vgradna izvedba, simetrična optika. Brez vidnega ohišja. Zaščita IP 40. Dovoljena priključna napetost 24 V DC +/- 25%. Dovoljeno temperaturno območje uporabe -15°C do +40°C. Svetilka omogoča avtomatsko adresiranje ter mešano programiranje trajnega in pripravnega spoja na istem tokokrogu brez dodatnega kabliranja. Osvetlitev se dosega z visoko zmogljivo LED diodo moči 1W. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; EyE 90 AP 4000K PLC | -Z16C Supply and installation: Dimmable LED luminaire for evacuation path illumination, recessed design, symmetrical optics. No visible housing. Protection IP 40. Permissible connection voltage 24 V DC +/- 25%. Permissible temperature range -15°C to +40°C. The luminaire allows automatic addressing and mixed programming of the permanent and standby junction on the same circuit without additional cabling. The illumination is achieved with a high performance 1W LED. 50.000 hours warranty. As for example: din-Sicherheitstechnik; EyE 90 AP 4000K PLC | kos | 16 |  | 0
2.20 | Dobava in montaža: Adapter s tesnilom za prilagoditev svetilke EYE v čiste prostore. Primeren za debeline stropa do 50mm! | Supply and installation: Adapter with gasket to adapt the EYE luminaire to clean rooms. Suitable for ceiling thicknesses up to 50mm! | kos | 16 |  | 0
2.21 | -Z18N Dobava in montaža: Dimabilna LED svetilka za osvetljevanje evakuacijske poti za vgradno montažo. Vijačna izvedba. Ohišje iz polikarbonata. Svetilka omogoča avtomatsko adresiranje ter mešano programiranje trajnega in pripravnega spoja na istem tokokrogu brez dodatnega kabliranja. Dovoljena priključna napetost 24V DC +/- 20%. Dovoljeno temperaturno območje uporabe -20°C do +40°C. Nazivna moč svetlobnega vira 1,1W. Barva svetlobe 4000K. Kot na primer; din-Sicherheitstechnik; Tube-264-PLC24-1-M, 4000K | -Z18N Supply and installation: Dimmable LED luminaire for evacuation path illumination for recessed mounting. Screw type design. Polycarbonate housing. The luminaire allows automatic addressing and mixed programming of permanent and ready junction on the same circuit without additional cabling. Permissible connection voltage 24V DC +/- 20%. Permissible operating temperature range -20°C to +40°C. Rated light source power 1,1W. Colour of light 4000K. As for example; din-Sicherheitstechnik; Tube-264-PLC24-1-M, 4000K | kos | 111 |  | 0
2.22 | Pribor za stropno nadgradno montažo svetilk TUBE 264. Material aluminij, barva signalno bela. Kot na primer: din-Sicherheitstechnik; Tube-264-M Deckenaufbaugehäuse | Accessories for ceiling mounting of TUBE 264 luminaires. Material aluminium, colour signal white. Such as: din-Sicherheitstechnik; Tube-264-M Deckenaufbaugehäuse | kos | 104 |  | 0
2.23 | -Z18Z Dobava in montaža: Dimabilna LED svetilka za osvetljevanje evakuacijske poti za vgradno montažo. Vijačna izvedba. Ohišje iz polikarbonata. Svetilka omogoča avtomatsko adresiranje ter mešano programiranje trajnega in pripravnega spoja na istem tokokrogu brez dodatnega kabliranja. Dovoljena priključna napetost 24V DC +/- 20%. Dovoljeno temperaturno območje uporabe -20°C do +40°C. Nazivna moč svetlobnega vira 1,1W. Barva svetlobe 4000K. Kot na primer; din-Sicherheitstechnik; Tube-264-PLC24-1-M, 4000K | -Z18Z Supply and installation: Dimmable LED luminaire for evacuation path illumination for recessed mounting. Screw type design. Polycarbonate housing. The luminaire allows automatic addressing and mixed programming of permanent and ready junction on the same circuit without additional cabling. Permissible connection voltage 24V DC +/- 20%. Permissible operating temperature range -20°C to +40°C. Rated light source power 1,1W. Colour of light 4000K. As for example; din-Sicherheitstechnik; Tube-264-PLC24-1-M, 4000K | kos | 118 |  | 0
2.24 | Pribor za stensko nadgradno montažo svetilk TUBE 264 vzporedno z zidom. Material aluminij, barva signalno bela. Kot na primer: din-Sicherheitstechnik; Tube-264-M Wandaufbaugehäuse | Accessories for wall mounting of TUBE 264 luminaires parallel to the wall. Material aluminium, colour signal white. Such as: din-Sicherheitstechnik; Tube-264-M Wandaufbaugehäuse | kos | 126 |  | 0
2.25 | -Z20N Dobava in montaža: Dimabilna LED svetilka za osvetljevanje evakuacijske poti za vgradno montažo. Vijačna izvedba. Ohišje iz polikarbonata. Svetilka omogoča avtomatsko adresiranje ter mešano programiranje trajnega in pripravnega spoja na istem tokokrogu brez dodatnega kabliranja. Dovoljena priključna napetost 24V DC +/- 20%. Dovoljeno temperaturno območje uporabe -20°C do +40°C. Nazivna moč svetlobnega vira 1,1W. Barva svetlobe 4000K. Kot na primer; din-Sicherheitstechnik; Tube-264-PLC24-2-M, 4000K | -Z20N Supply and installation: Dimmable LED luminaire for evacuation path illumination for flush mounting. Screw type design. Polycarbonate housing. The luminaire allows automatic addressing and mixed programming of permanent and ready junction on the same circuit without additional cabling. Permissible connection voltage 24V DC +/- 20%. Permissible operating temperature range -20°C to +40°C. Rated light source power 1,1W. Colour of light 4000K. As for example; din-Sicherheitstechnik; Tube-264-PLC24-2-M, 4000K | kos | 8 |  | 0
2.26 | Pribor za stropno nadgradno montažo svetilk TUBE 264. Material aluminij, barva signalno bela. Tip: din-Sicherheitstechnik; Tube-264-M Deckenaufbaugehäuse | Accessories for ceiling mounting of TUBE 264 luminaires. Material aluminium, colour signal white. Type: din-Sicherheitstechnik; Tube-264-M Deckenaufbaugehäuse | kos | 8 |  | 0
2.27 | -Z4P Dobava in montaža: Dimabilna LED varnostna svetilka s prosojno kapo. Ohišje iz polikarbonata bele barve RAL 9003, difuzor iz prosojnega polikarbonata. Nadgradna, modularno sestavljena svetilka zaščite IP 65, mehanska zaščita IK 07. Dovoljeno temperaturno območje uporabe -15oC do +40oC. Dovoljena priključna napetost 24V DC +/-20% (PLC24). Simetrična optika za enakomerno osvetljevanje poti umika in prostorov. Svetlobni vir: 15 x Mid-Power LED 1W; skupna svetilnost minimalno 187,5 lm. Hlajenje LED vira s posebno toplotno prevodno umetno maso za zanesljivo delovanje v trajnem spoju. Svetilka omogoča avtomatsko adresiranje ter mešano programiranje trajnega in pripravnega spoja na istem tokokrogu brez dodatnega kabliranja. Set priključnih sponk za linijsko vezavo 2 x 3 x 2,5mm2. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; CONCEPT 2 AP3 PLC | -Z4P Supply and installation: Dimabilna LED varnostna svetilka s prosojno kapo. Ohišje iz polikarbonata bele barve RAL 9003, difuzor iz prosojnega polikarbonata. Nadgradna, modularno sestavljena svetilka zaščite IP 65, mehanska zaščita IK 07. Dovoljeno temperaturno območje uporabe -15oC do +40oC. Dovoljena priključna napetost 24V DC +/-20% (PLC24). Simetrična optika za enakomerno osvetljevanje poti umika in prostorov. Svetlobni vir: 15 x Mid-Power LED 1W; skupna svetilnost minimalno 187,5 lm. Hlajenje LED vira s posebno toplotno prevodno umetno maso za zanesljivo delovanje v trajnem spoju. Svetilka omogoča avtomatsko adresiranje ter mešano programiranje trajnega in pripravnega spoja na istem tokokrogu brez dodatnega kabliranja. Set priključnih sponk za linijsko vezavo 2 x 3 x 2,5mm2. 50.000 hours warranty. As for example: din-Sicherheitstechnik; CONCEPT 2 AP3 PLC | kos | 145 |  | 0
2.28 | Pribor za spuščeno montažo svetilk serije CONCEPT. Komplet dveh jeklenic maksimalne dolžine 3 m s sponkami. Tip: din-Sicherheitstechnik; Stahlseil-Abhängung verzinkt 3m | Accessories for the lowered mounting of CONCEPT series luminaires. Set of two steel tubes with a maximum length of 3 m with clips. Type: din-Sicherheitstechnik; Stahlseil-Abhängung verzinkt 3m | kos | 145 |  | 0
2.29 | Pribor za spuščeno montažo svetilk CONCEPT. Komplet dveh obročnih vijakov z maticama in tesnili za visečo montažo svetilke. Brez jeklenice ali verige. Tip: din-Sicherheitstechnik; Concept-BE | Accessories for the lowered mounting of CONCEPT luminaires. Set of two ring bolts with nuts and gaskets for the hanging mounting of the luminaire. Without steel chain or chain. Type: din-Sicherheitstechnik; Concept-BE | kos | 145 |  | 0
2.30 | -Z4Z Dobava in montaža: Dimabilna LED varnostna svetilka s prosojno kapo. Ohišje iz polikarbonata bele barve RAL 9003, difuzor iz prosojnega polikarbonata. Nadgradna, modularno sestavljena svetilka zaščite IP 65, mehanska zaščita IK 07. Dovoljeno temperaturno območje uporabe -15oC do +40oC. Dovoljena priključna napetost 24V DC +/-20% (PLC24). Simetrična optika za enakomerno osvetljevanje poti umika in prostorov. Svetlobni vir: 15 x Mid-Power LED 1W; skupna svetilnost minimalno 187,5 lm. Hlajenje LED vira s posebno toplotno prevodno umetno maso za zanesljivo delovanje v trajnem spoju. Svetilka omogoča avtomatsko adresiranje ter mešano programiranje trajnega in pripravnega spoja na istem tokokrogu brez dodatnega kabliranja. Set priključnih sponk za linijsko vezavo 2 x 3 x 2,5mm2. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; CONCEPT 2 AP3 PLC | -Z4Z Supply and installation: Dimabilna LED varnostna svetilka s prosojno kapo. Ohišje iz polikarbonata bele barve RAL 9003, difuzor iz prosojnega polikarbonata. Nadgradna, modularno sestavljena svetilka zaščite IP 65, mehanska zaščita IK 07. Dovoljeno temperaturno območje uporabe -15oC do +40oC. Dovoljena priključna napetost 24V DC +/-20% (PLC24). Simetrična optika za enakomerno osvetljevanje poti umika in prostorov. Svetlobni vir: 15 x Mid-Power LED 1W; skupna svetilnost minimalno 187,5 lm. Hlajenje LED vira s posebno toplotno prevodno umetno maso za zanesljivo delovanje v trajnem spoju. Svetilka omogoča avtomatsko adresiranje ter mešano programiranje trajnega in pripravnega spoja na istem tokokrogu brez dodatnega kabliranja. Set priključnih sponk za linijsko vezavo 2 x 3 x 2,5mm2. 50.000 hours warranty. Such as: din-Sicherheitstechnik; CONCEPT 2 AP3 PLC | kos | 17 |  | 0
2.31 | Pribor za stensko montažo svetilk CONCEPT vzporedno z zidom. Ko na primer: din-Sicherheitstechnik; Concept-WA-PP-G Kunststoff | Accessories for wall mounting CONCEPT luminaires parallel to the wall. For example: din-Sicherheitstechnik; Concept-WA-PP-G Kunststoff | kos | 17 |  | 0
2.32 | -Z5P, Z6P Dobava in montaža: Dimabilna LED varnostna svetilka s prosojno kapo. Ohišje iz polikarbonata bele barve RAL 9003, difuzor iz prosojnega polikarbonata. Nadgradna, modularno sestavljena svetilka zaščite IP 65, mehanska zaščita IK 07. Dovoljeno temperaturno območje uporabe -15oC do +40oC. Dovoljena priključna napetost 24V DC +/-20% (PLC24). Simetrična optika za enakomerno osvetljevanje poti umika in prostorov. Svetlobni vir: 15 x Mid-Power LED 1W; skupna svetilnost minimalno 187,5 lm. Hlajenje LED vira s posebno toplotno prevodno umetno maso za zanesljivo delovanje v trajnem spoju. Svetilka omogoča avtomatsko adresiranje ter mešano programiranje trajnega in pripravnega spoja na istem tokokrogu brez dodatnega kabliranja. Set priključnih sponk za linijsko vezavo 2 x 3 x 2,5mm2. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; CONCEPT 2 AP3 PLC | -Z5P, Z6P Supply and installation: Dimabilna LED varnostna svetilka s prosojno kapo. Ohišje iz polikarbonata bele barve RAL 9003, difuzor iz prosojnega polikarbonata. Nadgradna, modularno sestavljena svetilka zaščite IP 65, mehanska zaščita IK 07. Dovoljeno temperaturno območje uporabe -15oC do +40oC. Dovoljena priključna napetost 24V DC +/-20% (PLC24). Simetrična optika za enakomerno osvetljevanje poti umika in prostorov. Svetlobni vir: 15 x Mid-Power LED 1W; skupna svetilnost minimalno 187,5 lm. Hlajenje LED vira s posebno toplotno prevodno umetno maso za zanesljivo delovanje v trajnem spoju. Svetilka omogoča avtomatsko adresiranje ter mešano programiranje trajnega in pripravnega spoja na istem tokokrogu brez dodatnega kabliranja. Set priključnih sponk za linijsko vezavo 2 x 3 x 2,5mm2. 50.000 hours warranty. Such as: din-Sicherheitstechnik; CONCEPT 2 AP3 PLC | kos | 61 |  | 0
2.33 | Pribor za spuščeno montažo svetilk serije CONCEPT. Komplet dveh jeklenic maksimalne dolžine 3 m s sponkami. Kot na primer: din-Sicherheitstechnik; Stahlseil-Abhängung verzinkt 3m | Accessories for the lowered mounting of CONCEPT series luminaires. Set of two 3 m maximum lengths with clamps. As for example: din-Sicherheitstechnik; Stahlseil-Abhängung verzinkt 3m | kos | 61 |  | 0
2.34 | Pribor za spuščeno montažo svetilk CONCEPT. Komplet dveh obročnih vijakov z maticama in tesnili za visečo montažo svetilke. Brez jeklenice ali verige. Kot na primer: din-Sicherheitstechnik; Concept-BE | Accessories for the lowered mounting of CONCEPT luminaires. Set of two ring bolts with nuts and gaskets for the hanging mounting of the luminaire. Without steel chain or chain. Such as: din-Sicherheitstechnik; Concept-BE | kos | 61 |  | 0
2.35 | Piktogramska LED plošča za montažo na svetilke serije CONCEPT. Materijal pleksi steklo debeline 8 mm. Puščica LEVO/DESNO, razpoznavnost 22 m (SIST EN 1838). Laserska gravura za optimalno osvetlitev piktogramskih znakov z notranje strani. Klik-fix sistem za montažo piktograma brez orodja. Priloženi nosilci za stoječo ali visečo montažo (za svetilke Z5P, Z6P). Kot na primer: din-Sicherheitstechnik; Concept-S2-PL/PR | LED pictogram panel for mounting on CONCEPT series luminaires. Material Plexiglas 8 mm thick. Arrow LEFT/RIGHT, visibility 22 m (SIST EN 1838). Laser engraving for optimum illumination of the pictograms from the inside. Click-fix system for tool-free mounting of the pictograms. Supplied brackets for standing or hanging mounting (for luminaires Z5P, Z6P). Such as: din-Sicherheitstechnik; Concept-S2-PL/PR | kos | 43 |  | 0
2.36 | Piktogramska LED plošča za montažo na svetilke serije CONCEPT. Material pleksi steklo debeline 8 mm. Puščica DOL, razpoznavnost 22 m (SIST EN 1838). Laserska gravura za optimalno osvetlitev piktogramskih znakov z notranje strani. Klik-fix sistem za montažo piktograma brez orodja. Priloženi nosilci za stoječo ali visečo montažo (za svetilke Z5P, Z6P). Kot na primer: din-Sicherheitstechnik; Concept-S2-PU | LED pictogram panel for mounting on CONCEPT series luminaires. Material Plexiglas 8 mm thick. DOWN arrow, visibility 22 m (SIST EN 1838). Laser engraving for optimum illumination of pictograms from the inside. Click-fix system for tool-free mounting of the pictogram. Supplied brackets for standing or hanging mounting (for luminaires Z5P, Z6P). Such as: din-Sicherheitstechnik; Concept-S2-PU | kos | 18 |  | 0
2.37 | -Z5Z, Z6Z Dobava in montaža: Dimabilna LED varnostna svetilka s prosojno kapo. Ohišje iz polikarbonata bele barve RAL 9003, difuzor iz prosojnega polikarbonata. Nadgradna, modularno sestavljena svetilka zaščite IP 65, mehanska zaščita IK 07. Dovoljeno temperaturno območje uporabe -15oC do +40oC. Dovoljena priključna napetost 24V DC +/-20% (PLC24). Simetrična optika za enakomerno osvetljevanje poti umika in prostorov. Svetlobni vir: 15 x Mid-Power LED 1W; skupna svetilnost minimalno 187,5 lm. Hlajenje LED vira s posebno toplotno prevodno umetno maso za zanesljivo delovanje v trajnem spoju. Svetilka omogoča avtomatsko adresiranje ter mešano programiranje trajnega in pripravnega spoja na istem tokokrogu brez dodatnega kabliranja. Set priključnih sponk za linijsko vezavo 2 x 3 x 2,5mm2. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; CONCEPT 2 AP3 PLC | -Z5Z, Z6Z Supply and installation: Dimabilna LED varnostna svetilka s prosojno kapo. Ohišje iz polikarbonata bele barve RAL 9003, difuzor iz prosojnega polikarbonata. Nadgradna, modularno sestavljena svetilka zaščite IP 65, mehanska zaščita IK 07. Dovoljeno temperaturno območje uporabe -15oC do +40oC. Dovoljena priključna napetost 24V DC +/-20% (PLC24). Simetrična optika za enakomerno osvetljevanje poti umika in prostorov. Svetlobni vir: 15 x Mid-Power LED 1W; skupna svetilnost minimalno 187,5 lm. Hlajenje LED vira s posebno toplotno prevodno umetno maso za zanesljivo delovanje v trajnem spoju. Svetilka omogoča avtomatsko adresiranje ter mešano programiranje trajnega in pripravnega spoja na istem tokokrogu brez dodatnega kabliranja. Set priključnih sponk za linijsko vezavo 2 x 3 x 2,5mm2. 50.000 hours warranty. Such as: din-Sicherheitstechnik; CONCEPT 2 AP3 PLC | kos | 54 |  | 0
2.38 | Pribor za stensko montažo svetilk CONCEPT vzporedno z zidom. Kot na primer: din-Sicherheitstechnik; Concept-WA-PP-G Kunststoff | Accessories for wall mounting CONCEPT luminaires parallel to the wall. For example: din-Sicherheitstechnik; Concept-WA-PP-G Kunststoff | kos | 54 |  | 0
2.39 | Piktogramska LED plošča za montažo na svetilke serije CONCEPT. Material pleksi steklo debeline 8 mm. Puščica DOL, razpoznavnost 22 m (SIST EN 1838). Laserska gravura za optimalno osvetlitev piktogramskih znakov z notranje strani. Klik-fix sistem za montažo piktograma brez orodja. Priloženi nosilci za stoječo ali visečo montažo. Kot na primer: din-Sicherheitstechnik; Concept-S2-PU | LED pictogram panel for mounting on CONCEPT series luminaires. 8 mm thick plexiglass material. DOWN arrow, visibility 22 m (SIST EN 1838). Laser engraving for optimum illumination of the pictograms from the inside. Click-fix system for tool-free mounting of the pictograms. Supplied brackets for standing or hanging mounting. Such as: din-Sicherheitstechnik; Concept-S2-PU | kos | 46 |  | 0
2.40 | Piktogramska LED plošča za montažo na svetilke serije CONCEPT. Materijal pleksi steklo debeline 8 mm. Puščica LEVO, razpoznavnost 22 m (SIST EN 1838). Laserska gravura za optimalno osvetlitev piktogramskih znakov z notranje strani. Klik-fix sistem za montažo piktograma brez orodja. Priloženi nosilci za stoječo ali visečo montažo. Kot na primer: din-Sicherheitstechnik; Concept-S2-PL | LED pictogram panel for mounting on CONCEPT series luminaires. Material Plexiglas 8 mm thick. Arrow LEFT, visibility 22 m (SIST EN 1838). Laser engraving for optimum illumination of the pictograms from the inside. Click-fix system for tool-free mounting of the pictogram. Brackets supplied for standing or hanging mounting. Such as: din-Sicherheitstechnik; Concept-S2-PL | kos | 4 |  | 0
2.41 | Piktogramska LED plošča za montažo na svetilke serije CONCEPT. Materijal pleksi steklo debeline 8 mm. Puščica DESNO, razpoznavnost 22 m (SIST EN 1838). Laserska gravura za optimalno osvetlitev piktogramskih znakov z notranje strani. Klik-fix sistem za montažo piktograma brez orodja. Priloženi nosilci za stoječo ali visečo montažo. Kot na primer: din-Sicherheitstechnik; Concept-S2-PR | LED pictogram panel for mounting on CONCEPT series luminaires. 8 mm thick plexiglass material. Arrow RIGHT, visibility 22 m (SIST EN 1838). Laser engraving for optimum illumination of the pictograms from the inside. Click-fix system for tool-free mounting of the pictograms. Supplied brackets for standing or hanging mounting. Such as: din-Sicherheitstechnik; Concept-S2-PR | kos | 4 |  | 0
2.42 | -Z7N, Z8N Dobava in montaža: Dimabilna piktogramska LED svetilka v patentirani din-LED-LASER tehnologiji. Ohišje za stropno in stensko nadgradno montažo, bele barve RAL 9003. Svetilka omogoča avtomatsko adresiranje ter mešano programiranje trajnega in pripravnega spoja na istem tokokrogu brez dodatnega kabliranja. Možnost viseče montaže piktogramske plošče na pendah ali jeklenih vrveh. Stopnja zaščite IP40. Dovoljeno temperaturno območje uporabe -15°C do +40°C. Dovoljena priključna napetost 24V DC +/-20%. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; STRING 2 DA, Gr.2 PLC | -Z7N, Z8N Supply and installation: Dimmable pictogram LED luminaire in patented din-LED-LASER technology. Housing for ceiling and wall mounting, white RAL 9003. The luminaire allows automatic addressing and mixed programming of permanent and standby junction on the same circuit without additional cabling. Possibility of hanging the pictogram panel on pendants or steel ropes. Protection rating IP40. Permissible temperature range -15°C to +40°C. Allowed connection voltage 24V DC +/-20%. 50.000 hours warranty. As for example: din-Sicherheitstechnik; STRING 2 DA, Gr.2 PLC | kos | 62 |  | 0
2.43 | Piktogramska LED plošča v patentirani din-LED-LASER tehnologiji, debelina plošče 16mm. Enakomerna osvetlitev piktograma dosežena z lasersko gravuro. Svetlobni vir integriran v ploščo. Zaprt rob standardno v beli barvi, po naročilu možna dobava v poljubnem RAL. Piktogramski znak do roba plošče omogoča maksimalno razdaljo razpoznavnosti. Razpoznavnost 22m, smer LEVO/DESNO. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; STRING 2 DA/DE, Pikto Gr.2 PL/PR | Pictogram LED panel in patented din-LED-LASER technology, panel thickness 16mm. Uniform illumination of the pictogram achieved by laser engraving. Light source integrated in the panel. Closed edge in white as standard, any RAL colour can be supplied on request. Pictogram sign to the edge of the panel allows maximum visibility distance. Visibility 22m, bearing LEFT/RIGHT. 50.000 hours warranty. For example: din-Sicherheitstechnik; STRING 2 DA/DE, Pikto Gr.2 PL/PR | kos | 51 |  | 0
2.44 | Piktogramska LED plošča v patentirani din-LED-LASER tehnologiji, debelina plošče 16mm. Enakomerna osvetlitev piktograma dosežena z lasersko gravuro. Svetlobni vir integriran v ploščo. Zaprt rob standardno v beli barvi, po naročilu možna dobava v poljubnem RAL. Piktogramski znak do roba plošče omogoča maksimalno razdaljo razpoznavnosti. Razpoznavnost 22m, smer DOL. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; STRING 2 DA/DE, Pikto Gr.2 PU | Pictogram LED panel in patented din-LED-LASER technology, panel thickness 16mm. Uniform illumination of the pictogram achieved by laser engraving. Light source integrated in the panel. Closed edge in white as standard, any RAL colour can be supplied on request. Pictogram sign to the edge of the panel allows maximum visibility distance. Visibility 22m, bearing DOWN. 50.000 hours warranty. As for example: din-Sicherheitstechnik; STRING 2 DA/DE, Pikto Gr.2 PU | kos | 11 |  | 0
2.45 | -Z7NLA, Z8NLA Dobava in montaža: Dimabilna piktogramska LED svetilka v patentirani din-LED-LASER tehnologiji. Ohišje za stropno in stensko nadgradno montažo, bele barve RAL 9003. Svetilka omogoča avtomatsko adresiranje ter mešano programiranje trajnega in pripravnega spoja na istem tokokrogu brez dodatnega kabliranja. Možnost viseče montaže piktogramske plošče na pendah ali jeklenih vrveh. Stopnja zaščite IP40. Dovoljeno temperaturno območje uporabe -15°C do +40°C. Dovoljena priključna napetost 24V DC +/-20%. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; STRING 2 DA, hp Gr.2 PLC | -Z7NLA, Z8NLA Supply and installation: Dimmable pictogram LED luminaire in patented din-LED-LASER technology. Housing for ceiling and wall mounting, white RAL 9003. The luminaire allows automatic addressing and mixed programming of permanent and standby junction on the same circuit without additional cabling. Possibility of hanging the pictogram panel on pendants or steel ropes. Protection rating IP40. Permissible temperature range -15°C to +40°C. Allowed connection voltage 24V DC +/-20%. 50.000 hours warranty. As for example: din-Sicherheitstechnik; STRING 2 DA, hp Gr.2 PLC | kos | 32 |  | 0
2.46 | Piktogramska LED plošča v patentirani din-LED-LASER tehnologiji, debelina plošče 16mm. Enakomerna osvetlitev piktograma dosežena z lasersko gravuro. Svetlobni vir za osvetlitev piktograma integriran v plošči. Plošča ima dodatno funkcijo optimalne osvetlitve poti umika oz. opreme APZ. Zaprt rob standardno v beli barvi, po naročilu možna dobava v poljubnem RAL. Piktogramski znak do roba plošče omogoča maksimalno razdaljo razpoznavnosti. Razpoznavnost 22m, smer LEVO/DESNO. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; STRING 2 DA/DE LA, Pikto Gr.2 PL/PR | Pictogram LED panel in patented din-LED-LASER technology, panel thickness 16mm. Uniform illumination of the pictogram achieved by laser engraving. Light source for pictogram illumination integrated in the panel. Panel has an additional function for optimum illumination of the escape route or APZ equipment. Closed edge in white as standard, on request in any RAL colour. Pictogram sign to the edge of the panel allows maximum visibility distance. Visibility 22m, bearing LEFT/RIGHT. 50.000 hours warranty. Such as: din-Sicherheitstechnik; STRING 2 DA/DE LA, Pikto Gr.2 PL/PR | kos | 19 |  | 0
2.47 | Piktogramska LED plošča v patentirani din-LED-LASER tehnologiji, debelina plošče 16mm. Enakomerna osvetlitev piktograma dosežena z lasersko gravuro. Svetlobni vir za osvetlitev piktograma integriran v plošči. Plošča ima dodatno funkcijo optimalne osvetlitve poti umika oz. opreme APZ. Zaprt rob standardno v beli barvi, po naročilu možna dobava v poljubnem RAL. Piktogramski znak do roba plošče omogoča maksimalno razdaljo razpoznavnosti. Razpoznavnost 22m, smer DOL. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; STRING 2 DA/DE LA, Pikto Gr.2 PU | Pictogram LED panel in patented din-LED-LASER technology, panel thickness 16mm. Uniform illumination of the pictogram achieved by laser engraving. Light source for pictogram illumination integrated in the panel. Panel has an additional function for optimum illumination of the escape route or APZ equipment. Closed edge in white as standard, on request in any RAL colour. Pictogram sign to the edge of the panel allows maximum visibility distance. Visibility 22m, bearing DOWN. 50.000 hours warranty. As for example: din-Sicherheitstechnik; STRING 2 DA/DE LA, Pikto Gr.2 PU | kos | 13 |  | 0
2.48 | -Z7NPLA, Z8NPLA Dobava in montaža: Dimabilna piktogramska LED svetilka v patentirani din-LED-LASER tehnologiji. Ohišje za stropno in stensko nadgradno montažo, bele barve RAL 9003. Svetilka omogoča avtomatsko adresiranje ter mešano programiranje trajnega in pripravnega spoja na istem tokokrogu brez dodatnega kabliranja. Možnost viseče montaže piktogramske plošče na pendah ali jeklenih vrveh. Stopnja zaščite IP40. Dovoljeno temperaturno območje uporabe -15°C do +40°C. Dovoljena priključna napetost 24V DC +/-20%. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; STRING 2 DA, hp Gr.2 PLC | -Z7NPLA, Z8NPLA Supply and installation: Dimmable pictogram LED luminaire in patented din-LED-LASER technology. Housing for ceiling and wall mounting, white RAL 9003. The luminaire allows automatic addressing and mixed programming of permanent and standby junction on the same circuit without additional cabling. Possibility of hanging the pictogram panel on pendants or steel ropes. Protection rating IP40. Permissible temperature range -15°C to +40°C. Allowed connection voltage 24V DC +/-20%. 50.000 hours warranty. As for example: din-Sicherheitstechnik; STRING 2 DA, hp Gr.2 PLC | kos | 13 |  | 0
2.49 | Set kovinskih jeklenic za spuščeno montažo piktogramske plošče na svetilkah serije STRING 2. S priborom za brezstopenjsko nastavljanje nivoja spuščanja, dolžine 4m. Tip: din-Sicherheitstechnik; STRING 2 Seilmontageset 4,0 m | Set of metal hoses for lowered mounting of the pictogram panel on STRING 2 series luminaires. With infinitely adjustable lowering level adjustment fittings, 4m long. Type: din-Sicherheitstechnik; STRING 2 Seilmontageset 4,0 m | kos | 13 |  | 0
2.50 | Piktogramska LED plošča v patentirani din-LED-LASER tehnologiji, debelina plošče 16mm. Enakomerna osvetlitev piktograma dosežena z lasersko gravuro. Svetlobni vir za osvetlitev piktograma integriran v plošči. Plošča ima dodatno funkcijo optimalne osvetlitve poti umika oz. opreme APZ. Zaprt rob standardno v beli barvi, po naročilu možna dobava v poljubnem RAL. Piktogramski znak do roba plošče omogoča maksimalno razdaljo razpoznavnosti. Razpoznavnost 22m, smer DOL. Garancija 50.000 ur. Tip: din-Sicherheitstechnik; STRING 2 DA/DE LA, Pikto Gr.2 PU | Pictogram LED panel in patented din-LED-LASER technology, panel thickness 16mm. Uniform illumination of the pictogram achieved by laser engraving. Light source for pictogram illumination integrated in the panel. Panel has an additional function for optimum illumination of the escape route or APZ equipment. Closed edge in white as standard, on request in any RAL colour. Pictogram sign to the edge of the panel allows maximum visibility distance. Visibility 22m, bearing DOWN. 50.000 hours warranty. Type: din-Sicherheitstechnik; STRING 2 DA/DE LA, Pikto Gr.2 PU | kos | 8 |  | 0
2.51 | Piktogramska LED plošča v patentirani din-LED-LASER tehnologiji, debelina plošče 16mm. Enakomerna osvetlitev piktograma dosežena z lasersko gravuro. Svetlobni vir za osvetlitev piktograma integriran v plošči. Plošča ima dodatno funkcijo optimalne osvetlitve poti umika oz. opreme APZ. Zaprt rob standardno v beli barvi, po naročilu možna dobava v poljubnem RAL. Piktogramski znak do roba plošče omogoča maksimalno razdaljo razpoznavnosti. Razpoznavnost 22m, smer LEVO/DESNO. Garancija 50.000 ur. Tip: din-Sicherheitstechnik; STRING 2 DA/DE LA, Pikto Gr.2 PL/PR | Pictogram LED panel in patented din-LED-LASER technology, panel thickness 16mm. Uniform illumination of the pictogram achieved by laser engraving. Light source for pictogram illumination integrated in the panel. Panel has an additional function for optimum illumination of the escape route or APZ equipment. Closed edge in white as standard, on request in any RAL colour. Pictogram sign to the edge of the panel allows maximum visibility distance. Visibility 22m, bearing LEFT/RIGHT. 50.000 hours warranty. Type: din-Sicherheitstechnik; STRING 2 DA/DE LA, Pikto Gr.2 PL/PR | kos | 5 |  | 0
2.52 | -Z7NP, Z8NP Dobava in montaža: Dimabilna piktogramska LED svetilka v patentirani din-LED-LASER tehnologiji. Ohišje za stropno in stensko nadgradno montažo, bele barve RAL 9003. Svetilka omogoča avtomatsko adresiranje ter mešano programiranje trajnega in pripravnega spoja na istem tokokrogu brez dodatnega kabliranja. Možnost viseče montaže piktogramske plošče na pendah ali jeklenih vrveh. Stopnja zaščite IP40. Dovoljeno temperaturno območje uporabe -15°C do +40°C. Dovoljena priključna napetost 24V DC +/-20%. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; STRING 2 DA, Gr.2 PLC | -Z7NP, Z8NP Supply and installation: Dimmable pictogram LED luminaire in patented din-LED-LASER technology. Housing for ceiling and wall mounting, white RAL 9003. The luminaire allows automatic addressing and mixed programming of permanent and standby junction on the same circuit without additional cabling. Possibility of hanging the pictogram panel on pendants or steel ropes. Protection rating IP40. Permissible temperature range -15°C to +40°C. Allowed connection voltage 24V DC +/-20%. 50.000 hours warranty. As for example: din-Sicherheitstechnik; STRING 2 DA, Gr.2 PLC | kos | 115 |  | 0
2.53 | Set kovinskih jeklenic za spuščeno montažo piktogramske plošče na svetilkah serije STRING 2. S priborom za brezstopenjsko nastavljanje nivoja spuščanja, dolžine 4m. Kot na primer: din-Sicherheitstechnik; STRING 2 Seilmontageset 4,0 m | Set of metal hoses for lowered mounting of the pictogram panel on STRING 2 series luminaires. With infinitely adjustable lowering level adjustment fittings, 4m long. As for example: din-Sicherheitstechnik; STRING 2 Seilmontageset 4,0 m | kos | 107 |  | 0
2.54 | Piktogramska LED plošča v patentirani din-LED-LASER tehnologiji, debelina plošče 16mm. Enakomerna osvetlitev piktograma dosežena z lasersko gravuro. Svetlobni vir integriran v ploščo. Zaprt rob standardno v beli barvi, po naročilu možna dobava v poljubnem RAL. Piktogramski znak do roba plošče omogoča maksimalno razdaljo razpoznavnosti. Razpoznavnost 22m, smer DOL. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; STRING 2 DA/DE, Pikto Gr.2 PU | Pictogram LED panel in patented din-LED-LASER technology, panel thickness 16mm. Uniform illumination of the pictogram achieved by laser engraving. Light source integrated in the panel. Closed edge in white as standard, any RAL colour can be supplied on request. Pictogram sign to the edge of the panel allows maximum visibility distance. Visibility 22m, bearing DOWN. 50.000 hours warranty. As for example: din-Sicherheitstechnik; STRING 2 DA/DE, Pikto Gr.2 PU | kos | 70 |  | 0
2.55 | Piktogramska LED plošča v patentirani din-LED-LASER tehnologiji, debelina plošče 16mm. Enakomerna osvetlitev piktograma dosežena z lasersko gravuro. Svetlobni vir integriran v ploščo. Zaprt rob standardno v beli barvi, po naročilu možna dobava v poljubnem RAL. Piktogramski znak do roba plošče omogoča maksimalno razdaljo razpoznavnosti. Razpoznavnost 22m, smer LEVO/DESNO. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; STRING 2 DA/DE, Pikto Gr.2 PL/PR | Pictogram LED panel in patented din-LED-LASER technology, panel thickness 16mm. Uniform illumination of the pictogram achieved by laser engraving. Light source integrated in the panel. Closed edge in white as standard, any RAL colour can be supplied on request. Pictogram sign to the edge of the panel allows maximum visibility distance. Visibility 22m, bearing LEFT/RIGHT. 50.000 hours warranty. For example: din-Sicherheitstechnik; STRING 2 DA/DE, Pikto Gr.2 PL/PR | kos | 37 |  | 0
2.56 | -Z8NPLA Dobava in montaža: Dimabilna piktogramska LED svetilka v patentirani din-LED-LASER tehnologiji. Ohišje za stropno in stensko nadgradno montažo, bele barve RAL 9003. Svetilka omogoča avtomatsko adresiranje ter mešano programiranje trajnega in pripravnega spoja na istem tokokrogu brez dodatnega kabliranja. Možnost viseče montaže piktogramske plošče na pendah ali jeklenih vrveh. Stopnja zaščite IP40. Dovoljeno temperaturno območje uporabe -15°C do +40°C. Dovoljena priključna napetost 24V DC +/-20%. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; STRING 2 DA, hp Gr.2 PLC | -Z8NPLA Supply and installation: Dimmable pictogram LED luminaire in patented din-LED-LASER technology. Housing for ceiling and wall mounting, white RAL 9003. The luminaire allows automatic addressing and mixed programming of permanent and standby junction on the same circuit without additional cabling. Possibility of hanging the pictogram panel on pendants or steel ropes. Protection rating IP40. Permissible temperature range -15°C to +40°C. Allowed connection voltage 24V DC +/-20%. 50.000 hours warranty. As for example: din-Sicherheitstechnik; STRING 2 DA, hp Gr.2 PLC | kos | 1 |  | 0
2.57 | Set kovinskih jeklenic za spuščeno montažo piktogramske plošče na svetilkah serije STRING 2. S priborom za brezstopenjsko nastavljanje nivoja spuščanja, dolžine 1,5m. Kot na primer: din-Sicherheitstechnik; STRING 2 Seilmontageset 1,5 m | Set of metal hoses for lowered mounting of the pictogram panel on STRING 2 series luminaires. With 1,5m length of accessories for infinitely variable adjustment of the lowering level. As for example: din-Sicherheitstechnik; STRING 2 Seilmontageset 1,5 m | kos | 1 |  | 0
2.58 | Piktogramska LED plošča v patentirani din-LED-LASER tehnologiji, debelina plošče 16mm. Enakomerna osvetlitev piktograma dosežena z lasersko gravuro. Svetlobni vir za osvetlitev piktograma integriran v plošči. Plošča ima dodatno funkcijo optimalne osvetlitve poti umika oz. opreme APZ. Zaprt rob standardno v beli barvi, po naročilu možna dobava v poljubnem RAL. Piktogramski znak do roba plošče omogoča maksimalno razdaljo razpoznavnosti. Razpoznavnost 22m, smer DOL. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; STRING 2 DA/DE LA, Pikto Gr.2 PU | Pictogram LED panel in patented din-LED-LASER technology, panel thickness 16mm. Uniform illumination of the pictogram achieved by laser engraving. Light source for pictogram illumination integrated in the panel. Panel has an additional function for optimum illumination of the escape route or APZ equipment. Closed edge in white as standard, on request in any RAL colour. Pictogram sign to the edge of the panel allows maximum visibility distance. Visibility 22m, bearing DOWN. 50.000 hours warranty. As for example: din-Sicherheitstechnik; STRING 2 DA/DE LA, Pikto Gr.2 PU | kos | 1 |  | 0
2.59 | -Z8SL Dobava in montaža: Dimabilna piktogramska LED svetilka v patentirani din-LED-LASER tehnologiji s funkcijo dodatnega osvetljevanja področja okoli svetilke. Ohišje za stropno vgradno montažo, bele barve RAL 9003. Vgrajeni dve visokozmogljivi LED z možnostjo nastavljanja sevalnega kota za optimalno osvetlitev poti umika oz. opreme APZ. Svetilka omogoča avtomatsko adresiranje ter mešano programiranje trajnega in pripravnega spoja na istem tokokrogu brez dodatnega kabliranja. Možnost viseče montaže piktogramske plošče na pendah ali jeklenih vrveh. Stopnja zaščite IP40. Dovoljeno temperaturno območje uporabe -15°C do +40°C. Dovoljena priključna napetost 24V DC +/-20%. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; STRING 2 DE plus, Gr.2 PLC | -Z8SL Supply and installation: Dimmable LED pictogram luminaire in patented din-LED-LASER technology with additional illumination function for the area around the luminaire. Ceiling-mounted housing, white RAL 9003. Two high-power LEDs with adjustable radiation angle for optimum illumination of the escape route or APZ equipment. The luminaire allows automatic addressing and mixed programming of the permanent and standby junction on the same circuit without additional cabling. Possibility of suspended mounting of the pictogram panel on pendants or steel ropes. Protection rating IP40. Permissible temperature range -15°C to +40°C. Allowed connection voltage 24V DC +/-20%. 50.000 hours warranty. As for example: din-Sicherheitstechnik; STRING 2 DE plus, Gr.2 PLC | kos | 29 |  | 0
2.60 | Piktogramska LED plošča v patentirani din-LED-LASER tehnologiji, debelina plošče 16mm. Enakomerna osvetlitev piktograma dosežena z lasersko gravuro. Svetlobni vir integriran v ploščo. Zaprt rob standardno v beli barvi, po naročilu možna dobava v poljubnem RAL. Piktogramski znak do roba plošče omogoča maksimalno razdaljo razpoznavnosti. Razpoznavnost 22m, smer DOL. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; STRING 2 DA/DE, Pikto Gr.2 PU | Pictogram LED panel in patented din-LED-LASER technology, panel thickness 16mm. Uniform illumination of the pictogram achieved by laser engraving. Light source integrated in the panel. Closed edge in white as standard, any RAL colour can be supplied on request. Pictogram sign to the edge of the panel allows maximum visibility distance. Visibility 22m, bearing DOWN. 50.000 hours warranty. As for example: din-Sicherheitstechnik; STRING 2 DA/DE, Pikto Gr.2 PU | kos | 29 |  | 0
2.61 | -Z9N Dobava in montaža: Dimabilna piktogramska LED svetilka v patentirani din-LED-LASER tehnologiji. Ohišje za stensko nadgradno ali delno vgradno montažo, bele barve RAL 9003, možnost dobave v poljubni barvi po izboru arhitekta. Svetilka omogoča avtomatsko adresiranje ter mešano programiranje trajnega in pripravnega spoja na istem tokokrogu brez dodatnega kabliranja. Stopnja zaščite IP20. Dovoljeno temperaturno območje uporabe -15°C do +40°C. Dovoljena priključna napetost 24V DC +/-20%. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; STRING 2 WAP/WAP plus, PLC | -Z9N Supply and installation: Dimmable pictogram LED luminaire in patented din-LED-LASER technology. Housing for wall-mounting or semi-recessed mounting, white RAL 9003, available in any colour of the architect's choice. The luminaire allows automatic addressing and mixed programming of permanent and standby junction on the same circuit without additional cabling. Protection rating IP20. Permissible temperature range -15°C to +40°C. Allowed connection voltage 24V DC +/-20%. 50.000 hours warranty. Such as: din-Sicherheitstechnik; STRING 2 WAP/WAP plus, PLC | kos | 67 |  | 0
2.62 | Piktogramska LED plošča v patentirani din-LED-LASER tehnologiji, debelina plošče 16mm. Enakomerna osvetlitev piktograma dosežena z lasersko gravuro. Svetlobni vir integriran v ploščo. Zaprt rob standardno v beli barvi, po naročilu možna dobava v poljubnem RAL. Piktogramski znak do roba plošče omogoča maksimalno razdaljo razpoznavnosti. Razpoznavnost 22m, smer DOL. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; STRING 2 WAP, Pikto Gr.2, PU | Pictogram LED panel in patented din-LED-LASER technology, panel thickness 16mm. Uniform illumination of the pictogram achieved by laser engraving. Light source integrated in the panel. Closed edge in white as standard, any RAL colour can be supplied on request. Pictogram sign to the edge of the panel allows maximum visibility distance. Visibility 22m, bearing DOWN. 50.000 hours warranty. Such as: din-Sicherheitstechnik; STRING 2 WAP, Pikto Gr.2, PU | kos | 67 |  | 0
2.63 | -Z9NLA Dobava in montaža: Dimabilna piktogramska LED svetilka v patentirani din-LED-LASER tehnologiji. Ohišje za stensko nadgradno ali delno vgradno montažo, bele barve RAL 9003, možnost dobave v poljubni barvi po izboru arhitekta. Svetilka omogoča avtomatsko adresiranje ter mešano programiranje trajnega in pripravnega spoja na istem tokokrogu brez dodatnega kabliranja. Stopnja zaščite IP20. Dovoljeno temperaturno območje uporabe -15°C do +40°C. Dovoljena priključna napetost 24V DC +/-20%. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; STRING 2 WAP/WAP plus, hp PLC | -Z9NLA Supply and installation: Dimmable pictogram LED luminaire in patented din-LED-LASER technology. Housing for wall-mounting or semi-recessed mounting, white RAL 9003, available in any colour of the architect's choice. The luminaire allows automatic addressing and mixed programming of permanent and standby junction on the same circuit without additional cabling. Protection rating IP20. Permissible temperature range -15°C to +40°C. Allowed connection voltage 24V DC +/-20%. 50.000 hours warranty. Such as: din-Sicherheitstechnik; STRING 2 WAP/WAP plus, hp PLC | kos | 150 |  | 0
2.64 | Piktogramska LED plošča v patentirani din-LED-LASER tehnologiji, debelina plošče 16mm. Enakomerna osvetlitev piktograma dosežena z lasersko gravuro. Svetlobni vir za osvetlitev piktograma integriran v plošči. Plošča ima dodatno funkcijo optimalne osvetlitve poti umika oz. opreme APZ. Zaprt rob standardno v beli barvi, po naročilu možna dobava v poljubnem RAL. Piktogramski znak do roba plošče omogoča maksimalno razdaljo razpoznavnosti. Razpoznavnost 22m, smer DESNO. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; STRING 2 WAP LA, Pikto Gr.2, PR | Pictogram LED panel in patented din-LED-LASER technology, panel thickness 16mm. Uniform illumination of the pictogram achieved by laser engraving. Light source for pictogram illumination integrated in the panel. Panel has an additional function for optimum illumination of the escape route or APZ equipment. Closed edge in white as standard, on request in any RAL colour. Pictogram sign to the edge of the panel allows maximum visibility distance. Bearing 22m, bearing RIGHT. 50.000 hours warranty. Such as: din-Sicherheitstechnik; STRING 2 WAP LA, Pikto Gr.2, PR | kos | 60 |  | 0
2.65 | Piktogramska LED plošča v patentirani din-LED-LASER tehnologiji, debelina plošče 16mm. Enakomerna osvetlitev piktograma dosežena z lasersko gravuro. Svetlobni vir za osvetlitev piktograma integriran v plošči. Plošča ima dodatno funkcijo optimalne osvetlitve poti umika oz. opreme APZ. Zaprt rob standardno v beli barvi, po naročilu možna dobava v poljubnem RAL. Piktogramski znak do roba plošče omogoča maksimalno razdaljo razpoznavnosti. Razpoznavnost 22m, smer DOL. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; STRING 2 WAP LA, Pikto Gr.2, PU | Pictogram LED panel in patented din-LED-LASER technology, panel thickness 16mm. Uniform illumination of the pictogram achieved by laser engraving. Light source for pictogram illumination integrated in the panel. Panel has an additional function for optimum illumination of the escape route or APZ equipment. Closed edge in white as standard, on request in any RAL colour. Pictogram sign to the edge of the panel allows maximum visibility distance. Visibility 22m, bearing DOWN. 50.000 hours warranty. Such as: din-Sicherheitstechnik; STRING 2 WAP LA, Pikto Gr.2, PU | kos | 54 |  | 0
2.66 | Piktogramska LED plošča v patentirani din-LED-LASER tehnologiji, debelina plošče 16mm. Enakomerna osvetlitev piktograma dosežena z lasersko gravuro. Svetlobni vir za osvetlitev piktograma integriran v plošči. Plošča ima dodatno funkcijo optimalne osvetlitve poti umika oz. opreme APZ. Zaprt rob standardno v beli barvi, po naročilu možna dobava v poljubnem RAL. Piktogramski znak do roba plošče omogoča maksimalno razdaljo razpoznavnosti. Razpoznavnost 22m, smer LEVO. Garancija 50.000 ur. Kot na primer: din-Sicherheitstechnik; STRING 2 WAP LA, Pikto Gr.2, PL | Pictogram LED panel in patented din-LED-LASER technology, panel thickness 16mm. Uniform illumination of the pictogram achieved by laser engraving. Light source for pictogram illumination integrated in the panel. Panel has an additional function for optimum illumination of the escape route or APZ equipment. Closed edge in white as standard, on request in any RAL colour. Pictogram sign to the edge of the panel allows maximum visibility distance. Visibility 22m, bearing LEFT. 50.000 hours warranty. Such as: din-Sicherheitstechnik; STRING 2 WAP LA, Pikto Gr.2, PL | kos | 35 |  | 0
2.67 | Piktogramska nalepka na aluminijasti ploščici, smer DOL. Razpoznavnost 16m. Kot na primer: din-Sicherheitstechnik; S2-PX-ALU, ohne Bohrung | Pictogram label on aluminium plate, direction DOWN. Visibility 16 m. As for example: din-Sicherheitstechnik; S2-PX-ALU, ohne Bohrung | kos | 13 |  | 0
| ZASILNA RAZSVETLJAVA | EMERGENCY LIGHTING |  |  |  | 0

## 3.7.3_Ostalo
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.7 | ELEKTRO DELA | ELECTRICAL WORKS
3.7.3 | OSTALO | OTHER |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
3 | OSTALO | OTHER
3.1 | Izvedba meritev in funkcionalnega pregleda elektroinstalacij z izdelavo zapisnikov in poročil za celoten sistem v sestavi : | Carrying out measurements and functional inspection of the electrical installations, producing minutes and reports for the entire system as a whole: | kpl | 1 |  | 0
| - merjenje osvetlitve z izdelavo grafičnih načrtov merilnih točk | - measuring illuminance by producing graphical plans of the measuring points
| - svetlobnotehnične meritve zunanje razsvetljave | - light-technical measurements of external lighting
| - svetlobnotehnične meritve zasilne razsvetljave | - light-technical measurements of emergency lighting
| - merjenje izolacijske upornosti | - insulation resistance measurement
| - funkcionalni preizkus | - functional test
3.2 | Pozitivne ocene, atesti, certifikati in potrdila ustreznih inštitucij za dokazovanje primerne kakovosti vgrajenih naprav, napeljav, materialov in montažnih del (EIMV, IVD, ZAG, SIQ in podobno). | Positive evaluations, attestations, certificates and attestations of the relevant institutions to prove the adequate quality of the installed devices, installations, materials and assembly works (EIMV, IVD, ZAG, SIQ, etc.). | kpl | 1 |  | 0
3.3 | Razna nepredvidena dela, ki se obračunajo po urah s potrditvijo nadzornika v gradbenem dnevniku. | Miscellaneous unforeseen work, billed by the hour with the supervisor's approval in the construction logbook. | ur | 24 |  | 0
| OSTALO | OTHER |  |  |  | 0