## 0_Naslovnica
OPOZORILO! Vsi prevodi v angleščino so strojno izdelani in zgolj informativne narave. V primeru kakršnekoli nejasnosti ali dvoma izključno velja izvirno besedilo v slovenščini. WARNING! All translations into English have been produced by machine translation and are provided for informational purposes only. In the event of any ambiguity or uncertainty, the original Slovenian text shall prevail exclusively.
| / | / | [5 empty] | /
| Sprem./Rev.: | Opis spremembe/Description of Changes: | [5 empty] | Datum/Date: | Podpis/Signature:
| Investitor/Investor: |  |  |  |  | Gradnja/Facility
|  |  | Univerza v Ljubljani Kongresni trg 12 1000 Ljubljana, Slovenija |  |  | Fakulteta za strojništvo/Faculty of Mechanical Engineering
| Projektant/Design Engineer: |  |  |  |  | Del objekta/sistem/Building/System:
|  |  | IBE, svetovanje, projektiranje in inženiring Ljubljana, Slovenija |  |  | STAVBA FAKULTETE/FACULTY BUILDING
| Projektant/Design Engineer: |  |  |  |  | Vrsta načrta/Documentation:
3 NAČRT S PODROČJA ELEKTROTEHNIKE/ DOC. IN THE FIELD OF ELECTRICAL ENGINEERING
|  | Ime in priimek/Name and Surname: |  |  | Id. št./Id. No: | Vsebina risbe (dokumenta)/Document Title:
| Vodja proj./ Des. Manager: | Boštjan Vuga, univ. dipl. inž. arh., grad. dip. (AA) |  |  | ZAPS 0035 PA PPN | PR. POPIS ELEKTRO DEL/BOQ OF ELEC. WORKS 3/8 Univerz. kabliranje, WiFi in drugi IKS/Struct. cabling, WiFi, and Other I&C Systems
| Poobl. strok./ Cert. Profess.: | Robert Bobovnik, dipl. inž. el. |  |  | IZS E-2380
| Poobl. strok./ Cert. Profess.: |  |  |  |  | Št. proj./ Proj. No.: | 362-19 |  | Vrsta dokument./ Document. Type: | DZR
| Izdelal/ Creator: | Enis Rokša, mag. inž. el. |  |  |  | Klas. ozn./ Class. No.: | -- |  | Stran/ Page: | 1/*
| Datum/ Date: | maj/May 2026 |  | Merilo/ Scale: | / | Ident. ozn./ Id. No: | JULFS--6E9352P

## 0_Osebe
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
POOBLAŠČENI STROKOVNJAKI, ODGOVORNI ZA IZDELAVO PROJEKTANTSKEGA POPISA:
Id. št. ZAPS/IZS | Pooblaščeni strokovnjak | Strokovno področje
IZS E-2380 | Robert Bobovnik, dipl. inž. el. | Univerzalno kabliranje, WiFi in drugi IKS
SODELAVCI PRI IZDELAVI PROJEKTANTSKEGA POPISA:
/ | Robert Stavar | Univerzalno kabliranje, WiFi in drugi IKS
CERTIFIED EXPERTS RESPONSIBLE FOR ELABORATING THE BILL OF QUANTITIES:
Id. No ZAPS/IZS | Certified Expert | Area of Expertise
IZS E-2380 | Robert Bobovnik, dipl. inž. el. | Universal cabling, WiFi and other IKS
COLABORATORS IN THE ELABORATING THE BILL OF QUANTITIES:
/ | Robert Stavar | Universal cabling, WiFi and other IKS

## 0.1_Uvod-STP
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
0.1 | SPLOŠNI TEHNIČNI POGOJI | GENERAL TECHNICAL CONDITIONS
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic operator with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
0.1.1 | Izvajalec se obveže, da bo upošteval veljavno zakonodajo, ki ureja graditev objektov v Republiki Sloveniji, vključno s povezanimi podzakonskimi akti, predpisi, tehničnimi smernicami, standardi, pravili stroke in dobro gradbeno prakso. Prav tako mora izvajalec upoštevati vse zahteve izdanega integralnega gradbenega dovoljenja in vsa dela izvesti skladno s projektno dokumentacijo ter ostalimi pogoji, objavljenimi v razpisni dokumentaciji. | The Contractor undertakes to comply with the applicable legislation governing the construction of buildings in the Republic of Slovenia, including related by-laws, regulations, technical guidelines, standards, professional rules and good construction practice. The Contractor shall also comply with all the requirements of the integral building permit issued and shall carry out all works in accordance with the project documentation and other conditions published in the tender documentation.
0.1.2 | Dela lahko izvaja samo izvajalec, ki je registriran za opravljanje gradbene dejavnosti in ima za tovrstna dela ustrezno zavarovanje za škodo, certifikate, tehnično izobražen kader, sredstva ter je usposobljen za samostojno pripravo in izvedbo del. | The work may only be carried out by a contractor who is registered to carry out construction work and who has the appropriate insurance for such work, certificates, technically trained staff, resources and is qualified to prepare and carry out the work independently.
0.1.3 | Izvajalec odgovarja za kakovost izvedbe vseh del. | The Contractor shall be responsible for the quality of the execution of all works.
0.1.4 | Izvajalec nosi vso odgovornost za nesreče in škodo, ki nastane na objektu ali v okolici zaradi njegovega dela. | The Contractor shall bear all liability for accidents and damage to the installation or the surrounding area caused by his work.
0.1.5 | Pred oddajo ponudbe se je izvajalec dolžan seznaniti z območjem predvidenim za gradnjo in temu prilagoditi vsa potrebna dela, kar mora biti zajeto v ponudbi. V neposredni bližini predvidene gradnje se nahajajo stavbe, v katerih potekajo izobraževalni in raziskovalni procesi. Zato bo izvajalec moral izvajati kontrolo hrupa in kontrolo vibracij. Dela, ki so hrupna in dela, ki povzročajo vibracije bo izvajalec moral preprečiti oziroma jih izvesti na način, da povzročajo minimalne vplive. Tehnologijo rušenja, pilotiranja in tehnologijo izvedbe ostalih del bo izvajalec moral prilagoditi tako, da bo vpliv minimalen. Izvajalec mora preprečiti in zmanjšati emisije delcev iz gradbišča na najmanjšo možno mero. | Before submitting a tender, the contractor is obliged to familiarise himself with the area to be constructed and to adapt any necessary works accordingly, which must be included in the tender. In the immediate vicinity of the proposed construction, there are buildings in which educational and research processes take place. The contractor will therefore be required to carry out noise and vibration control. Noise and vibration works will have to be avoided or carried out in such a way as to minimise the impact. Demolition, piling and other works will have to be adapted to minimise the impact. The contractor must avoid and minimise the emission of particulates emitted from the construction site as far as is reasonably practicable.
0.1.6 | Izvajalec je pred oddajo ponudbe dolžan pregledati projektno dokumentacijo in ostale pogoje, ki so del razpisne dokumentacije V primeru morebitnih napak in neskladij je izvajalec dolžan na to opozoriti naročnika pred oddajo ponudbe. | The Contractor is obliged to review the project documentation and other conditions forming part of the tender documentation before submitting the tender In case of any errors or inconsistencies, the Contractor is obliged to bring these to the attention of the Contracting Authority before submitting the tender.
0.1.7 | Pred oddajo ponudbe je izvajalec dolžan preveriti ustreznost popisov del in količin v teh popisih ter njihovo skladnost z ostalimi dokumenti projektne dokumentacije, ki so del razpisne dokumentacije. Prav tako je izvajalec dolžan preveriti vse detajle in sheme. Vse izmere je potrebno preveriti po posameznih projektih oz. načrtih, ki sestavljajo razpisno dokumentacijo. V primeru ugotovljenih neskladij je v času priprave ponudbe obvezan o tem obvestiti naročnika. | Before submitting a tender, the Contractor shall check the adequacy of the inventories of works and quantities in these Bills of Quantities and their conformity with the other documents of the project documentation forming part of the tender documentation. The Contractor shall also check all details and diagrams. All measurements shall be checked against the individual projects or plans forming part of the tender documentation. In the event of any discrepancies, the Contractor shall inform the Contracting Authority at the time of preparing the tender.
0.1.8 | Pred oddajo ponudbe je izvajalec dolžan v tem popisu preveriti zmnožke in seštevke ter prenose le-teh v rekapitulacijo. Izvajalec se s pripravo ponudbe obvezuje, da je prebral vse celice in elemente celotnega popisa, vključno z vsemi postavkami in splošnimi navodili ali določili in je preveril pravilnost preračuna ter s tem zagotavlja ponudbeno vrednost. | Before submitting a tender, the Contractor is required to check the products and totals in this Bill of Quantities (BoQ) and their transfer to the recapitulation. The Contractor undertakes, by preparing a tender, to have read all the cells and elements of the complete BoQ, including all headings and general instructions or provisions, and to have checked the correctness of the conversion, thereby guaranteeing the value of the tender.
0.1.9 | Dela bo izvajalec moral izvajati po predloženi projektni dokumentaciji, detajlih in z upoštevanjem navodil in potrditev projektanta, nadzornika in investitorja. Vso potrebno delavniško dokumentacijo zagotovi izvajalec del v okviru ponujene cene. | The Contractor shall carry out the works in accordance with the submitted design documents, details and subject to the instructions and approvals of the Designer, the Supervisor and the Investor. All necessary workshop documentation shall be provided by the Contractor within the scope of the price quoted.
0.1.10 | Pred izvedbo posameznih del je izvajalec dolžan pregledati projektno dokumentacijo za izvedbo gradnje (PZI) in elaborate. Na morebitne napake v dokumentaciji ali neskladja med posameznimi načrti ali deli načrtov (popisi del, tehnična poročila, lokacijski in tehnični prikazi) izvajalec opozori nadzornika in projektanta, in se z njima pravočasno uskladi. | The Contractor shall review the Detailed Design documentation (PZI) and the studies before carrying out the individual works. The Contractor shall draw the attention of the Supervisor and the Designer to any errors in the documentation or discrepancies between the individual designs or parts of designs (BoQ, technical reports, location and technical drawings) and shall coordinate with them in good time.
0.1.11 | Tehnični opisi, prikazi, detajli, sheme ter ostali dokumenti v PZI dokumentaciji predstavljajo dodaten opis popisnih postavk gradbeno obrtniških in inštalacijskih del ter jih je potrebno dosledno upoštevati skupaj s popisom del. | The technical descriptions, illustrations, details, diagrams and other documents in the Detailed Design documentation (PZI) are additional descriptions of the BoQ inventory items of the building, construction and installation works and must be strictly followed together with the BoQ.
0.1.12 | Specifikacije in zahteve, navedene v popisu, se ne smejo upoštevati kot edine zahteve. Izvajalec je dolžan v ceni zajeti in dobaviti vse elemente opreme ter opraviti dela in storitve, ki niso eksplicitno navedeni, a so bistvenega pomena za funkcionalnost, skladnost s predpisi ter kontinuirano, zanesljivo in varno obratovanje opreme. | The specifications and requirements set out in the BoQ shall not be taken as the only requirements. The Contractor shall be obliged to include in the price and supply all items of equipment and to carry out works and services which are not expressly mentioned but which are essential for the functionality, regulatory compliance and continuous, reliable and safe operation of the equipment.
0.1.13 | Vsa dela morajo biti izvedena kvalitetno in iz materialov z zahtevanimi lastnostmi, izvedena skladno z veljavno zakonodajo in z upoštevanjem navodil za vgradnjo za izbrane materiale in opremo, s predložitvijo predpisanih izjav o lastnostih in/ali certifikatov. Vsi gradbeni proizvodi (GP) morajo biti označeni s CE oznako. | All work shall be of good quality and be executed with materials of the required characteristics, in accordance with the applicable legislation and in compliance with the installation instructions for the materials and equipment selected, and shall be accompanied by the prescribed declarations of performance and/or certificates. All construction products (GP) shall bear the CE marking.
0.1.14 | Za vsako opisano delo v popisu je potrebno upoštevati celotno potrebno delo, ves osnovni in pomožni material, prevoz materiala in orodja na objekt, notranje transporte, delovne in pomožne odre, zaključno čiščenje in odstranitev odpadkov po dovršenem delu. | For each work described in the inventory, the total work required, all basic and ancillary materials, the transport of materials and tools to the site, internal transports, working and ancillary scaffolding, final cleaning and the disposal of waste after the work has been completed must be taken into account.
0.1.15 | Vsa delovna sredstva, organizacija in koordinacija del, pripravljalna, spremljajoča in zaključna dela, potrebni montažni in tesnilni materiali ter podkonstrukcije so sestavni del posameznih postavk. | All labour, organisation and coordination of the works, preparatory, accompanying and finishing works, necessary prefabrication and sealing materials and substructures are part of the individual items.
0.1.16 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - načrt organizacije gradbišča s podrobnim terminskim planom in izvedba vseh pripravljalnih del, postavitev, organizacija, zaščita in prijava gradbišča, gradbiščnih objektov, ureditev začasnih deponij, tekoče vzdrževanje, skupaj s plačilom splošnih stroškov pristojbin in davkov upravnih organov, pridobivanju raznih dovoljenj in soglasij za izvedbo, ograditev gradbišča in postavitev gradbene table in prometne signalizacije, zagotavljanje ustrezne varnosti na gradbišču, tekoče vzdrževanje in končna odstranitev gradbišča; - zagotovitev potrebnih začasnih površin za transportne poti in gradnjo izven območja gradbišča s plačilom stroškov za sanacijo in vzpostavitev okoliških zemljišč in objektov v prvotno stanje (soglasja, odškodnine, itd.); - začasni odvoz, deponiranje in vračanje izkopanega materiala, ki ga ne bo možno deponirati na gradbišču; - odvoz in zagotovitev odstranjevanja odpadnega gradbenega materiala skladno z zakonodajo na področju ravnanja z odpadki (odvoz na urejene deponije s plačilom komunalnih prispevkov in taks itd.); - oteženi izkop v mokrem terenu, izkop v vodi, odvod meteorne vode iz gradbene jame in vode, ki se izceja iz bočnih strani izkopov; - ustrezno varovanje izkopa gradbene jame za objekt in ostalih manjših posameznih izkopov za izvedbo komunalne infrastrukture brez posegov na sosednja zemljišča; - ustrezno varovanje obstoječih objektov, infrastrukture in okolice v času gradnje ter dokumentiranje vseh morebitnih škodnih dogodkov; - pripravljalna, spremljajoča in zaključna dela (zakoličbe, zagotovitev potrebnih komunalnih priključkov za potrebe izvajanja gradnje, izvedba začasnih inštalacij, označevanje podzemnih vodov, postavljanje in vzdrževanje zakoličbenih profilov, izvedba in označevanje novih in starih križanj ter morebitna zaščita križanj komunalnih vodov, geodetski posnetki in izdajanje vmesnih posnetkov izvedene infrastrukture naročniku, izdelava zbirnih kart, itd.), v kolikor ni to drugače določeno; - pridobivanje soglasij in izvedba morebitnih zapor na vseh cestah s plačilom stroškov, nadomestil in pristojbin; - zagotovitev oz. postavitev in končna odstranitev po zaključku gradnje začasnih skladišč in začasnega pisarniškega kontejnerskega objekta vključno z opremo za dve delovni mesti in za skupne operativne sestanke vel. ca. 40 m2 za potrebe naročnika, s tekočim vzdrževanjem in čiščenjem. | The following must also be included or taken into account in the uniform prices for individual items: - a construction site organisation plan with a detailed timetable and the execution of all preparatory works, the setting-up, organisation, protection and registration of the construction site, site facilities, the arrangement of temporary storage facilities, ongoing maintenance, including the payment of general costs of fees and taxes of the administrative authorities, the obtaining of various permits and consents for the execution, the fencing of the site and the erection of construction signs and traffic signals, the provision of adequate security on the site, ongoing maintenance and the final dismantling of the construction site; - provision of the necessary temporary areas for transport routes and off-site construction, with costs for restoration and reinstatement of surrounding land and buildings (consents, compensation, etc.); - temporary removal, storage and return of excavated material that cannot be stored on site; - removing and disposing of waste building materials in accordance with waste management legislation (removal to regulated landfill sites with payment of municipal fees and charges, etc.); - difficult excavation in wet ground, excavation in water, drainage of rainwater from the construction pit and water draining from the sides of excavations; - adequate protection of the excavation of the construction pit for the building and other small individual excavations for the implementation of the utility infrastructure without encroaching on neighbouring land; - adequate protection of existing facilities, infrastructure and the surrounding area during construction, and documentation of any damage incidents; - preparatory, accompanying and finishing works (stake-out, provision of the necessary utility connections for the needs of construction, execution of temporary installations, marking of underground lines, installation and maintenance of stake-out profiles, execution and marking of new and old crossings and possible protection of crossings of utility lines, geodetic surveys and issuing of intermediate images of the completed infrastructure to the client, production of summary maps, etc.), unless otherwise specified; - obtaining consents and implementing any road closures, with costs, compensation and fees; - provision or erection and final removal on completion of construction of temporary storage and temporary office container building including equipment for two workstations and for joint operational meetings of approx. 40 m2 for the needs of the client, with ongoing maintenance and cleaning.
0.1.17 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - izdelava montažne tehnične dokumentacije, detajlov izvedbe in vse druge potrebne delavniške dokumentacije (s področja arhitekture, gradbeništva, elektrotehnike, strojništva in zunanje ter krajinske ureditve) ter pridobitev obvezne potrditve s strani projektanta, nadzornika in investitorja; - odprava vseh vrst inštalacijskih kolizij z izvajanjem potrebnih premikov inštalacij in njihovim usklajevanjem na mestu montaže, vse v obsegu, ki ne vpliva na projektirano rešitev ali tip inštalacij oz. opreme; - zagotavljanje kompletnosti elektro-instalacijskih sistemov s področja avtomatike za doseganje njihove popolne funkcionalnosti delovanja; - stroški za nadzor in koordinacijo izvedbe vseh elektro napeljav, ki so predmet končne instalacije proizvoda (senčila, vrata, okna,…); - izdelava montažnih skic in detajlov za izvedbo v dogovoru z vodjo gradnje in nadzornikom; - izdelava in predstavitev vzorcev v ustrezni velikosti za potrditev projektanta, nadzornika in investitorja; - zagotavljanje varnosti in zdravja pri delu, zlasti izvajanje vseh del, ki izhajajo in ukrepov, ki izhajajo iz določil veljavnih predpisov varstva pri delu in zahtev Varnostnega načrta;- stroški garancij, ki jih mora izvajalec predložiti naročniku. | The following must also be included or taken into account in the uniform prices for individual items: - preparation of prefabricated technical documentation, construction details and all other necessary workshop documentation (architectural, civil, electrical, mechanical, exterior and landscaping) and obtaining the mandatory approval of the designer, the supervisor and the investor; - elimination of all types of installation conflicts by carrying out the necessary relocation of installations and their coordination at the installation site, all to the extent that it does not affect the design solution or the type of installation or equipment; - ensuring the completeness of electrical installation systems in the automation sector to achieve their full operational functionality; - the cost of supervising and coordinating the installation of all the electrical installations that are the subject of the final installation of the product (blinds, doors, windows, etc.); - preparation of erection drawings and details for implementation in agreement with the construction manager and supervisor; - production and presentation of samples in appropriate sizes for the approval of the designer, the supervisor and the investor; - ensuring health and safety at work, in particular the implementation of all the works arising from and the measures resulting from the provisions of the applicable occupational safety regulations and the requirements of the Safety Plan; - the cost of the guarantees to be provided by the contractor to the client.
0.1.18 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - strošek vodje del glavnega izvajalca, ki bo izvajal tudi koordinacijo s podizvajalci in z drugimi izvajalci, ki jih bo izbral naročnik in bo opravljal delo vodje gradbišča; - koordinacija del z ostalimi izvajalci oz. podizvajalci del, projektantom, nadzornikom in investitorjem pri medsebojnem usklajevanju organizacije gradbišča in časovnega načrta del ter pri usklajevanju izdelave plana montaže, potrjenih s strani vseh udeležencev gradnje; - stroški koordinacije, sodelovanja in usklajevanja z dobavitelji tehnološke, laboratorijske, eksperimentalne in vse ostale pohištvene ter multimedijske opreme ter z vsemi ostalimi dobavitelji oz. podizvajalci na objektu; - stroški izdelave situacij; - stroški zavarovanja objekta v času izvedbe del in delavcev ter materiala na gradbišču v času izvajanja del, od začetka del do pridobitve uporabnega dovoljenja za objekt. Zavarovanje mora biti sklenjeno pri ustrezni zavarovalni družbi najmanj v višini pogodbene vrednosti ali v zakonsko predpisani vrednosti (v kolikor zavarovanje v višini pogodbene vrednosti presega zakonsko dovoljeno), za ves čas trajanja izvedbe del do uspešne primopredaje objekta; - preizkušanje kvalitete materiala, ki se vgrajuje in dokazovanje kvalitete s certifikati oz. tehničnimi soglasji; - izvedba vseh zahtevanih testov in preizkusov (npr. tlačni preizkusi, termografski pregledi, meritve elektromagnetnega sevanja, hrupa, itd.), poskusnega obratovanja celotnega objekta s poudarkom na vseh inštalacijah ter izvajanje predpisanega monitoringa v skladu s Poročilom o vplivih na okolje (pred gradnjo, med gradnjo in po končani gradnji); - izdelava izkaza požarne varnosti, vključno s sprotnim spremljanjem gradnje in izvajanjem požarnovarnostnih zahtev ter izdelava Požarnega reda z obveznimi prilogami; - izdelava Izkaza zaščite pred hrupom v stavbah; - izdelava Izkaza energijskih lastnosti stavbe in energetske izkaznice; - sodelovanje z izvajalci gradbenega in projektantskega nadzora in investitorjem za izvedbo tehničnega pregleda in priprava primopredaje, ki mora vsebovati vso zahtevano dokumentacijo, predvsem pa: izjave o skladnosti, požarni izkaz in ostale izkaze ter obvezne tabele, dokazilo o zanesljivosti objekta (DZO), certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo in vzdrževanje ter vse ostale dokumente v skladu s predpisi in pogodbenimi določili. | The following must also be included or taken into account in the uniform prices of the individual items: - the cost of a works manager for the main contractor, who will also coordinate with subcontractors and other contractors selected by the client and act as site manager; - coordination of the works with other contractors or subcontractors, the designer, the supervisor and the investor in coordinating the organisation of the construction site and the timetable for the works, and in coordinating the production of an installation plan approved by all the participants in the construction; - the costs of coordination, cooperation and coordination with suppliers of technological, laboratory, experimental and all other furniture and multimedia equipment, as well as with all other suppliers or subcontractors on the site; - the cost of drawing up situations; - the cost of insuring the building during the execution of the works and the workers and materials on site during the execution of the works, from the start of the works until the building has been licensed for occupation. The insurance must be taken out with a suitable insurance company for at least the contract value or the legal value (if the insurance for the contract value exceeds the legal value), for the entire duration of the works until the successful handover of the building; - testing the quality of the material to be installed and proving it with certificates or technical approvals; - carrying out all required tests and trials (e.g. pressure tests, thermographic inspections, electromagnetic radiation measurements, noise measurements, etc.), trial operation of the entire building, with emphasis on all installations, and carrying out the required monitoring in accordance with the Environmental Impact Assessment Report (before, during and after construction); - preparation of a fire safety statement, including ongoing monitoring of construction and implementation of fire safety requirements, and preparation of a Fire Safety Order with mandatory annexes; - preparation of a Noise Protection Statement for buildings; - preparation of the Building Energy Performance Report and Energy Performance Certificate; - cooperation with the construction and design supervision contractors and the investor to carry out the technical inspection and prepare the handover, which must include all the required documentation, in particular: declarations of conformity, fire and other statements and mandatory tables, proof of reliability of the building (DZO), certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use and maintenance, and all other documents in accordance with the regulations and the contractual provisions.
0.1.19 | V enotnih cenah posameznih postavk, ki se nanašajo na opremo in posamezne sisteme, mora biti zajeto oz. upoštevano tudi naslednje: - dobava oz. transport, - stroški za vse delovne stroje za dvigovanje bremen in delovne košare za dostope do delovišč; - morebitni stroški povzročeni upravljavcem GJI, ki bi nastali v zvezi s predmetno gradnjo; - montaža, vključno s pomožnim montažnim materialom (vezni, tesnilni in pritrdilni material, sidra, nosilni profili, podkonstrukcije in podobno) in navodili proizvajalca, - odprava vseh kolizij sistemov s stenami in med sistemi, - izvedba vseh potrebnih tesnjenj, - priključitev in nastavitve, vključno z morebitnim kalibriranjem, - zagon, testiranje in meritve, vključno s poročili, - šolanje uporabnikov oz. vzdrževalnega osebja za uporabo in vzdrževanje sistemov, - navodila za obratovanje in vzdrževanje, - vsi potrebni certifikati, izjave o skladnosti oz. potrdila ter - vsa druga pomožna dela in material, da se zagotovi funkcionalnost posamezne postavke popisa. | The following must also be included or taken into account in the uniform prices for individual items relating to equipment and individual systems: - delivery/transport, - the cost of all lifting machines and work baskets for access to work sites; - any costs incurred to the operators of utility infrastructure (GJI) in connection with the subject construction; - installation, including ancillary installation materials (bonding, sealing and fixing materials, anchors, support profiles, substructures, etc.) and manufacturer's instructions, - eliminating all system-to-wall and system-to-system collisions, - all necessary sealing work, - connection and set-up, including calibration if necessary, - commissioning, testing and measurements, including reports, - training users or maintenance staff in the use and maintenance of the systems, - operating and maintenance instructions, - any necessary certificates, declarations of conformity or attestations; and - all other ancillary works and materials to ensure the functionality of each inventory item.
0.1.20 | Vsi odri morajo biti upoštevani v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All scaffolding must be included in the uniform prices of the items listed, except where specifically mentioned.
0.1.21 | Vsi delovni in pomožni odri, lestve in ostala potrebna pomožna sredstva, kot tudi čiščenje vseh elementov po končanih delih, mora biti upoštevano v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All working and auxiliary scaffolding, ladders and other necessary ancillaries, as well as the cleaning of all elements after completion of the works, shall be included in the uniform prices of the items listed, except those specifically mentioned.
0.1.22 | Delavniško dokumentacijo za vse nosilne jeklene konstrukcije in podkonstrukcije izdela izvajalec, strošek izdelave delavniške dokumentacije se upošteva v ponujenih cenah in se ne obračuna posebej. | The cost of the shop drawings for all steelwork and substructures shall be included in the prices quoted and shall not be charged separately.
0.1.23 | V enotnih cenah postavk mora biti vključeno tudi vgrajevanje vseh instalacijskih razvodov v opaže armirano betonskih elementov in izdelava prehodov inštalacij ter dodatno izrezovanje utorov in prebojev v kamnite, zidane ali armirano-betonske stene, ponovno demontiranje in montiranje vseh vrst montažnih sten, vsa dodatna dela za zagotavljanje primernih križanj med posameznimi instalacijskimi vodi, izdelava vseh vrst ojačitev konstrukcij in podobna dela, ki zagotavljajo kakovostno vgradnjo vseh vrst instalacijskih vodov in niso posebej navedena v popisu GOI del. V ponudbi morajo biti upoštevana vsa drobna strojna in elektro instalacijska dela in transporti. | The installation of all installation ducts in the formwork of reinforced concrete elements and the construction of installation penetrations, as well as the additional cutting of grooves and penetrations in stone, masonry or reinforced concrete walls, the reassembly and reinstallation of all types of prefabricated walls, all additional work to ensure adequate crossings between individual installation ducts, the construction of all types of structural reinforcement and similar work to ensure the quality installation of all types of installation ducts and not specifically mentioned in the BoQ of the Construction, installation and finishing works (GOI) shall also be included in the uniform prices of the items. The tender shall take into account all minor mechanical and electrical installation work and transport.
0.1.24 | Vsi kovinski elementi in konstrukcije, ki bi lahko bili izpostavljeni atmosferskim in ostalim korozijskim vplivom, morajo biti ustrezno protikorozijsko zaščiteni. | All metallic elements and structures that could be exposed to atmospheric and other corrosive influences must be adequately protected against corrosion.
0.1.25 | Za vse večje jeklene dele se skladno s predpisi, izdelajo ustrezne ozemljitve, nevidno pritrjene in speljane na splošno ozemljitev objekta. | For all major steel parts, appropriate earth connections shall be made in accordance with the regulations, invisibly attached and connected to the general earth of the building.
0.1.26 | Za vse vidne elemente in serijske elemente je obvezna predhodna uskladitev obdelav, barv in materialov s projektantom na podlagi dostavljenih vzorcev v ustrezni velikosti. Obvezna je preveritev dejanskih mer na licu mesta in posledična prilagoditev elementov in njihove montaže. | For all visible elements and serial elements, it is mandatory to coordinate the finishes, colours and materials with the designer beforehand on the basis of the supplied samples in the appropriate size. It is mandatory to check the actual dimensions on site and to adjust the elements and their installation accordingly.
0.1.27 | Dimenzije obrtniških izdelkov in količine je potrebno pred naročanjem preveriti na objektu. Potrebna je uskladitev vseh elementov (kljuke, okovje, detajlne konstrukcije in obdelave, itd.) s projektantom, nadzornikom in investitorjem. Izvajalec je dolžan pred izdelavo predložiti projektantu v potrditev ustrezne delavniške načrte in detajle. | The dimensions of the workmanship and quantities must be checked on site before ordering. All elements (hooks, fittings, detailed construction and finishes, etc.) must be coordinated with the designer, the supervisor and the investor. The contractor is obliged to submit the relevant workshop plans and details to the designer for approval before manufacture.
0.1.28 | V posameznih postavkah popisa so navedeni proizvajalci in/ali tipi posameznih sistemov, materialov ali opreme, s čimer so zgolj natančno opredeljene zahtevane tehnične lastnosti. Izvajalec del lahko ponudi nadomesten sistem, material ali opremo drugega proizvajalca in tipa, pri čemer morajo biti tehnične lastnosti ponujenega sistema, materiala ali opreme enakovredne ali boljše od opredeljenih v popisu, dimenzijsko pa ne smejo presegati projektiranih dimenzij. Vse funkcijske in tehnične karakteristike nadomestnih sistemov, materialov ali opreme mora izvajalec dokazati z ustrezno dokumentacijo. Vse morebitne posledice zaradi spremembe sistemov, materialov ali opreme vključno z morebitnimi spremembami oz. dopolnitvami BIM modelov in projektne dokumentacije, stroškovno in časovno bremenijo izvajalca. | The individual items of the Inventory shall specify the manufacturers and/or types of the individual systems, materials or equipment, thereby merely specifying the required technical characteristics. The Contractor may offer a substitute system, material or equipment of a different manufacturer and type, provided that the technical characteristics of the offered system, material or equipment shall be equivalent to or better than those specified in the BoQ, and shall not exceed the design dimensions. All functional and technical characteristics of the substitute systems, materials or equipment shall be demonstrated by the Contractor with appropriate documentation. Any consequences resulting from changes to systems, materials or equipment, including any changes or additions to the BIM models and project documentation, shall be borne by the Contractor in terms of cost and time.
0.1.29 | Vsako zamenjavo, uporabo in končni izbor nadomestnih sistemov, materialov, proizvodov in opreme morajo obvezno in pravočasno (pred dobavo in vgradnjo) pisno potrditi projektant (vseh sodelujočih strok), nadzornik in investitor. | Any replacement, use and final selection of alternative systems, materials, products and equipment must be approved in writing by the designer (of all disciplines involved), the supervisor and the investor in a timely manner (prior to delivery and installation).
0.1.30 | Izvajalec mora v ponudbeno ceno vključiti tudi: - ves čas gradnje sprotno beleženje sprememb oz. odstopanj od PZI dokumentacije, vključno z izdelavo tekstualnega opisa sprememb, - pripravo podlog na nivoju PZI, ki so potrebne za posodobitev oz. uskladitev BIM modela z izvedenim stanjem (LOD 500) in izdelavo projektne dokumentacije izvedenih del (PID), - mesečno predajanje potrjenih sprememb opreme in materiala, ki vplivajo na BIM model, v formatu IFC, - vzdrževanje in uporabljanje pri izvedbi zadnje veljavne revizije PZI dokumentacije, vključno z dopolnitvami PZI načrtov, ki so nastali zaradi sprememb med gradnjo. | The contractor must also include in the tender price: - keeping a record of changes or deviations from the construction documentation (PZI) throughout construction, including a textual description of the changes, - preparation of the Detailed Design (PZI) level documents required to update or align the BIM model with the as-built condition (LOD 500) and the preparation of the as-built project documentation for the works (PID), - monthly submission of approved equipment and material changes affecting the BIM model in IFC format, - maintenance and use in the execution of the last valid revision of the construction documentation (PZI), including additions to the construction design documentation (PZI) resulting from changes during construction.

## 0.2_Uvod-DGNB
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
0.2 | SPLOŠNI TEHNIČNI POGOJI ZA PODROČJE DGNB CERTIFICIRANJA | GENERAL TECHNICAL CONDITIONS FOR DGNB CERTIFICATION
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic entity with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
| Splošni pogoji za področje DGNB certificiranja predstavljajo dopolnilo splošnim tehničnim pogojem in ne odpravljajo drugih obveznosti in odgovornosti, ki jih ima izvajalec v skladu s predpisi in pogodbo. | The General Conditions for DGNB Certification are complementary to the General Technical Conditions and do not exclude other obligations and responsibilities that the Contractor has under the Regulations and the Contract.
0.2.1 | Izvajalec mora v svojih ponudbah upoštevati, da se bo objekt certificiral v skladu z zahtevami DGNB sistema certificiranja trajnostne gradnje, ter pravočasno (vsaj 60 dni pred vgradnjo posameznega produkta) dostaviti vso ustrezno dokumentacijo za vse v ponudbi zajete materiale, elemente in opremo. Zahtevana je uporaba materialov, elementov ali opreme, ki so okolju in ljudem prijazni, energetsko učinkoviti in obenem ustrezajo zahtevam DGNB sistema. Zahtevan nivo certifikata je: ZLATI CERTIFIKAT | The Contractor shall take into account in its tenders that the building will be certified in accordance with the requirements of the DGNB Sustainable Building Certification Scheme and shall deliver all relevant documentation for all materials, elements and equipment included in the tender in a timely manner (at least 60 days before the installation of each product). The use of materials, elements or equipment that are environmentally and human friendly, energy efficient and at the same time meet the requirements of the DGNB system is required. The required level of certification is: GOLD CERTIFICATE
0.2.2 | Podrobnejši opis DGNB sistema in navodila za posamezne kriterije so dostopna v dokumentu"DGNB Criteria Set New Construction Buildings, Version 2020 International", ki je na voljo na DGNB spletni strani https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria | A more detailed description of the DGNB system and guidance on the individual criteria is available in the document "DGNB Criteria Set New Construction Buildings, Version 2020 International", available on the DGNB website https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria
0.2.3 | Izvajalec mora v svojih ponudbah upoštevati, da je potrebno skladno z določili DGNB certifikacijskega sistema, pravočasno (pred pričetkom gradnje) dostaviti vso ustrezno dokumentacijo, za vse v ponudbi zajete materiale, elemente in opremo (tehnični list, varnostni list, izjava o lastnostih, tehnična navodila za ravnanje, servisiranje, vzdrževanje,...) v slovenskem jeziku. Vgradnja kakršnihkoli materialov, elementov ali opreme, se izvede zgolj na podlagi predhodne preveritve posredovane dokumentacije in obenem potrditve s strani nadzornika. | The Contractor must take into account in its tenders that, in accordance with the provisions of the DGNB certification system, all relevant documentation for all materials, elements and equipment included in the tender (technical data sheet, safety data sheet, declaration of properties, technical instructions for handling, servicing, maintenance,...) must be delivered on time (prior to the start of construction) in the Slovene language (in accordance with the provisions of the DGNB certification system). The installation of any materials, elements or equipment shall be subject to prior checking of the submitted documentation and, at the same time, to the approval of the Supervisor.
0.2.4 | Izbrani materiali, elementi, naprave, sistemi in oprema morajo prispevati k večji trajnosti stavbe v smeri zagotavljanja energetske učinkovitosti, ekonomičnega in enostavnega vzdrževanja ter čiščenja, dolge življenjske dobe, uporabe okolju prijaznih materialov ipd. | The materials, elements, appliances, systems and equipment chosen must contribute to the sustainability of the building in terms of energy efficiency, economic and easy maintenance and cleaning, long lifetime, use of environmentally friendly materials, etc.
0.2.5 | Predloženi dokumenti za vse uporabljene materiale, elemente in opremo morajo izpolnjevati zahteve najmanj kakovostne stopnje QS3 (zaželeno QS4), iz dokumenta: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001) | The documents submitted for all materials, components and equipment used shall meet the requirements of at least quality level QS3 (preferably QS4) of the document DGNB Quality Grades for Materials, Components and Equipment (JULFS--7X9001)
0.2.6 | V kolikor izbrani materiali oz. elementi, navedeni v posameznih postavkah, ne ustrezajo vsaj kakovostni stopnji QS3 iz seznama: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), je izvajalec dolžan na to opozoriti projektanta, nadzor in investitorja ter podati predlog ustreznega materiala oz. elementa. | If the selected materials or elements listed in the individual items do not meet at least quality level QS3 of the list of DGNB quality classes for materials, elements and equipment (JULFS--7X9001), the Contractor shall draw this to the attention of the Designer, the Supervisor and the Investor, and shall make a proposal for a suitable material or element.
0.2.7 | Izvajalec lahko v svoji ponudbi predlaga alternativne produkte in rešitve glede na predvidene s projektom, pod pogojem, da le-te prav tako izpolnjujejo vse navedene zahteve. Pri morebitnih predlaganih alternativnih produktih oz. rešitvah je potrebno upoštevati najmanj enake ali boljše lastnosti v smislu življenjske dobe, obstojnosti, ter enostavnosti in stroška čiščenja ter vzdrževanja v primerjavi s projektom predpisanimi rešitvami. Za alternativne rešitve izvajalec pridobi soglasje projektanta, nadzornika in investitorja pred pričetkom gradnje. | The Contractor may propose alternative products and solutions to those envisaged by the project in its tender, provided that they also meet all the requirements set out above. Any alternative products or solutions proposed shall have at least the same or better characteristics in terms of service life, durability, and ease and cost of cleaning and maintenance compared to the solutions envisaged by the project. For alternative solutions, the contractor shall obtain the agreement of the designer, the supervisor and the investor before starting construction.
0.2.8 | Izvajalec med gradnjo dnevno beleži vsa eventualna odstopanja od PZI projektne dokumentacije ter podatke pravočasno posreduje naročniku, nadzoru in projektantu. Potrjene spremembe vnese v podlage za izdelavo PID in posodobitev BIM modelov. | During construction, the Contractor shall record on a daily basis any deviations from the Detailed Design documentation (PZI) and shall provide the information to the Client, Supervision and the Designer in a timely manner. Confirmed changes shall be entered into the basis for the As-built documentation (PID) and BIM model updates.
0.2.9 | Izvajalec med gradnjo sproti izpolnjuje Seznam vseh konstrukcijskih sestav s pripadajočimi vgrajenimi gradbenimi materiali in dokumentira naslednje podatke o vgrajenih materialih (v slovenskem jeziku): - Varnostni list - Tehnični list - Izjavo o lastnostih (če je relevantno) - Izkazovanje morebiti obstoječega okoljskega certifikata (Tip I - okoljski znak ali Tip III - okoljska produktna deklaracija /EPD) - Izjavo proizvajalca ali dobavitelja, da produkt ustreza zahtevam ENV1.2 - Tehnična navodila za ravnanje, servisiranje, vzdrževanje oziroma ostale, z zakonom predpisane dokumente in dokumentacijo. | During construction, the Contractor shall keep a List of all structural assemblies with their associated construction materials and document the following information on the materials installed (in Slovene language): - Safety Data Sheet - Technical Data Sheet - Declaration of performance (if applicable) - Demonstration of any existing environmental certification (Type I - Ecolabel or Type III - Environmental Product Declaration /EPD) - A declaration by the manufacturer or supplier that the product complies with the requirements of ENV1.2 - Technical instructions for handling, servicing, maintenance or other documents and documentation required by law.
0.2.10 | Za vse vgrajene bistvene tehnične sisteme mora izvajalec zagotoviti obstoj pooblaščenega servisa, ki deluje na območju Republike Slovenije, da ima investitor možnost skleniti ustrezno pogodbo o vzdrževanju. Med bistvene tehnične sisteme sodijo npr.: sistemi ogrevanja in hlajenja, priprava tehnoloških medijev, prezračevanje in klimatizacija, sistemi detekcije in gašenja požara, sistemi tehničnega varovanja, BMS in CNS sistemi upravljanja stavbe, razsvetljava, komunikacijski in WI-FI sistemi,... | For all installed essential technical systems, the contractor must ensure the existence of an authorised service centre operating in the territory of the Republic of Slovenia, so that the investor has the possibility of concluding an appropriate maintenance contract. The essential technical systems include, for example: heating and cooling systems, technological media preparation, ventilation and air conditioning, fire detection and extinguishing systems, technical security systems, BMS and CNS building management systems, lighting, communication and WI-FI systems,...
0.2.11 | Zaželeno je, da imajo uporabljeni elementi in materiali okoljsko oznako Tip I. (kot npr. ENCODE, BLUE ANGEL, ipd...). | It is preferable that the elements and materials used have a Type I environmental label (such as ENCODE, BLUE ANGEL, etc...).
0.2.12 | Izvajalec bo za elemente iz lesa moral dokazovati izvor z navedbo izvorne države in tipa lesa, FSC / PEFC certifikat z dodatnim pripadajočim potrdilom Chain of custody-trgovski certifikat dobavitelja - ta se dokazuje z dobavnicami, računi ali enakovredno. Za izdelke iz naravnega kamna iz EU držav je potrebna deklaracija, da je izvor in procesiranje teh izdelkov v celoti v EU državah. Za izdelke iz naravnega kamna, ki prihajajo iz držav izven EU, je potrebno predložiti dokazilo o izpolnjevanju ILO konvencije 182, ki vključuje neodvisna inšpekcijska poročila. | For wood elements, the contractor will be required to provide proof of origin, indicating the country of origin and the type of wood, FSC/PEFC certification with an additional Chain of Custody certificate - the supplier's trade certificate - this shall be evidenced by delivery notes, invoices or equivalent. For natural stone products from EU countries, a declaration that the sourcing and processing of these products is entirely in EU countries is required. For natural stone products from non-EU countries, proof of compliance with ILO Convention 182, including independent inspection reports, is required.
0.2.13 | Izobraževanje udeležencev pri gradnji Izvajalec je dolžan vse udeležence pri gradnji podrobneje seznaniti tudi z relevantnimi koncepti, študijami, elaborati, ki opredelujejo trajnostni način gradnje za naslednja področja: - zaščita pred hrupom (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)) - zaščita pred prašenjem - zaščita tal in podzemne vode (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)), Analiza tveganja za onesnaženje vodnega telesa podzemne vode št. 0346-023/2023, maj 2023 (Geološko projektiranje d.o.o.)) - ravnanje z gradbenimi odpadki (Načrt gospodarjenja z gradbenimi odpadki) Izobraževanja se izvajajo skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.1 1.2, 2.2, 3.2 in 4.2 Training for the parties implementing the construction work | Training of construction participants The contractor is also obliged to inform all construction participants in detail about relevant concepts, studies, elaborations defining sustainable construction methods for the following areas: - noise protection (Environmental Impact Assessment Report No 100123-11523, dated 11.5.2023, supplemented on 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.)) - dust protection - protection of soil and groundwater (Environmental Impact Assessment Report No. 100123-11523, dated 11.5.2023, supplemented 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.), Risk analysis for contamination of the groundwater No. 0346-023/2023, May 2023 (Geološko projektiranje d.o.o.)) - construction waste management (Construction Waste Management Plan) The training shall be carried out in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.1 1.2, 2.2, 3.2 and 4.2 Training for the parties implementing the construction work
0.2.14 | Navodila za obratovanje in vzdrževanje objekta Izvajalec pripravi Navodila za obratovanje in vzdrževanje objekta skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilih: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual | Instructions for the operation and maintenance of the facility The Contractor shall prepare the Operation and Maintenance Instructions for the Facility in accordance with the applicable Slovenian legislation and the DGNB System Instructions specified in the Criteria: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual
0.2.15 | Meritve kontrole kakovosti gradnje Izvajalec mora upoštevati, da se bodo po koncu gradnje izvedle naslednje meritve: - meritve zrakotesnosti - meritve s termokamero (termografija) - meritve akustike - meritve zvočne zaščite ovoja stavbe - meritve zvočne zaščite ločilnih elementov med posameznimi prostori različnih namembnosti - meritve udarnega zvoka - meritve vlažnosti vgrajenih elementov, pred vgradnjo finalnih tlakov - test odvoda dima in toplote Meritve morajo opraviti ustrezno usposobljeni preskusni organi ali strokovnjaki ter rezultate oceniti in primerjati z zahtevami. Obseg opravljenih meritev mora biti sorazmeren z velikostjo zgradbe in mora ustrezno odražati cilj preverjanja kakovosti zgradbe. Smiselno je, da izvajalec del tekom gradnje za sprotno kontrolo kakovosti vgrajenih materialov, elementov in opreme, sam izvaja meritve. Končne meritve (ob primopredaji) izvede tretja oseba kot neodvisna potrditev doseganja zahtev. Meritve se izvajajo skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 2. Quality control measurements | Construction quality control measurements The contractor must take into account that the following measurements will be carried out after completion of the construction: - airtightness measurements - thermal camera measurements (thermography) - acoustics measurements - measurements of the sound insulation of the building envelope - measurements of the sound insulation of the separating elements between different rooms of different uses - impact sound measurements - moisture measurements of the installed elements, prior to the installation of the final flooring - smoke and heat extraction test The measurements shall be carried out by suitably qualified test bodies or experts and the results evaluated and compared with the requirements. The extent of the measurements carried out shall be proportionate to the size of the building and shall adequately reflect the objective of the building quality verification. It is reasonable for the contractor to carry out his own measurements during construction to check the quality of the materials, elements and equipment installed. Final measurements (at handover) are carried out by a third party as an independent confirmation of compliance with the requirements. The measurements shall be carried out in accordance with the applicable Slovenian legislation and the DGNB system instructions specified in the benchmark: PRO 2.2 2. Quality control measurements
0.2.16 | Zagotavljanje kakovosti za uporabljene gradbene proizvode Izvajalec mora zagotavljati izvajanje primerjav med definiranim in dejansko uporabljenim materialom, elementom ali opremo skladno seznamom: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), vključno z dokazno dokumentacijo ugotovitev primerjav ter skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 3.1 Quality assurance for the used construction products | Quality assurance for the construction products used The Contractor shall ensure that comparisons are made between the defined and the actual material, element or equipment used in accordance with the list: DGNB Quality Grades of Installed Materials, Elements and Equipment (JULFS--7X9001), including supporting documentation of the findings of the comparisons, and in accordance with the DGNB system instructions defined in the Criterion: PRO 2.2 3.1 Quality assurance for the used construction products
0.2.17 | Zaščita pred vlago Izvajalec predloži dokumentacijo, ki dokazuje, da je bil izveden program prezračevanja, prilagojen stavbi, s čimer se zagotovi pogoje, da so vgrajeni gradbeni elementi ustrezno suhi, skladno z navodili DGNB opredeljenimi v merilu: PRO 2.2 4.1 Mould prevention | Protection against moisture The Contractor shall provide documentation demonstrating that a building-specific ventilation programme has been implemented to ensure that the building elements installed are adequately dry, in accordance with the DGNB guidelines specified in the criteria: PRO 2.2 4.1 Mould prevention
0.2.18 | Preizkusi delovanja sistemov Izvajalec sodeluje pri izvedbi predhodnega in končnega preizkusa delovanja vseh bistvenih tehničnih komponent stavbe in pripravi ustrezne dokazne dokumentacije ter pri usposabljanju vzdrževalcev/upravljalcev stavbe, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators | System performance tests The Contractor shall be involved in the performance of the preliminary and final performance tests of all essential technical components of the building and the preparation of the relevant supporting documentation, as well as in the training of the maintenance/management staff of the building, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators
0.2.19 | Poročilo o zagonu objekta Izvajalec sodeluje pri pripravi končnega poročila o zagonu objekta, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 5.1 Creation of a detailed final report | Commissioning report The Contractor shall be involved in the preparation of the final commissioning report, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 5.1 Creation of a detailed final report
0.2.20 | Koncept celovitega delovanja sistemov v stavbi Izvajalec sodeluje pri procesu implementiranja stalnega nadzora in nastavitev delovanja stavbe ter usposabljanju vzdrževalcev/upravljalcev stavbe. Navedeno se izvede v skladu z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 6.1 Creation and handover of an integral operating concept | The concept of integrated building systems The contractor is involved in the process of implementing the building's continuous monitoring and settings and training the building's maintenance/management staff. This shall be done in accordance with the DGNB system instructions defined in the benchmark: PRO 2.3 6.1 Creation and handover of an integral operating concept
0.2.21 | Prilagoditev nastavitev sistemov po začetni fazi uporabe objekta Izvajalec sodeluje pri ponovnem pregledu delovanja vseh bistvenih tehničnih sistemov ter eventualni ponovni prilagoditvi teh sistemov s strani strokovnjaka oz. (neodvisne) tretje osebe. Postopek se izvede po približno 10–14 mesecih po zaključku gradnje, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 7.1 Readjustment of the system following initial operating phase | Adjusting system settings after the initial phase of use of the building The Contractor shall be involved in the re-examination of the functioning of all essential technical systems and the possible re-adjustment of these systems by an expert or (independent) third party. The procedure shall be carried out approximately 10-14 months after completion of construction, in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.3 7.1 Readjustment of the system following initial operating phase

## 3.8.0_Rekapitulacija
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
| REKAPITULACIJA STROŠKOV ELEKTRO DEL | COST SUMMARY OF ELECTRICAL WORKS
| 3 NAČRT S PODROČJA ELEKTROTEHNIKE | 3 DOCUMENTATION IN THE FIELD OF ELECTRICAL ENGINEERING
| 3/8 Univerzalno kabliranje, WiFi in drugi IKS | 3/8 Structured cabling, WiFi, and Other Information and Communication Systems
3.8 | ELEKTRO DELA | ELECTRICAL WORKS
3.8.1 | UNIVERZALNO KABLIRANJE, WiFi in drugi IKS | UNIVERSAL CABLING, WiFi and other IKS | 0
3.8.2 | STREŽNIŠKI PROSTOR | SERVER ROOM | 0
3.8.3 | OSTALO | OTHER | 0
0
0 | NEPREDVIDENA DELA | UNFORSEEN WORKS | 0
| SKUPAJ ELEKTRO DELA | TOTAL ELECTRICAL WORKS | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT

## 3.8.1_IKS
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.8 | ELEKTRO DELA | ELECTRICAL WORKS
3.8.1 | UNIVERZALNO KABLIRANJE, WiFi in drugi IKS | UNIVERSAL CABLING, WiFi and other IKS | [5 empty] | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description |  |  | EM | Količina | Cena/EM | Cena
1 | UNIVERZALNO KABLIRANJE, WiFi in drugi IKS | UNIVERSAL CABLING, WiFi and other IKS
1.1 | Dobava in montaža prostostoječih kovinskih omar za potrebe komunikacijskega vozlišča P1-1 (z oznako TK.P1-1-LAN, TK.P1-1-FTP.1, TK.P1-1-FTP.2). Omara, kot na primer: Rittal, VX 5312.124, dimenzije: 2200 mm x 800 mm x 800 mm (VxŠXG), 47U na podstavku višine 100 mm. Sestava omare je naslednja: | Supply and installation of free-standing metal cabinets for the P1-1 communication hub (designated TK.P1-1-LAN, TK.P1-1-FTP.1, TK.P1-1-FTP.2). Cabinet, for example: Rittal, VX 5312.124, dimensions: 2200 mm x 800 mm x 800 mm (HxWxD), 47U on a base height of 100 mm. The wardrobe is composed as follows: |  |  | kpl | 1 |  | 0
| - omara komunikacijskega vozlišča, Rittal, VX 5312.124 | - communication hub cabinet, Rittal, VX 5312.124 | kos | 3
| - steklena vrata spredaj, VX IT 5051.215 | - glass door at front, VX IT 5051.215 | kos | 3
| - kovinska vrata zadaj, VX IT 5051.223 | - metal rear door, VX IT 5051.223 | kos | 3
| - stranska stena omare, VX 8128.245 | - side wall of cabinet, VX 8128.245 | kos | 2
| - standardni 19" montažni profil 47HE (sprednji) VX IT 5302.108 | - standard 19" mounting profile 47HE (front) VX IT 5302.108 | kos | 6
| - standardni 19" montažni profil 47HE (zadnji) VX IT 5302.109 | - standard 19" mounting profile 47HE (rear) VX IT 5302.109 | kos | 6
| - montažni nosilec 800 MM standardni, VX IT 5302.167 | - mounting bracket 800 MM standard, VX IT 5302.167 | kpl | 6
| - montažni nosilec 800 MM, VX IT 5302.169 | - mounting bracket 800 MM, VX IT 5302.169 | kos | 24
| - montažna letev 17x64 MM, 800 MM, VX 8617.040 | - mounting bar 17x64 MM, 800 MM, VX 8617.040 | kos | 6
| - ojačitveni kotnik za 19 profile 800 MM, IT 5302.124 | - reinforcement angle for 19 profiles 800 MM, IT 5302.124 | kpl | 3
| - streha, SV 9681.688 | - roof, SV 9681.688 | kos | 3
| - podstavek kotni element s ploščo spredaj/zadaj, 100 mm, VX 8640.003 | - pedestal corner element with front/rear panel, 100 mm, VX 8640.003 | kos | 6
| '- podstavek stranska zapiralna plošča, 100 mm, VX 8640.034 | - pedestal side closing plate, 100 mm, VX 8640.034 | kos | 6
| - vertikalni urejevalnik kablov, DK 5302.053 | - vertical cable cutter, DK 5302.053 | kos | 6
| - povezovalni kotnik notranji, VX 8617.500 | - connecting angle internal, VX 8617.500 | kpl | 2
| - pokrov spoja omare RAL7035, 800 MM, TS 8800.885 | - cabinet joint cover RAL7035, 800 MM, TS 8800.885 | kos | 2
| - konfortna ročka za odpiranje, VX 8618.201, | - comfort opening handle, VX 8618.201, | kos | 3
| - cilinder vložek (Sistemski ključ) TS8611.180 | - cylinder insert (System key) TS8611.180 | kos | 3
| - ščetinasta zaščita uvoda kablov 2x1m, DK 7825.375 | - bristle cable entry protector 2x1m, DK 7825.375 | kos | 3
| - polica, DK 5501.665 | - shelf, DK 5501.665 | kos | 3
| - ventilator s filtrom, vgrajen na zgornjem delu kovinske stranice priključni kabel…, ventilator priklopljen preko svoje varovalke, SK 3239.108 | - fan with filter, mounted on the upper part of the metal side, connecting cable..., fan connected via its own fuse, SK 3239.108 | kos | 3
| - filterska rešetka vgrajena na spodnjem delu kovinske stranice, SK 3239.208 | - filter grate mounted on the lower part of the metal side, SK 3239.208 | kos | 3
| - končno stikalo SZ 4127.010 | - limit switch SZ 4127.010 | kos | 3
| - termostat, SK 3110.000 | - thermostat, SK 3110.000 | kos | 3
| - predal za dokumentacijo, SZ 2514.000 | - documentation drawer, SZ 2514.000 | kos | 1
| - vtična razdelilna letev s 9 ''schuko'' vtičnicami, z vgrajeno prenapetostno zaščito tretje stopnje, DK 7240.330 | - plug-in distribution board with 9 "schuko" sockets, with built-in surge protector of third level, DK 7240.330 | kos | 3
| - v omaro so vgrajeni 19" okvirji (profili) za montažo “patch” panelov in ostale aktivne in pasivne opreme. | - 19" frames (profiles) for mounting patch panels and other active and passive equipment are built into the cabinet.
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc.
| V komunikacijsko vozlišče (z oznako TK.P1-1-LAN, TK.P1-1-FTP.1, TK.P1-1-FTP.2) se dobavi in vgradi naslednja pasivna oprema: | The following passive equipment shall be supplied and installed in the communication node (designated TK.P1-1-LAN, TK.P1-1-FTP.1, TK.P1-1-FTP.2):
| - “patch” panel 19”, 24 vtičnic FTP, RJ-45 Cat.6, višine 1/2U, kot naprimer: Leviton, tip: LSA Style, Shielded, Black (koda: C6CPNLF240K2H). | - "patch" panel 19", 24 sockets FTP, RJ-45 Cat.6, height 1/2U, as for example Leviton, type: LSA Style, Shielded, Black (code: C6CPNLF240K2H). | kos | 22
| - optični “patch” panel 19” višina 1U, za 12 LC duplex konektorjev(24 vlaken), komplet s konektorji (LC Duplex Single-mode) in vsem potrebnim montažnim materialom (LC/LC spojniki, kaseta, "Pigtails" ...), kot naprimer Leviton, tip LC Duplex Single Mode, koda: FPCC1SXSM24LC2 | - optical patch panel 19" height 1U, for 12 LC duplex connectors (24 fibres), complete with connectors (LC Duplex Single-mode) and all necessary mounting material (LC/LC connectors, cassette, pigtails, etc.), e.g. Leviton, type LC Duplex Single Mode, code: FPCC1SXSM24LC2 | kos | 2
| - optični “patch” panel 19” višina 1U, za 12 LC duplex konektorjev(24 vlaken), komplet s konektorji (LC Duplex Multi-mode) in vsem potrebnim montažnim materialom (LC/LC spojniki, kaseta, "Pigtails" ...), kot naprimer Leviton, tip LC Duplex Multimode, koda: FPCC1SXMM24LC2 | - optical patch panel 19" height 1U, for 12 LC duplex connectors (24 fibres), complete with connectors (LC Duplex Multi-mode) and all necessary mounting material (LC/LC connectors, cassette, pigtails, etc.), e.g. Leviton, type LC Duplex Multimode, code: FPCC1SXMM24LC2 | kos | 1
| - urejevalnik kablov (organiser) 19”, kot naprimer Leviton tip: 1U Rack Mounted - 5 ring, (koda: MMCACCCM001) | - 19" cable manager (organiser), such as Leviton type: 1U Rack Mounted - 5 ring, (code: MMCACCCM001) | kos | 18
| - ranžirni "patch" kablI za računalniško omrežje, F/FTP Cat.6A, RJ-45 to RJ-45, kot naprimer Levinton različnih dolžin od 1,5m do 5m. Priključitev "patch" kablov na eni strani pasivno oprema(delilni paneli) in na drugi aktivno opremo (ethernet stikala). | - patch cables for computer networking, F/FTP Cat.6A, RJ-45 to RJ-45, such as Levinton, in different lengths from 1.5m to 5m. Connection of patch cables to passive equipment (distribution panels) on one side and to active equipment (Ethernet switches) on the other side (Ethernet switches) Connection of patch cables to passive equipment (distribution panels) on one side and to active equipment (Ethernet switches) on the other side. | kos | 514
| -optični MM 50/125 ranžirni "patch" kabel, dvovlakenski z SC to SC - duplex konektorji, kot naprimer Leviton, dolžine 1,5m. | -optical MM 50/125 patch cable, double-fibre with SC to SC - duplex connectors, such as Leviton, 1,5m long. | kos | 12
| -optični SM 9/125 ranžirni "patch" kabel, dvovlakenski z SC to SC - duplex konektorji, kot naprimer Leviton, dolžine 1,5m. | -sM 9/125 optical patch cable, double-fibre with SC to SC - duplex connectors, such as Leviton, 1,5m long. | kos | 24
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, … | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc
1.2 | Dobava in montaža prostostoječih kovinskih omar za potrebe komunikacijskega vozlišča P1-2 (z oznako TK.P1-2-LAN, TK.P1-2-FTP.1, TK.P1-2-FTP.2). Omara, kot na primer: Rittal, VX 5312.114, dimenzije: 2200 mm x 800 mm x 800 mm (VxŠXG), 47U na podstavku višine 100 mm. Sestava omare je naslednja: | Supply and installation of free-standing metal cabinets for the P1-2 communication hub (designated TK.P1-2-LAN, TK.P1-2-FTP.1, TK.P1-2-FTP.2). Cabinet, for example: Rittal, VX 5312.114, dimensions: 2200 mm x 800 mm x 800 mm (HxWxD), 47U on a base height of 100 mm. The wardrobe is composed as follows: |  |  | kpl | 1 |  | 0
| - omara komunikacijskega vozlišča, Rittal, VX 5312.124 | - communication hub cabinet, Rittal, VX 5312.124 | kos | 3
| - steklena vrata spredaj, VX IT 5051.215 | - glass door at front, VX IT 5051.215 | kos | 3
| - kovinska vrata zadaj, VX IT 5051.223 | - metal rear door, VX IT 5051.223 | kos | 3
| - stranska stena omare, VX 8128.245 | - side wall of cabinet, VX 8128.245 | kos | 2
| - standardni 19" montažni profil 47HE (sprednji) VX IT 5302.108 | - standard 19" mounting profile 47HE (front) VX IT 5302.108 | kos | 6
| - standardni 19" montažni profil 47HE (zadnji) VX IT 5302.109 | - standard 19" mounting profile 47HE (rear) VX IT 5302.109 | kos | 6
| - montažni nosilec 800 MM standardni, VX IT 5302.167 | - mounting bracket 800 MM standard, VX IT 5302.167 | kpl | 6
| - montažni nosilec 800 MM, VX IT 5302.169 | - mounting bracket 800 MM, VX IT 5302.169 | kos | 24
| - montažna letev 17x64 MM, 800 MM, VX 8617.040 | - mounting bar 17x64 MM, 800 MM, VX 8617.040 | kos | 6
| - ojačitveni kotnik za 19 profile 800 MM, IT 5302.124 | - reinforcement angle for 19 profiles 800 MM, IT 5302.124 | kpl | 3
| - streha, SV 9681.688 | - roof, SV 9681.688 | kos | 3
| - podstavek kotni element s ploščo spredaj/zadaj, 100 mm, VX 8640.003 | - pedestal corner element with front/rear panel, 100 mm, VX 8640.003 | kos | 6
| '- podstavek stranska zapiralna plošča, 100 mm, VX 8640.034 | - pedestal side closing plate, 100 mm, VX 8640.034 | kos | 6
| - vertikalni urejevalnik kablov, DK 5302.053 | - vertical cable cutter, DK 5302.053 | kos | 6
| - povezovalni kotnik notranji, VX 8617.500 | - connecting angle internal, VX 8617.500 | kpl | 2
| - pokrov spoja omare RAL7035, 800 MM, TS 8800.885 | - cabinet joint cover RAL7035, 800 MM, TS 8800.885 | kos | 2
| - konfortna ročka za odpiranje, VX 8618.201, | - comfort opening handle, VX 8618.201, | kos | 3
| - cilinder vložek (Sistemski ključ) TS8611.180 | - cylinder insert (System key) TS8611.180 | kos | 3
| - ščetinasta zaščita uvoda kablov 2x1m, DK 7825.375 | - bristle cable entry protector 2x1m, DK 7825.375 | kos | 3
| - polica, DK 5501.665 | - shelf, DK 5501.665 | kos | 3
| - ventilator s filtrom, vgrajen na zgornjem delu kovinske stranice priključni kabel…, ventilator priklopljen preko svoje varovalke, SK 3239.108 | - fan with filter, mounted on the upper part of the metal side, connecting cable..., fan connected via its own fuse, SK 3239.108 | kos | 3
| - filterska rešetka vgrajena na spodnjem delu kovinske stranice, SK 3239.208 | - filter grate mounted on the lower part of the metal side, SK 3239.208 | kos | 3
| - končno stikalo SZ 4127.010 | - limit switch SZ 4127.010 | kos | 3
| - termostat, SK 3110.000 | - thermostat, SK 3110.000 | kos | 3
| - predal za dokumentacijo, SZ 2514.000 | - documentation drawer, SZ 2514.000 | kos | 1
| - vtična razdelilna letev s 9 ''schuko'' vtičnicami, z vgrajeno prenapetostno zaščito tretje stopnje, DK 7240.330 | - plug-in distribution board with 9 "schuko" sockets, with built-in surge protector of third level, DK 7240.330 | kos | 3
| - v omaro so vgrajeni 19" okvirji (profili) za montažo “patch” panelov in ostale aktivne in pasivne opreme. | - 19" frames (profiles) for mounting patch panels and other active and passive equipment are built into the cabinet.
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc.
| V komunikacijsko vozlišče (z oznako TK.P1-2-LAN, TK.P1-2-FTP.1, TK.P1-2-FTP.2) se dobavi in vgradi naslednja pasivna oprema: | The following passive equipment shall be supplied and installed in the communication node (designated TK.P1-2-LAN, TK.P1-2-FTP.1, TK.P1-2-FTP.2):
| - “patch” panel 19”, 24 vtičnic FTP, RJ-45 Cat.6, višine 1/2U, kot naprimer: Leviton, tip: LSA Style, Shielded, Black (koda: C6CPNLF240K2H). | - "patch" panel 19", 24 sockets FTP, RJ-45 Cat.6, height 1/2U, as for example Leviton, type: LSA Style, Shielded, Black (code: C6CPNLF240K2H). | kos | 20
| - optični “patch” panel 19” višina 1U, za 12 LC duplex konektorjev(24 vlaken), komplet s konektorji (LC Duplex Single-mode) in vsem potrebnim montažnim materialom (LC/LC spojniki, kaseta, "Pigtails" ...), kot naprimer Leviton, tip LC Duplex Single Mode, koda: FPCC1SXSM24LC2 | - optical patch panel 19" height 1U, for 12 LC duplex connectors (24 fibres), complete with connectors (LC Duplex Single-mode) and all necessary mounting material (LC/LC connectors, cassette, pigtails, etc.), e.g. Leviton, type LC Duplex Single Mode, code: FPCC1SXSM24LC2 | kos | 2
| - optični “patch” panel 19” višina 1U, za 12 LC duplex konektorjev(24 vlaken), komplet s konektorji (LC Duplex Multi-mode) in vsem potrebnim montažnim materialom (LC/LC spojniki, kaseta, "Pigtails" ...), kot naprimer Leviton, tip LC Duplex Multimode, koda: FPCC1SXMM24LC2 | - optical patch panel 19" height 1U, for 12 LC duplex connectors (24 fibres), complete with connectors (LC Duplex Multi-mode) and all necessary mounting material (LC/LC connectors, cassette, pigtails, etc.), e.g. Leviton, type LC Duplex Multimode, code: FPCC1SXMM24LC2 | kos | 2
| - urejevalnik kablov (organiser) 19”, kot naprimer Leviton tip: 1U Rack Mounted - 5 ring, (koda: MMCACCCM001) | - 19" cable manager (organiser), such as Leviton type: 1U Rack Mounted - 5 ring, (code: MMCACCCM001) | kos | 17
| - ranžirni "patch" kablI za računalniško omrežje, F/FTP Cat.6A, RJ-45 to RJ-45, kot naprimer Levinton različnih dolžin od 1,5m do 5m. Priključitev "patch" kablov na eni strani pasivno oprema(delilni paneli) in na drugi aktivno opremo (ethernet stikala). | - patch cables for computer networking, F/FTP Cat.6A, RJ-45 to RJ-45, such as Levinton, in different lengths from 1.5m to 5m. Connection of patch cables to passive equipment (distribution panels) on one side and to active equipment (Ethernet switches) on the other side (Ethernet switches) Connection of patch cables to passive equipment (distribution panels) on one side and to active equipment (Ethernet switches) on the other side. | kos | 476
| -optični MM 50/125 ranžirni "patch" kabel, dvovlakenski z SC to SC - duplex konektorji, kot naprimer Leviton, dolžine 1,5m. | -optical MM 50/125 patch cable, double-fibre with SC to SC - duplex connectors, such as Leviton, 1,5m long. | kos | 12
| -optični SM 9/125 ranžirni "patch" kabel, dvovlakenski z SC to SC - duplex konektorji, kot naprimer Leviton, dolžine 1,5m. | -sM 9/125 optical patch cable, double-fibre with SC to SC - duplex connectors, such as Leviton, 1,5m long. | kos | 24
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, … | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc
1.3 | Dobava in montaža prostostoječih kovinskih omar za potrebe komunikacijskega vozlišča P1-3 (z oznako TK.P1-3-LAN, TK.P1-3-FTP.1, TK.P1-3-FTP.2). Omara, kot na primer: Rittal, VX 5312.114, dimenzije: 2200 mm x 800 mm x 800 mm (VxŠXG), 47U na podstavku višine 100 mm. Sestava omare je naslednja: | Supply and installation of free-standing metal cabinets for the P1-3 communication hub (designated TK.P1-3-LAN, TK.P1-3-FTP.1, TK.P1-3-FTP.2). Cabinet, for example: Rittal, VX 5312.114, dimensions: 2200 mm x 800 mm x 800 mm (HxWxD), 47U on a base height of 100 mm. The wardrobe is composed as follows: |  |  | kpl | 1 |  | 0
| - omara komunikacijskega vozlišča, Rittal, VX 5312.124 | - communication hub cabinet, Rittal, VX 5312.124 | kos | 3
| - steklena vrata spredaj, VX IT 5051.215 | - glass door at front, VX IT 5051.215 | kos | 3
| - kovinska vrata zadaj, VX IT 5051.223 | - metal rear door, VX IT 5051.223 | kos | 3
| - stranska stena omare, VX 8128.245 | - side wall of cabinet, VX 8128.245 | kos | 2
| - standardni 19" montažni profil 47HE (sprednji) VX IT 5302.108 | - standard 19" mounting profile 47HE (front) VX IT 5302.108 | kos | 6
| - standardni 19" montažni profil 47HE (zadnji) VX IT 5302.109 | - standard 19" mounting profile 47HE (rear) VX IT 5302.109 | kos | 6
| - montažni nosilec 800 MM standardni, VX IT 5302.167 | - mounting bracket 800 MM standard, VX IT 5302.167 | kpl | 6
| - montažni nosilec 800 MM, VX IT 5302.169 | - mounting bracket 800 MM, VX IT 5302.169 | kos | 24
| - montažna letev 17x64 MM, 800 MM, VX 8617.040 | - mounting bar 17x64 MM, 800 MM, VX 8617.040 | kos | 6
| - ojačitveni kotnik za 19 profile 800 MM, IT 5302.124 | - reinforcement angle for 19 profiles 800 MM, IT 5302.124 | kpl | 3
| - streha, SV 9681.688 | - roof, SV 9681.688 | kos | 3
| - podstavek kotni element s ploščo spredaj/zadaj, 100 mm, VX 8640.003 | - pedestal corner element with front/rear panel, 100 mm, VX 8640.003 | kos | 6
| '- podstavek stranska zapiralna plošča, 100 mm, VX 8640.034 | - pedestal side closing plate, 100 mm, VX 8640.034 | kos | 6
| - vertikalni urejevalnik kablov, DK 5302.053 | - vertical cable cutter, DK 5302.053 | kos | 6
| - povezovalni kotnik notranji, VX 8617.500 | - connecting angle internal, VX 8617.500 | kpl | 2
| - pokrov spoja omare RAL7035, 800 MM, TS 8800.885 | - cabinet joint cover RAL7035, 800 MM, TS 8800.885 | kos | 2
| - konfortna ročka za odpiranje, VX 8618.201, | - comfort opening handle, VX 8618.201, | kos | 3
| - cilinder vložek (Sistemski ključ) TS8611.180 | - cylinder insert (System key) TS8611.180 | kos | 3
| - ščetinasta zaščita uvoda kablov 2x1m, DK 7825.375 | - bristle cable entry protector 2x1m, DK 7825.375 | kos | 3
| - polica, DK 5501.665 | - shelf, DK 5501.665 | kos | 3
| - ventilator s filtrom, vgrajen na zgornjem delu kovinske stranice priključni kabel…, ventilator priklopljen preko svoje varovalke, SK 3239.108 | - fan with filter, mounted on the upper part of the metal side, connecting cable..., fan connected via its own fuse, SK 3239.108 | kos | 3
| - filterska rešetka vgrajena na spodnjem delu kovinske stranice, SK 3239.208 | - filter grate mounted on the lower part of the metal side, SK 3239.208 | kos | 3
| - končno stikalo SZ 4127.010 | - limit switch SZ 4127.010 | kos | 3
| - termostat, SK 3110.000 | - thermostat, SK 3110.000 | kos | 3
| - predal za dokumentacijo, SZ 2514.000 | - documentation drawer, SZ 2514.000 | kos | 1
| - vtična razdelilna letev s 9 ''schuko'' vtičnicami, z vgrajeno prenapetostno zaščito tretje stopnje, DK 7240.330 | - plug-in distribution board with 9 "schuko" sockets, with built-in surge protector of third level, DK 7240.330 | kos | 5
| - v omaro so vgrajeni 19" okvirji (profili) za montažo “patch” panelov in ostale aktivne in pasivne opreme. | - 19" frames (profiles) for mounting patch panels and other active and passive equipment are built into the cabinet.
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc.
| V komunikacijsko vozlišče (z oznako TK.P1-3-LAN, TK.P1-3-FTP.1, TK.P1-3-FTP.2) se dobavi in vgradi naslednja pasivna oprema: | The following passive equipment shall be supplied and installed in the communication node (designated TK.P1-3-LAN, TK.P1-3-FTP.1, TK.P1-3-FTP.2):
| - “patch” panel 19”, 24 vtičnic FTP, RJ-45 Cat.6, višine 1/2U, kot naprimer: Leviton, tip: LSA Style, Shielded, Black (koda: C6CPNLF240K2H). | - "patch" panel 19", 24 sockets FTP, RJ-45 Cat.6, height 1/2U, as for example Leviton, type: LSA Style, Shielded, Black (code: C6CPNLF240K2H). | kos | 31
| - optični “patch” panel 19” višina 1U, za 12 LC duplex konektorjev(24 vlaken), komplet s konektorji (LC Duplex Single-mode) in vsem potrebnim montažnim materialom (LC/LC spojniki, kaseta, "Pigtails" ...), kot naprimer Leviton, tip LC Duplex Single Mode, koda: FPCC1SXSM24LC2 | - optical patch panel 19" height 1U, for 12 LC duplex connectors (24 fibres), complete with connectors (LC Duplex Single-mode) and all necessary mounting material (LC/LC connectors, cassette, pigtails, etc.), e.g. Leviton, type LC Duplex Single Mode, code: FPCC1SXSM24LC2 | kos | 2
| - optični “patch” panel 19” višina 1U, za 12 LC duplex konektorjev(24 vlaken), komplet s konektorji (LC Duplex Multi-mode) in vsem potrebnim montažnim materialom (LC/LC spojniki, kaseta, "Pigtails" ...), kot naprimer Leviton, tip LC Duplex Multimode, koda: FPCC1SXMM24LC2 | - optical patch panel 19" height 1U, for 12 LC duplex connectors (24 fibres), complete with connectors (LC Duplex Multi-mode) and all necessary mounting material (LC/LC connectors, cassette, pigtails, etc.), e.g. Leviton, type LC Duplex Multimode, code: FPCC1SXMM24LC2 | kos | 1
| - urejevalnik kablov (organiser) 19”, kot naprimer Leviton tip: 1U Rack Mounted - 5 ring, (koda: MMCACCCM001) | - 19" cable manager (organiser), such as Leviton type: 1U Rack Mounted - 5 ring, (code: MMCACCCM001) | kos | 20
| - ranžirni "patch" kablI za računalniško omrežje, F/FTP Cat.6A, RJ-45 to RJ-45, kot naprimer Levinton različnih dolžin od 1,5m do 5m. Priključitev "patch" kablov na eni strani pasivno oprema(delilni paneli) in na drugi aktivno opremo (ethernet stikala). | - patch cables for computer networking, F/FTP Cat.6A, RJ-45 to RJ-45, such as Levinton, in different lengths from 1.5m to 5m. Connection of patch cables to passive equipment (distribution panels) on one side and to active equipment (Ethernet switches) on the other side (Ethernet switches) Connection of patch cables to passive equipment (distribution panels) on one side and to active equipment (Ethernet switches) on the other side. | kos | 732
| -optični MM 50/125 ranžirni "patch" kabel, dvovlakenski z SC to SC - duplex konektorji, kot naprimer Leviton, dolžine 1,5m. | -optical MM 50/125 patch cable, double-fibre with SC to SC - duplex connectors, such as Leviton, 1,5m long. | kos | 12
| -optični SM 9/125 ranžirni "patch" kabel, dvovlakenski z SC to SC - duplex konektorji, kot naprimer Leviton, dolžine 1,5m. | -sM 9/125 optical patch cable, double-fibre with SC to SC - duplex connectors, such as Leviton, 1,5m long. | kos | 24
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, … | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc
1.4 | Dobava in montaža prostostoječih kovinskih omar za potrebe komunikacijskega vozlišča P1-4 (z oznako TK.P1-4-LAN, TK.P1-4-FTP.1, TK.P1-4-FTP.2). Omara, kot na primer: Rittal, VX 5312.114, dimenzije: 2200 mm x 800 mm x 800 mm (VxŠXG), 47U na podstavku višine 100 mm. Sestava omare je naslednja: | Supply and installation of free-standing metal cabinets for the P1-4 communication hub (designated TK.P1-4-LAN, TK.P1-4-FTP.1, TK.P1-4-FTP.2). Cabinet, for example: Rittal, VX 5312.114, dimensions: 2200 mm x 800 mm x 800 mm (HxWxD), 47U on a base height of 100 mm. The wardrobe is composed as follows: |  |  | kpl | 1 |  | 0
| - omara komunikacijskega vozlišča, Rittal, VX 5312.124 | - communication hub cabinet, Rittal, VX 5312.124 | kos | 3
| - steklena vrata spredaj, VX IT 5051.215 | - glass door at front, VX IT 5051.215 | kos | 3
| - kovinska vrata zadaj, VX IT 5051.223 | - metal rear door, VX IT 5051.223 | kos | 3
| - stranska stena omare, VX 8128.245 | - side wall of cabinet, VX 8128.245 | kos | 2
| - standardni 19" montažni profil 47HE (sprednji) VX IT 5302.108 | - standard 19" mounting profile 47HE (front) VX IT 5302.108 | kos | 6
| - standardni 19" montažni profil 47HE (zadnji) VX IT 5302.109 | - standard 19" mounting profile 47HE (rear) VX IT 5302.109 | kos | 6
| - montažni nosilec 800 MM standardni, VX IT 5302.167 | - mounting bracket 800 MM standard, VX IT 5302.167 | kpl | 6
| - montažni nosilec 800 MM, VX IT 5302.169 | - mounting bracket 800 MM, VX IT 5302.169 | kos | 24
| - montažna letev 17x64 MM, 800 MM, VX 8617.040 | - mounting bar 17x64 MM, 800 MM, VX 8617.040 | kos | 6
| - ojačitveni kotnik za 19 profile 800 MM, IT 5302.124 | - reinforcement angle for 19 profiles 800 MM, IT 5302.124 | kpl | 3
| - streha, SV 9681.688 | - roof, SV 9681.688 | kos | 3
| - podstavek kotni element s ploščo spredaj/zadaj, 100 mm, VX 8640.003 | - pedestal corner element with front/rear panel, 100 mm, VX 8640.003 | kos | 6
| '- podstavek stranska zapiralna plošča, 100 mm, VX 8640.034 | - pedestal side closing plate, 100 mm, VX 8640.034 | kos | 6
| - vertikalni urejevalnik kablov, DK 5302.053 | - vertical cable cutter, DK 5302.053 | kos | 6
| - povezovalni kotnik notranji, VX 8617.500 | - connecting angle internal, VX 8617.500 | kpl | 2
| - pokrov spoja omare RAL7035, 800 MM, TS 8800.885 | - cabinet joint cover RAL7035, 800 MM, TS 8800.885 | kos | 2
| - konfortna ročka za odpiranje, VX 8618.201, | - comfort opening handle, VX 8618.201, | kos | 3
| - cilinder vložek (Sistemski ključ) TS8611.180 | - cylinder insert (System key) TS8611.180 | kos | 3
| - ščetinasta zaščita uvoda kablov 2x1m, DK 7825.375 | - bristle cable entry protector 2x1m, DK 7825.375 | kos | 3
| - polica, DK 5501.665 | - shelf, DK 5501.665 | kos | 3
| - ventilator s filtrom, vgrajen na zgornjem delu kovinske stranice priključni kabel…, ventilator priklopljen preko svoje varovalke, SK 3239.108 | - fan with filter, mounted on the upper part of the metal side, connecting cable..., fan connected via its own fuse, SK 3239.108 | kos | 3
| - filterska rešetka vgrajena na spodnjem delu kovinske stranice, SK 3239.208 | - filter grate mounted on the lower part of the metal side, SK 3239.208 | kos | 3
| - končno stikalo SZ 4127.010 | - limit switch SZ 4127.010 | kos | 3
| - termostat, SK 3110.000 | - thermostat, SK 3110.000 | kos | 3
| - predal za dokumentacijo, SZ 2514.000 | - documentation drawer, SZ 2514.000 | kos | 1
| - vtična razdelilna letev s 9 ''schuko'' vtičnicami, z vgrajeno prenapetostno zaščito tretje stopnje, DK 7240.330 | - plug-in distribution board with 9 "schuko" sockets, with built-in surge protector of third level, DK 7240.330 | kos | 3
| - v omaro so vgrajeni 19" okvirji (profili) za montažo “patch” panelov in ostale aktivne in pasivne opreme. | - 19" frames (profiles) for mounting patch panels and other active and passive equipment are built into the cabinet.
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc.
| V komunikacijsko vozlišče (z oznako TK.P1-4-LAN, TK.P1-4-FTP.1, TK.P1-4-FTP.2) se dobavi in vgradi naslednja pasivna oprema: | The following passive equipment shall be supplied and installed in the communication node (designated TK.P1-4-LAN, TK.P1-4-FTP.1, TK.P1-4-FTP.2):
| - “patch” panel 19”, 24 vtičnic FTP, RJ-45 Cat.6, višine 1/2U, kot naprimer: Leviton, tip: LSA Style, Shielded, Black (koda: C6CPNLF240K2H). | - "patch" panel 19", 24 sockets FTP, RJ-45 Cat.6, height 1/2U, as for example Leviton, type: LSA Style, Shielded, Black (code: C6CPNLF240K2H). | kos | 22
| - optični “patch” panel 19” višina 1U, za 12 LC duplex konektorjev(24 vlaken), komplet s konektorji (LC Duplex Single-mode) in vsem potrebnim montažnim materialom (LC/LC spojniki, kaseta, "Pigtails" ...), kot naprimer Leviton, tip LC Duplex Single Mode, koda: FPCC1SXSM24LC2 | - optical patch panel 19" height 1U, for 12 LC duplex connectors (24 fibres), complete with connectors (LC Duplex Single-mode) and all necessary mounting material (LC/LC connectors, cassette, pigtails, etc.), e.g. Leviton, type LC Duplex Single Mode, code: FPCC1SXSM24LC2 | kos | 2
| - optični “patch” panel 19” višina 1U, za 12 LC duplex konektorjev(24 vlaken), komplet s konektorji (LC Duplex Multi-mode) in vsem potrebnim montažnim materialom (LC/LC spojniki, kaseta, "Pigtails" ...), kot naprimer Leviton, tip LC Duplex Multimode, koda: FPCC1SXMM24LC2 | - optical patch panel 19" height 1U, for 12 LC duplex connectors (24 fibres), complete with connectors (LC Duplex Multi-mode) and all necessary mounting material (LC/LC connectors, cassette, pigtails, etc.), e.g. Leviton, type LC Duplex Multimode, code: FPCC1SXMM24LC2 | kos | 2
| - urejevalnik kablov (organiser) 19”, kot naprimer Leviton tip: 1U Rack Mounted - 5 ring, (koda: MMCACCCM001) | - 19" cable manager (organiser), such as Leviton type: 1U Rack Mounted - 5 ring, (code: MMCACCCM001) | kos | 16
| - ranžirni "patch" kablI za računalniško omrežje, F/FTP Cat.6A, RJ-45 to RJ-45, kot naprimer Levinton različnih dolžin od 1,5m do 5m. Priključitev "patch" kablov na eni strani pasivno oprema(delilni paneli) in na drugi aktivno opremo (ethernet stikala). | - patch cables for computer networking, F/FTP Cat.6A, RJ-45 to RJ-45, such as Levinton, in different lengths from 1.5m to 5m. Connection of patch cables to passive equipment (distribution panels) on one side and to active equipment (Ethernet switches) on the other side (Ethernet switches) Connection of patch cables to passive equipment (distribution panels) on one side and to active equipment (Ethernet switches) on the other side. | kos | 516
| -optični MM 50/125 ranžirni "patch" kabel, dvovlakenski z SC to SC - duplex konektorji, kot naprimer Leviton, dolžine 1,5m. | -optical MM 50/125 patch cable, double-fibre with SC to SC - duplex connectors, such as Leviton, 1,5m long. | kos | 12
| -optični SM 9/125 ranžirni "patch" kabel, dvovlakenski z SC to SC - duplex konektorji, kot naprimer Leviton, dolžine 1,5m. | -sM 9/125 optical patch cable, double-fibre with SC to SC - duplex connectors, such as Leviton, 1,5m long. | kos | 24
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, … | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc
1.5 | Dobava in montaža prostostoječih kovinskih omar za potrebe komunikacijskega vozlišča P1-5 (z oznako TK.P1-5-LAN, TK.P1-5-FTP.1, TK.P1-5-FTP.2). Omara, kot na primer: Rittal, VX 5312.114, dimenzije: 2200 mm x 800 mm x 800 mm (VxŠXG), 47U na podstavku višine 100 mm. Sestava omare je naslednja: | Supply and installation of free-standing metal cabinets for the P1-5 communication hub (designated TK.P1-5-LAN, TK.P1-5-FTP.1, TK.P1-5-FTP.2). Cabinet, for example: Rittal, VX 5312.114, dimensions: 2200 mm x 800 mm x 800 mm (HxWxD), 47U on a base height of 100 mm. The wardrobe is composed as follows: |  |  | kpl | 1 |  | 0
| - omara komunikacijskega vozlišča, Rittal, VX 5312.124 | - communication hub cabinet, Rittal, VX 5312.124 | kos | 3
| - steklena vrata spredaj, VX IT 5051.215 | - glass door at front, VX IT 5051.215 | kos | 3
| - kovinska vrata zadaj, VX IT 5051.223 | - metal rear door, VX IT 5051.223 | kos | 3
| - stranska stena omare, VX 8128.245 | - side wall of cabinet, VX 8128.245 | kos | 2
| - standardni 19" montažni profil 47HE (sprednji) VX IT 5302.108 | - standard 19" mounting profile 47HE (front) VX IT 5302.108 | kos | 6
| - standardni 19" montažni profil 47HE (zadnji) VX IT 5302.109 | - standard 19" mounting profile 47HE (rear) VX IT 5302.109 | kos | 6
| - montažni nosilec 800 MM standardni, VX IT 5302.167 | - mounting bracket 800 MM standard, VX IT 5302.167 | kpl | 6
| - montažni nosilec 800 MM, VX IT 5302.169 | - mounting bracket 800 MM, VX IT 5302.169 | kos | 24
| - montažna letev 17x64 MM, 800 MM, VX 8617.040 | - mounting bar 17x64 MM, 800 MM, VX 8617.040 | kos | 6
| - ojačitveni kotnik za 19 profile 800 MM, IT 5302.124 | - reinforcement angle for 19 profiles 800 MM, IT 5302.124 | kpl | 3
| - streha, SV 9681.688 | - roof, SV 9681.688 | kos | 3
| - podstavek kotni element s ploščo spredaj/zadaj, 100 mm, VX 8640.003 | - pedestal corner element with front/rear panel, 100 mm, VX 8640.003 | kos | 6
| '- podstavek stranska zapiralna plošča, 100 mm, VX 8640.034 | - pedestal side closing plate, 100 mm, VX 8640.034 | kos | 6
| - vertikalni urejevalnik kablov, DK 5302.053 | - vertical cable cutter, DK 5302.053 | kos | 6
| - povezovalni kotnik notranji, VX 8617.500 | - connecting angle internal, VX 8617.500 | kpl | 2
| - pokrov spoja omare RAL7035, 800 MM, TS 8800.885 | - cabinet joint cover RAL7035, 800 MM, TS 8800.885 | kos | 2
| - konfortna ročka za odpiranje, VX 8618.201, | - comfort opening handle, VX 8618.201, | kos | 3
| - cilinder vložek (Sistemski ključ) TS8611.180 | - cylinder insert (System key) TS8611.180 | kos | 3
| - ščetinasta zaščita uvoda kablov 2x1m, DK 7825.375 | - bristle cable entry protector 2x1m, DK 7825.375 | kos | 3
| - polica, DK 5501.665 | - shelf, DK 5501.665 | kos | 3
| - ventilator s filtrom, vgrajen na zgornjem delu kovinske stranice priključni kabel…, ventilator priklopljen preko svoje varovalke, SK 3239.108 | - fan with filter, mounted on the upper part of the metal side, connecting cable..., fan connected via its own fuse, SK 3239.108 | kos | 3
| - filterska rešetka vgrajena na spodnjem delu kovinske stranice, SK 3239.208 | - filter grate mounted on the lower part of the metal side, SK 3239.208 | kos | 3
| - končno stikalo SZ 4127.010 | - limit switch SZ 4127.010 | kos | 3
| - termostat, SK 3110.000 | - thermostat, SK 3110.000 | kos | 3
| - predal za dokumentacijo, SZ 2514.000 | - documentation drawer, SZ 2514.000 | kos | 1
| - vtična razdelilna letev s 9 ''schuko'' vtičnicami, z vgrajeno prenapetostno zaščito tretje stopnje, DK 7240.330 | - plug-in distribution board with 9 "schuko" sockets, with built-in surge protection of third level, DK 7240.330 | kos | 2
| - v omaro so vgrajeni 19" okvirji (profili) za montažo “patch” panelov in ostale aktivne in pasivne opreme. | - 19" frames (profiles) for mounting patch panels and other active and passive equipment are built into the cabinet.
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc.
| V komunikacijsko vozlišče (z oznako TK.P1-5-LAN, TK.P1-5-FTP.1, TK.P1-5-FTP.2) se dobavi in vgradi naslednja pasivna oprema: | The following passive equipment shall be supplied and installed in the communication node (designated TK.P1-5-LAN, TK.P1-5-FTP.1, TK.P1-5-FTP.2):
| - “patch” panel 19”, 24 vtičnic FTP, RJ-45 Cat.6, višine 1/2U, kot naprimer: Leviton, tip: LSA Style, Shielded, Black (koda: C6CPNLF240K2H). | - "patch" panel 19", 24 sockets FTP, RJ-45 Cat.6, height 1/2U, as for example Leviton, type: LSA Style, Shielded, Black (code: C6CPNLF240K2H). | kos | 15
| - optični “patch” panel 19” višina 1U, za 12 LC duplex konektorjev(24 vlaken), komplet s konektorji (LC Duplex Single-mode) in vsem potrebnim montažnim materialom (LC/LC spojniki, kaseta, "Pigtails" ...), kot naprimer Leviton, tip LC Duplex Single Mode, koda: FPCC1SXSM24LC2 | - optical patch panel 19" height 1U, for 12 LC duplex connectors (24 fibres), complete with connectors (LC Duplex Single-mode) and all necessary mounting material (LC/LC connectors, cassette, pigtails, etc.), e.g. Leviton, type LC Duplex Single Mode, code: FPCC1SXSM24LC2 | kos | 2
| - optični “patch” panel 19” višina 1U, za 12 LC duplex konektorjev(24 vlaken), komplet s konektorji (LC Duplex Multi-mode) in vsem potrebnim montažnim materialom (LC/LC spojniki, kaseta, "Pigtails" ...), kot naprimer Leviton, tip LC Duplex Multimode, koda: FPCC1SXMM24LC2 | - optical patch panel 19" height 1U, for 12 LC duplex connectors (24 fibres), complete with connectors (LC Duplex Multi-mode) and all necessary mounting material (LC/LC connectors, cassette, pigtails, etc.), e.g. Leviton, type LC Duplex Multimode, code: FPCC1SXMM24LC2 | kos | 1
| - urejevalnik kablov (organiser) 19”, kot naprimer Leviton tip: 1U Rack Mounted - 5 ring, (koda: MMCACCCM001) | - 19" cable manager (organiser), such as Leviton type: 1U Rack Mounted - 5 ring, (code: MMCACCCM001) | kos | 12
| - ranžirni "patch" kablI za računalniško omrežje, F/FTP Cat.6A, RJ-45 to RJ-45, kot naprimer Levinton različnih dolžin od 1,5m do 5m. Priključitev "patch" kablov na eni strani pasivno oprema(delilni paneli) in na drugi aktivno opremo (ethernet stikala). | - patch cables for computer networking, F/FTP Cat.6A, RJ-45 to RJ-45, such as Levinton, in different lengths from 1.5m to 5m. Connection of patch cables to passive equipment (distribution panels) on one side and to active equipment (Ethernet switches) on the other side (Ethernet switches) Connection of patch cables to passive equipment (distribution panels) on one side and to active equipment (Ethernet switches) on the other side. | kos | 338
| -optični MM 50/125 ranžirni "patch" kabel, dvovlakenski z SC to SC - duplex konektorji, kot naprimer Leviton, dolžine 1,5m. | -optical MM 50/125 patch cable, double-fibre with SC to SC - duplex connectors, such as Leviton, 1,5m long. | kos | 12
| -optični SM 9/125 ranžirni "patch" kabel, dvovlakenski z SC to SC - duplex konektorji, kot naprimer Leviton, dolžine 1,5m. | -sM 9/125 optical patch cable, double-fibre with SC to SC - duplex connectors, such as Leviton, 1,5m long. | kos | 24
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, … | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc
1.6 | Dobava in montaža prostostoječih kovinskih omar za potrebe komunikacijskega vozlišča P1-6 (z oznako TK.P1-6-LAN, TK.P1-6-FTP.1, TK.P1-6-FTP.2). Omara, kot na primer: Rittal, VX 5312.114, dimenzije: 2200 mm x 800 mm x 800 mm (VxŠXG), 47U na podstavku višine 100 mm. Sestava omare je naslednja: | Supply and installation of free-standing metal cabinets for the P1-6 communication hub (designated TK.P1-6-LAN, TK.P1-6-FTP.1, TK.P1-6-FTP.2). Cabinet, for example: Rittal, VX 5312.114, dimensions: 2200 mm x 800 mm x 800 mm (HxWxD), 47U on a base height of 100 mm. The wardrobe is composed as follows: |  |  | kpl | 1 |  | 0
| - omara komunikacijskega vozlišča, Rittal, VX 5312.124 | - communication hub cabinet, Rittal, VX 5312.124 | kos | 3
| - steklena vrata spredaj, VX IT 5051.215 | - glass door at front, VX IT 5051.215 | kos | 3
| - kovinska vrata zadaj, VX IT 5051.223 | - metal rear door, VX IT 5051.223 | kos | 3
| - stranska stena omare, VX 8128.245 | - side wall of cabinet, VX 8128.245 | kos | 2
| - standardni 19" montažni profil 47HE (sprednji) VX IT 5302.108 | - standard 19" mounting profile 47HE (front) VX IT 5302.108 | kos | 6
| - standardni 19" montažni profil 47HE (zadnji) VX IT 5302.109 | - standard 19" mounting profile 47HE (rear) VX IT 5302.109 | kos | 6
| - montažni nosilec 800 MM standardni, VX IT 5302.167 | - mounting bracket 800 MM standard, VX IT 5302.167 | kpl | 6
| - montažni nosilec 800 MM, VX IT 5302.169 | - mounting bracket 800 MM, VX IT 5302.169 | kos | 24
| - montažna letev 17x64 MM, 800 MM, VX 8617.040 | - mounting bar 17x64 MM, 800 MM, VX 8617.040 | kos | 6
| - ojačitveni kotnik za 19 profile 800 MM, IT 5302.124 | - reinforcement angle for 19 profiles 800 MM, IT 5302.124 | kpl | 3
| - streha, SV 9681.688 | - roof, SV 9681.688 | kos | 3
| - podstavek kotni element s ploščo spredaj/zadaj, 100 mm, VX 8640.003 | - pedestal corner element with front/rear panel, 100 mm, VX 8640.003 | kos | 6
| '- podstavek stranska zapiralna plošča, 100 mm, VX 8640.034 | - pedestal side closing plate, 100 mm, VX 8640.034 | kos | 6
| - vertikalni urejevalnik kablov, DK 5302.053 | - vertical cable cutter, DK 5302.053 | kos | 6
| - povezovalni kotnik notranji, VX 8617.500 | - connecting angle internal, VX 8617.500 | kpl | 2
| - pokrov spoja omare RAL7035, 800 MM, TS 8800.885 | - cabinet joint cover RAL7035, 800 MM, TS 8800.885 | kos | 2
| - konfortna ročka za odpiranje, VX 8618.201, | - comfort opening handle, VX 8618.201, | kos | 3
| - cilinder vložek (Sistemski ključ) TS8611.180 | - cylinder insert (System key) TS8611.180 | kos | 3
| - ščetinasta zaščita uvoda kablov 2x1m, DK 7825.375 | - bristle cable entry protector 2x1m, DK 7825.375 | kos | 3
| - polica, DK 5501.665 | - shelf, DK 5501.665 | kos | 3
| - ventilator s filtrom, vgrajen na zgornjem delu kovinske stranice priključni kabel…, ventilator priklopljen preko svoje varovalke, SK 3239.108 | - fan with filter, mounted on the upper part of the metal side, connecting cable..., fan connected via its own fuse, SK 3239.108 | kos | 3
| - filterska rešetka vgrajena na spodnjem delu kovinske stranice, SK 3239.208 | - filter grate mounted on the lower part of the metal side, SK 3239.208 | kos | 3
| - končno stikalo SZ 4127.010 | - limit switch SZ 4127.010 | kos | 3
| - termostat, SK 3110.000 | - thermostat, SK 3110.000 | kos | 3
| - predal za dokumentacijo, SZ 2514.000 | - documentation drawer, SZ 2514.000 | kos | 1
| - vtična razdelilna letev s 9 ''schuko'' vtičnicami, z vgrajeno prenapetostno zaščito tretje stopnje, DK 7240.330 | - plug-in distribution board with 9 "schuko" sockets, with built-in surge protection of third level, DK 7240.330 | kos | 3
| - v omaro so vgrajeni 19" okvirji (profili) za montažo “patch” panelov in ostale aktivne in pasivne opreme. | - 19" frames (profiles) for mounting patch panels and other active and passive equipment are built into the cabinet.
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc.
| V komunikacijsko vozlišče (z oznako TK.P1-6-LAN, TK.P1-6-FTP.1, TK.P1-6-FTP.2) se dobavi in vgradi naslednja pasivna oprema: | The following passive equipment shall be supplied and installed in the communication node (designated TK.P1-6-LAN, TK.P1-6-FTP.1, TK.P1-6-FTP.2):
| - “patch” panel 19”, 24 vtičnic FTP, RJ-45 Cat.6, višine 1/2U, kot naprimer: Leviton, tip: LSA Style, Shielded, Black (koda: C6CPNLF240K2H). | - "patch" panel 19", 24 sockets FTP, RJ-45 Cat.6, height 1/2U, as for example Leviton, type: LSA Style, Shielded, Black (code: C6CPNLF240K2H). | kos | 19
| - optični “patch” panel 19” višina 1U, za 12 LC duplex konektorjev(24 vlaken), komplet s konektorji (LC Duplex Single-mode) in vsem potrebnim montažnim materialom (LC/LC spojniki, kaseta, "Pigtails" ...), kot naprimer Leviton, tip LC Duplex Single Mode, koda: FPCC1SXSM24LC2 | - optical patch panel 19" height 1U, for 12 LC duplex connectors (24 fibres), complete with connectors (LC Duplex Single-mode) and all necessary mounting material (LC/LC connectors, cassette, pigtails, etc.), e.g. Leviton, type LC Duplex Single Mode, code: FPCC1SXSM24LC2 | kos | 2
| - optični “patch” panel 19” višina 1U, za 12 LC duplex konektorjev(24 vlaken), komplet s konektorji (LC Duplex Multi-mode) in vsem potrebnim montažnim materialom (LC/LC spojniki, kaseta, "Pigtails" ...), kot naprimer Leviton, tip LC Duplex Multimode, koda: FPCC1SXMM24LC2 | - optical patch panel 19" height 1U, for 12 LC duplex connectors (24 fibres), complete with connectors (LC Duplex Multi-mode) and all necessary mounting material (LC/LC connectors, cassette, pigtails, etc.), e.g. Leviton, type LC Duplex Multimode, code: FPCC1SXMM24LC2 | kos | 1
| - urejevalnik kablov (organiser) 19”, kot naprimer Leviton tip: 1U Rack Mounted - 5 ring, (koda: MMCACCCM001) | - 19" cable manager (organiser), such as Leviton type: 1U Rack Mounted - 5 ring, (code: MMCACCCM001) | kos | 15
| - ranžirni "patch" kablI za računalniško omrežje, F/FTP Cat.6A, RJ-45 to RJ-45, kot naprimer Levinton različnih dolžin od 1,5m do 5m. Priključitev "patch" kablov na eni strani pasivno oprema(delilni paneli) in na drugi aktivno opremo (ethernet stikala). | - patch cables for computer networking, F/FTP Cat.6A, RJ-45 to RJ-45, such as Levinton, in different lengths from 1.5m to 5m. Connection of patch cables to passive equipment (distribution panels) on one side and to active equipment (Ethernet switches) on the other side (Ethernet switches) Connection of patch cables to passive equipment (distribution panels) on one side and to active equipment (Ethernet switches) on the other side. | kos | 440
| -optični MM 50/125 ranžirni "patch" kabel, dvovlakenski z SC to SC - duplex konektorji, kot naprimer Leviton, dolžine 1,5m. | -optical MM 50/125 patch cable, double-fibre with SC to SC - duplex connectors, such as Leviton, 1,5m long. | kos | 12
| -optični SM 9/125 ranžirni "patch" kabel, dvovlakenski z SC to SC - duplex konektorji, kot naprimer Leviton, dolžine 1,5m. | -sM 9/125 optical patch cable, double-fibre with SC to SC - duplex connectors, such as Leviton, 1,5m long. | kos | 24
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, … | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc
1.7 | Dobava in montaža prostostoječih kovinskih omar za potrebe komunikacijskega vozlišča N2-1 (z oznako TK.N2-1-LAN, TK.N2-1-FTP.1, TK.N2-1-FTP.2). Omara, kot na primer: Rittal, VX 5312.114, dimenzije: 2200 mm x 800 mm x 800 mm (VxŠXG), 47U na podstavku višine 100 mm. Sestava omare je naslednja: | Supply and installation of free-standing metal cabinets for the needs of the N2-1 communication hub (designated TK.N2-1-LAN, TK.N2-1-FTP.1, TK.N2-1-FTP.2). Cabinet, for example: Rittal, VX 5312.114, dimensions: 2200 mm x 800 mm x 800 mm (HxWxDxWxD), 47U on a base height of 100 mm. The wardrobe is composed as follows: |  |  | kpl | 1 |  | 0
| - omara komunikacijskega vozlišča, Rittal, VX 5312.124 | - communication hub cabinet, Rittal, VX 5312.124 | kos | 3
| - steklena vrata spredaj, VX IT 5051.215 | - glass door at front, VX IT 5051.215 | kos | 3
| - kovinska vrata zadaj, VX IT 5051.223 | - metal rear door, VX IT 5051.223 | kos | 3
| - stranska stena omare, VX 8128.245 | - side wall of cabinet, VX 8128.245 | kos | 2
| - standardni 19" montažni profil 47HE (sprednji) VX IT 5302.108 | - standard 19" mounting profile 47HE (front) VX IT 5302.108 | kos | 6
| - standardni 19" montažni profil 47HE (zadnji) VX IT 5302.109 | - standard 19" mounting profile 47HE (rear) VX IT 5302.109 | kos | 6
| - montažni nosilec 800 MM standardni, VX IT 5302.167 | - mounting bracket 800 MM standard, VX IT 5302.167 | kpl | 6
| - montažni nosilec 800 MM, VX IT 5302.169 | - mounting bracket 800 MM, VX IT 5302.169 | kos | 24
| - montažna letev 17x64 MM, 800 MM, VX 8617.040 | - mounting bar 17x64 MM, 800 MM, VX 8617.040 | kos | 6
| - ojačitveni kotnik za 19 profile 800 MM, IT 5302.124 | - reinforcement angle for 19 profiles 800 MM, IT 5302.124 | kpl | 3
| - streha, SV 9681.688 | - roof, SV 9681.688 | kos | 3
| - podstavek kotni element s ploščo spredaj/zadaj, 100 mm, VX 8640.003 | - pedestal corner element with front/rear panel, 100 mm, VX 8640.003 | kos | 6
| '- podstavek stranska zapiralna plošča, 100 mm, VX 8640.034 | - pedestal side closing plate, 100 mm, VX 8640.034 | kos | 6
| - vertikalni urejevalnik kablov, DK 5302.053 | - vertical cable cutter, DK 5302.053 | kos | 6
| - povezovalni kotnik notranji, VX 8617.500 | - connecting angle internal, VX 8617.500 | kpl | 2
| - pokrov spoja omare RAL7035, 800 MM, TS 8800.885 | - cabinet joint cover RAL7035, 800 MM, TS 8800.885 | kos | 2
| - konfortna ročka za odpiranje, VX 8618.201, | - comfort opening handle, VX 8618.201, | kos | 3
| - cilinder vložek (Sistemski ključ) TS8611.180 | - cylinder insert (System key) TS8611.180 | kos | 3
| - ščetinasta zaščita uvoda kablov 2x1m, DK 7825.375 | - bristle cable entry protector 2x1m, DK 7825.375 | kos | 3
| - polica, DK 5501.665 | - shelf, DK 5501.665 | kos | 3
| - ventilator s filtrom, vgrajen na zgornjem delu kovinske stranice priključni kabel…, ventilator priklopljen preko svoje varovalke, SK 3239.108 | - fan with filter, mounted on the upper part of the metal side, connecting cable..., fan connected via its own fuse, SK 3239.108 | kos | 3
| - filterska rešetka vgrajena na spodnjem delu kovinske stranice, SK 3239.208 | - filter grate mounted on the lower part of the metal side, SK 3239.208 | kos | 3
| - končno stikalo SZ 4127.010 | - limit switch SZ 4127.010 | kos | 3
| - termostat, SK 3110.000 | - thermostat, SK 3110.000 | kos | 3
| - predal za dokumentacijo, SZ 2514.000 | - documentation drawer, SZ 2514.000 | kos | 1
| - vtična razdelilna letev s 9 ''schuko'' vtičnicami, z vgrajeno prenapetostno zaščito tretje stopnje, DK 7240.330 | - plug-in distribution board with 9 "schuko" sockets, with built-in surge protector of third level, DK 7240.330 | kos | 3
| - v omaro so vgrajeni 19" okvirji (profili) za montažo “patch” panelov in ostale aktivne in pasivne opreme. | - 19" frames (profiles) for mounting patch panels and other active and passive equipment are built into the cabinet.
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc.
| V komunikacijsko vozlišče (z oznako TK.N2-1-LAN, TK.N2-1-FTP.1, TK.N2-1-FTP.2) se dobavi in vgradi naslednja pasivna oprema: | The following passive equipment shall be supplied and installed in the communication node (designated TK.N2-1-LAN, TK.N2-1-FTP.1, TK.N2-1-FTP.2):
| - “patch” panel 19”, 24 vtičnic FTP, RJ-45 Cat.6, višine 1/2U, kot naprimer: Leviton, tip: LSA Style, Shielded, Black (koda: C6CPNLF240K2H). | - "patch" panel 19", 24 sockets FTP, RJ-45 Cat.6, height 1/2U, as for example Leviton, type: LSA Style, Shielded, Black (code: C6CPNLF240K2H). | kos | 19
| - optični “patch” panel 19” višina 1U, za 12 LC duplex konektorjev(24 vlaken), komplet s konektorji (LC Duplex Single-mode) in vsem potrebnim montažnim materialom (LC/LC spojniki, kaseta, "Pigtails" ...), kot naprimer Leviton, tip LC Duplex Single Mode, koda: FPCC1SXSM24LC2 | - optical patch panel 19" height 1U, for 12 LC duplex connectors (24 fibres), complete with connectors (LC Duplex Single-mode) and all necessary mounting material (LC/LC connectors, cassette, pigtails, etc.), e.g. Leviton, type LC Duplex Single Mode, code: FPCC1SXSM24LC2 | kos | 2
| - optični “patch” panel 19” višina 1U, za 12 LC duplex konektorjev(24 vlaken), komplet s konektorji (LC Duplex Multi-mode) in vsem potrebnim montažnim materialom (LC/LC spojniki, kaseta, "Pigtails" ...), kot naprimer Leviton, tip LC Duplex Multimode, koda: FPCC1SXMM24LC2 | - optical patch panel 19" height 1U, for 12 LC duplex connectors (24 fibres), complete with connectors (LC Duplex Multi-mode) and all necessary mounting material (LC/LC connectors, cassette, pigtails, etc.), e.g. Leviton, type LC Duplex Multimode, code: FPCC1SXMM24LC2 | kos | 1
| - urejevalnik kablov (organiser) 19”, kot naprimer Leviton tip: 1U Rack Mounted - 5 ring, (koda: MMCACCCM001) | - 19" cable manager (organiser), such as Leviton type: 1U Rack Mounted - 5 ring, (code: MMCACCCM001) | kos | 18
| - ranžirni "patch" kablI za računalniško omrežje, F/FTP Cat.6A, RJ-45 to RJ-45, kot naprimer Levinton različnih dolžin od 1,5m do 5m. Priključitev "patch" kablov na eni strani pasivno oprema(delilni paneli) in na drugi aktivno opremo (ethernet stikala). | - patch cables for computer networking, F/FTP Cat.6A, RJ-45 to RJ-45, such as Levinton, in different lengths from 1.5m to 5m. Connection of patch cables to passive equipment (distribution panels) on one side and to active equipment (Ethernet switches) on the other side (Ethernet switches) Connection of patch cables to passive equipment (distribution panels) on one side and to active equipment (Ethernet switches) on the other side. | kos | 454
| -optični MM 50/125 ranžirni "patch" kabel, dvovlakenski z SC to SC - duplex konektorji, kot naprimer Leviton, dolžine 1,5m. | -optical MM 50/125 patch cable, double-fibre with SC to SC - duplex connectors, such as Leviton, 1,5m long. | kos | 12
| -optični SM 9/125 ranžirni "patch" kabel, dvovlakenski z SC to SC - duplex konektorji, kot naprimer Leviton, dolžine 1,5m. | -sM 9/125 optical patch cable, double-fibre with SC to SC - duplex connectors, such as Leviton, 1,5m long. | kos | 24
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, … | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc
1.8 | Dobava in montaža prostostoječih kovinskih omar za potrebe komunikacijskega vozlišča N2-2 (z oznako TK.N2-2-LAN, TK.N2-2-FTP.1, TK.N2-2-FTP.2). Omara, kot na primer: Rittal, VX 5312.114, dimenzije: 2200 mm x 800 mm x 800 mm (VxŠXG), 47U na podstavku višine 100 mm. Sestava omare je naslednja: | Supply and installation of free-standing metal cabinets for the needs of the N2-2 communication hub (designated TK.N2-2-LAN, TK.N2-2-FTP.1, TK.N2-2-FTP.2). Cabinet, e.g. Rittal, VX 5312.114, dimensions: 2200 mm x 800 mm x 800 mm (HxWxDxWxD), 47U on a base height of 100 mm. The wardrobe is composed as follows: |  |  | kpl | 1 |  | 0
| - omara komunikacijskega vozlišča, Rittal, VX 5312.124 | - communication hub cabinet, Rittal, VX 5312.124 | kos | 3
| - steklena vrata spredaj, VX IT 5051.215 | - glass door at front, VX IT 5051.215 | kos | 3
| - kovinska vrata zadaj, VX IT 5051.223 | - metal rear door, VX IT 5051.223 | kos | 3
| - stranska stena omare, VX 8128.245 | - side wall of cabinet, VX 8128.245 | kos | 2
| - standardni 19" montažni profil 47HE (sprednji) VX IT 5302.108 | - standard 19" mounting profile 47HE (front) VX IT 5302.108 | kos | 6
| - standardni 19" montažni profil 47HE (zadnji) VX IT 5302.109 | - standard 19" mounting profile 47HE (rear) VX IT 5302.109 | kos | 6
| - montažni nosilec 800 MM standardni, VX IT 5302.167 | - mounting bracket 800 MM standard, VX IT 5302.167 | kpl | 6
| - montažni nosilec 800 MM, VX IT 5302.169 | - mounting bracket 800 MM, VX IT 5302.169 | kos | 24
| - montažna letev 17x64 MM, 800 MM, VX 8617.040 | - mounting bar 17x64 MM, 800 MM, VX 8617.040 | kos | 6
| - ojačitveni kotnik za 19 profile 800 MM, IT 5302.124 | - reinforcement angle for 19 profiles 800 MM, IT 5302.124 | kpl | 3
| - streha, SV 9681.688 | - roof, SV 9681.688 | kos | 3
| - podstavek kotni element s ploščo spredaj/zadaj, 100 mm, VX 8640.003 | - pedestal corner element with front/rear panel, 100 mm, VX 8640.003 | kos | 6
| '- podstavek stranska zapiralna plošča, 100 mm, VX 8640.034 | - pedestal side closing plate, 100 mm, VX 8640.034 | kos | 6
| - vertikalni urejevalnik kablov, DK 5302.053 | - vertical cable cutter, DK 5302.053 | kos | 6
| - povezovalni kotnik notranji, VX 8617.500 | - connecting angle internal, VX 8617.500 | kpl | 2
| - pokrov spoja omare RAL7035, 800 MM, TS 8800.885 | - cabinet joint cover RAL7035, 800 MM, TS 8800.885 | kos | 2
| - konfortna ročka za odpiranje, VX 8618.201, | - comfort opening handle, VX 8618.201, | kos | 3
| - cilinder vložek (Sistemski ključ) TS8611.180 | - cylinder insert (System key) TS8611.180 | kos | 3
| - ščetinasta zaščita uvoda kablov 2x1m, DK 7825.375 | - bristle cable entry protector 2x1m, DK 7825.375 | kos | 3
| - polica, DK 5501.665 | - shelf, DK 5501.665 | kos | 3
| - ventilator s filtrom, vgrajen na zgornjem delu kovinske stranice priključni kabel…, ventilator priklopljen preko svoje varovalke, SK 3239.108 | - fan with filter, mounted on the upper part of the metal side, connecting cable..., fan connected via its own fuse, SK 3239.108 | kos | 3
| - filterska rešetka vgrajena na spodnjem delu kovinske stranice, SK 3239.208 | - filter grate mounted on the lower part of the metal side, SK 3239.208 | kos | 3
| - končno stikalo SZ 4127.010 | - limit switch SZ 4127.010 | kos | 3
| - termostat, SK 3110.000 | - thermostat, SK 3110.000 | kos | 3
| - predal za dokumentacijo, SZ 2514.000 | - documentation drawer, SZ 2514.000 | kos | 1
| - vtična razdelilna letev s 9 ''schuko'' vtičnicami, z vgrajeno prenapetostno zaščito tretje stopnje, DK 7240.330 | - plug-in distribution board with 9 "schuko" sockets, with built-in surge protector of third level, DK 7240.330 | kos | 3
| - v omaro so vgrajeni 19" okvirji (profili) za montažo “patch” panelov in ostale aktivne in pasivne opreme. | - 19" frames (profiles) for mounting patch panels and other active and passive equipment are built into the cabinet.
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc.
| V komunikacijsko vozlišče (z oznako TK.N2-2-LAN, TK.N2-2-FTP.1, TK.N2-2-FTP.2) se dobavi in vgradi naslednja pasivna oprema: | The following passive equipment shall be supplied and installed in the communication node (designated TK.N2-2-LAN, TK.N2-2-FTP.1, TK.N2-2-FTP.2):
| - “patch” panel 19”, 24 vtičnic FTP, RJ-45 Cat.6, višine 1/2U, kot naprimer: Leviton, tip: LSA Style, Shielded, Black (koda: C6CPNLF240K2H). | - "patch" panel 19", 24 sockets FTP, RJ-45 Cat.6, height 1/2U, as for example Leviton, type: LSA Style, Shielded, Black (code: C6CPNLF240K2H). | kos | 19
| - optični “patch” panel 19” višina 1U, za 12 LC duplex konektorjev(24 vlaken), komplet s konektorji (LC Duplex Single-mode) in vsem potrebnim montažnim materialom (LC/LC spojniki, kaseta, "Pigtails" ...), kot naprimer Leviton, tip LC Duplex Single Mode, koda: FPCC1SXSM24LC2 | - optical patch panel 19" height 1U, for 12 LC duplex connectors (24 fibres), complete with connectors (LC Duplex Single-mode) and all necessary mounting material (LC/LC connectors, cassette, pigtails, etc.), e.g. Leviton, type LC Duplex Single Mode, code: FPCC1SXSM24LC2 | kos | 2
| - optični “patch” panel 19” višina 1U, za 12 LC duplex konektorjev(24 vlaken), komplet s konektorji (LC Duplex Multi-mode) in vsem potrebnim montažnim materialom (LC/LC spojniki, kaseta, "Pigtails" ...), kot naprimer Leviton, tip LC Duplex Multimode, koda: FPCC1SXMM24LC2 | - optical patch panel 19" height 1U, for 12 LC duplex connectors (24 fibres), complete with connectors (LC Duplex Multi-mode) and all necessary mounting material (LC/LC connectors, cassette, pigtails, etc.), e.g. Leviton, type LC Duplex Multimode, code: FPCC1SXMM24LC2 | kos | 1
| - urejevalnik kablov (organiser) 19”, kot naprimer Leviton tip: 1U Rack Mounted - 5 ring, (koda: MMCACCCM001) | - 19" cable manager (organiser), such as Leviton type: 1U Rack Mounted - 5 ring, (code: MMCACCCM001) | kos | 17
| - ranžirni "patch" kablI za računalniško omrežje, F/FTP Cat.6A, RJ-45 to RJ-45, kot naprimer Levinton različnih dolžin od 1,5m do 5m. Priključitev "patch" kablov na eni strani pasivno oprema(delilni paneli) in na drugi aktivno opremo (ethernet stikala). | - patch cables for computer networking, F/FTP Cat.6A, RJ-45 to RJ-45, such as Levinton, in different lengths from 1.5m to 5m. Connection of patch cables to passive equipment (distribution panels) on one side and to active equipment (Ethernet switches) on the other side (Ethernet switches) Connection of patch cables to passive equipment (distribution panels) on one side and to active equipment (Ethernet switches) on the other side. | kos | 480
| -optični MM 50/125 ranžirni "patch" kabel, dvovlakenski z SC to SC - duplex konektorji, kot naprimer Leviton, dolžine 1,5m. | -optical MM 50/125 patch cable, double-fibre with SC to SC - duplex connectors, such as Leviton, 1,5m long. | kos | 12
| -optični SM 9/125 ranžirni "patch" kabel, dvovlakenski z SC to SC - duplex konektorji, kot naprimer Leviton, dolžine 1,5m. | -sM 9/125 optical patch cable, double-fibre with SC to SC - duplex connectors, such as Leviton, 1,5m long. | kos | 24
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, … | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc
1.9 | Dobava in montaža prostostoječih kovinskih omar za potrebe komunikacijskega vozlišča N2-3(z oznako TK.N2-3-LAN, TK.N2-3-FTP.1, TK.N2-3-FTP.2). Omara, kot na primer: Rittal, VX 5312.114, dimenzije: 2200 mm x 800 mm x 800 mm (VxŠXG), 47U na podstavku višine 100 mm. Sestava omare je naslednja: | Supply and installation of free-standing metal cabinets for the needs of the N2-3 communication hub (designated TK.N2-3-LAN, TK.N2-3-FTP.1, TK.N2-3-FTP.2). Cabinet, for example: Rittal, VX 5312.114, dimensions: 2200 mm x 800 mm x 800 mm (HxWxDxWxD), 47U on a base height of 100 mm. The wardrobe is composed as follows: |  |  | kpl | 1 |  | 0
| - omara komunikacijskega vozlišča, Rittal, VX 5312.124 | - communication hub cabinet, Rittal, VX 5312.124 | kos | 3
| - steklena vrata spredaj, VX IT 5051.215 | - glass door at front, VX IT 5051.215 | kos | 3
| - kovinska vrata zadaj, VX IT 5051.223 | - metal rear door, VX IT 5051.223 | kos | 3
| - stranska stena omare, VX 8128.245 | - side wall of cabinet, VX 8128.245 | kos | 2
| - standardni 19" montažni profil 47HE (sprednji) VX IT 5302.108 | - standard 19" mounting profile 47HE (front) VX IT 5302.108 | kos | 6
| - standardni 19" montažni profil 47HE (zadnji) VX IT 5302.109 | - standard 19" mounting profile 47HE (rear) VX IT 5302.109 | kos | 6
| - montažni nosilec 800 MM standardni, VX IT 5302.167 | - mounting bracket 800 MM standard, VX IT 5302.167 | kpl | 6
| - montažni nosilec 800 MM, VX IT 5302.169 | - mounting bracket 800 MM, VX IT 5302.169 | kos | 24
| - montažna letev 17x64 MM, 800 MM, VX 8617.040 | - mounting bar 17x64 MM, 800 MM, VX 8617.040 | kos | 6
| - ojačitveni kotnik za 19 profile 800 MM, IT 5302.124 | - reinforcement angle for 19 profiles 800 MM, IT 5302.124 | kpl | 3
| - streha, SV 9681.688 | - roof, SV 9681.688 | kos | 3
| - podstavek kotni element s ploščo spredaj/zadaj, 100 mm, VX 8640.003 | - pedestal corner element with front/rear panel, 100 mm, VX 8640.003 | kos | 6
| '- podstavek stranska zapiralna plošča, 100 mm, VX 8640.034 | - pedestal side closing plate, 100 mm, VX 8640.034 | kos | 6
| - vertikalni urejevalnik kablov, DK 5302.053 | - vertical cable cutter, DK 5302.053 | kos | 6
| - povezovalni kotnik notranji, VX 8617.500 | - connecting angle internal, VX 8617.500 | kpl | 2
| - pokrov spoja omare RAL7035, 800 MM, TS 8800.885 | - cabinet joint cover RAL7035, 800 MM, TS 8800.885 | kos | 2
| - konfortna ročka za odpiranje, VX 8618.201, | - comfort opening handle, VX 8618.201, | kos | 3
| - cilinder vložek (Sistemski ključ) TS8611.180 | - cylinder insert (System key) TS8611.180 | kos | 3
| - ščetinasta zaščita uvoda kablov 2x1m, DK 7825.375 | - bristle cable entry protector 2x1m, DK 7825.375 | kos | 3
| - polica, DK 5501.665 | - shelf, DK 5501.665 | kos | 3
| - ventilator s filtrom, vgrajen na zgornjem delu kovinske stranice priključni kabel…, ventilator priklopljen preko svoje varovalke, SK 3239.108 | - fan with filter, mounted on the upper part of the metal side, connecting cable..., fan connected via its own fuse, SK 3239.108 | kos | 3
| - filterska rešetka vgrajena na spodnjem delu kovinske stranice, SK 3239.208 | - filter grate mounted on the lower part of the metal side, SK 3239.208 | kos | 3
| - končno stikalo SZ 4127.010 | - limit switch SZ 4127.010 | kos | 3
| - termostat, SK 3110.000 | - thermostat, SK 3110.000 | kos | 3
| - predal za dokumentacijo, SZ 2514.000 | - documentation drawer, SZ 2514.000 | kos | 1
| - vtična razdelilna letev s 9 ''schuko'' vtičnicami, z vgrajeno prenapetostno zaščito tretje stopnje, DK 7240.330 | - plug-in distribution board with 9 "schuko" sockets, with built-in surge protector of third level, DK 7240.330 | kos | 2
| - v omaro so vgrajeni 19" okvirji (profili) za montažo “patch” panelov in ostale aktivne in pasivne opreme. | - 19" frames (profiles) for mounting patch panels and other active and passive equipment are built into the cabinet.
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc.
| V komunikacijsko vozlišče (z oznako TK.N2-3-LAN, TK.N2-3-FTP.1, TK.N2-3-FTP.2) se dobavi in vgradi naslednja pasivna oprema: | The following passive equipment shall be supplied and installed in the communication node (designated TK.N2-3-LAN, TK.N2-3-FTP.1, TK.N2-3-FTP.2):
| - “patch” panel 19”, 24 vtičnic FTP, RJ-45 Cat.6, višine 1/2U, kot naprimer: Leviton, tip: LSA Style, Shielded, Black (koda: C6CPNLF240K2H). | - "patch" panel 19", 24 sockets FTP, RJ-45 Cat.6, height 1/2U, as for example Leviton, type: LSA Style, Shielded, Black (code: C6CPNLF240K2H). | kos | 18
| - optični “patch” panel 19” višina 1U, za 12 LC duplex konektorjev(24 vlaken), komplet s konektorji (LC Duplex Single-mode) in vsem potrebnim montažnim materialom (LC/LC spojniki, kaseta, "Pigtails" ...), kot naprimer Leviton, tip LC Duplex Single Mode, koda: FPCC1SXSM24LC2 | - optical patch panel 19" height 1U, for 12 LC duplex connectors (24 fibres), complete with connectors (LC Duplex Single-mode) and all necessary mounting material (LC/LC connectors, cassette, pigtails, etc.), e.g. Leviton, type LC Duplex Single Mode, code: FPCC1SXSM24LC2 | kos | 2
| - optični “patch” panel 19” višina 1U, za 12 LC duplex konektorjev(24 vlaken), komplet s konektorji (LC Duplex Multi-mode) in vsem potrebnim montažnim materialom (LC/LC spojniki, kaseta, "Pigtails" ...), kot naprimer Leviton, tip LC Duplex Multimode, koda: FPCC1SXMM24LC2 | - optical patch panel 19" height 1U, for 12 LC duplex connectors (24 fibres), complete with connectors (LC Duplex Multi-mode) and all necessary mounting material (LC/LC connectors, cassette, pigtails, etc.), e.g. Leviton, type LC Duplex Multimode, code: FPCC1SXMM24LC2 | kos | 1
| - urejevalnik kablov (organiser) 19”, kot naprimer Leviton tip: 1U Rack Mounted - 5 ring, (koda: MMCACCCM001) | - 19" cable manager (organiser), such as Leviton type: 1U Rack Mounted - 5 ring, (code: MMCACCCM001) | kos | 17
| - ranžirni "patch" kablI za računalniško omrežje, F/FTP Cat.6A, RJ-45 to RJ-45, kot naprimer Levinton različnih dolžin od 1,5m do 5m. Priključitev "patch" kablov na eni strani pasivno oprema(delilni paneli) in na drugi aktivno opremo (ethernet stikala). | - patch cables for computer networking, F/FTP Cat.6A, RJ-45 to RJ-45, such as Levinton, in different lengths from 1.5m to 5m. Connection of patch cables to passive equipment (distribution panels) on one side and to active equipment (Ethernet switches) on the other side (Ethernet switches) Connection of patch cables to passive equipment (distribution panels) on one side and to active equipment (Ethernet switches) on the other side. | kos | 440
| -optični MM 50/125 ranžirni "patch" kabel, dvovlakenski z SC to SC - duplex konektorji, kot naprimer Leviton, dolžine 1,5m. | -optical MM 50/125 patch cable, double-fibre with SC to SC - duplex connectors, such as Leviton, 1,5m long. | kos | 12
| -optični SM 9/125 ranžirni "patch" kabel, dvovlakenski z SC to SC - duplex konektorji, kot naprimer Leviton, dolžine 1,5m. | -sM 9/125 optical patch cable, double-fibre with SC to SC - duplex connectors, such as Leviton, 1,5m long. | kos | 24
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, … | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc
1.10 | Dobava in montaža prostostoječih kovinskih omar za potrebe komunikacijskega vozlišča N2-4(z oznako TK.N2-4-LAN, TK.N2-4-FTP.1, TK.N2-4-FTP.2). Omara, kot na primer: Rittal, VX 5312.114, dimenzije: 2200 mm x 800 mm x 800 mm (VxŠXG), 47U na podstavku višine 100 mm. Sestava omare je naslednja: | Supply and installation of free-standing metal cabinets for the needs of the N2-4 communication hub (designated TK.N2-4-LAN, TK.N2-4-FTP.1, TK.N2-4-FTP.2). Cabinet, for example: Rittal, VX 5312.114, dimensions: 2200 mm x 800 mm x 800 mm (HxWxDxWxD), 47U on a base height of 100 mm. The wardrobe is composed as follows: |  |  | kpl | 1 |  | 0
| - omara komunikacijskega vozlišča, Rittal, VX 5312.124 | - communication hub cabinet, Rittal, VX 5312.124 | kos | 3
| - steklena vrata spredaj, VX IT 5051.215 | - glass door at front, VX IT 5051.215 | kos | 3
| - kovinska vrata zadaj, VX IT 5051.223 | - metal rear door, VX IT 5051.223 | kos | 3
| - stranska stena omare, VX 8128.245 | - side wall of cabinet, VX 8128.245 | kos | 2
| - standardni 19" montažni profil 47HE (sprednji) VX IT 5302.108 | - standard 19" mounting profile 47HE (front) VX IT 5302.108 | kos | 6
| - standardni 19" montažni profil 47HE (zadnji) VX IT 5302.109 | - standard 19" mounting profile 47HE (rear) VX IT 5302.109 | kos | 6
| - montažni nosilec 800 MM standardni, VX IT 5302.167 | - mounting bracket 800 MM standard, VX IT 5302.167 | kpl | 6
| - montažni nosilec 800 MM, VX IT 5302.169 | - mounting bracket 800 MM, VX IT 5302.169 | kos | 24
| - montažna letev 17x64 MM, 800 MM, VX 8617.040 | - mounting bar 17x64 MM, 800 MM, VX 8617.040 | kos | 6
| - ojačitveni kotnik za 19 profile 800 MM, IT 5302.124 | - reinforcement angle for 19 profiles 800 MM, IT 5302.124 | kpl | 3
| - streha, SV 9681.688 | - roof, SV 9681.688 | kos | 3
| - podstavek kotni element s ploščo spredaj/zadaj, 100 mm, VX 8640.003 | - pedestal corner element with front/rear panel, 100 mm, VX 8640.003 | kos | 6
| '- podstavek stranska zapiralna plošča, 100 mm, VX 8640.034 | - pedestal side closing plate, 100 mm, VX 8640.034 | kos | 6
| - vertikalni urejevalnik kablov, DK 5302.053 | - vertical cable cutter, DK 5302.053 | kos | 6
| - povezovalni kotnik notranji, VX 8617.500 | - connecting angle internal, VX 8617.500 | kpl | 2
| - pokrov spoja omare RAL7035, 800 MM, TS 8800.885 | - cabinet joint cover RAL7035, 800 MM, TS 8800.885 | kos | 2
| - konfortna ročka za odpiranje, VX 8618.201, | - comfort opening handle, VX 8618.201, | kos | 3
| - cilinder vložek (Sistemski ključ) TS8611.180 | - cylinder insert (System key) TS8611.180 | kos | 3
| - ščetinasta zaščita uvoda kablov 2x1m, DK 7825.375 | - bristle cable entry protector 2x1m, DK 7825.375 | kos | 3
| - polica, DK 5501.665 | - shelf, DK 5501.665 | kos | 3
| - ventilator s filtrom, vgrajen na zgornjem delu kovinske stranice priključni kabel…, ventilator priklopljen preko svoje varovalke, SK 3239.108 | - fan with filter, mounted on the upper part of the metal side, connecting cable..., fan connected via its own fuse, SK 3239.108 | kos | 3
| - filterska rešetka vgrajena na spodnjem delu kovinske stranice, SK 3239.208 | - filter grate mounted on the lower part of the metal side, SK 3239.208 | kos | 3
| - končno stikalo SZ 4127.010 | - limit switch SZ 4127.010 | kos | 3
| - termostat, SK 3110.000 | - thermostat, SK 3110.000 | kos | 3
| - predal za dokumentacijo, SZ 2514.000 | - documentation drawer, SZ 2514.000 | kos | 1
| - vtična razdelilna letev s 9 ''schuko'' vtičnicami, z vgrajeno prenapetostno zaščito tretje stopnje, DK 7240.330 | - plug-in distribution board with 9 "schuko" sockets, with built-in surge protector of third level, DK 7240.330 | kos | 4
| - v omaro so vgrajeni 19" okvirji (profili) za montažo “patch” panelov in ostale aktivne in pasivne opreme. | - 19" frames (profiles) for mounting patch panels and other active and passive equipment are built into the cabinet.
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc.
| V komunikacijsko vozlišče (z oznako TK.N2-4-LAN, TK.N2-4-FTP.1, TK.N2-4-FTP.2) se dobavi in vgradi naslednja pasivna oprema: | The following passive equipment shall be supplied and installed in the communication node (designated TK.N2-4-LAN, TK.N2-4-FTP.1, TK.N2-4-FTP.2):
| - “patch” panel 19”, 24 vtičnic FTP, RJ-45 Cat.6, višine 1/2U, kot naprimer: Leviton, tip: LSA Style, Shielded, Black (koda: C6CPNLF240K2H). | - "patch" panel 19", 24 sockets FTP, RJ-45 Cat.6, height 1/2U, as for example Leviton, type: LSA Style, Shielded, Black (code: C6CPNLF240K2H). | kos | 28
| - optični “patch” panel 19” višina 1U, za 12 LC duplex konektorjev(24 vlaken), komplet s konektorji (LC Duplex Single-mode) in vsem potrebnim montažnim materialom (LC/LC spojniki, kaseta, "Pigtails" ...), kot naprimer Leviton, tip LC Duplex Single Mode, koda: FPCC1SXSM24LC2 | - optical patch panel 19" height 1U, for 12 LC duplex connectors (24 fibres), complete with connectors (LC Duplex Single-mode) and all necessary mounting material (LC/LC connectors, cassette, pigtails, etc.), e.g. Leviton, type LC Duplex Single Mode, code: FPCC1SXSM24LC2 | kos | 2
| - optični “patch” panel 19” višina 1U, za 12 LC duplex konektorjev(24 vlaken), komplet s konektorji (LC Duplex Multi-mode) in vsem potrebnim montažnim materialom (LC/LC spojniki, kaseta, "Pigtails" ...), kot naprimer Leviton, tip LC Duplex Multimode, koda: FPCC1SXMM24LC2 | - optical patch panel 19" height 1U, for 12 LC duplex connectors (24 fibres), complete with connectors (LC Duplex Multi-mode) and all necessary mounting material (LC/LC connectors, cassette, pigtails, etc.), e.g. Leviton, type LC Duplex Multimode, code: FPCC1SXMM24LC2 | kos | 1
| - urejevalnik kablov (organiser) 19”, kot naprimer Leviton tip: 1U Rack Mounted - 5 ring, (koda: MMCACCCM001) | - 19" cable manager (organiser), such as Leviton type: 1U Rack Mounted - 5 ring, (code: MMCACCCM001) | kos | 20
| - ranžirni "patch" kablI za računalniško omrežje, F/FTP Cat.6A, RJ-45 to RJ-45, kot naprimer Levinton različnih dolžin od 1,5m do 5m. Priključitev "patch" kablov na eni strani pasivno oprema(delilni paneli) in na drugi aktivno opremo (ethernet stikala). | - patch cables for computer networking, F/FTP Cat.6A, RJ-45 to RJ-45, such as Levinton, in different lengths from 1.5m to 5m. Connection of patch cables to passive equipment (distribution panels) on one side and to active equipment (Ethernet switches) on the other side (Ethernet switches) Connection of patch cables to passive equipment (distribution panels) on one side and to active equipment (Ethernet switches) on the other side. | kos | 658
| -optični MM 50/125 ranžirni "patch" kabel, dvovlakenski z SC to SC - duplex konektorji, kot naprimer Leviton, dolžine 1,5m. | -optical MM 50/125 patch cable, double-fibre with SC to SC - duplex connectors, such as Leviton, 1,5m long. | kos | 12
| -optični SM 9/125 ranžirni "patch" kabel, dvovlakenski z SC to SC - duplex konektorji, kot naprimer Leviton, dolžine 1,5m. | -sM 9/125 optical patch cable, double-fibre with SC to SC - duplex connectors, such as Leviton, 1,5m long. | kos | 24
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, … | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc
1.11 | Priklop komunikacijskega vozlišča na brezprekinitveni vir napajanja 230VAC, 50 Hz UPS. | Connecting the communication hub to an uninterruptible power supply 230VAC, 50 Hz UPS. |  |  | kpl | 10 |  | 0
1.12 | Dobava in polaganje na kabelske police oz. uvlečenje v inštalacijske cevi, vključno z označevalnimi ploščicami, razvodnicami ter drobnim in spojnim materialom: | Supply and installation on cable racks or insertion into conduits, including marker plates, conduit boxes, small and jointing materials: |  |  | m | 175000 |  | 0
| -F/FTP-Category 6A, 4x2x23 AWG, brezhalogenski, kot naprimer: Leviton | -F/FTP-Category 6A, 4x2x23 AWG, halogen-free, such as Leviton
1.13 | Dobava in polaganje kablov na kabelsko polico od komunikacijskega vozlišča P1-6 do P1-5 | Supply and installation of cables on the cable rack from communication node P1-6 to P1-5 |  |  | m | 62 |  | 0
| - optični kabel SM O3 (24 vlaken), 9/125um (ITU-U G.652.D) | - sM O3 fibre optic cable (24 fibres), 9/125um (ITU-U G.652.D) | kos | 1
| - optični kabel MM OM5 (12 vlaken), 50/125um (ISO/IEC 11801-1) | - mM OM5 fibre optic cable (12 fibres), 50/125um (ISO/IEC 11801-1) | kos | 1
| - FTP kabel Cat 6A | - FTP cable Cat 6A | kos | 6
| Kabel je potrebno ustrezno zaključiti na nov optični delilnik in patch panel v komunikacijskem vozlišču P1-6 in na nov optični delilnik in patch panel v komunikacijskem vozlišču P1-5 | The cable must be properly terminated to the new optical splitter and patch panel in the P1-6 communication node and to the new optical splitter and patch panel in the P1-5 communication node
1.14 | Dobava in polaganje kablov na kabelsko polico od komunikacijskega vozlišča P1-5 do P1-3 | Supply and installation of cables on the cable rack from communication node P1-5 to P1-3 |  |  | m | 65 |  | 0
| - optični kabel SM O3 (24 vlaken), 9/125um (ITU-U G.652.D) | - sM O3 fibre optic cable (24 fibres), 9/125um (ITU-U G.652.D) | kos | 1
| - optični kabel MM OM5 (12 vlaken), 50/125um (ISO/IEC 11801-1) | - mM OM5 fibre optic cable (12 fibres), 50/125um (ISO/IEC 11801-1) | kos | 1
| - FTP kabel Cat 6A | - FTP cable Cat 6A | kos | 6
| Kabel je potrebno ustrezno zaključiti na nov optični delilnik in patch panel v komunikacijskem vozlišču P1-5 in na nov optični delilnik in patch panel v komunikacijskem vozlišču P1-3 | The cable must be properly terminated to the new optical splitter and patch panel in the P1-5 communication node and to the new optical splitter and patch panel in the P1-3 communication node
1.15 | Dobava in polaganje kablov na kabelsko polico od komunikacijskega vozlišča P1-3 do P1-4 | Supply and installation of cables on the cable rack from communication node P1-3 to P1-4 |  |  | m | 114 |  | 0
| - optični kabel SM O3 (24 vlaken), 9/125um (ITU-U G.652.D) | - sM O3 fibre optic cable (24 fibres), 9/125um (ITU-U G.652.D) | kos | 1
| - optični kabel MM OM5 (12 vlaken), 50/125um (ISO/IEC 11801-1) | - mM OM5 fibre optic cable (12 fibres), 50/125um (ISO/IEC 11801-1) | kos | 1
| - FTP kabel Cat 6A | - FTP cable Cat 6A | kos | 6
| Kabel je potrebno ustrezno zaključiti na nov optični delilnik in patch panel v komunikacijskem vozlišču P1-3 in na nov optični delilnik in patch panel v komunikacijskem vozlišču P1-4 | The cable must be properly terminated to the new optical splitter and patch panel in the P1-3 communication node and to the new optical splitter and patch panel in the P1-4 communication node
1.16 | Dobava in polaganje kablov na kabelsko polico od komunikacijskega vozlišča P1-4 do P1-2 | Supply and installation of cables on the cable rack from communication node P1-4 to P1-2 |  |  | m | 70 |  | 0
| - optični kabel SM O3 (24 vlaken), 9/125um (ITU-U G.652.D) | - sM O3 fibre optic cable (24 fibres), 9/125um (ITU-U G.652.D) | kos | 1
| - optični kabel MM OM5 (12 vlaken), 50/125um (ISO/IEC 11801-1) | - mM OM5 fibre optic cable (12 fibres), 50/125um (ISO/IEC 11801-1) | kos | 1
| - FTP kabel Cat 6A | - FTP cable Cat 6A | kos | 6
| Kabel je potrebno ustrezno zaključiti na nov optični delilnik in patch panel v komunikacijskem vozlišču P1-4 in na nov optični delilnik in patch panel v komunikacijskem vozlišču P1-2 | The cable must be properly terminated to the new optical splitter and patch panel in the P1-4 communication node and to the new optical splitter and patch panel in the P1-2 communication node
1.17 | Dobava in polaganje kablov na kabelsko polico od komunikacijskega vozlišča P1-2 do P1-1 | Supply and installation of cables on the cable rack from communication node P1-2 to P1-1 |  |  | m | 100 |  | 0
| - optični kabel SM O3 (24 vlaken), 9/125um (ITU-U G.652.D) | - sM O3 fibre optic cable (24 fibres), 9/125um (ITU-U G.652.D) | kos | 1
| - optični kabel MM OM5 (12 vlaken), 50/125um (ISO/IEC 11801-1) | - mM OM5 fibre optic cable (12 fibres), 50/125um (ISO/IEC 11801-1) | kos | 1
| - FTP kabel Cat 6A | - FTP cable Cat 6A | kos | 6
| Kabel je potrebno ustrezno zaključiti na nov optični delilnik in patch panel v komunikacijskem vozlišču P1-2 in na nov optični delilnik in patch panel v komunikacijskem vozlišču P1-1 | The cable must be properly terminated to the new optical splitter and patch panel in the P1-2 communication node and to the new optical splitter and patch panel in the P1-1 communication node
1.18 | Dobava in polaganje kablov na kabelsko polico od komunikacijskega vozlišča P1-1 do N2-1 | Supply and installation of cables on the cable rack from communication node P1-1 to N2-1 |  |  | m | 25 |  | 0
| - optični kabel SM O3 (24 vlaken), 9/125um (ITU-U G.652.D) | - sM O3 fibre optic cable (24 fibres), 9/125um (ITU-U G.652.D) | kos | 1
| - optični kabel MM OM5 (12 vlaken), 50/125um (ISO/IEC 11801-1) | - mM OM5 fibre optic cable (12 fibres), 50/125um (ISO/IEC 11801-1) | kos | 1
| - FTP kabel Cat 6A | - FTP cable Cat 6A | kos | 6
| Kabel je potrebno ustrezno zaključiti na nov optični delilnik in patch panel v komunikacijskem vozlišču P1-1 in na nov optični delilnik in patch panel v komunikacijskem vozlišču N2-1 | The cable must be properly terminated to the new optical splitter and patch panel in the P1-1 communication node and to the new optical splitter and patch panel in the N2-1 communication node
1.19 | Dobava in polaganje kablov na kabelsko polico od komunikacijskega vozlišča N2-1 do N2-3 | Supply and installation of cables on the cable rack from communication node N2-1 to N2-3 |  |  | m | 130 |  | 0
| - optični kabel SM O3 (24 vlaken), 9/125um (ITU-U G.652.D) | - sM O3 fibre optic cable (24 fibres), 9/125um (ITU-U G.652.D) | kos | 1
| - optični kabel MM OM5 (12 vlaken), 50/125um (ISO/IEC 11801-1) | - mM OM5 fibre optic cable (12 fibres), 50/125um (ISO/IEC 11801-1) | kos | 1
| - FTP kabel Cat 6A | - FTP cable Cat 6A | kos | 6
| Kabel je potrebno ustrezno zaključiti na nov optični delilnik in patch panel v komunikacijskem vozlišču N2-1 in na nov optični delilnik in patch panel v komunikacijskem vozlišču N2-3 | The cable must be properly terminated to the new optical splitter and patch panel in the N2-1 communication node and to the new optical splitter and patch panel in the N2-3 communication node
1.20 | Dobava in polaganje kablov na kabelsko polico od komunikacijskega vozlišča N2-3 do N2-4 | Supply and installation of cables on the cable rack from communication node N2-3 to N2-4 |  |  | m | 100 |  | 0
| - optični kabel SM O3 (24 vlaken), 9/125um (ITU-U G.652.D) | - sM O3 fibre optic cable (24 fibres), 9/125um (ITU-U G.652.D) | kos | 1
| - optični kabel MM OM5 (12 vlaken), 50/125um (ISO/IEC 11801-1) | - mM OM5 fibre optic cable (12 fibres), 50/125um (ISO/IEC 11801-1) | kos | 1
| - FTP kabel Cat 6A | - FTP cable Cat 6A | kos | 6
| Kabel je potrebno ustrezno zaključiti na nov optični delilnik in patch panel v komunikacijskem vozlišču N2-3 in na nov optični delilnik in patch panel v komunikacijskem vozlišču N2-4 | The cable must be properly terminated to the new optical splitter and patch panel in the N2-3 communication node and to the new optical splitter and patch panel in the N2-4 communication node
1.21 | Dobava in polaganje kablov na kabelsko polico od komunikacijskega vozlišča N2-4 do N2-2 | Supply and installation of cables on the cable rack from communication node N2-4 to N2-2 |  |  | m | 85 |  | 0
| - optični kabel SM O3 (24 vlaken), 9/125um (ITU-U G.652.D) | - sM O3 fibre optic cable (24 fibres), 9/125um (ITU-U G.652.D) | kos | 1
| - optični kabel MM OM5 (12 vlaken), 50/125um (ISO/IEC 11801-1) | - mM OM5 fibre optic cable (12 fibres), 50/125um (ISO/IEC 11801-1) | kos | 1
| - FTP kabel Cat 6A | - FTP cable Cat 6A | kos | 6
| Kabel je potrebno ustrezno zaključiti na nov optični delilnik in patch panel v komunikacijskem vozlišču N2-4 in na nov optični delilnik in patch panel v komunikacijskem vozlišču N2-2 | The cable must be properly terminated to the new optical splitter and patch panel in the N2-4 communication node and to the new optical splitter and patch panel in the N2-2 communication node
1.22 | Dobava in polaganje kablov na kabelsko polico od komunikacijskega vozlišča N2-2 do GKV-LAN | Supply and installation of cables on the cable rack from the N2-2 communication node to GKV-LAN |  |  | m | 35 |  | 0
| - optični kabel SM O3 (24 vlaken), 9/125um (ITU-U G.652.D) | - sM O3 fibre optic cable (24 fibres), 9/125um (ITU-U G.652.D) | kos | 1
| - optični kabel MM OM5 (12 vlaken), 50/125um (ISO/IEC 11801-1) | - mM OM5 fibre optic cable (12 fibres), 50/125um (ISO/IEC 11801-1) | kos | 1
| - FTP kabel Cat 6A | - FTP cable Cat 6A | kos | 6
| Kabel je potrebno ustrezno zaključiti na nov optični delilnik in patch panel v komunikacijskem vozlišču N2-2 in na nov optični delilnik in patch panel v komunikacijskem vozlišču GKV-LAN | The cable must be properly terminated to the new optical splitter and patch panel in the N2-2 communication node and to the new optical splitter and patch panel in the GKV-LAN communication node
1.23 | Dobava in polaganje kablov na kabelsko polico od komunikacijskega vozlišča GKV-LAN do P1-6 | Supply and installation of cables on the cable rack from the GKV-LAN communication node to P1-6 |  |  | m | 165 |  | 0
| - optični kabel SM O3 (24 vlaken), 9/125um (ITU-U G.652.D) | - sM O3 fibre optic cable (24 fibres), 9/125um (ITU-U G.652.D) | kos | 1
| - optični kabel MM OM5 (12 vlaken), 50/125um (ISO/IEC 11801-1) | - mM OM5 fibre optic cable (12 fibres), 50/125um (ISO/IEC 11801-1) | kos | 1
| - FTP kabel Cat 6A | - FTP cable Cat 6A | kos | 6
| Kabel je potrebno ustrezno zaključiti na nov optični delilnik in patch panel v komunikacijskem vozlišču GKV-LAN in na nov optični delilnik in patch panel v komunikacijskem vozlišču P1-6 | The cable must be properly terminated to the new optical splitter and patch panel in the GKV-LAN communication node and to the new optical splitter and patch panel in the P1-6 communication node
1.24 | Dobava in montaža komunikacijske vtičnice z dvema konektorjema RJ45 Categorije 6a, s protiprašnim pokrovom, komplet z vsemi potrebnimi komponentami za montažo v parapetni kanal, kot na primer: TEM ČATEŽ, Leviton ali R&M | Supply and installation of a communication socket with two RJ45 Category 6a connectors, with dust cover, complete with all necessary components for installation in the parapet duct, such as TEM ČATEŽ, Leviton or R&M |  |  | kos | 869 |  | 0
1.25 | Dobava in montaža komunikacijske vtičnice z dvema konektorjema RJ45 Categorije 6a, s protiprašnim pokrovom, komplet z vsemi potrebnimi komponentami za podometno montažo, kot na primer TEM ČATEŽ, Leviton ali R&M | Supply and installation of a communication socket with two RJ45 Category 6a connectors, with dust cover, complete with all necessary components for flush mounting, such as TEM ČATEŽ, Leviton or R&M |  |  | kos | 13 |  | 0
1.26 | Dobava in montaža komunikacijske vtičnice z dvema konektorjema RJ45 Categorije 6a, s protiprašnim pokrovom, komplet z vsemi potrebnimi komponentami za nadometno montažo kot na primer TEM ČATEŽ, Leviton ali R&M | Supply and installation of a communication socket with two RJ45 Category 6a connectors, with dust cover, complete with all necessary components for overhead mounting such as TEM ČATEŽ, Leviton or R&M |  |  | kos | 16 |  | 0
1.27 | Dobava in montaža komunikacijske vtičnice z enim konektorjem RJ45 Categorije 6a, s protiprašnim pokrovom, komplet z vsemi potrebnimi komponentami za nadometno montažo kot na primer TEM ČATEŽ, Leviton ali R&M | Supply and installation of a communication socket with one RJ45 Category 6a connector, with dust cover, complete with all necessary components for overhead mounting such as TEM ČATEŽ, Leviton or R&M |  |  | kos | 29 |  | 0
1.28 | Dobava in montaža komunikacijske vtičnice z enim konektorjema RJ45 Categorije 6a, s protiprašnim pokrovom, komplet z vsemi potrebnimi komponentami za podometno montažo, kot na primer TEM ČATEŽ, Leviton ali R&M | Supply and installation of a communication socket with one RJ45 Category 6a connector, with dust cover, complete with all necessary components for flush mounting, such as TEM ČATEŽ, Leviton or R&M |  |  | kos | 3 |  | 0
1.29 | Dobava in montaža komunikacijske vtičnice z dvema konektorjema RJ45 Categorije 6a, v zaščiti vsaj IP44, s protiprašnim pokrovom, antibakterijskim premazom, komplet z vsemi potrebnimi komponentami za podometno montažo vgrajena v čistih prostorih na steno kot na primer TEM ČATEŽ, Leviton ali R&M | Supply and installation of a communication socket with two RJ45 Category 6a connectors, at least IP44 protection, with dust cover, antibacterial coating, complete with all necessary components for flush mounting, installed in clean rooms on a wall such as TEM ČATEŽ, Leviton or R&M |  |  | kos | 46 |  | 0
1.30 | Dobava in montaža komunikacijske vtičnice z dvema konektorjema RJ45 Cat 6A,v zaščiti vsaj IP44, s protiprašnim pokrovom, antibakterijskim premazom, komplet z vsemi potrebnimi komponentami za montažo vgrajena v čistih prostorih v parapetni kanal kot na primer TEM ČATEŽ, Leviton ali R&M | Supply and installation of a communication socket with two RJ45 Cat 6A connectors, at least IP44 protection, with dust cover, antibacterial coating, complete with all necessary components for installation in clean rooms in a parapet duct such as TEM ČATEŽ, Leviton or R&M |  |  | kos | 16 |  | 0
1.31 | Dobava in montaža komunikacijske vtičnice z enim konektorjema RJ45 Categorije 6a, s protiprašnim pokrovom za podometno montažo. Vtičnica je namenjena za priključitev WiFi, kot naprimer TEM, Leviton ali R&M | Supply and installation of a communication socket with one RJ45 Category 6a connector, with dust cover for flush mounting. The socket is designed for connecting WiFi, such as TEM, Leviton or R&M |  |  | kos | 47 |  | 0
1.32 | Dobava in montaža komunikacijske vtičnice z enim konektorjema RJ45 Categorije 6a, s protiprašnim pokrovom za nadometno montažo. Vtičnica je namenjena za priključitev WiFi, kot naprimer TEM, Leviton ali R&M | Supply and installation of a communication socket with one RJ45 Category 6a connector, with dust cover for overhead mounting. The socket is designed for connecting WiFi, such as TEM, Leviton or R&M |  |  | kos | 175 |  | 0
1.33 | Zaključevanje F/FTP kabla na vtičnice RJ45 Cat.6a. (1xRJ45) | Termination of F/FTP cable to RJ45 Cat.6a. sockets (1xRJ45) |  |  | kos | 2174 |  | 0
1.34 | Zaključitev F/FTP kabla, na patch panelih komplet z Snap-In konektorji RJ45 Cat 6A v komunikacijskih vozliščih. Komplet z vsem potrebnim inštalacijskim materalom | Termination of F/FTP cable, on patch panels complete with RJ45 Cat 6A snap-in connectors in communication nodes. Complete with all necessary installation material |  |  | kos | 2210 |  | 0
1.35 | Komunikacijske vtičnice v talnih dozah so specificirane v popisu električnih inštalacij. | The communication sockets in the floor boxes are specified in the electrical installation inventory.
1.36 | Montaža WIFI dostopnih točk po navodilu proizvajalca | Installation of WIFI access points according to the manufacturer's instructions |  |  | kos | 175 |  | 0
1.37 | Izdelava ethernet priključka in priključitev na vtičnico RJ45 ter montaža GMP ure po navodilu proizvajalca komplet z montažo konektorja RJ45 Categorije 6A, na F/FTP kablu, komplet z predpripravo kabla in z vsemi potrebnimi inštalacijskim materialom (ohišje konektorja, …). | Ethernet connection and RJ45 socket connection and installation of the GMP clock according to the manufacturer's instructions, complete with installation of the RJ45 Category 6A connector, on F/FTP cable, complete with pre-preparation of the cable and all necessary installation materials (connector housing, etc.). |  |  | kos | 8 |  | 0
1.38 | Ura za montažo na steno, enostranska, NTP, napajanje POE, komplet z pritrdilnim materialom, kot naprimer: Peweta 91.350.611 | Wall-mount clock, single-sided, NTP, POE power supply, complete with fixing material, e.g. Peweta 91.350.611 |  |  | kos | 28 |  | 0
1.39 | Ura za montažo na strop s konzolo, dvostranska, NTP, napajanje POE, komplet z pritrdilnim materialom, kot naprimer: Peweta 91.352.614 | Ceiling-mounted clock with console, double-sided, NTP, POE power supply, complete with fixing material, e.g. Peweta 91.352.614 |  |  | kos | 8 |  | 0
1.40 | Izdelava ethernet priključka za centralo javljanja požara (CJP). Montaža na vtičnico RJ45, komplet z montažo konektorja RJ45 Categorije 6A, na kablu, komplet z predpripravo kabla in z vsemi potrebnimi inštalacijskim materialom (ohišje konektorja, …). Parametriranje in integracija CJP v Ethernet omrežje. | Creation of the Ethernet connector for the fire panel (CJP). Installation on RJ45 socket, complete with RJ45 Category 6A connector, on cable, complete with pre-preparation of the cable and all necessary installation materials (connector housing, etc.). Parameterisation and integration of the CJP into the Ethernet network. |  |  | kos | 2 |  | 0
1.41 | Izdelava ethernet priključka za krmilnik prezračevanje in klimatizacijo prostorov in industrijskih ethernet stikal. Montaža na vtičnico RJ45 ki bo dobavljena z omarami prezračevanja in klimatizacije, komplet z predpripravo kabla in z vsemi potrebnimi inštalacijskim materialom. Parametriranje in integracija krmilnikov v Ethernet omrežje. | Ethernet connector for the HVAC controller and industrial Ethernet switches. Installation on the RJ45 socket to be supplied with the HVAC cabinets, complete with pre-cabling and all necessary installation materials. Parameterisation and integration of the controllers into the Ethernet network. |  |  | kos | 20 |  | 0
1.42 | Izdelava ethernet priključka za protivlomno centralo. Montaža na vtičnico RJ45 ki bo dobavljena z protivlomna centrala, komplet z predpripravo kabla in z vsemi potrebnimi inštalacijskim materialom. Parametriranje in integracija protivlomne centrale v Ethernet omrežje. | Creation of the Ethernet connector for the burglar alarm control panel. Installation on the RJ45 socket supplied with the burglar alarm control panel, complete with pre-preparation of the cable and all necessary installation materials. Parameterisation and integration of the burglar alarm control panel into the Ethernet network. |  |  | kos | 1 |  | 0
1.43 | Dobava in polaganje izolacijskih cevi in inšalacijskih kanalov: | Supply and installation of insulation pipes and ducts:
| - Trde izolacijske cevi fi 13,5-29, PN, komplet z obešalnim priborom. | - Rigid insulation pipes fi 13,5-29, PN, complete with hanger fittings. |  |  | m | 3400 |  | 0
| - Gibljive zaščitne cevi fi 16-48, RBT, | - Flexible protection tubes fi 16-48, RBT, |  |  | m | 11500 |  | 0
| - Nerjaveče kovinske zaščitne cevi INOX fi 25-70, komplet z pritrdilnim priborom | - Stainless metal protective tubes INOX fi 25-70, complete with fittings |  |  | m | 3000 |  | 0
1.44 | Kabelske police so specificirane v popisu NN razvod. | The cable racks are specified in the LV inventory.
1.45 | Izvajalec inštalacij informacijskega komunikacijskega sistema mora biti usposobljen za izvedbo telekomunikacijskih kabelskih sistemov za kategorijo 6a (Categorije 6a). Pri izvedbi univerzalnega kabliranja oz. TK kabelskih sistemov, mora izvajalec inštalacij upoštavati zahteve podane v standardu SIST EN 50173 za kategorijo 6a (Categorija 6a). | The contractor for the installation of the information communication system shall be qualified for the installation of telecommunication cabling systems for Category 6a (Category 6a). When installing universal cabling or TK cable systems, the installer must comply with the requirements of SIST EN 50173 for Category 6a (Category 6a). |  |  | kpl | 1 |  | 0
1.46 | Izdelava tesnenja prehodov kablov in kabelskih inštalacij za kable Cat. 6A, 23AWG in optične kable (24 vlaken) skozi požarne sektorje, ki ga z ustreznimi materiali izvede izvajalec z licenco ter na koncu izda ustrezni certifikat (izvedba in uporabljen material v skladu s standardom DIN 4102). | Sealing of cable penetrations and cable installations for Cat. 6A, 23AWG and fibre optic cables (24 fibres) through fire sectors, carried out by a licensed contractor using suitable materials and finally certified (execution and material used in accordance with DIN 4102). |  |  | kos | 55 |  | 0
1.47 | Vrtanje odprtin v stenah in ploščah, premer x dolžina lukenj (mm): 50 x 150 | Drilling holes in walls and panels, diameter x length of holes (mm): 50 x 150 |  |  | kos | 50 |  | 0
1.48 | Vrtanje odprtin v stenah in ploščah do fi 120 mm | Drilling holes in walls and panels up to 120 mm fi |  |  | kos | 85 |  | 0
1.49 | Meritve informacijskega komunikacijskega sistema (linka) v skladu s standardi SIST EN 50173 in spuščanje v pogon. Izvajalec univerzalnega kabliranja je dolžan dostaviti rezultate meritev, opravljenih z ustreznim instrumentom, potrjenim s strani proizvajalca pasivne opreme. Rezultati morajo biti (tudi) v originalnem formatu instrumenta. | Measurement of the information communication system (link) in accordance with SIST EN 50173 and commissioning. The universal cabling contractor shall be obliged to deliver the results of measurements made with a suitable instrument certified by the passive equipment manufacturer. The results shall (also) be in the original format of the instrument. |  |  | kpl | 1 |  | 0
1.50 | Meritev optičnih povezav z OTDR in merilnikom moči in spuščanje v pogon. Izvajalec optičnih povezav je dolžan dostaviti rezultate meritev, opravljenih z ustreznim instrumentom, potrjenim s strani proizvajalca opreme. Rezultati morajo biti (tudi) v originalnem formatu instrumenta. | Measurement of optical links with OTDR and power meter and drive down. The optical contractor shall be obliged to deliver the results of the measurements made with a suitable instrument certified by the equipment manufacturer. The results shall (also) be in the original format of the instrument. |  |  | kpl | 1 |  | 0
1.51 | Izobraževanje uporabnikov in vzdrževalcev | User and maintenance training |  |  | kpl | 1 |  | 0
| UNIVERZALNO KABLIRANJE, WiFi in drugi IKS | UNIVERSAL CABLING, WiFi and other IKS | [5 empty] | 0

## 3.8.2_STREŽNIŠKI PROSTOR
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.8 | ELEKTRO DELA | ELECTRICAL WORKS
3.8.2 | STREŽNIŠKI PROSTOR | SERVER ROOM | [5 empty] | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description |  |  | EM | Količina | Cena/EM | Cena
2 | STREŽNIŠKI PROSTOR | SERVER ROOM
| STREŽNIŠKE IN KOMUNIKACIJSKE RACK OMARE | SERVER AND COMMUNICATION RACK CABINETS
2.1 | Dobava in montaža 19” rack omare – KOMUNIKACIJSKA OMARA 42HE v oznaki GKV-LAN | Supply and installation of 19" rack cabinet - COMMUNICATIONS CABINET 42HE in code GKV-LAN |  |  | kpl | 1 |  | 0
| • Višina: < 2000mm • Širina: 750mm • Globina: 1200mm • Min. globina namestitve opreme: manjša ali enaka 300mm • Maks. globina namestitve opreme: večja ali enaka 900mm • Omara mora za zadnjim 19” rastrom omogočati vsaj še 150mm prostora za brezvijačno namestitev električnih razdelilcev in vertikalnih organizatorjev ožičenja , ki ne zasedajo koristnega prostora v omari (0U) – vsaj 4 montažna mesta po celi višini, dva na levi strani in dva na desni strani omare • Nosilnost: >1500kg • Ustreznost po EIA 310-E (stopnja perforiranosti vrat, namestitev opreme) • Visoko nosilna kolesa, 4x, ki se uporabljajo zgolj za transport/premik omare. Po namestitvi omare na končno pozicijo, se omaro fiksira s štirimi prednameščenimi nivelirnimi nogicami. • Barva omare mora biti enotna, črna ali bela • Perforirana vrata spredaj, tovarniško ozemljena preko ohišja omare • Perforirana dvokrilna vrata zadaj, tovarniško ozemljena preko ohišja • Omara mora biti samostoječa, kovinska, z antikorozijsko zaščito | - Height: < 2000mm - Width: 750mm - Depth: 1200mm - Min. installation depth of equipment: less than or equal to 300mm - Max. installation depth of equipment: greater than or equal to 900mm - The cabinet must allow at least 150mm of space behind the rear 19" rack for screwless mounting of electrical distributors and vertical wiring organisers that do not take up useful space in the cabinet (0U) - at least 4 full height mounting positions, two on the left side and two on the right side of the cabinet - Load capacity: >1500kg - EIA 310-E compliance (degree of door perforation, equipment installation) - High load-bearing wheels, 4x, used only for transport/movement of the cabinet. After the cabinet has been placed in its final position, the cabinet is fixed with four pre-installed levelling feet. - The colour of the cabinet must be uniform, black or white - Perforated door at front, grounded at the factory through the cabinet body - Perforated bi-fold doors at rear, factory earthed through housing - The cabinet shall be freestanding, metal, with corrosion protection
| • Okvir mora imeti vse robove posnete, noben rob ne sme biti oster • Okvirji omare morajo biti medsebojno povezljivi v vseh smereh • Omara mora omogočati vijačno povezavo s sosednjo omaro'• 19” nosilci premični po šinah vodoravno naprej/nazaj • Numeracija višinskih enot na 19” nosilcih (po 1U) | - The frame must have all edges chamfered, no edge must be sharp - Cabinet frames shall be interconnectible in all directions - The cabinet must be able to be bolted to the adjacent cabinet'- 19" brackets movable horizontally forward/rearward on the rails - Numbering of height units on 19" beams (by 1U)
| • Omara mora biti opremljena z enostavno snemljivimi stranicami levo in desno• Montažni pribor (matice s kletko in vijaki), ozemljitev med seboj • Omara mora imeti snemljivo streho in ločene uvode za kable v strehi, brez ostrih robov • Možnost montažne namestitve s pregradami ločenih kanalov na strehi omare za jakotočne in šibkotočne instalacije Kot naprimer tip APC NetShelter SX ali enakovredno | - The cabinet shall be equipped with easily removable left and right sides - mounting accessories (nuts with cage and screws), earthing between each other - The cabinet shall have a removable roof and separate cable entries in the roof, without sharp edges - Prefabricated installation with separate duct baffles on the roof of the cabinet for both low- and high-current installations Such as APC NetShelter SX or equivalent
| V komunikacijsko vozlišče (z oznako GKV-LAN) se dobavi in vgradi naslednja pasivna oprema: | The following passive equipment shall be supplied and installed in the communication node (designated GKV-LAN):
| - “patch” panel 19”, 24 vtičnic FTP, RJ-45 Cat.6, višine 1/2U, kot naprimer: Leviton, tip: LSA Style, Shielded, Black (koda: C6CPNLF240K2H). | - "patch" panel 19", 24 sockets FTP, RJ-45 Cat.6, height 1/2U, as for example Leviton, type: LSA Style, Shielded, Black (code: C6CPNLF240K2H). | kos | 1
| - optični “patch” panel 19” višina 1U, za 12 LC duplex konektorjev(24 vlaken), komplet s konektorji (LC Duplex Single-mode) in vsem potrebnim montažnim materialom (LC/LC spojniki, kaseta, "Pigtails" ...), kot naprimer Leviton, tip LC Duplex Single Mode, koda: FPCC1SXSM24LC2 | - optical patch panel 19" height 1U, for 12 LC duplex connectors (24 fibres), complete with connectors (LC Duplex Single-mode) and all necessary mounting material (LC/LC connectors, cassette, pigtails, etc.), e.g. Leviton, type LC Duplex Single Mode, code: FPCC1SXSM24LC2 | kos | 2
| - optični “patch” panel 19” višina 1U, za 12 LC duplex konektorjev(24 vlaken), komplet s konektorji (LC Duplex Multi-mode) in vsem potrebnim montažnim materialom (LC/LC spojniki, kaseta, "Pigtails" ...), kot naprimer Leviton, tip LC Duplex Multimode, koda: FPCC1SXMM24LC2 | - optical patch panel 19" height 1U, for 12 LC duplex connectors (24 fibres), complete with connectors (LC Duplex Multi-mode) and all necessary mounting material (LC/LC connectors, cassette, pigtails, etc.), e.g. Leviton, type LC Duplex Multimode, code: FPCC1SXMM24LC2 | kos | 1
| - urejevalnik kablov (organiser) 19”, kot naprimer Leviton tip: 1U Rack Mounted - 5 ring, (koda: MMCACCCM001) | - 19" cable manager (organiser), such as Leviton type: 1U Rack Mounted - 5 ring, (code: MMCACCCM001) | kos | 3
| - optični “patch” panel 19” višina 1U, za 24 LC duplex konektorjev (48 vlaken), komplet s konektorji (LC Duplex Single-mode) in vsem potrebnim montažnim materialom (LC/LC spojniki, kaseta, "Pigtails" ...), kot naprimer Leviton, tip LC Duplex Single Mode, koda: FPCC1SXSM48LC2 | - optical patch panel 19" height 1U, for 24 LC duplex connectors (48 fibres), complete with connectors (LC Duplex Single-mode) and all necessary mounting material (LC/LC connectors, cassette, pigtails, etc.), e.g. Leviton, type LC Duplex Single Mode, code: FPCC1SXSM48LC2 | kos | 2
2.2 | Vertikalni organizatorji ožičenja za namestitev v 42U komunikacijsko omaro spredaj levo in desno v obliki prstov/grabelj na vsakih 1U. Globina organizatorja vsaj 150mm, širina vsaj 120mm. | Vertical wiring organisers for installation in 42U front left and right finger/grab style communication racks every 1U. Minimum 150mm depth, minimum 120mm width. |  |  | kpl | 1 |  | 0
2.3 | Dobava in montaža 19” rack omare – STREŽNIŠKA OMARA 42HE • Višina: < 2000mm • Širina: 750mm • Globina: 1200mm • Min. globina namestitve opreme: manjša ali enaka 300mm • Maks. globina namestitve opreme: večja ali enaka 1000mm • Omara mora za zadnjim 19” rastrom omogočati vsaj še 300mm prostora za brezvijačno namestitev električnih razdelilcev in vertikalnih organizatorjev ožičenja , ki ne zasedajo koristnega prostora v omari (0U) – vsaj 8 montažnih mest po celi višini, štiri na levi strani in štiri na desni strani omare • Nosilnost: >1500 • Ustreznost po EIA 310-E (stopnja perforiranosti vrat, namestitev opreme) • Visoko nosilna kolesa, 4x, ki se uporabljajo zgolj za transport/premik omare. Po namestitvi omare na končno pozicijo, se omaro fiksira s štirimi prednameščenimi nivelirnimi nogicami. • Barva omare mora biti enotna, črna ali bela • Perforirana vrata spredaj, tovarniško ozemljena preko ohišja omare • Perforirana dvokrilna vrata zadaj, tovarniško ozemljena preko ohišja • Omara mora biti samostoječ, kovinska, z antikorozijsko zaščito • Okvir mora imeti vse robove posnete, noben rob ne sme biti oster • Okvirji omare morajo biti medsebojno povezljivi v vseh smereh • Omara mora omogočati vijačno povezavo s sosednjo omaro • 19” nosilci premični po šinah vodoravno naprej/nazaj • Numeracija višinskih enot na 19” nosilcih (po 1U) • Omara mora biti opremljena z enostavno snemljivimi stranicami levo in desno • Montažni pribor (matice s kletko in vijaki), ozemljitev med seboj • Omara mora imeti snemljivo streho in ločene uvode za kable v strehi, brez ostrih robov • Možnost montažne namestitve s pregradami ločenih kanalov na strehi omare za jakotočne in šibkotočne instalacije Kot naprimer tip APC NetShelter SX ali enakovredno | Supply and installation of 19" rack cabinets - 42HE RACK CABINET - Height: < 2000mm - Width: 750mm - Depth: 1200mm - Min. installation depth of equipment: less than or equal to 300mm - Max. installation depth of equipment: greater than or equal to 1000mm - The cabinet shall allow at least 300 mm of space behind the rear 19" rack for screwless mounting of electrical distributors and vertical wiring organisers that do not take up useful space in the cabinet (0U) - at least 8 mounting positions at full height, four on the left side and four on the right side of the cabinet - Load capacity: >1500 - EIA 310-E compliance (degree of door perforation, equipment installation) - High load-bearing wheels, 4x, used only for transport/movement of the cabinet. After the cabinet has been placed in its final position, the cabinet is fixed with four pre-installed levelling feet. - The colour of the cabinet must be uniform, black or white - Perforated door at front, grounded at the factory through the cabinet body - Perforated bi-fold doors at rear, factory earthed through the casing - The cabinet shall be freestanding, metal, with corrosion protection - The frame must have all edges chamfered, no edge must be sharp - Cabinet frames shall be interconnectible in all directions - The cabinet shall be capable of being screwed into an adjacent cabinet - 19" beams horizontally movable forward/rearward - Numbering of height units on 19" beams (by 1U) - The cabinet shall be fitted with easily removable left and right-hand sides - Mounting accessories (nuts with cage and screws), earthing between each other - The cabinet shall have a removable roof and separate cable entries in the roof, without sharp edges - Prefabricated installation with separate duct baffles on the roof of the cabinet for both low- and high-current installations Such as APC NetShelter SX or equivalent |  |  | kpl | 6 |  | 0
| • Omara mora omogočati vijačno povezavo s sosednjo omaro • 19” nosilci premični po šinah vodoravno naprej/nazaj • Numeracija višinskih enot na 19” nosilcih (po 1U) • Omara mora biti opremljena z enostavno snemljivimi stranicami levo in desno • Montažni pribor (matice s kletko in vijaki), ozemljitev med seboj • Omara mora imeti snemljivo streho in ločene uvode za kable v strehi, brez ostrih robov • Možnost montažne namestitve s pregradami ločenih kanalov na strehi omare za jakotočne in šibkotočne instalacije Kot naprimer tip APC NetShelter SX ali enakovredno | - The cabinet shall be capable of being screwed into an adjacent cabinet - 19" beams horizontally movable forward/rearward - Numbering of height units on 19" beams (by 1U) - The cabinet shall be fitted with easily removable left and right-hand sides - Mounting accessories (nuts with cage and screws), earthing between each other - The cabinet shall have a removable roof and separate cable entries in the roof, without sharp edges - Prefabricated installation with separate duct baffles on the roof of the cabinet for both low- and high-current installations Such as APC NetShelter SX or equivalent
2.4 | Dobava in montaža notranjih stranskih elementov rack omar za zapiranje prostora med 19” rastrom in stranico rack omare (spredaj, levo in desno) - preprečevanje mešanja zraka med toplo in hladno cono | Supply and installation of internal rack side elements to close the space between the 19" rack and the rack side (front, left and right) - to prevent air mixing between the hot and cold zones |  |  | kpl | 7 |  | 0
2.5 | 1U slepi paneli z brezvijačno montažo za preprečitev mešanja zraka med hladno in toplo cono | 1U blanking panels with screwless mounting to prevent air mixing between cold and warm zones |  |  | kos | 200 |  | 0
2.6 | Izvedba kabelskega korita na strehi strežniških in komunikacijskih omar, širine 750mm, za namestitev jakotočnih kablov. Kabelske poti se izvede s posebnimi tovarniško izdelanimi pregradami brezvijačno nameščenimi na streho omar. Širina kabelske poti mora biti vsaj 300mm. Izvedba kabelskega korita mora omogočati galvansko ločeni prehod šibkotočnih kablov pod kabelskim koritom na sosednjo vrsto rack (korito v obliki črke H s prehodom v spodnjem prekatu). | The construction of a cable tray on the roof of the server and communication cabinets, 750 mm wide, for the installation of jackup cables. The cable pathways shall be provided by means of special factory-made bulkheads screwlessly mounted on the roof of the cabinets. The width of the cable pathway shall be at least 300 mm. The construction of the cable tray shall allow galvanically isolated passage of the low-current cables under the tray to the adjacent row of rack (H-shaped tray with a passageway in the lower compartment). |  |  | kpl | 7 |  | 0
2.7 | Izvedba dveh prekatov kabelskih poti na strehi strežniških in komunikacijskih omar, širine 750mm, za namestitev šibkotočnih kablov. Kabelske poti se izvede s posebnimi tovarniško izdelanimi pregradami brezvijačno nameščenimi na streho omar z možnostjo spreminjanja širine posameznega prekata. Izvedba prekatov mora omogočati prehod kablov iz enega prekata v drugega v višini poteka kablov (skozi prekat). | The construction of two 750 mm wide cable pathways on the roof of the server and communication cabinets for the installation of low-frequency cables. The cable pathways shall be constructed with special factory-built bulkheads screwlessly mounted on the roof of the cabinets, with the possibility of varying the width of the individual pathways. The design of the pathways shall allow the passage of cables from one pathway to the other at the level of the cable passage (through the pathway). |  |  | kpl | 7 |  | 0
2.8 | Dobava in namestitev vertikalnih organizatorjev kablov z brezvijačno montažo v zadnjem delu strežniške ali komunikacijske omare z vsaj 16 rinkami, razporejenimi po celi višini omare (0HE) | Supply and installation of vertical cable organisers with screwless mounting in the rear of a server or communication cabinet with at least 16 files distributed over the entire height of the cabinet (0HE) |  |  | kos | 14 |  | 0
2.9 | Dobava, montaža in konfiguracija rackPDU vertikalnih razdelilnih letev za montažo v FS in LAB strežniške rack omare z naslednjimi karakteristikami: - Zagotovitev dvojnega napajanja A+B v vsaki omari - brezvijačna namestitev v zadnjem delu omar na način, da razdelilec ne zaseda koristnega prostora v omari (0U) - vgrajen priključek za nadzor preko Ethernet omrežja (WEB/SNMP nadzor) in integracija v centralni nadzorni sistem infrastrukture podatkovnega centra DCIM - LCD displej - zagotovitev meritve na nivoju letve naslednjih parametrov: moč (kW, kVA), tok (A), napetost (V) - prikaz lokalno na LCD displeju in preko SNMP nadzora - nastavitev mejnih vrednosti z alarmiranjem preko nadzornega sistema - možnost priklopa senzorjev za temperaturo in vlago - vhodni tok 1x 32A (1-fazno) - vhodni priključek IEC309 32A 1P+N+PE - izhodni priključki minimalno 36x IEC 320 C13 (vsak 10A) vtičnic in 6x IEC 320 C19 (vsak 16A) Kot naprimer tip APC RackPDU Metered 2G, ZeroU 7kW ali enakovredno | Supply, installation and configuration of rackPDU vertical distribution rails for installation in FS and LAB server rack cabinets with the following characteristics: - Provide dual A+B power supply in each cabinet - screwless installation in the rear of the enclosure so that the distributor does not take up any useful space in the enclosure (0U) - built-in connection for control via Ethernet network (WEB/SNMP control) and integration into the central control system of the DCIM data centre infrastructure - LCD display - provide lath-level measurement of the following parameters: power (kW, kVA), current (A), voltage (V) - display locally on LCD and via SNMP control - setting limit values with alarming via the monitoring system - possibility to connect temperature and humidity sensors - input current 1x 32A (1-phase) - iEC309 32A 1P+N+PE input connector - output connections minimum 36x IEC 320 C13 (10A each) sockets and 6x IEC 320 C19 (16A each) sockets Such as APC RackPDU Metered 2G, ZeroU 7kW or equivalent |  |  | kpl | 8 |  | 0
2.10 | Dobava, montaža in konfiguracija rackPDU vertikalnih razdelilnih letev za montažo v HPC strežniške rack omare z naslednjimi karakteristikami: - Zagotovitev dvojnega napajanja A+B v vsaki omari - brezvijačna namestitev v zadnjem delu omar na način, da razdelilec ne zaseda koristnega prostora v omari (0U) - vgrajen priključek za nadzor preko Ethernet omrežja (WEB/SNMP nadzor) in integracija v centralni nadzorni sistem infrastrukture podatkovnega centra DCIM - LCD displej - zagotovitev meritve na nivoju letve naslednjih parametrov: moč (kW, kVA), tok (A), napetost (V) - prikaz lokalno na LCD displeju in preko SNMP nadzora - nastavitev mejnih vrednosti z alarmiranjem preko nadzornega sistema - možnost priklopa senzorjev za temperaturo in vlago - vhodni tok 3x 16A (3-fazno) - vhodni priključek IEC309 16A 3P+N+PE - izhodni priključki minimalno 36x IEC 320 C13 (vsak 10A) vtičnic in 6x IEC 320 C19 (vsak 16A) Kot naprimer tip APC RackPDU Metered 2G, ZeroU 11kW ali enakovredno | Supply, installation and configuration of rackPDU vertical distribution rails for installation in HPC server rack cabinets with the following characteristics: - Provide dual A+B power supply in each cabinet - screwless installation in the rear of the enclosure so that the distributor does not take up any useful space in the enclosure (0U) - built-in connection for control via Ethernet network (WEB/SNMP control) and integration into the central control system of the DCIM data centre infrastructure - LCD display - provide lath level measurement of the following parameters: power (kW, kVA), current (A), voltage (V) - display locally on LCD and via SNMP control - setting limit values with alarming via the monitoring system - possibility to connect temperature and humidity sensors - input current 3x 16A (3-phase) - iEC309 16A 3P+N+PE input connector - output connections minimum 36x IEC 320 C13 (10A each) sockets and 6x IEC 320 C19 (16A each) sockets Such as APC RackPDU Metered 2G, ZeroU 11kW or equivalent |  |  | kpl | 4 |  | 0
2.11 | Dobava, montaža in konfiguracija rackPDU vertikalnih razdelilnih letev za montažo v TK komunikacijsko rack omaro z naslednjimi karakteristikami: - Zagotovitev dvojnega napajanja A+B v vsaki omari - brezvijačna namestitev v zadnjem delu omar na način, da razdelilec ne zaseda koristnega prostora v omari (0U) - vgrajen priključek za nadzor preko Ethernet omrežja (WEB/SNMP nadzor) in integracija v centralni nadzorni sistem infrastrukture podatkovnega centra DCIM - LCD displej - zagotovitev meritve na nivoju letve naslednjih parametrov: moč (kW, kVA), tok (A), napetost (V) - prikaz lokalno na LCD displeju in preko SNMP nadzora - nastavitev mejnih vrednosti z alarmiranjem preko nadzornega sistema - možnost priklopa senzorjev za temperaturo in vlago - vhodni tok 1x 16A (1-fazno) - vhodni priključek IEC309 16A 1P+N+PE - izhodni priključki minimalno 18x IEC 320 C13 (vsak 10A) vtičnic in 2x IEC 320 C19 (vsak 16A) Kot naprimer tip APC RackPDU Metered, ZeroU 3kW ali enakovredno | Supply, installation and configuration of rackPDU vertical distribution rails for installation in a TK communication rack cabinet with the following characteristics: - Provide dual A+B power supply in each cabinet - screwless installation in the rear of the enclosure so that the distributor does not take up any useful space in the enclosure (0U) - built-in connection for control via Ethernet network (WEB/SNMP control) and integration into the central control system of the DCIM data centre infrastructure - LCD display - provide lath level measurement of the following parameters: power (kW, kVA), current (A), voltage (V) - display locally on LCD and via SNMP control - setting limit values with alarming via the monitoring system - possibility to connect temperature and humidity sensors - input current 1x 16A (1-phase) - iEC309 16A 1P+N+PE input connector - output connections minimum 18x IEC 320 C13 (10A each) sockets and 2x IEC 320 C19 (16A each) Such as APC RackPDU Metered, ZeroU 3kW or equivalent |  |  | kpl | 2 |  | 0
2.12 | Dobava, montaža in konfiguracija avtomatskega preklopnega stikala, ki omogoča napajanje porabnikov z enim napajalnikom iz dveh virov A+B - Max celotna poraba toka: 16A - Vhodne povezave 2x IEC309 16A 2P+E - Izhodne povezave 8x IEC 320 C13 (vsak 10A) - Vgrajen priključek za nadzor preko Ethernet omrežja (WEB/SNMP nadzor) in integracija v centralni nadzorni sistem infrastrukture podatkovnega centra DCIM - Dostop preko gesla - LED ekran s prikazom trenutne obremenitve stikala - tok, A Kot naprimer tip APC RackATS, 16A ali enakovredno | Supply, installation and configuration of an automatic transfer switch to allow the supply of two A+B power sources to consumers with a single power supply - Max total current consumption: 16A - Input connections 2x IEC309 16A 2P+E - Output connections 8x IEC 320 C13 (10A each) - Built-in connection for monitoring via Ethernet (WEB/SNMP monitoring) and integration into the central monitoring system of the DCIM data centre infrastructure - Password access - LED display showing the current load of the switch - current, A Such as APC RackATS type, 16A or equivalent |  |  | kpl | 1 |  | 0
2.13 | Izvedba zaprte tople cone dolžine min 6150mm in širine 1200mm: - Zaprta topla cona mora biti zgrajena v celoti za vrsto omar, hladilnih in drugih enot. - Modularna vodila za namestitev stropnih elementov, ki omogočajo enostavno odpiranje in odstranjevanje plošč zaprte cone - Možnost prilagajanja širine konstrukcije zaprte cone, ki omogoča kasnejšo vgradnjo drugačnih komunikacijkih omar, z drugačno globino. - Stropni elementi iz prozornega, slabo gorljivega materiala, ki ustreza odzivu na ogenj vsaj B-s2, d0 po EN13501-1 - 1x drsna vrata za vstop v zaprto cono z mehkim zapiranjem - vodilo za vrata - zaprta cona na drugi strani sloni na steno - montaža | Construction of an enclosed warm zone with a minimum length of 6150 mm and a width of 1200 mm: - The enclosed warm zone must be built entirely to accommodate a range of cupboards, refrigeration and other units. - Modular ceiling element mounting rails for easy opening and removal of closed zone panels - The width of the closed zone construction can be adjusted to allow for the subsequent installation of different communication cabinets with different depths. - Ceiling elements of transparent, low-combustible material having a reaction to fire performance not less than B-s2, d0 to EN13501-1 - 1x sliding door for entry to the enclosed zone with soft closing - door guide - the closed zone on the other side is leaning against the wall - assembly |  |  | kos | 1 |  | 0
2.14 | Izdelava posnetkov za projekt izvedenih del z vrisom sprememb nastalih med gradnjo v projektno dokumentacijo (PZI načrt) v papirni obliki, ki jih potrdi nadzor po ZGO in predaja teh ostalim izdelovalcem PID načrta, izdelava navodil za obratovanje, navodil za vzdrževanje in periodične preglede | Preparation of the design drawings for the project of the works carried out with the incorporation of the changes made during construction into the project documentation (PZI plan) in paper form, approved by the PGI supervision and handed over to the other PID plan producers, preparation of the operating instructions, maintenance instructions and periodic inspections |  |  | kpl | 1 |  | 0
| BREZPREKINITVENO NAPAJANJE - UPS | UNINTERRUPTIBLE POWER SUPPLY - OOPS
2.15 | Dobava in montaža UPS sistema nazivne moči 40kVA/kW + 1 rezervni močnostni modul. Zagotavljati mora oskrbo kritičnih porabnikov z električno energijo. Minimalne tehnične značilnosti UPS sistema: - Možnost delovanja v ekonomičnem režimu z vzporednim napajanjem aktivnega dela bremena preko statičnega obvoda in delovanjem razsmernika (Inverter), ki oskrbuje reaktivni del bremena ter omogoča polnjenje baterij – delovanje po IEC 62040-3 Class 1 – brezprekinitveni preklop (kot na primer ECOnversion mode) - Učinkovitost: v normalnem načinu delovanja (dvojna pretvorba) vsaj 97% pri bremenu nad 75%. Učinkovitost: v ekonomičnem režimu z vzporednim napajanjem aktivnega dela bremena preko statičnega obvoda in delovanjem razsmernika (Inverter), ki oskrbuje reaktivni del bremena ter omogoča polnjenje baterij – delovanje po IEC 62040-3 Class 1 – brezprekinitveni preklop vsaj 99% pri bremenu nad 75%. - N+1 redundantni močnostni modul s funkcionalnostjo zamenjave modulov med delovanjem v On-line načinu delovanja - LiveSwap ali enakovredna tehnologija zamenjave močnostnih modulov v on-line načinu delovanja UPS mora zagotavljati varovanje pred električnim oblokom z incidentno energijo <1,2 cal/cm2, merjeno 200mm od sprednje plošče UPS | Supply and installation of a UPS system with a rated power of 40kVA/kW + 1 standby power module. It must ensure the supply of electricity to critical customers. Minimum technical characteristics of the UPS system: - Possibility to operate in economy mode by supplying the active part of the load in parallel via a static bypass and the operation of an inverter supplying the reactive part of the load and allowing the batteries to be charged - IEC 62040-3 Class 1 operation - Continuous switching (such as ECOnversion mode) - Efficiency: in normal operation (double conversion) at least 97% at loads above 75%. Efficiency: in economy mode, with parallel supply of the active part of the load via a static bypass and operation of an inverter supplying the reactive part of the load and allowing charging of the batteries - IEC 62040-3 Class 1 operation - uninterruptible switching of at least 99% at loads above 75%. - N+1 redundant power module with module swap functionality during On-line operation - LiveSwap or equivalent power module swapping technology in on-line UPS operation mode shall provide arc flash protection with an incident energy <1,2 cal/cm2 measured 200mm from the UPS front panel
| - On-line tehnologija delovanja z dvojno pretvorbo - Nazivna moč: 40kVA/40kW, izhodni faktor moči od 0.7 ind. do 0.7 kap. brez znižanja nazivne navidezne moči (kVA) - Vhodna napetost: 3f+N+PE, 340-460V AC 50Hz - Vhodni faktor moč ≥ 0,99 pri bremenu ≥50% - Vhodno harmonsko tokovno popačenje: THDi <3% pri 100% bremenu - Izhodna napetost: 3f+N+PE, 400V AC 50Hz - Izhodni faktor moči: 1 - Glasnost pri obratovanju : ≤ 70 dBA pri 100% bremenu - Avtonomija: ≥ 10min pri 100% bremenu (40kW) izhodne moči oz. ≥ 25min pri 50% bremenu (20kW) - Preobremenitvena zmogljivost v normalnem načinu delovanja: 10 minut 125% in 60 sekund 150% - Vgrajeno statično in servisno by-pass stikalo - Vgrajena Backfeed zaščita - Uporabniški vmesnik: LCD prikazovalnik na dotik - Komunikacijski vmesnik: Ethernet (SNMP) in Modbus - Priključki: zbiralke (močnostni priključki), vrstne sponke (krmilni priključki) - Priključitev: single mains - enojni dovodni kabel ali dual mains - ločen dovodni kabel za UPS in by-pass - Dimenzije in teža UPS skupaj z baterijami ne sme presegati: 600 x 2000 x 900 mm (šxvxg), 750kg - Delovna temperatura: 0-40 °C | - On-line double-conversion operating technology - Rated power: 40kVA/40kW, power factor output from 0.7 ind. to 0.7 cap. without reduction of rated apparent power (kVA) - Input voltage: 3f+N+PE, 340-460V AC 50Hz - Power input factor ≥ 0.99 at ≥50% load - Input harmonic current distortion: THDi <3% at 100% load - Output voltage: 3f+N+PE, 400V AC 50Hz - Output power factor: 1 - Operating loudness : ≤ 70 dBA at 100% load - Autonomy: ≥ 10min at 100% load (40kW) output or ≥ 25min at 50% load (20kW) - Overload capacity in normal operation: 10 minutes 125% and 60 seconds 150% - Built-in static and service by-pass switch - Built-in Backfeed Protection - User interface: LCD touchscreen display - Communication interface: Ethernet (SNMP) and Modbus - Connectors: busbars (power connectors), in-line terminals (control connectors) - Connection: single mains - single inlet cable or dual mains - separate inlet cable for UPS and by-pass - Dimensions and weight of the UPS including batteries must not exceed: 600 x 2000 x 900 mm (WxHxD), 750kg - Operating temperature: 0-40 °C
| - Mehanska zaščita: IP20 - UPS sistem mora vsebovati tudi zunanje obhodno stikalo, ki omogoča preklop na omrežno napajanje in fizični odklop UPSa brez prekinitve napajanja porabnikov - MAINTENANCE BYPASS PANE - Montaža in zagon opreme na pripravljene elektrilčne instalacije s strani tehnika certificiranega s strani proizvajalca ponujenega modela - Kot naprimer APC GALAXY VS 40kW N+1 ali enakovredno | - Mechanical protection: IP20 - The UPS system shall also include an external bypass switch to allow switching to mains power and physically disconnecting the UPS without interrupting the power supply to the consumers - MAINTENANCE BYPASS PANE - Installation and commissioning of the equipment on the prepared electrical installations by a technician certified by the manufacturer of the model offered - Such as APC GALAXY VS 40kW N+1 or equivalent |  |  | kpl | 2 |  | 0
2.16 | Dobava razdelilnega sestava za UPS napravo. Priklop na pripravljen otcep iz DEA razdelilnega sestava (3f, 40 kVA). Izdelava delavniških shem UPS razdelilnika, glede na dobavljeno opremo strežniškega prostora. Pred izvedbo pridobiti potrditev o ustreznosti delavniških risb od investitorja, nadzora in projektanta. | Supply of the UPS distribution assembly. Connection to the prepared DEA distribution assembly (3f, 40 kVA). Drawing up of the workshop drawings of the UPS distribution unit, according to the supplied equipment of the server room. Obtain confirmation of the adequacy of the workshop drawings from the investor, the supervisor and the designer before implementation. 3. Electrical installation of the UPS distribution unit. |  |  | kpl | 2 |  | 0
2.17 | Izdelava posnetkov za projekt izvedenih del z vrisom sprememb nastalih med gradnjo v projektno dokumentacijo (PZI načrt) v papirni obliki, ki jih potrdi nadzor po ZGO in predaja teh ostalim izdelovalcem PID načrta, izdelava navodil za obratovanje, navodil za vzdrževanje in periodične preglede | Preparation of the design drawings for the project of the works carried out with the incorporation of the changes made during construction into the project documentation (PZI plan) in paper form, approved by the PGI supervision and handed over to the other PID plan producers, preparation of the operating instructions, maintenance instructions and periodic inspections |  |  | kpl | 1 |  | 0
| UNIVERZALNO OŽIČENJE STREŽNIŠKE SOBE | UNIVERSAL SERVER ROOM WIRING
2.18 | Dobava in polaganje kabla EN-ClassEA (EIA/TIA Cat 6A) 23 AWG S/FTP 4 Pair LSHF/LSZH Cable Orange EuroClass - CPR razred B2ca-s1a-d1-a1 (EN50575) požarne varnosti - Dovoljena sila vleke med montažo >100N (10kg) - Dovoljen radij ukrivljenosti med delovanjem do 4xdiameter kabla - Dovoljena temperatura med delovanjem 0°C do 60°C - Dovoljena PoE obremenitev v skladu z IEEE802.3bt Type4 (90W) - Dovoljen maksimalni diameter kabla zaradi prostora: <7,5 mm - Ustrezno standardom EN 50173-1 and EN 50288-10-1 - Ustrezati mora za Cisco UPoE (60 Watts), Cisco UPoE+ (90 Watts) in Power over HDBaseT™ PoH (95 Watts) kot npr. Leviton/Brand-Rex ali enakovredno | Supply and installation of EN-ClassEA (EIA/TIA Cat 6A) 23 AWG S/FTP 4 Pair LSHF/LSZH Cable Orange EuroClass - CPR class B2ca-s1a-d1-a1 (EN50575) fire safety - Permissible towing force during installation >100N (10kg) - Permissible radius of curvature during operation up to 4x cable diameter - Permissible operating temperature 0°C to 60°C - Allowable PoE load according to IEEE802.3bt Type4 (90W) - Maximum cable diameter allowed due to space: <7.5 mm - Compliant with EN 50173-1 and EN 50288-10-1 - It must be suitable for Cisco UPoE (60 Watts), Cisco UPoE+ (90 Watts) and Power over HDBaseT™ PoH (95 Watts) such as Leviton/Brand-Rex or equivalent |  |  | m | 2500 |  | 0
2.19 | Stikalni panel EN-ClassEA (EIA/TIA Cat 6A) 48p FTP, zaključen, kot npr. Brand-Rex/Leviton ali enakovredno sestavljen iz: a.) Nosilec 19" vgradne višine 2U(2HE) z odprtinami za vgradnjo do max 48 priključnih konektorjev RJ45, možnost barvnega kodiranja in organizatorjem kablov 1kos ter ozemljitvijo - barva ČRNA b.) Zaključni konektor RJ45 tipa FTP EN-ClassEA (EIA/TIA Cat6A) kot npr. Leviton-AtlasX1 48kos s karakteristikami: - barva črna - kovinsko ohišje za preprečevanje PoE pregrevanja - ToolFree zaključevanje - Pozlačeni (min 1μm - mikrometer) bakreni kontakti - Testiran na min 750 vklopov in 20 prevezav - RFT Retention Force Technology - kvalitetna PoE povezava in preprečevanje poškodb pri uporabi različnih konektorjev (RJ11, RJ12, RJ45) - Dovoljena temperatura med delovanjem 0°C do 60°C - Dovoljena PoE obremenitev v skladu z IEEE802.3bt Type4 (90W) | EN-ClassEA (EIA/TIA Cat 6A) 48p FTP switchboard, terminated, such as Brand-Rex/Leviton or equivalent, consisting of: a.) 19" 2U(2HE) mounting height bracket with mounting holes for up to 48 RJ45 connectors, colour coding, 1 piece cable organiser and earthing - colour BLACK b.) RJ45 termination connector of FTP type EN-ClassEA (EIA/TIA Cat6A) such as Leviton-AtlasX1 48 pieces with the characteristics: - colour black - metal housing to prevent PoE overheating - ToolFree termination - Gold-plated (min 1μm - micrometer) copper contacts - Tested for min 750 switch-ons and 20 reconnections - RFT Retention Force Technology - quality PoE connection and damage prevention when using different connectors (RJ11, RJ12, RJ45) - Permissible operating temperature 0°C to 60°C - Allowable PoE load according to IEEE802.3bt Type4 (90W)
| - Maxsimalna obremenitev 100W in 0,5A na vodnik v stalnem delovanju - Možnost menjave čelnih napisnih oznak | - Max load 100W and 0.5A per conductor in continuous operation - Possibility to change the front lettering |  |  | kom | 12 |  | 0
2.20 | 1HE 19" organizer horizontalni - panelni razvod, kot npr. Leviton/Brandrex ali enakovredno | 1HE 19" horizontal organiser - panel distribution, e.g. Leviton/Brandrex or equivalent |  |  | kom | 12 |  | 0
2.21 | Slim priključni kabel U/FTP cat 6A, 10Gigabit, izjemno prožni in tanki, LSOH, 1m, dobavljivi v sedmih različnih barvah, kot npr. Leviton/Brand-Rex ali enakovredno | Slim U/FTP cat 6A, 10Gigabit, extremely flexible and thin, LSOH, 1m, available in seven different colours, e.g. Leviton/Brand-Rex or equivalent |  |  | kom | 100 |  | 0
2.22 | Slim priključni kabel U/FTP cat 6A, 10Gigabit, izjemno prožni in tanki, LSOH, 2m, dobavljivi v sedmih različnih barvah, kot npr. Leviton/Brand-Rex ali enakovredno | Slim U/FTP cat 6A, 10Gigabit, extremely flexible and thin, LSOH, 2m, available in seven different colours, e.g. Leviton/Brand-Rex or equivalent |  |  | kom | 100 |  | 0
2.23 | Slim priključni kabel U/FTP cat 6A, 10Gigabit, izjemno prožni in tanki, LSOH, 3m, dobavljivi v sedmih različnih barvah, kot npr. Leviton/Brand-Rex ali enakovredno | Slim U/FTP cat 6A, 10Gigabit, extremely flexible and thin, LSOH, 3m, available in seven different colours, e.g. Leviton/Brand-Rex or equivalent |  |  | kom | 100 |  | 0
2.24 | Meritve UTP/FTP EN-ClassEA instalacije (poročilo bakrenih meritev za 25-letno sistemsko garancijo proizvajalca) | UTP/FTP EN-ClassEA installation measurements (copper measurement report for 25-year system warranty from the manufacturer) |  |  | kom | 288 |  | 0
2.25 | MTP(ž)/MTP(ž) tovarniško zaključen optični kabel notranji LSZH singlemodni OS2, 12 nitni, dolžine 7m kot npr. Leviton BrandRex ali enakovredno - CPR razred požarne varnosti Cca - Standardna polariteta B (Polarity B, po ANSI/TIA) - Skladno z IEEE 802.3ba (40/100GbE standard) - Skladno z OS2 po ITU-T 652.D in ITU-T 657.A1 - Maksimalno slabljenje pri 1310nm in 1550nm mora biti <0,5dB/km - Proizavajalec mora ponujati kable, ki se barvno razlikujejo glede na tip in število vlaken - Dovoljen maksimalni diameter kabla zaradi prostora: <5 mm - Parameter Insertion Loss mora biti ≤ 0,35dB - Dovoljena temperatura med delovanjem vsaj do 60°C | MTP(f)/MTP(f) factory terminated fibre optic cable indoor LSZH single mode OS2, 12 strands, 7m length as e.g. Leviton BrandRex or equivalent - CPR fire safety class Cca - Standard Polarity B (Polarity B, per ANSI/TIA) - Compliant with IEEE 802.3ba (40/100GbE standard) - OS2 compliant according to ITU-T 652.D and ITU-T 657.A1 - Maximum attenuation at 1310nm and 1550nm shall be <0.5dB/km - The manufacturer shall offer cables which are distinguishable in colour according to the type and number of fibres - Maximum cable diameter allowed due to space: <5 mm - Insertion Loss parameter must be ≤ 0,35dB - Permissible operating temperature at least up to 60°C |  |  | kos | 2 |  | 0
2.26 | MTP(ž)/MTP(ž) tovarniško zaključen optični kabel notranji LSZH singlemodni OS2, 12 nitni, dolžine 10m kot npr. Leviton BrandRex ali enakovredno - CPR razred požarne varnosti Cca - Standardna polariteta B (Polarity B, po ANSI/TIA) - Skladno z IEEE 802.3ba (40/100GbE standard) - Skladno z OS2 po ITU-T 652.D in ITU-T 657.A1 - Maksimalno slabljenje pri 1310nm in 1550nm mora biti <0,5dB/km - Proizavajalec mora ponujati kable, ki se barvno razlikujejo glede na tip in število vlaken - Dovoljen maksimalni diameter kabla zaradi prostora: <5 mm - Parameter Insertion Loss mora biti ≤ 0,35dB - Dovoljena temperatura med delovanjem vsaj do 60°C | MTP(f)/MTP(f) factory terminated fibre optic cable indoor LSZH single mode OS2, 12 strands, 10m length as e.g. Leviton BrandRex or equivalent - CPR fire safety class Cca - Standard Polarity B (Polarity B, per ANSI/TIA) - Compliant with IEEE 802.3ba (40/100GbE standard) - OS2 compliant according to ITU-T 652.D and ITU-T 657.A1 - Maximum attenuation at 1310nm and 1550nm shall be <0.5dB/km - The manufacturer shall offer cables which are distinguishable in colour according to the type and number of fibres - Maximum cable diameter allowed due to space: <5 mm - Insertion Loss parameter must be ≤ 0,35dB - Permissible operating temperature at least up to 60°C |  |  | kos | 2 |  | 0
2.27 | MTP(ž)/MTP(ž) tovarniško zaključen optični kabel notranji LSZH singlemodni OS2, 12 nitni, dolžine 12m kot npr. Leviton BrandRex ali enakovredno - CPR razred požarne varnosti Cca - Standardna polariteta B (Polarity B, po ANSI/TIA) - Skladno z IEEE 802.3ba (40/100GbE standard) - Skladno z OS2 po ITU-T 652.D in ITU-T 657.A1 - Maksimalno slabljenje pri 1310nm in 1550nm mora biti <0,5dB/km - Proizavajalec mora ponujati kable, ki se barvno razlikujejo glede na tip in število vlaken - Dovoljen maksimalni diameter kabla zaradi prostora: <5 mm - Parameter Insertion Loss mora biti ≤ 0,35dB - Dovoljena temperatura med delovanjem vsaj do 60°C | MTP(ž)/MTP(ž) factory terminated fibre optic cable indoor LSZH single mode OS2, 12 strands, 12m length as e.g. Leviton BrandRex or equivalent - CPR fire safety class Cca - Standard Polarity B (Polarity B, per ANSI/TIA) - Compliant with IEEE 802.3ba (40/100GbE standard) - OS2 compliant according to ITU-T 652.D and ITU-T 657.A1 - Maximum attenuation at 1310nm and 1550nm shall be <0.5dB/km - The manufacturer shall offer cables which are distinguishable in colour according to the type and number of fibres - Maximum cable diameter allowed due to space: <5 mm - Insertion Loss parameter must be ≤ 0,35dB - Permissible operating temperature at least up to 60°C |  |  | kos | 2 |  | 0
2.28 | Optični modularni delilnik visoke gostote za brezvijačno namesitev optičnih in bakrenih modulov ali kaset, skupne kapacitete najmanj 96 optičnih vlaken na 1U višine komplet z organizatorjem optičnih kablov na zadnji strani in setom za označevanje spredaj, kot npr. Leviton/Brand-Rex ali enakovredno, ki ustreza najmanj sledečim zahtevam: - Panel omogoča namestitev bakrenih oklopljenih in neoklopljenih ter optičih modulov ali kaset - Namestitev ali odstranitev modulov/kaset brez orodja - Organizator na zadnji strani panela za pritrditev kablov - Proizvajalec mora omogočati namestitev BLANK panelov na mesta, kjer trenutno ni modulov/kaset - Numeracija portov | High-density modular optical splitter for screwless mounting of optical and copper modules or cassettes, with a total capacity of at least 96 optical fibres per 1U height, complete with optical cable organiser at the rear and a front marking set such as Leviton/Brand-Rex or equivalent, meeting at least the following requirements: - The panel allows the installation of copper shielded and unshielded and fibre optic modules or cassettes - Installing or removing modules/cassettes without tools - Organiser on the back of the panel for attaching cables - The manufacturer must allow BLANK panels to be installed in locations where there are currently no modules/cassettes - Port numbering |  |  | kos | 7 |  | 0
2.29 | Blank modul/kastea za modularni optični panel (pokrije mesto, ki ga sicer zasede 1 modul/kaseta za 12 optičnih vlaken) | Blank module/box for modular fibre optic panel (covers the space otherwise occupied by 1 12-fibre module/box) |  |  | kom | 2 |  | 0
2.30 | Optični modul/kaseta za priklop 12 SingleMode optičnih vlaken, za namestitev v modularni optični panel. Modul/kaseta mora imeti zadaj moški priključek MTP za priklop tovarniško zaključenih Singlemode OS2 optičnih kablov, spredaj pa LC duplex konektorje, kot npr. Leviton/Brand-Rex ali enakovredno in ustrezati najmanj sledečim zahtevam: - Namestitev ali odstranitev modulov/kaset brez orodja - Modul/kaseta mora biti tovarniška zaključena med Singlemode OS2 MTP in LC duplex konektorji - LC konekterji morajo biti opremljeni z vratci, ki zagotavljajo IP5x zaščito in so skladna z IEC60529 - SingleMode modul/kaseta mora zagotavljati optični Insertion Loss ≤ 0,5dB - Modul/kaseta mora zagotavljati univerzalno polariteto (Universal Polarity) in pri uporabi MTP-MTP kabla s polaritetoB omogočati uporabo enakih modulov/kaset in enakih standardnih A-B optičnih priključnih kablov na obeh straneh - Dovoljena temperatura med delovanjem vsaj do 60°C | Optical module/cassette for the connection of 12 SingleMode optical fibres, for installation in a modular optical panel. The module/cassette shall have an MTP male connector at the rear for the connection of factory terminated Singlemode OS2 fibre optic cables, and LC duplex connectors at the front, such as Leviton/Brand-Rex or equivalent, and shall meet at least the following requirements: - Installing or removing modules/cassettes without tools - The module/cassette must be factory terminated between Singlemode OS2 MTP and LC duplex connectors - LC connectors shall be fitted with gates providing IP5x protection and complying with IEC60529 - SingleMode module/cassette shall provide optical Insertion Loss ≤ 0,5dB - The module/cassette shall provide Universal Polarity and, when using MTP-MTP cable with polarity B, shall allow the use of identical modules/cassettes and identical standard A-B fibre optic connection cables on both sides - Permissible operating temperature at least up to 60°C |  |  | kom | 12 |  | 0
2.31 | Priključni kabel FO 4xLC 2m OS2 SM, kot npr. Leviton/Brand-Rex | Connection cable FO 4xLC 2m OS2 SM, e.g. Leviton/Brand-Rex |  |  | kom | 20 |  | 0
2.32 | Priključni kabel FO 4xLC 3m OS2 SM, kot npr. Leviton/Brand-Rex | Connection cable FO 4xLC 3m OS2 SM, e.g. Leviton/Brand-Rex |  |  | kom | 20 |  | 0
2.33 | Meritev optičnega vlakna | Optical fibre measurement |  |  | kom | 72 |  | 0
2.34 | Označevanje vseh elementov z trajnimi nalepkami | Marking of all elements with permanent labels |  |  | kpl | 1 |  | 0
2.35 | Izdelava posnetkov za projekt izvedenih del z vrisom sprememb nastalih med gradnjo v projektno dokumentacijo (PZI načrt) v papirni obliki, ki jih potrdi nadzor po ZGO in predaja teh ostalim izdelovalcem PID načrta | Preparation of the design drawings for the works in progress with the incorporation of the changes made during construction into the project documentation (PZI plan) in paper form, approved by the PGI supervision and handing over to the other PID plan producers |  |  | kpl | 1 |  | 0
2.36 | Priprava, oddaja dokumentacije in pridobitev sistemske garancije proizvajalca minimalno 25 let na kompletno podatkovno ožičenje podatkovnega centra. Vgradnja opreme mora biti izvedena s strani pooblaščenega izvajalca | Preparation, submission of documentation and obtaining of a system warranty from the manufacturer for a minimum of 25 years for the complete data centre cabling. Installation of the equipment must be carried out by an authorised contractor |  |  | kpl | 1 |  | 0
| STROJNE INSTALACIJE ZA STREŽNIŠKO SOBO | MECHANICAL INSTALLATIONS FOR THE SERVER ROOM
2.37 | INROW hladilne enote Vodno hlajen hladilni modul za namestitev v vrsto strežniških/ komunikacijskih omar za precizno hlajenje opreme v podatkovnem centru (InRow) z naslednjimi karakteristikami in gradniki: • temperaturni režim hladilne vode 9/14°C • zajem zraka po celotni višini hladilne enote s strani tople cone, ki se preko hladilnih registrov ter ventilatorjev vpihuje v področje hladne cone • dovod hladilnega medija mora biti omogočen iz spodnje ali zgornje strani enote • vgrajen tropotni regulacijski ventil z elektro motornim pogonom za regulacijo pretoka • InRow enota mora zagotavljati možnost prehoda izbire delovanja ventilov med dvo- ali tripotnim načinom pretoka hladilnega medija in možnost prehoda med enim in drugim režimom med obratovanjem enote. • zaporni ventil na dovodu • vgrajen mikroprocesorski krmilnik • merilnik pretoka vode • pralni filter za zajem zraka • aksialni ventilatorji po celi višini naprave, z zvezno krmiljeno regulacijo vrtljajev • vroča zamenjava okvarjenega ventilatorja med delovanjem (hot-swap) • hladilni registri iz Cu cevi z Al lamelam • temperaturni senzorji za meritev temperature vstopnega in izstopnega zraka ter v sosednji rack omari (vsaj 3 senzorji) • temperaturni senzorji za meritev temperature hladilnega medija na dovodu in povratku • senzor za prisotnost vode, ki se napelje pod rack omarami | INROW refrigeration units Water-cooled cooling module for installation in a range of server/communication cabinets for precision cooling of equipment in the data centre (InRow) with the following characteristics and building blocks: - cooling water temperature 9/14°C - air is drawn in from the warm zone over the entire height of the cooling unit, and is blown into the cold zone area via cooling registers and fans - the cooling medium must be supplied from either the bottom or the top of the unit - built-in tropical control valve with electric motor drive for flow control - The InRow unit shall provide the capability to switch the selection of valve operation between two-way or three-way refrigerant flow modes and the capability to switch between one and the other during operation of the unit. - inlet stop valve - built-in microprocessor controller - Water flow meter - Washing filter for air intake - axial fans throughout the entire height of the unit, with continuously variable speed control - hot-swap replacement of a faulty fan during operation - cooling registers made of Cu tubes with Al lamellae - Temperature sensors to measure the temperature of the inlet and outlet air and in the adjacent rack cabinet (at least 3 sensors) - Temperature sensors for measuring the temperature of the cooling medium at the inlet and return - water sensor to be installed under rack cabinets
| • meritev in prikaz trenutne hladilne moči v kW • prikaz vseh meritev in parametrov na lokalni konzoli • regulacija vrtljajev ventilatorjev in tropotnega regulacijskega ventila hladilnega modula naj bo odvisna od temperature vode in zraka. Ključni parameter naj bo temperatura zraka izmerjena s senzorjem hladilne enote, ki se namesti v sosednjo rack omaro in daje podatek o dejanski temperaturi zraka na vhodu v opremo. • posoda za kondenzat s črpalko za odvod kondenzata. Krmiljenje črpalke za kondenzat z alarmiranjem izpada. • dvojno A+B napajanje (dva redundančna napajalnika) preko strehe InRow enot • priključek za nadzor preko Ethernet omrežja (WEB in SNMP nadzor) in integracija v centralni nadzorni sistem infrastrukture podatkovnega centra DCIM, enota mora omogočati tudi Modbus povezljivost • Beleženje meritev iz vseh senzorjev in hranjenje v log datotekah • možnost enostavne izgradnje zaprte tople cone, med dvema vrstama omar in hladilnih modulov (Hot Air Containment System) • integrirana možnost za povezavo in delovanje hladilnih modulov v skupine z medsebojno izmenjavo izmerjenih vrednosti temperatur in obratovalnih stanj z namenom skupinskega hlajenja z usklajeno regulacijo hladilne moči za celotno skupino. Enote morajo omogočati povezovanje v skupino vsaj 4 enot. • LCD barvni na dotik občutljivi ekran za spremljanje parametrov in alarmov | - measurement and display of the current cooling power in kW - display of all measurements and parameters on the local console - The speed control of the fans and the tropical control valve of the cooling module should be dependent on the water and air temperature. The key parameter should be the air temperature measured by a sensor of the cooling unit, which shall be installed in an adjacent rack cabinet and give an indication of the actual air temperature at the equipment inlet. - Condensate tank with condensate drainage pump. Control of the condensate pump with failure alarm. - Dual A+B power supply (two redundant power supplies) via the roof of the InRow units - connection for control via Ethernet (WEB and SNMP control) and integration into the central control system of the DCIM data centre infrastructure, the unit must also be Modbus-enabled - Logging of measurements from all sensors and storage in log files - the possibility to easily build a closed warm zone between two types of cabinets and cooling modules (Hot Air Containment System) - integrated capability to connect and operate cooling modules in groups by exchanging measured temperature values and operating states with each other for the purpose of group cooling with coordinated cooling power control for the whole group. Units shall be capable of grouping at least 4 units. - LCD colour touch-sensitive display for monitoring parameters and alarms
| • Možnost prilagodljive izvedba dveh prekatov kabelskih poti na strehi InRow enote, za namestitev šibkotočnih in jakotočnih kablov (tovarniška izvedba, s posebnimi pregradami nameščenimi na streho enote z možnostjo kasnejšega spreminjanja širine posameznega prekata). Izvedba prekatov mora omogočati prehod kablov iz enega prekata v drugega v višini poteka kablov (skozi prekat). | - Flexible design of two cable pathway compartments on the roof of the InRow unit, for the installation of low-voltage and jackup cables (factory design, with special barriers installed on the roof of the unit, with the possibility to change the width of each compartment at a later stage). The design of the compartments shall allow the passage of cables from one compartment to another at the height of the cable run (through the compartment).
| MINIMALNE ZAHTEVE TEHNIČNIH KARAKTERISTIK Vhodni parametri za izračun hladilne moči in ostalih zahtevanih parametrov delovanja: - temperatura povratnega zraka iz tople cone Tpovr.zr. ≤ 33°C, - računska relativna vlažnost = 30%, - vstopna temperatura hladilnega medija (voda) 9°C, - izstopna temperatura hladilnega medija (voda) 14°C, - pretok zraka skozi Inrow enoto ≤ 5500 m^3/h - nadmorska višina = 300m. Zahtevana hladilna moč in ostali parametri delovanja (k ponudbi priložiti izračun proizvajalca, ki dokazuje doseganje spodaj navedenih minimalnih zahtev glede na zgoraj navedene vhodne pogoje obratovanja): - Neto senzibilna hladilna moč Qhl.net.senz ≥ 20 kW - SHR (Sensible Heat Ratio) ≥ 90% - Poraba električne energije InRow enote < 1kW - Temperatura izpihanega zraka ≤ 21°C - Pretok hladilnega medija (voda) skozi Inrow enoto < 1,2 l/s - Padec tlaka hladilnega medij (voda) na InRow enoti < 60 kPa | MINIMUM REQUIREMENTS FOR TECHNICAL CHARACTERISTICS Input parameters for calculating cooling power and other required operating parameters: - temperature of the return air from the warm zone Tpovr.zr. ≤ 33°C, - calculated relative humidity = 30%, - inlet temperature of the cooling medium (water) 9°C, - outlet temperature of the cooling medium (water) 14°C, - air flow through the Inrow unit ≤ 5500 m^3/h - altitude = 300m. Required cooling power and other operating parameters (manufacturer's calculation to be attached to the tender, demonstrating that the minimum requirements below are met given the above input operating conditions): - Net sensible cooling power Qhl.net.senz ≥ 20 kW - SHR (Sensible Heat Ratio) ≥ 90% - InRow unit power consumption < 1kW - Exhaust air temperature ≤ 21°C - Coolant flow (water) through the Inrow unit < 1.2 l/s - Coolant pressure drop (water) at InRow unit < 60 kPa
| Ponudnik mora k ponudbi priložiti simulacijo delovnja sistema hlajenja, ki ob upoštevanju zgoraj definiranih vhodnih parametrov dokazuje doseganje zahtevane skupne hladilne moči za tlorisno postavitev strežniške sobe vsaj 40kW in zadostne količine ohlajenega zraka za vse rack omare in sicer pri obremenitvi 2kW za komunikacijsko omaro in 5kW za FS in LAB strežniške omare in 9kW za HPC strežniški omari. Simulacija mora upoštevati zahtevane pretoke zraka za vsako rack omaro in sicer 350m3/h za komunikacijsko omaro, 850m3/h za FS in LAB strežniške omare in 1500m3/h za HPC strežniški omari (skupaj za vrsto 6.750m3/h). Simulacija mora dokazati, da pri odpovedi ene od treh InRow enot, sistem hlajenja še vedno zagotavlja zadostne pretoke zraka vsem rack omaram in da je hladilna moč InRow enote ≥ 20kW. | Ponudnik mora k ponudbi priložiti simulacijo delovnja sistema hlajenja, ki ob upoštevanju zgoraj definiranih vhodnih parametrov dokazuje doseganje zahtevane skupne hladilne moči za tlorisno postavitev strežniške sobe vsaj 40kW in zadostne količine ohlajenega zraka za vse rack omare in sicer pri obremenitvi 2kW za komunikacijsko omaro in 5kW za FS in LAB strežniške omare in 9kW za HPC strežniški omari. Simulacija mora upoštevati zahtevane pretoke zraka za vsako rack omaro in sicer 350m3/h za komunikacijsko omaro, 850m3/h za FS in LAB strežniške omare in 1500m3/h za HPC strežniški omari (skupaj za vrsto 6.750m3/h). Simulacija mora dokazati, da pri odpovedi ene od treh InRow enot, sistem hlajenja še vedno zagotavlja zadostne pretoke zraka vsem rack omaram in da je hladilna moč InRow enote ≥ 20kW.
| - Širina enote do 300mm, višina enote ne sme presegati 2000mm in mora biti enaka višini ponujenih strežniških in komunikacijskih omar - Globina enote mora biti enaka globini ponujenih strežniških in komunikacijskih omar. Zadnja stranica InRow enote mora biti poravnana z zadnjimi vrati strežniških in komunikacijskih omar (na strani tople cone). Priklop in zagon InRow enote mora biti izveden s strani izvajalca, ki je za to pooblaščen s strani proizvajalca ponujenih naprav. Dobavljeno z vsem tesnilnim in montažnim materialom, ožičenjem, zagonom, navodili za uporabo ter poučevanjem osebja. Kot naprimer APC tip ACRC 301S ali enakovredno | - Unit width up to 300mm, unit height must not exceed 2000mm and must be the same height as the server and communication cabinets offered - The depth of the unit shall be the same as the depth of the server and communication cabinets offered. The rear side of the InRow unit shall be aligned with the rear door of the server and communication cabinets (on the warm zone side). Connection and commissioning of the InRow unit must be carried out by a contractor authorised by the manufacturer of the equipment offered. Supplied with all sealing and installation materials, wiring, commissioning, operating instructions and staff training. Such as APC type ACRC 301S or equivalent |  |  | kpl | 3 |  | 0
2.38 | Izvedba kabelskega korita na strehi INROW notranje enote, širine 300mm, za namestitev jakotočnih kablov. Kabelske poti se izvede s posebnimi tovarniško izdelanimi pregradami brezvijačno nameščenimi na streho omar. Širina kabelske poti mora biti vsaj 300mm. Izvedba kabelskega korita mora omogočati galvansko ločeni prehod šibkotočnih kablov pod kabelskim koritom na sosednjo vrsto rack (korito v obliki črke H s prehodom v spodnjem prekatu). | The construction of a cable tray on the roof of the INROW indoor unit, 300mm wide, for the installation of jackup cables. Cable pathways shall be provided by special factory-made bulkheads screwlessly mounted on the roof of the enclosures. The width of the cable pathway shall be at least 300mm. The construction of the cable tray shall allow galvanically isolated passage of the low-current cables under the tray to the adjacent row of racks (H-shaped tray with a passageway in the lower compartment). |  |  | kos | 3 |  | 0
2.39 | Izvedba dveh prekatov kabelskih poti na strehi INROW notranje enote, širine 300mm, za namestitev šibkotočnih kablov. Kabelske poti se izvede s posebnimi tovarniško izdelanimi pregradami brezvijačno nameščenimi na streho omar z možnostjo spreminjanja širine posameznega prekata. Izvedba prekatov mora omogočati prehod kablov iz enega prekata v drugega v višini poteka kablov (skozi prekat). | The construction of two 300mm wide cable pathways on the roof of the INROW indoor unit for the installation of low current cables. The cable pathways shall be constructed with special factory made bulkheads screwlessly mounted on the roof of the cabinets with the possibility to change the width of each lane. The design of the laneways shall allow the passage of cables from one lane to the other within the cable passage height (through the laneway).The cable pathways shall be constructed with special factory made bulkheads. |  |  | kpl | 3 |  | 0
2.40 | Predizolirani fleksibilni priključki, ojačani z jekleno pletenico, namenjeni za vezavo in-row naprav, z navojnimi priključki ter tesnilnim materialom, povprečne dolžine 200 cm DN 50, PN 6 | Pre-insulated flexible connectors, reinforced with steel braid, for the connection of in-growth devices, with threaded connections and sealing material, average length 200 cm DN 50, PN 6 |  |  | kos | 6 |  | 0
2.41 | Toplotna izolacija razvoda hladilne vode z izolacijskimi cevaki oziroma izolacijskim ploščami (za cevi od DN200) iz sintetičnega kavčuka z zaprto celično strukturo. Cevna izolacija izpolnjuje pogoje za preprečevanje toplotnih izgub, korozije, rosenja in kondenzacije, prenosa hrupa na gradbeno konstrukcijo, elastična in odporna od -50°C do +105 °C, z visoko odpornostjo proti prehodu vodne pare (η>10.000) skladno z EN 12086 in EN 13469 in nizko toplotno prevodnostjo (λd(0°C)=0,036 W/mK) skladno z EN 8497, skupaj z lepilom ter obdelavo fazonskih kosov ter armatur debeline 19mm | Thermal insulation of cooling water distribution pipes with insulation tubes or insulation boards (for pipes from DN200) made of synthetic rubber with a closed cell structure. The pipe insulation meets the conditions for preventing heat loss, corrosion, rusting and condensation, noise transmission to the building structure, elastic and resistant from -50°C to +105°C, with high resistance to water vapour transmission (η>10,000) according to EN 12086 and EN 13469 and low thermal conductivity (λd(0°C)=0.036 W/mK) according to EN 8497, including adhesive, and the treatment of the chamfer pieces and the fittings thickness 19mm
| f 60,3 x 3,65 mm (DN 50) | f 60.3 x 3.65 mm (DN 50) |  |  | m | 30 |  | 0
| f 76,1 x 3,20 mm (DN 65) | f 76.1 x 3.20 mm (DN 65) |  |  | m | 30 |  | 0
2.42 | Hidravlično uravnovešanje sistema hladilne vode - nastavitve pretokov v strojnici | Hydraulic balancing of the cooling water system - engine room flow settings |  |  | kpl | 1 |  | 0
2.43 | Testiranje in zagon InRow sistema - nastavitev parametrov delovanja - poizkusni zagon in 24 urni nadzor delovanja - poučevanje uporabnika | Testing and commissioning the InRow system - setting the operating parameters - trial start-up and 24-hour operation monitoring - teaching the user |  |  | kpl | 3 |  | 0
2.44 | Dobava in izvedba vsega potrebnega ožičenja za LMI InRow enote in senzorskega sistema za povezavo na centralni nadzorni sistem. | Supply and installation of all necessary wiring for the LMI InRow units and the sensor system for connection to the central control system. |  |  | kpl | 3 |  | 0
2.45 | Vzpostavitev LMI nadzora, v skladu s tehničnimi specifikacijami, ki omogoča nadzor nad nameščenimi InRow enotami. Za spremljanje okolijskih parametrov in delovanja hlajenja računalniškega prostora je predviden nadzorni sistem, ki bo spremljal, arhiviral okolijske podatke računalniškega prostora, ter po potrebi alarmiral preko SNMP sporočil in elektronske pošte. Za vsako InRow enoto je potrebno omogočiti: • Monitoring temperature in izliva vode • Spremljanje temperature na vhodu hladnega zraka v sosednjo strežniško omaro • Spremljanje izliva vode linijsko • Komunikacija z nadzornim sistemom mora biti možna preko HTTP protokola in SNMP sporočil, kot tudi preko elektronske pošte • Zagotovljeno on-line spremljanje stanja parametrov preko WEB vmesnika • Nadzorni sistem mora omogočati vnos mejnih vrednosti in samodejno alarmiranje v primeru prekoračitve nastavljenih vrednosti • Nadzorni sistem je lahko skupen z nadzornim sistemom strežniške sobe. | Establishment of LMI control, in accordance with the technical specifications, allowing control of the installed InRow units. To monitor the environmental parameters and cooling performance of the computer room, a monitoring system is planned to monitor, archive the environmental data of the computer room and, if necessary, alarm via SNMP messages and e-mail. For each InRow unit it is necessary to enable: - Monitoring water temperature and outflow - Monitoring the temperature at the cold air inlet to the adjacent server cabinet - Monitoring water outflow line by line - Communication with the control system must be possible via HTTP protocol and SNMP messages, as well as via e-mail - On-line monitoring of parameters via WEB interface - The monitoring system must be able to input limit values and automatically alarm in the event of set values being exceeded - The control system may be shared with the server room control system. |  |  | kpl | 1 |  | 0
2.46 | Izdelava posnetkov za projekt izvedenih del z vrisom sprememb nastalih med gradnjo v projektno dokumentacijo (PZI načrt) v papirni obliki, ki jih potrdi nadzor po ZGO in predaja teh ostalim izdelovalcem PID načrta, izdelava navodil za obratovanje, navodil za vzdrževanje in periodične preglede | Preparation of the design drawings for the project of the works carried out with the incorporation of the changes made during construction into the project documentation (PZI plan) in paper form, approved by the PGI supervision and handed over to the other PID plan producers, preparation of the operating instructions, maintenance instructions and periodic inspections |  |  | kpl | 1 |  | 0
| CENTRALNO NADZORNI SISTEM (CNS) STREŽNIŠKE SOBE | CENTRAL CONTROL SYSTEM (CNS) SERVER ROOM
2.47 | Dobava in namestitev v rack omaro temperaturnega senzorja s priključnim kablom s priklopom na posebno napravo za merjenje okoljskih parametrov, konfiguracija, parametriranje, komplet s priključnimi kabli | Supply and installation in a rack cabinet of a temperature sensor with connection cable to a special device for measuring environmental parameters, configuration, parameterisation, complete with connection cables |  |  | kos | 6 |  | 0
2.48 | Dobava in namestitev v rack omaro kombiniranega temperaturnega senzorja in senzorja relativne vlažnosti, priklop na posebno napravo za merjenje okoljskih parametrov, konfiguracija, parametriranje, komplet s priključnimi kabli | Supply and installation in a rack cabinet of a combined temperature and relative humidity sensor, connection to a special device for measuring environmental parameters, configuration, parameterisation, complete with connection cables |  |  | kos | 1 |  | 0
2.49 | Dobava in namestitev senzorja za izliv vode s priključnim kablom s priklopom na posebno napravo za merjenje okoljskih parametrov, konfiguracija, parametriranje, komplet s priključnimi kabli | Supply and installation of a water outflow sensor with connection cable to a special device for measuring environmental parameters, configuration, parameterisation, complete with connection cables |  |  | kos | 3 |  | 0
2.50 | Dobava in namestitev v rack omaro naprave za spremljanje okoljskih parametrov, konfiguracija, parametriranje. Priklop vsaj za 6 senzorjev. Razžiritev z dodatnimi moduli za priklop dodatnih senzorjev. Initegriran nadzor preko SNMP in MODBUS protokola. Kot na primer APC NetBotz Rack Monitor 250 ali enakovredno | Supply and installation in rack cabinet of device for monitoring environmental parameters, configuration, parameterisation. Connection for at least 6 sensors. Expansion with additional modules for connecting additional sensors. Initegrated control via SNMP and MODBUS protocol. Such as APC NetBotz Rack Monitor 250 or equivalent |  |  | kos | 1 |  | 0
2.51 | Dobava in namestitev v rack omaro razširitvenega modula za priklop dodatnih senzorjev na napravo za spremljanje okoljskih parametrov, konfiguracija, parametriranje. Priklop vsaj za 6 senzorjev, komplet z ožičenjem UTP. Kot na primer APC NetBotz Rack Senzor Pod 150 ali enakovredno | Supply and installation in a rack cabinet of an expansion module for connecting additional sensors to the device for monitoring environmental parameters, configuration, parameterisation. Connection for at least 6 sensors, complete with UTP wiring. Such as APC NetBotz Rack Sensor Pod 150 or equivalent |  |  | kos | 1 |  | 0
2.52 | Dobava in namestitev programske opreme za centralni nadzorni strežnik podatkovnega centra z minimalnao specifikacijo: - Nadzorna programska oprema mora zagotavljati nadzor vsaj nad SNMP in MODBUS nadzorljivimi napravami. - Zagotovljen mora biti nadzor nad sistemom InRow hlajenja podatkovnega centra, UPS napravami, napajalnimi letvami v rack omarah, okolijskimi senzorji, ATS stikali, itd. - Nadzorni strežnik mora zagotavljatu nadzor tudi nad SNMP in MODBUS napravami drugih proizvajalcev kot so ponujene. - Nadzorni strežnik mora omogočati nadzor nad vsaj 25 napravami ter omogočati nadaljno nadgradnjo števila naprav. - Ponujeni sistem DCIM mora biti standardna komponenta, v redni proizvodnji pri proizvajalcu in ne narejen po naročilu samo za predmetni projekt - Komunikacija z nadzornim sistemom mora biti omogočena preko HTTP in SNMP protokola, kot tudi preko elektronske pošte. - Zagotovljeno mora biti on-line spremljanje stanja parametrov preko WEB vmesnika. Nadzorni sistem mora omogočati vnos mejnih vrednosti in samodejno alarmiranje v primeru prekoračitve nastavljenih vrednosti. - Nadzorovani parametri in alarmi prekoračitve nastavljenih mejnih vrednosti se morajo beležiti tudi v »oblaku« in mora biti zagotovljen dostop do podatkov preko mobilne aplikacije (OS Android in iOS) - tudi v primeru izpada podatkovne povezave do podatkovnega centra. | Supply and installation of software for a central control server for the data centre with a minimum specification: - The control software shall provide control of at least SNMP and MODBUS controllable devices. - Control of the InRow data centre cooling system, UPS devices, rack power strips, environmental sensors, ATS switches, etc. must be ensured. - The control server shall also provide control of SNMP and MODBUS devices from other manufacturers than those offered. - The control server must be able to control at least 25 devices and be able to further upgrade the number of devices. - The DCIM system offered must be a standard component, in regular production by the manufacturer, and not custom-made for the project in question only - Communication with the control system must be enabled via HTTP and SNMP protocols, as well as via email. - On-line monitoring of the status of the parameters via a WEB interface shall be provided. The monitoring system shall allow the input of limit values and automatic alarming in the event of set values being exceeded. - Monitored parameters and alarms of exceeding set limits must also be recorded in the cloud and data must be accessible via a mobile app (Android and iOS) - even in the event of a data connection failure to the data centre.
| - Namestitev nadzorne programske opreme na strežnik, ki ga zagotovi investitor - Konfiguracija DCIM in parametriranje, izdelava WEB dashboard prikazov za sistem napajanja, hlajenja, UPS. - 5 let podpore s strani proizvajalca z vključenimi brezplačnimi nadgradnjimi z novimi verzijami programske opreme Kot naprimer tip APC EcostruxureIT s 25 licencami in 5 leti podopore ali enakovredno | - Installation of the control software on a server provided by the investor - DCIM configuration and parameterisation, creation of WEB dashboard displays for power, cooling, UPS systems. - 5 years of manufacturer support including free upgrades with new software versions Such as the APC EcostruxureIT type with 25 licences and 5 years of support or equivalent |  |  | kpl | 1 |  | 0
2.53 | Izvedba podatkovnih povezav do vseh nadzorovanih naprav. S/FTP povezave zaključiti na priključnem panelu, poleg panela namestiti Ethernet omrežna stikala (zagotovi investitor) in izvesti povezave med panelom, omrežnim stikalom in nadzornim strežnikom. Na strani nadzorovanih naprav podatkovne kable zaključiti na RJ45 konektorju in ustrezno označiti (ploščica ali obstojna nalepka) ter opraviti meritev | Make data connections to all monitored devices. Terminate S/FTP connections at the connection panel, install Ethernet network switches (provided by the investor) next to the panel and make connections between the panel, network switch and control server. Terminate data cables at the RJ45 connector on the side of the monitored devices and label them accordingly (plaque or durable label) and make measurements |  |  | kpl | 1 |  | 0
2.54 | Programiranje, nastavitev senzorjev in ostale periferne opreme, priprava alarmnih stanj in povezovanje na CNS sistem. Zagon in testiranje delovanja | Programming, setting of sensors and other peripheral equipment, preparation of alarm conditions and connection to the CNS system. Commissioning and operational testing |  |  | kpl | 1 |  | 0
2.55 | Šolanje uporabnikov | User training |  |  | kpl | 1 |  | 0
2.56 | Izdelava posnetkov za projekt izvedenih del z vrisom sprememb nastalih med gradnjo v projektno dokumentacijo (PZI načrt) v papirni obliki, ki jih potrdi nadzor po ZGO in predaja teh ostalim izdelovalcem PID načrta, izdelava navodil za obratovanje, navodil za vzdrževanje in periodične preglede | Preparation of the design drawings for the project of the works carried out with the incorporation of the changes made during construction into the project documentation (PZI plan) in paper form, approved by the PGI supervision and handed over to the other PID plan producers, preparation of the operating instructions, maintenance instructions and periodic inspections |  |  | kpl | 1 |  | 0
| STREŽNIŠKI PROSTOR | SERVER ROOM | [5 empty] | 0

## 3.8.3_Ostalo
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.8 | ELEKTRO DELA | ELECTRICAL WORKS
3.8.3 | OSTALO | OTHER |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
3 | OSTALO | OTHER
3.1 | Navodila za obratovanje in vzdrževanje. Izdelana natančna obratovalna navodila glede posameznih stikalnih manipulacij in komunikacij za zagotavljanje rezervnega napajanja in ponovne vzpostavitve normalnega napajanja. | Operating and maintenance instructions. Detailed operating instructions on individual switching manipulations and communications to ensure back-up power and restoration of normal power supply. | kpl | 1 |  | 0
3.2 | Pozitivne ocene, atesti, certifikati in potrdila ustreznih inštitucij za dokazovanje primerne kakovosti vgrajenih naprav, napeljav, materialov in montažnih del (EIMV, IVD, ZAG, SIQ in podobno). | Positive evaluations, attestations, certificates and attestations of the relevant institutions to prove the adequate quality of the installed devices, installations, materials and assembly works (EIMV, IVD, ZAG, SIQ, etc.). | kpl | 1 |  | 0
| OSTALO | OTHER |  |  |  | 0