## 0_Naslovnica
OPOZORILO! Vsi prevodi v angleščino so strojno izdelani in zgolj informativne narave. V primeru kakršnekoli nejasnosti ali dvoma izključno velja izvirno besedilo v slovenščini. WARNING! All translations into English have been produced by machine translation and are provided for informational purposes only. In the event of any ambiguity or uncertainty, the original Slovenian text shall prevail exclusively.
| / | / | [5 empty] | /
| Sprem./Rev.: | Opis spremembe/Description of Changes: | [5 empty] | Datum/Date: | Podpis/Signature:
| Investitor/Investor: |  |  |  |  | Gradnja/Facility
|  |  | Univerza v Ljubljani Kongresni trg 12 1000 Ljubljana, Slovenija |  |  | Fakulteta za strojništvo/Faculty of Mechanical Engineering
| Projektant/Design Engineer: |  |  |  |  | Del objekta/sistem/Building/System:
|  |  | IBE, svetovanje, projektiranje in inženiring Ljubljana, Slovenija |  |  | STAVBA FAKULTETE/FACULTY BUILDING
| Projektant/Design Engineer: |  |  |  |  | Vrsta načrta/Documentation:
3 NAČRT S PODROČJA ELEKTROTEHNIKE/ DOC. IN THE FIELD OF ELECTRICAL ENGINEERING
|  | Ime in priimek/Name and Surname: |  |  | Id. št./Id. No: | Vsebina risbe (dokumenta)/Document Title:
| Vodja proj./ Des. Manager: | Boštjan Vuga, univ. dipl. inž. arh., grad. dip. (AA) |  |  | ZAPS 0035 PA PPN | PR. POPIS ELEKTRO DEL/BOQ OF ELEC. WORKS 3/9 Akt. sist. protipož. zaščite in javlj. plinov/ Active Fire Prot. Systems and Gas Detection
| Poobl. strok./ Cert. Profess.: | Robert Bobovnik, dipl.inž.el. |  |  | IZS E-2380
| Poobl. strok./ Cert. Profess.: |  |  |  |  | Št. proj./ Proj. No.: | 362-19 |  | Vrsta dokument./ Document. Type: | DZR
| Izdelal/ Creator: | Enis Rokša, mag.inž.el. |  |  |  | Klas. ozn./ Class. No.: | -- |  | Stran/ Page: | 1/*
| Datum/ Date: | maj/May 2026 |  | Merilo/ Scale: | / | Ident. ozn./ Id. No: | JULFS--6E9402P

## 0_Osebe
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
POOBLAŠČENI STROKOVNJAKI, ODGOVORNI ZA IZDELAVO PROJEKTANTSKEGA POPISA:
Id. št. ZAPS/IZS | Pooblaščeni strokovnjak | Strokovno področje
IZS E-2380 | Robert Bobovnik, dipl.inž.el. | Aktivni sistemi protipožarne zaščite
SODELAVCI PRI IZDELAVI PROJEKTANTSKEGA POPISA:
/ | Robert Stavar, el. energ. | Aktivni sistemi protipožarne zaščite
CERTIFIED EXPERTS RESPONSIBLE FOR ELABORATING THE BILL OF QUANTITIES:
Id. No ZAPS/IZS | Certified Expert | Area of Expertise
IZS E-2380 | Robert Bobovnik, dipl.inž.el. | Active fire protection systems
COLABORATORS IN THE ELABORATING THE BILL OF QUANTITIES:
/ | Robert Stavar, el. energ. | Active fire protection systems

## 0.1_Uvod-STP
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
0.1 | SPLOŠNI TEHNIČNI POGOJI | GENERAL TECHNICAL CONDITIONS
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic operator with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
0.1.1 | Izvajalec se obveže, da bo upošteval veljavno zakonodajo, ki ureja graditev objektov v Republiki Sloveniji, vključno s povezanimi podzakonskimi akti, predpisi, tehničnimi smernicami, standardi, pravili stroke in dobro gradbeno prakso. Prav tako mora izvajalec upoštevati vse zahteve izdanega integralnega gradbenega dovoljenja in vsa dela izvesti skladno s projektno dokumentacijo ter ostalimi pogoji, objavljenimi v razpisni dokumentaciji. | The Contractor undertakes to comply with the applicable legislation governing the construction of buildings in the Republic of Slovenia, including related by-laws, regulations, technical guidelines, standards, professional rules and good construction practice. The Contractor shall also comply with all the requirements of the integral building permit issued and shall carry out all works in accordance with the project documentation and other conditions published in the tender documentation.
0.1.2 | Dela lahko izvaja samo izvajalec, ki je registriran za opravljanje gradbene dejavnosti in ima za tovrstna dela ustrezno zavarovanje za škodo, certifikate, tehnično izobražen kader, sredstva ter je usposobljen za samostojno pripravo in izvedbo del. | The work may only be carried out by a contractor who is registered to carry out construction work and who has the appropriate insurance for such work, certificates, technically trained staff, resources and is qualified to prepare and carry out the work independently.
0.1.3 | Izvajalec odgovarja za kakovost izvedbe vseh del. | The Contractor shall be responsible for the quality of the execution of all works.
0.1.4 | Izvajalec nosi vso odgovornost za nesreče in škodo, ki nastane na objektu ali v okolici zaradi njegovega dela. | The Contractor shall bear all liability for accidents and damage to the installation or the surrounding area caused by his work.
0.1.5 | Pred oddajo ponudbe se je izvajalec dolžan seznaniti z območjem predvidenim za gradnjo in temu prilagoditi vsa potrebna dela, kar mora biti zajeto v ponudbi. V neposredni bližini predvidene gradnje se nahajajo stavbe, v katerih potekajo izobraževalni in raziskovalni procesi. Zato bo izvajalec moral izvajati kontrolo hrupa in kontrolo vibracij. Dela, ki so hrupna in dela, ki povzročajo vibracije bo izvajalec moral preprečiti oziroma jih izvesti na način, da povzročajo minimalne vplive. Tehnologijo rušenja, pilotiranja in tehnologijo izvedbe ostalih del bo izvajalec moral prilagoditi tako, da bo vpliv minimalen. Izvajalec mora preprečiti in zmanjšati emisije delcev iz gradbišča na najmanjšo možno mero. | Before submitting a tender, the contractor is obliged to familiarise himself with the area to be constructed and to adapt any necessary works accordingly, which must be included in the tender. In the immediate vicinity of the proposed construction, there are buildings in which educational and research processes take place. The contractor will therefore be required to carry out noise and vibration control. Noise and vibration works will have to be avoided or carried out in such a way as to minimise the impact. Demolition, piling and other works will have to be adapted to minimise the impact. The contractor must avoid and minimise the emission of particulates emitted from the construction site as far as is reasonably practicable.
0.1.6 | Izvajalec je pred oddajo ponudbe dolžan pregledati projektno dokumentacijo in ostale pogoje, ki so del razpisne dokumentacije V primeru morebitnih napak in neskladij je izvajalec dolžan na to opozoriti naročnika pred oddajo ponudbe. | The Contractor is obliged to review the project documentation and other conditions forming part of the tender documentation before submitting the tender In case of any errors or inconsistencies, the Contractor is obliged to bring these to the attention of the Contracting Authority before submitting the tender.
0.1.7 | Pred oddajo ponudbe je izvajalec dolžan preveriti ustreznost popisov del in količin v teh popisih ter njihovo skladnost z ostalimi dokumenti projektne dokumentacije, ki so del razpisne dokumentacije. Prav tako je izvajalec dolžan preveriti vse detajle in sheme. Vse izmere je potrebno preveriti po posameznih projektih oz. načrtih, ki sestavljajo razpisno dokumentacijo. V primeru ugotovljenih neskladij je v času priprave ponudbe obvezan o tem obvestiti naročnika. | Before submitting a tender, the Contractor shall check the adequacy of the inventories of works and quantities in these Bills of Quantities and their conformity with the other documents of the project documentation forming part of the tender documentation. The Contractor shall also check all details and diagrams. All measurements shall be checked against the individual projects or plans forming part of the tender documentation. In the event of any discrepancies, the Contractor shall inform the Contracting Authority at the time of preparing the tender.
0.1.8 | Pred oddajo ponudbe je izvajalec dolžan v tem popisu preveriti zmnožke in seštevke ter prenose le-teh v rekapitulacijo. Izvajalec se s pripravo ponudbe obvezuje, da je prebral vse celice in elemente celotnega popisa, vključno z vsemi postavkami in splošnimi navodili ali določili in je preveril pravilnost preračuna ter s tem zagotavlja ponudbeno vrednost. | Before submitting a tender, the Contractor is required to check the products and totals in this Bill of Quantities (BoQ) and their transfer to the recapitulation. The Contractor undertakes, by preparing a tender, to have read all the cells and elements of the complete BoQ, including all headings and general instructions or provisions, and to have checked the correctness of the conversion, thereby guaranteeing the value of the tender.
0.1.9 | Dela bo izvajalec moral izvajati po predloženi projektni dokumentaciji, detajlih in z upoštevanjem navodil in potrditev projektanta, nadzornika in investitorja. Vso potrebno delavniško dokumentacijo zagotovi izvajalec del v okviru ponujene cene. | The Contractor shall carry out the works in accordance with the submitted design documents, details and subject to the instructions and approvals of the Designer, the Supervisor and the Investor. All necessary workshop documentation shall be provided by the Contractor within the scope of the price quoted.
0.1.10 | Pred izvedbo posameznih del je izvajalec dolžan pregledati projektno dokumentacijo za izvedbo gradnje (PZI) in elaborate. Na morebitne napake v dokumentaciji ali neskladja med posameznimi načrti ali deli načrtov (popisi del, tehnična poročila, lokacijski in tehnični prikazi) izvajalec opozori nadzornika in projektanta, in se z njima pravočasno uskladi. | The Contractor shall review the Detailed Design documentation (PZI) and the studies before carrying out the individual works. The Contractor shall draw the attention of the Supervisor and the Designer to any errors in the documentation or discrepancies between the individual designs or parts of designs (BoQ, technical reports, location and technical drawings) and shall coordinate with them in good time.
0.1.11 | Tehnični opisi, prikazi, detajli, sheme ter ostali dokumenti v PZI dokumentaciji predstavljajo dodaten opis popisnih postavk gradbeno obrtniških in inštalacijskih del ter jih je potrebno dosledno upoštevati skupaj s popisom del. | The technical descriptions, illustrations, details, diagrams and other documents in the Detailed Design documentation (PZI) are additional descriptions of the BoQ inventory items of the building, construction and installation works and must be strictly followed together with the BoQ.
0.1.12 | Specifikacije in zahteve, navedene v popisu, se ne smejo upoštevati kot edine zahteve. Izvajalec je dolžan v ceni zajeti in dobaviti vse elemente opreme ter opraviti dela in storitve, ki niso eksplicitno navedeni, a so bistvenega pomena za funkcionalnost, skladnost s predpisi ter kontinuirano, zanesljivo in varno obratovanje opreme. | The specifications and requirements set out in the BoQ shall not be taken as the only requirements. The Contractor shall be obliged to include in the price and supply all items of equipment and to carry out works and services which are not expressly mentioned but which are essential for the functionality, regulatory compliance and continuous, reliable and safe operation of the equipment.
0.1.13 | Vsa dela morajo biti izvedena kvalitetno in iz materialov z zahtevanimi lastnostmi, izvedena skladno z veljavno zakonodajo in z upoštevanjem navodil za vgradnjo za izbrane materiale in opremo, s predložitvijo predpisanih izjav o lastnostih in/ali certifikatov. Vsi gradbeni proizvodi (GP) morajo biti označeni s CE oznako. | All work shall be of good quality and be executed with materials of the required characteristics, in accordance with the applicable legislation and in compliance with the installation instructions for the materials and equipment selected, and shall be accompanied by the prescribed declarations of performance and/or certificates. All construction products (GP) shall bear the CE marking.
0.1.14 | Za vsako opisano delo v popisu je potrebno upoštevati celotno potrebno delo, ves osnovni in pomožni material, prevoz materiala in orodja na objekt, notranje transporte, delovne in pomožne odre, zaključno čiščenje in odstranitev odpadkov po dovršenem delu. | For each work described in the inventory, the total work required, all basic and ancillary materials, the transport of materials and tools to the site, internal transports, working and ancillary scaffolding, final cleaning and the disposal of waste after the work has been completed must be taken into account.
0.1.15 | Vsa delovna sredstva, organizacija in koordinacija del, pripravljalna, spremljajoča in zaključna dela, potrebni montažni in tesnilni materiali ter podkonstrukcije so sestavni del posameznih postavk. | All labour, organisation and coordination of the works, preparatory, accompanying and finishing works, necessary prefabrication and sealing materials and substructures are part of the individual items.
0.1.16 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - načrt organizacije gradbišča s podrobnim terminskim planom in izvedba vseh pripravljalnih del, postavitev, organizacija, zaščita in prijava gradbišča, gradbiščnih objektov, ureditev začasnih deponij, tekoče vzdrževanje, skupaj s plačilom splošnih stroškov pristojbin in davkov upravnih organov, pridobivanju raznih dovoljenj in soglasij za izvedbo, ograditev gradbišča in postavitev gradbene table in prometne signalizacije, zagotavljanje ustrezne varnosti na gradbišču, tekoče vzdrževanje in končna odstranitev gradbišča; - zagotovitev potrebnih začasnih površin za transportne poti in gradnjo izven območja gradbišča s plačilom stroškov za sanacijo in vzpostavitev okoliških zemljišč in objektov v prvotno stanje (soglasja, odškodnine, itd.); - začasni odvoz, deponiranje in vračanje izkopanega materiala, ki ga ne bo možno deponirati na gradbišču; - odvoz in zagotovitev odstranjevanja odpadnega gradbenega materiala skladno z zakonodajo na področju ravnanja z odpadki (odvoz na urejene deponije s plačilom komunalnih prispevkov in taks itd.); - oteženi izkop v mokrem terenu, izkop v vodi, odvod meteorne vode iz gradbene jame in vode, ki se izceja iz bočnih strani izkopov; - ustrezno varovanje izkopa gradbene jame za objekt in ostalih manjših posameznih izkopov za izvedbo komunalne infrastrukture brez posegov na sosednja zemljišča; - ustrezno varovanje obstoječih objektov, infrastrukture in okolice v času gradnje ter dokumentiranje vseh morebitnih škodnih dogodkov; - pripravljalna, spremljajoča in zaključna dela (zakoličbe, zagotovitev potrebnih komunalnih priključkov za potrebe izvajanja gradnje, izvedba začasnih inštalacij, označevanje podzemnih vodov, postavljanje in vzdrževanje zakoličbenih profilov, izvedba in označevanje novih in starih križanj ter morebitna zaščita križanj komunalnih vodov, geodetski posnetki in izdajanje vmesnih posnetkov izvedene infrastrukture naročniku, izdelava zbirnih kart, itd.), v kolikor ni to drugače določeno; - pridobivanje soglasij in izvedba morebitnih zapor na vseh cestah s plačilom stroškov, nadomestil in pristojbin; - zagotovitev oz. postavitev in končna odstranitev po zaključku gradnje začasnih skladišč in začasnega pisarniškega kontejnerskega objekta vključno z opremo za dve delovni mesti in za skupne operativne sestanke vel. ca. 40 m2 za potrebe naročnika, s tekočim vzdrževanjem in čiščenjem. | The following must also be included or taken into account in the uniform prices for individual items: - a construction site organisation plan with a detailed timetable and the execution of all preparatory works, the setting-up, organisation, protection and registration of the construction site, site facilities, the arrangement of temporary storage facilities, ongoing maintenance, including the payment of general costs of fees and taxes of the administrative authorities, the obtaining of various permits and consents for the execution, the fencing of the site and the erection of construction signs and traffic signals, the provision of adequate security on the site, ongoing maintenance and the final dismantling of the construction site; - provision of the necessary temporary areas for transport routes and off-site construction, with costs for restoration and reinstatement of surrounding land and buildings (consents, compensation, etc.); - temporary removal, storage and return of excavated material that cannot be stored on site; - removing and disposing of waste building materials in accordance with waste management legislation (removal to regulated landfill sites with payment of municipal fees and charges, etc.); - difficult excavation in wet ground, excavation in water, drainage of rainwater from the construction pit and water draining from the sides of excavations; - adequate protection of the excavation of the construction pit for the building and other small individual excavations for the implementation of the utility infrastructure without encroaching on neighbouring land; - adequate protection of existing facilities, infrastructure and the surrounding area during construction, and documentation of any damage incidents; - preparatory, accompanying and finishing works (stake-out, provision of the necessary utility connections for the needs of construction, execution of temporary installations, marking of underground lines, installation and maintenance of stake-out profiles, execution and marking of new and old crossings and possible protection of crossings of utility lines, geodetic surveys and issuing of intermediate images of the completed infrastructure to the client, production of summary maps, etc.), unless otherwise specified; - obtaining consents and implementing any road closures, with costs, compensation and fees; - provision or erection and final removal on completion of construction of temporary storage and temporary office container building including equipment for two workstations and for joint operational meetings of approx. 40 m2 for the needs of the client, with ongoing maintenance and cleaning.
0.1.17 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - izdelava montažne tehnične dokumentacije, detajlov izvedbe in vse druge potrebne delavniške dokumentacije (s področja arhitekture, gradbeništva, elektrotehnike, strojništva in zunanje ter krajinske ureditve) ter pridobitev obvezne potrditve s strani projektanta, nadzornika in investitorja; - odprava vseh vrst inštalacijskih kolizij z izvajanjem potrebnih premikov inštalacij in njihovim usklajevanjem na mestu montaže, vse v obsegu, ki ne vpliva na projektirano rešitev ali tip inštalacij oz. opreme; - zagotavljanje kompletnosti elektro-instalacijskih sistemov s področja avtomatike za doseganje njihove popolne funkcionalnosti delovanja; - stroški za nadzor in koordinacijo izvedbe vseh elektro napeljav, ki so predmet končne instalacije proizvoda (senčila, vrata, okna,…); - izdelava montažnih skic in detajlov za izvedbo v dogovoru z vodjo gradnje in nadzornikom; - izdelava in predstavitev vzorcev v ustrezni velikosti za potrditev projektanta, nadzornika in investitorja; - zagotavljanje varnosti in zdravja pri delu, zlasti izvajanje vseh del, ki izhajajo in ukrepov, ki izhajajo iz določil veljavnih predpisov varstva pri delu in zahtev Varnostnega načrta;- stroški garancij, ki jih mora izvajalec predložiti naročniku. | The following must also be included or taken into account in the uniform prices for individual items: - preparation of prefabricated technical documentation, construction details and all other necessary workshop documentation (architectural, civil, electrical, mechanical, exterior and landscaping) and obtaining the mandatory approval of the designer, the supervisor and the investor; - elimination of all types of installation conflicts by carrying out the necessary relocation of installations and their coordination at the installation site, all to the extent that it does not affect the design solution or the type of installation or equipment; - ensuring the completeness of electrical installation systems in the automation sector to achieve their full operational functionality; - the cost of supervising and coordinating the installation of all the electrical installations that are the subject of the final installation of the product (blinds, doors, windows, etc.); - preparation of erection drawings and details for implementation in agreement with the construction manager and supervisor; - production and presentation of samples in appropriate sizes for the approval of the designer, the supervisor and the investor; - ensuring health and safety at work, in particular the implementation of all the works arising from and the measures resulting from the provisions of the applicable occupational safety regulations and the requirements of the Safety Plan; - the cost of the guarantees to be provided by the contractor to the client.
0.1.18 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - strošek vodje del glavnega izvajalca, ki bo izvajal tudi koordinacijo s podizvajalci in z drugimi izvajalci, ki jih bo izbral naročnik in bo opravljal delo vodje gradbišča; - koordinacija del z ostalimi izvajalci oz. podizvajalci del, projektantom, nadzornikom in investitorjem pri medsebojnem usklajevanju organizacije gradbišča in časovnega načrta del ter pri usklajevanju izdelave plana montaže, potrjenih s strani vseh udeležencev gradnje; - stroški koordinacije, sodelovanja in usklajevanja z dobavitelji tehnološke, laboratorijske, eksperimentalne in vse ostale pohištvene ter multimedijske opreme ter z vsemi ostalimi dobavitelji oz. podizvajalci na objektu; - stroški izdelave situacij; - stroški zavarovanja objekta v času izvedbe del in delavcev ter materiala na gradbišču v času izvajanja del, od začetka del do pridobitve uporabnega dovoljenja za objekt. Zavarovanje mora biti sklenjeno pri ustrezni zavarovalni družbi najmanj v višini pogodbene vrednosti ali v zakonsko predpisani vrednosti (v kolikor zavarovanje v višini pogodbene vrednosti presega zakonsko dovoljeno), za ves čas trajanja izvedbe del do uspešne primopredaje objekta; - preizkušanje kvalitete materiala, ki se vgrajuje in dokazovanje kvalitete s certifikati oz. tehničnimi soglasji; - izvedba vseh zahtevanih testov in preizkusov (npr. tlačni preizkusi, termografski pregledi, meritve elektromagnetnega sevanja, hrupa, itd.), poskusnega obratovanja celotnega objekta s poudarkom na vseh inštalacijah ter izvajanje predpisanega monitoringa v skladu s Poročilom o vplivih na okolje (pred gradnjo, med gradnjo in po končani gradnji); - izdelava izkaza požarne varnosti, vključno s sprotnim spremljanjem gradnje in izvajanjem požarnovarnostnih zahtev ter izdelava Požarnega reda z obveznimi prilogami; - izdelava Izkaza zaščite pred hrupom v stavbah; - izdelava Izkaza energijskih lastnosti stavbe in energetske izkaznice; - sodelovanje z izvajalci gradbenega in projektantskega nadzora in investitorjem za izvedbo tehničnega pregleda in priprava primopredaje, ki mora vsebovati vso zahtevano dokumentacijo, predvsem pa: izjave o skladnosti, požarni izkaz in ostale izkaze ter obvezne tabele, dokazilo o zanesljivosti objekta (DZO), certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo in vzdrževanje ter vse ostale dokumente v skladu s predpisi in pogodbenimi določili. | The following must also be included or taken into account in the uniform prices of the individual items: - the cost of a works manager for the main contractor, who will also coordinate with subcontractors and other contractors selected by the client and act as site manager; - coordination of the works with other contractors or subcontractors, the designer, the supervisor and the investor in coordinating the organisation of the construction site and the timetable for the works, and in coordinating the production of an installation plan approved by all the participants in the construction; - the costs of coordination, cooperation and coordination with suppliers of technological, laboratory, experimental and all other furniture and multimedia equipment, as well as with all other suppliers or subcontractors on the site; - the cost of drawing up situations; - the cost of insuring the building during the execution of the works and the workers and materials on site during the execution of the works, from the start of the works until the building has been licensed for occupation. The insurance must be taken out with a suitable insurance company for at least the contract value or the legal value (if the insurance for the contract value exceeds the legal value), for the entire duration of the works until the successful handover of the building; - testing the quality of the material to be installed and proving it with certificates or technical approvals; - carrying out all required tests and trials (e.g. pressure tests, thermographic inspections, electromagnetic radiation measurements, noise measurements, etc.), trial operation of the entire building, with emphasis on all installations, and carrying out the required monitoring in accordance with the Environmental Impact Assessment Report (before, during and after construction); - preparation of a fire safety statement, including ongoing monitoring of construction and implementation of fire safety requirements, and preparation of a Fire Safety Order with mandatory annexes; - preparation of a Noise Protection Statement for buildings; - preparation of the Building Energy Performance Report and Energy Performance Certificate; - cooperation with the construction and design supervision contractors and the investor to carry out the technical inspection and prepare the handover, which must include all the required documentation, in particular: declarations of conformity, fire and other statements and mandatory tables, proof of reliability of the building (DZO), certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use and maintenance, and all other documents in accordance with the regulations and the contractual provisions.
0.1.19 | V enotnih cenah posameznih postavk, ki se nanašajo na opremo in posamezne sisteme, mora biti zajeto oz. upoštevano tudi naslednje: - dobava oz. transport, - stroški za vse delovne stroje za dvigovanje bremen in delovne košare za dostope do delovišč; - morebitni stroški povzročeni upravljavcem GJI, ki bi nastali v zvezi s predmetno gradnjo; - montaža, vključno s pomožnim montažnim materialom (vezni, tesnilni in pritrdilni material, sidra, nosilni profili, podkonstrukcije in podobno) in navodili proizvajalca, - odprava vseh kolizij sistemov s stenami in med sistemi, - izvedba vseh potrebnih tesnjenj, - priključitev in nastavitve, vključno z morebitnim kalibriranjem, - zagon, testiranje in meritve, vključno s poročili, - šolanje uporabnikov oz. vzdrževalnega osebja za uporabo in vzdrževanje sistemov, - navodila za obratovanje in vzdrževanje, - vsi potrebni certifikati, izjave o skladnosti oz. potrdila ter - vsa druga pomožna dela in material, da se zagotovi funkcionalnost posamezne postavke popisa. | The following must also be included or taken into account in the uniform prices for individual items relating to equipment and individual systems: - delivery/transport, - the cost of all lifting machines and work baskets for access to work sites; - any costs incurred to the operators of utility infrastructure (GJI) in connection with the subject construction; - installation, including ancillary installation materials (bonding, sealing and fixing materials, anchors, support profiles, substructures, etc.) and manufacturer's instructions, - eliminating all system-to-wall and system-to-system collisions, - all necessary sealing work, - connection and set-up, including calibration if necessary, - commissioning, testing and measurements, including reports, - training users or maintenance staff in the use and maintenance of the systems, - operating and maintenance instructions, - any necessary certificates, declarations of conformity or attestations; and - all other ancillary works and materials to ensure the functionality of each inventory item.
0.1.20 | Vsi odri morajo biti upoštevani v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All scaffolding must be included in the uniform prices of the items listed, except where specifically mentioned.
0.1.21 | Vsi delovni in pomožni odri, lestve in ostala potrebna pomožna sredstva, kot tudi čiščenje vseh elementov po končanih delih, mora biti upoštevano v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All working and auxiliary scaffolding, ladders and other necessary ancillaries, as well as the cleaning of all elements after completion of the works, shall be included in the uniform prices of the items listed, except those specifically mentioned.
0.1.22 | Delavniško dokumentacijo za vse nosilne jeklene konstrukcije in podkonstrukcije izdela izvajalec, strošek izdelave delavniške dokumentacije se upošteva v ponujenih cenah in se ne obračuna posebej. | The cost of the shop drawings for all steelwork and substructures shall be included in the prices quoted and shall not be charged separately.
0.1.23 | V enotnih cenah postavk mora biti vključeno tudi vgrajevanje vseh instalacijskih razvodov v opaže armirano betonskih elementov in izdelava prehodov inštalacij ter dodatno izrezovanje utorov in prebojev v kamnite, zidane ali armirano-betonske stene, ponovno demontiranje in montiranje vseh vrst montažnih sten, vsa dodatna dela za zagotavljanje primernih križanj med posameznimi instalacijskimi vodi, izdelava vseh vrst ojačitev konstrukcij in podobna dela, ki zagotavljajo kakovostno vgradnjo vseh vrst instalacijskih vodov in niso posebej navedena v popisu GOI del. V ponudbi morajo biti upoštevana vsa drobna strojna in elektro instalacijska dela in transporti. | The installation of all installation ducts in the formwork of reinforced concrete elements and the construction of installation penetrations, as well as the additional cutting of grooves and penetrations in stone, masonry or reinforced concrete walls, the reassembly and reinstallation of all types of prefabricated walls, all additional work to ensure adequate crossings between individual installation ducts, the construction of all types of structural reinforcement and similar work to ensure the quality installation of all types of installation ducts and not specifically mentioned in the BoQ of the Construction, installation and finishing works (GOI) shall also be included in the uniform prices of the items. The tender shall take into account all minor mechanical and electrical installation work and transport.
0.1.24 | Vsi kovinski elementi in konstrukcije, ki bi lahko bili izpostavljeni atmosferskim in ostalim korozijskim vplivom, morajo biti ustrezno protikorozijsko zaščiteni. | All metallic elements and structures that could be exposed to atmospheric and other corrosive influences must be adequately protected against corrosion.
0.1.25 | Za vse večje jeklene dele se skladno s predpisi, izdelajo ustrezne ozemljitve, nevidno pritrjene in speljane na splošno ozemljitev objekta. | For all major steel parts, appropriate earth connections shall be made in accordance with the regulations, invisibly attached and connected to the general earth of the building.
0.1.26 | Za vse vidne elemente in serijske elemente je obvezna predhodna uskladitev obdelav, barv in materialov s projektantom na podlagi dostavljenih vzorcev v ustrezni velikosti. Obvezna je preveritev dejanskih mer na licu mesta in posledična prilagoditev elementov in njihove montaže. | For all visible elements and serial elements, it is mandatory to coordinate the finishes, colours and materials with the designer beforehand on the basis of the supplied samples in the appropriate size. It is mandatory to check the actual dimensions on site and to adjust the elements and their installation accordingly.
0.1.27 | Dimenzije obrtniških izdelkov in količine je potrebno pred naročanjem preveriti na objektu. Potrebna je uskladitev vseh elementov (kljuke, okovje, detajlne konstrukcije in obdelave, itd.) s projektantom, nadzornikom in investitorjem. Izvajalec je dolžan pred izdelavo predložiti projektantu v potrditev ustrezne delavniške načrte in detajle. | The dimensions of the workmanship and quantities must be checked on site before ordering. All elements (hooks, fittings, detailed construction and finishes, etc.) must be coordinated with the designer, the supervisor and the investor. The contractor is obliged to submit the relevant workshop plans and details to the designer for approval before manufacture.
0.1.28 | V posameznih postavkah popisa so navedeni proizvajalci in/ali tipi posameznih sistemov, materialov ali opreme, s čimer so zgolj natančno opredeljene zahtevane tehnične lastnosti. Izvajalec del lahko ponudi nadomesten sistem, material ali opremo drugega proizvajalca in tipa, pri čemer morajo biti tehnične lastnosti ponujenega sistema, materiala ali opreme enakovredne ali boljše od opredeljenih v popisu, dimenzijsko pa ne smejo presegati projektiranih dimenzij. Vse funkcijske in tehnične karakteristike nadomestnih sistemov, materialov ali opreme mora izvajalec dokazati z ustrezno dokumentacijo. Vse morebitne posledice zaradi spremembe sistemov, materialov ali opreme vključno z morebitnimi spremembami oz. dopolnitvami BIM modelov in projektne dokumentacije, stroškovno in časovno bremenijo izvajalca. | The individual items of the Inventory shall specify the manufacturers and/or types of the individual systems, materials or equipment, thereby merely specifying the required technical characteristics. The Contractor may offer a substitute system, material or equipment of a different manufacturer and type, provided that the technical characteristics of the offered system, material or equipment shall be equivalent to or better than those specified in the BoQ, and shall not exceed the design dimensions. All functional and technical characteristics of the substitute systems, materials or equipment shall be demonstrated by the Contractor with appropriate documentation. Any consequences resulting from changes to systems, materials or equipment, including any changes or additions to the BIM models and project documentation, shall be borne by the Contractor in terms of cost and time.
0.1.29 | Vsako zamenjavo, uporabo in končni izbor nadomestnih sistemov, materialov, proizvodov in opreme morajo obvezno in pravočasno (pred dobavo in vgradnjo) pisno potrditi projektant (vseh sodelujočih strok), nadzornik in investitor. | Any replacement, use and final selection of alternative systems, materials, products and equipment must be approved in writing by the designer (of all disciplines involved), the supervisor and the investor in a timely manner (prior to delivery and installation).
0.1.30 | Izvajalec mora v ponudbeno ceno vključiti tudi: - ves čas gradnje sprotno beleženje sprememb oz. odstopanj od PZI dokumentacije, vključno z izdelavo tekstualnega opisa sprememb, - pripravo podlog na nivoju PZI, ki so potrebne za posodobitev oz. uskladitev BIM modela z izvedenim stanjem (LOD 500) in izdelavo projektne dokumentacije izvedenih del (PID), - mesečno predajanje potrjenih sprememb opreme in materiala, ki vplivajo na BIM model, v formatu IFC, - vzdrževanje in uporabljanje pri izvedbi zadnje veljavne revizije PZI dokumentacije, vključno z dopolnitvami PZI načrtov, ki so nastali zaradi sprememb med gradnjo. | The contractor must also include in the tender price: - keeping a record of changes or deviations from the construction documentation (PZI) throughout construction, including a textual description of the changes, - preparation of the Detailed Design (PZI) level documents required to update or align the BIM model with the as-built condition (LOD 500) and the preparation of the as-built project documentation for the works (PID), - monthly submission of approved equipment and material changes affecting the BIM model in IFC format, - maintenance and use in the execution of the last valid revision of the construction documentation (PZI), including additions to the construction design documentation (PZI) resulting from changes during construction.

## 0.2_Uvod-DGNB
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
0.2 | SPLOŠNI TEHNIČNI POGOJI ZA PODROČJE DGNB CERTIFICIRANJA | GENERAL TECHNICAL CONDITIONS FOR DGNB CERTIFICATION
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic entity with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
| Splošni pogoji za področje DGNB certificiranja predstavljajo dopolnilo splošnim tehničnim pogojem in ne odpravljajo drugih obveznosti in odgovornosti, ki jih ima izvajalec v skladu s predpisi in pogodbo. | The General Conditions for DGNB Certification are complementary to the General Technical Conditions and do not exclude other obligations and responsibilities that the Contractor has under the Regulations and the Contract.
0.2.1 | Izvajalec mora v svojih ponudbah upoštevati, da se bo objekt certificiral v skladu z zahtevami DGNB sistema certificiranja trajnostne gradnje, ter pravočasno (vsaj 60 dni pred vgradnjo posameznega produkta) dostaviti vso ustrezno dokumentacijo za vse v ponudbi zajete materiale, elemente in opremo. Zahtevana je uporaba materialov, elementov ali opreme, ki so okolju in ljudem prijazni, energetsko učinkoviti in obenem ustrezajo zahtevam DGNB sistema. Zahtevan nivo certifikata je: ZLATI CERTIFIKAT | The Contractor shall take into account in its tenders that the building will be certified in accordance with the requirements of the DGNB Sustainable Building Certification Scheme and shall deliver all relevant documentation for all materials, elements and equipment included in the tender in a timely manner (at least 60 days before the installation of each product). The use of materials, elements or equipment that are environmentally and human friendly, energy efficient and at the same time meet the requirements of the DGNB system is required. The required level of certification is: GOLD CERTIFICATE
0.2.2 | Podrobnejši opis DGNB sistema in navodila za posamezne kriterije so dostopna v dokumentu"DGNB Criteria Set New Construction Buildings, Version 2020 International", ki je na voljo na DGNB spletni strani https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria | A more detailed description of the DGNB system and guidance on the individual criteria is available in the document "DGNB Criteria Set New Construction Buildings, Version 2020 International", available on the DGNB website https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria
0.2.3 | Izvajalec mora v svojih ponudbah upoštevati, da je potrebno skladno z določili DGNB certifikacijskega sistema, pravočasno (pred pričetkom gradnje) dostaviti vso ustrezno dokumentacijo, za vse v ponudbi zajete materiale, elemente in opremo (tehnični list, varnostni list, izjava o lastnostih, tehnična navodila za ravnanje, servisiranje, vzdrževanje,...) v slovenskem jeziku. Vgradnja kakršnihkoli materialov, elementov ali opreme, se izvede zgolj na podlagi predhodne preveritve posredovane dokumentacije in obenem potrditve s strani nadzornika. | The Contractor must take into account in its tenders that, in accordance with the provisions of the DGNB certification system, all relevant documentation for all materials, elements and equipment included in the tender (technical data sheet, safety data sheet, declaration of properties, technical instructions for handling, servicing, maintenance,...) must be delivered on time (prior to the start of construction) in the Slovene language (in accordance with the provisions of the DGNB certification system). The installation of any materials, elements or equipment shall be subject to prior checking of the submitted documentation and, at the same time, to the approval of the Supervisor.
0.2.4 | Izbrani materiali, elementi, naprave, sistemi in oprema morajo prispevati k večji trajnosti stavbe v smeri zagotavljanja energetske učinkovitosti, ekonomičnega in enostavnega vzdrževanja ter čiščenja, dolge življenjske dobe, uporabe okolju prijaznih materialov ipd. | The materials, elements, appliances, systems and equipment chosen must contribute to the sustainability of the building in terms of energy efficiency, economic and easy maintenance and cleaning, long lifetime, use of environmentally friendly materials, etc.
0.2.5 | Predloženi dokumenti za vse uporabljene materiale, elemente in opremo morajo izpolnjevati zahteve najmanj kakovostne stopnje QS3 (zaželeno QS4), iz dokumenta: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001) | The documents submitted for all materials, components and equipment used shall meet the requirements of at least quality level QS3 (preferably QS4) of the document DGNB Quality Grades for Materials, Components and Equipment (JULFS--7X9001)
0.2.6 | V kolikor izbrani materiali oz. elementi, navedeni v posameznih postavkah, ne ustrezajo vsaj kakovostni stopnji QS3 iz seznama: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), je izvajalec dolžan na to opozoriti projektanta, nadzor in investitorja ter podati predlog ustreznega materiala oz. elementa. | If the selected materials or elements listed in the individual items do not meet at least quality level QS3 of the list of DGNB quality classes for materials, elements and equipment (JULFS--7X9001), the Contractor shall draw this to the attention of the Designer, the Supervisor and the Investor, and shall make a proposal for a suitable material or element.
0.2.7 | Izvajalec lahko v svoji ponudbi predlaga alternativne produkte in rešitve glede na predvidene s projektom, pod pogojem, da le-te prav tako izpolnjujejo vse navedene zahteve. Pri morebitnih predlaganih alternativnih produktih oz. rešitvah je potrebno upoštevati najmanj enake ali boljše lastnosti v smislu življenjske dobe, obstojnosti, ter enostavnosti in stroška čiščenja ter vzdrževanja v primerjavi s projektom predpisanimi rešitvami. Za alternativne rešitve izvajalec pridobi soglasje projektanta, nadzornika in investitorja pred pričetkom gradnje. | The Contractor may propose alternative products and solutions to those envisaged by the project in its tender, provided that they also meet all the requirements set out above. Any alternative products or solutions proposed shall have at least the same or better characteristics in terms of service life, durability, and ease and cost of cleaning and maintenance compared to the solutions envisaged by the project. For alternative solutions, the contractor shall obtain the agreement of the designer, the supervisor and the investor before starting construction.
0.2.8 | Izvajalec med gradnjo dnevno beleži vsa eventualna odstopanja od PZI projektne dokumentacije ter podatke pravočasno posreduje naročniku, nadzoru in projektantu. Potrjene spremembe vnese v podlage za izdelavo PID in posodobitev BIM modelov. | During construction, the Contractor shall record on a daily basis any deviations from the Detailed Design documentation (PZI) and shall provide the information to the Client, Supervision and the Designer in a timely manner. Confirmed changes shall be entered into the basis for the As-built documentation (PID) and BIM model updates.
0.2.9 | Izvajalec med gradnjo sproti izpolnjuje Seznam vseh konstrukcijskih sestav s pripadajočimi vgrajenimi gradbenimi materiali in dokumentira naslednje podatke o vgrajenih materialih (v slovenskem jeziku): - Varnostni list - Tehnični list - Izjavo o lastnostih (če je relevantno) - Izkazovanje morebiti obstoječega okoljskega certifikata (Tip I - okoljski znak ali Tip III - okoljska produktna deklaracija /EPD) - Izjavo proizvajalca ali dobavitelja, da produkt ustreza zahtevam ENV1.2 - Tehnična navodila za ravnanje, servisiranje, vzdrževanje oziroma ostale, z zakonom predpisane dokumente in dokumentacijo. | During construction, the Contractor shall keep a List of all structural assemblies with their associated construction materials and document the following information on the materials installed (in Slovene language): - Safety Data Sheet - Technical Data Sheet - Declaration of performance (if applicable) - Demonstration of any existing environmental certification (Type I - Ecolabel or Type III - Environmental Product Declaration /EPD) - A declaration by the manufacturer or supplier that the product complies with the requirements of ENV1.2 - Technical instructions for handling, servicing, maintenance or other documents and documentation required by law.
0.2.10 | Za vse vgrajene bistvene tehnične sisteme mora izvajalec zagotoviti obstoj pooblaščenega servisa, ki deluje na območju Republike Slovenije, da ima investitor možnost skleniti ustrezno pogodbo o vzdrževanju. Med bistvene tehnične sisteme sodijo npr.: sistemi ogrevanja in hlajenja, priprava tehnoloških medijev, prezračevanje in klimatizacija, sistemi detekcije in gašenja požara, sistemi tehničnega varovanja, BMS in CNS sistemi upravljanja stavbe, razsvetljava, komunikacijski in WI-FI sistemi,... | For all installed essential technical systems, the contractor must ensure the existence of an authorised service centre operating in the territory of the Republic of Slovenia, so that the investor has the possibility of concluding an appropriate maintenance contract. The essential technical systems include, for example: heating and cooling systems, technological media preparation, ventilation and air conditioning, fire detection and extinguishing systems, technical security systems, BMS and CNS building management systems, lighting, communication and WI-FI systems,...
0.2.11 | Zaželeno je, da imajo uporabljeni elementi in materiali okoljsko oznako Tip I. (kot npr. ENCODE, BLUE ANGEL, ipd...). | It is preferable that the elements and materials used have a Type I environmental label (such as ENCODE, BLUE ANGEL, etc...).
0.2.12 | Izvajalec bo za elemente iz lesa moral dokazovati izvor z navedbo izvorne države in tipa lesa, FSC / PEFC certifikat z dodatnim pripadajočim potrdilom Chain of custody-trgovski certifikat dobavitelja - ta se dokazuje z dobavnicami, računi ali enakovredno. Za izdelke iz naravnega kamna iz EU držav je potrebna deklaracija, da je izvor in procesiranje teh izdelkov v celoti v EU državah. Za izdelke iz naravnega kamna, ki prihajajo iz držav izven EU, je potrebno predložiti dokazilo o izpolnjevanju ILO konvencije 182, ki vključuje neodvisna inšpekcijska poročila. | For wood elements, the contractor will be required to provide proof of origin, indicating the country of origin and the type of wood, FSC/PEFC certification with an additional Chain of Custody certificate - the supplier's trade certificate - this shall be evidenced by delivery notes, invoices or equivalent. For natural stone products from EU countries, a declaration that the sourcing and processing of these products is entirely in EU countries is required. For natural stone products from non-EU countries, proof of compliance with ILO Convention 182, including independent inspection reports, is required.
0.2.13 | Izobraževanje udeležencev pri gradnji Izvajalec je dolžan vse udeležence pri gradnji podrobneje seznaniti tudi z relevantnimi koncepti, študijami, elaborati, ki opredelujejo trajnostni način gradnje za naslednja področja: - zaščita pred hrupom (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)) - zaščita pred prašenjem - zaščita tal in podzemne vode (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)), Analiza tveganja za onesnaženje vodnega telesa podzemne vode št. 0346-023/2023, maj 2023 (Geološko projektiranje d.o.o.)) - ravnanje z gradbenimi odpadki (Načrt gospodarjenja z gradbenimi odpadki) Izobraževanja se izvajajo skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.1 1.2, 2.2, 3.2 in 4.2 Training for the parties implementing the construction work | Training of construction participants The contractor is also obliged to inform all construction participants in detail about relevant concepts, studies, elaborations defining sustainable construction methods for the following areas: - noise protection (Environmental Impact Assessment Report No 100123-11523, dated 11.5.2023, supplemented on 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.)) - dust protection - protection of soil and groundwater (Environmental Impact Assessment Report No. 100123-11523, dated 11.5.2023, supplemented 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.), Risk analysis for contamination of the groundwater No. 0346-023/2023, May 2023 (Geološko projektiranje d.o.o.)) - construction waste management (Construction Waste Management Plan) The training shall be carried out in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.1 1.2, 2.2, 3.2 and 4.2 Training for the parties implementing the construction work
0.2.14 | Navodila za obratovanje in vzdrževanje objekta Izvajalec pripravi Navodila za obratovanje in vzdrževanje objekta skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilih: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual | Instructions for the operation and maintenance of the facility The Contractor shall prepare the Operation and Maintenance Instructions for the Facility in accordance with the applicable Slovenian legislation and the DGNB System Instructions specified in the Criteria: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual
0.2.15 | Meritve kontrole kakovosti gradnje Izvajalec mora upoštevati, da se bodo po koncu gradnje izvedle naslednje meritve: - meritve zrakotesnosti - meritve s termokamero (termografija) - meritve akustike - meritve zvočne zaščite ovoja stavbe - meritve zvočne zaščite ločilnih elementov med posameznimi prostori različnih namembnosti - meritve udarnega zvoka - meritve vlažnosti vgrajenih elementov, pred vgradnjo finalnih tlakov - test odvoda dima in toplote Meritve morajo opraviti ustrezno usposobljeni preskusni organi ali strokovnjaki ter rezultate oceniti in primerjati z zahtevami. Obseg opravljenih meritev mora biti sorazmeren z velikostjo zgradbe in mora ustrezno odražati cilj preverjanja kakovosti zgradbe. Smiselno je, da izvajalec del tekom gradnje za sprotno kontrolo kakovosti vgrajenih materialov, elementov in opreme, sam izvaja meritve. Končne meritve (ob primopredaji) izvede tretja oseba kot neodvisna potrditev doseganja zahtev. Meritve se izvajajo skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 2. Quality control measurements | Construction quality control measurements The contractor must take into account that the following measurements will be carried out after completion of the construction: - airtightness measurements - thermal camera measurements (thermography) - acoustics measurements - measurements of the sound insulation of the building envelope - measurements of the sound insulation of the separating elements between different rooms of different uses - impact sound measurements - moisture measurements of the installed elements, prior to the installation of the final flooring - smoke and heat extraction test The measurements shall be carried out by suitably qualified test bodies or experts and the results evaluated and compared with the requirements. The extent of the measurements carried out shall be proportionate to the size of the building and shall adequately reflect the objective of the building quality verification. It is reasonable for the contractor to carry out his own measurements during construction to check the quality of the materials, elements and equipment installed. Final measurements (at handover) are carried out by a third party as an independent confirmation of compliance with the requirements. The measurements shall be carried out in accordance with the applicable Slovenian legislation and the DGNB system instructions specified in the benchmark: PRO 2.2 2. Quality control measurements
0.2.16 | Zagotavljanje kakovosti za uporabljene gradbene proizvode Izvajalec mora zagotavljati izvajanje primerjav med definiranim in dejansko uporabljenim materialom, elementom ali opremo skladno seznamom: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), vključno z dokazno dokumentacijo ugotovitev primerjav ter skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 3.1 Quality assurance for the used construction products | Quality assurance for the construction products used The Contractor shall ensure that comparisons are made between the defined and the actual material, element or equipment used in accordance with the list: DGNB Quality Grades of Installed Materials, Elements and Equipment (JULFS--7X9001), including supporting documentation of the findings of the comparisons, and in accordance with the DGNB system instructions defined in the Criterion: PRO 2.2 3.1 Quality assurance for the used construction products
0.2.17 | Zaščita pred vlago Izvajalec predloži dokumentacijo, ki dokazuje, da je bil izveden program prezračevanja, prilagojen stavbi, s čimer se zagotovi pogoje, da so vgrajeni gradbeni elementi ustrezno suhi, skladno z navodili DGNB opredeljenimi v merilu: PRO 2.2 4.1 Mould prevention | Protection against moisture The Contractor shall provide documentation demonstrating that a building-specific ventilation programme has been implemented to ensure that the building elements installed are adequately dry, in accordance with the DGNB guidelines specified in the criteria: PRO 2.2 4.1 Mould prevention
0.2.18 | Preizkusi delovanja sistemov Izvajalec sodeluje pri izvedbi predhodnega in končnega preizkusa delovanja vseh bistvenih tehničnih komponent stavbe in pripravi ustrezne dokazne dokumentacije ter pri usposabljanju vzdrževalcev/upravljalcev stavbe, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators | System performance tests The Contractor shall be involved in the performance of the preliminary and final performance tests of all essential technical components of the building and the preparation of the relevant supporting documentation, as well as in the training of the maintenance/management staff of the building, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators
0.2.19 | Poročilo o zagonu objekta Izvajalec sodeluje pri pripravi končnega poročila o zagonu objekta, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 5.1 Creation of a detailed final report | Commissioning report The Contractor shall be involved in the preparation of the final commissioning report, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 5.1 Creation of a detailed final report
0.2.20 | Koncept celovitega delovanja sistemov v stavbi Izvajalec sodeluje pri procesu implementiranja stalnega nadzora in nastavitev delovanja stavbe ter usposabljanju vzdrževalcev/upravljalcev stavbe. Navedeno se izvede v skladu z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 6.1 Creation and handover of an integral operating concept | The concept of integrated building systems The contractor is involved in the process of implementing the building's continuous monitoring and settings and training the building's maintenance/management staff. This shall be done in accordance with the DGNB system instructions defined in the benchmark: PRO 2.3 6.1 Creation and handover of an integral operating concept
0.2.21 | Prilagoditev nastavitev sistemov po začetni fazi uporabe objekta Izvajalec sodeluje pri ponovnem pregledu delovanja vseh bistvenih tehničnih sistemov ter eventualni ponovni prilagoditvi teh sistemov s strani strokovnjaka oz. (neodvisne) tretje osebe. Postopek se izvede po približno 10–14 mesecih po zaključku gradnje, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 7.1 Readjustment of the system following initial operating phase | Adjusting system settings after the initial phase of use of the building The Contractor shall be involved in the re-examination of the functioning of all essential technical systems and the possible re-adjustment of these systems by an expert or (independent) third party. The procedure shall be carried out approximately 10-14 months after completion of construction, in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.3 7.1 Readjustment of the system following initial operating phase

## 3.9.0_Rekapitulacija
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
| REKAPITULACIJA STROŠKOV ELEKTRO DEL | COST SUMMARY OF ELECTRICAL WORKS
| 3 NAČRT S PODROČJA ELEKTROTEHNIKE | 3 DOCUMENTATION IN THE FIELD OF ELECTRICAL ENGINEERING
| 3/9 Aktivni sistemi protipožarne zaščite in javljanje plinov | 3/9 Active Fire Protection Systems and Gas Detection
3.9 | ELEKTRO DELA | ELECTRICAL WORKS
3.9.1 | AKTIVNI SISTEMI PROTIPOŽARNE ZAŠČITE | ACTIVE FIRE PROTECTION SYSTEMS | 0
3.9.2 | ODVOD DIMA IN TOPLOTE | SMOKE AND HEAT EXTRACTION | 0
3.9.3 | JAVLJANJE PLINA | GAS REPORTING | 0
3.9.4 | OSTALO | OTHER | 0
0
0 | NEPREDVIDENA DELA | UNFORSEEN WORKS | 0
| SKUPAJ ELEKTRO DELA | TOTAL ELECTRICAL WORKS | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT

## 3.9.1_JP
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.9 | ELEKTRO DELA | ELECTRICAL WORKS
3.9.1 | AKTIVNI SISTEMI PROTIPOŽARNE ZAŠČITE | ACTIVE FIRE PROTECTION SYSTEMS | [5 empty] | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description |  |  | EM | Količina | Cena/EM | Cena
1 | AKTIVNI SISTEMI PROTIPOŽARNE ZAŠČITE | ACTIVE FIRE PROTECTION SYSTEMS
1.1 | Dobava in montaža modularne adresne centralne naprave v oznaki CJP-1 kot naprimer: SINTESO FC2060-AA, SIEMENS, dobava modulov za 6x FDnet adresni zanki, max.1512 adresnih elementov. Možnost povezave centralne naprave v mrežo central FCnet. Spomin za 2000 dogodkov. Ethernet priključek RJ45. Možnost oddaljenega dostopa in upravljanja sistema preko Ethernet mreže. Integracija na varnostne nadzorne sisteme preko BACnet protokola. Centrala vsebuje še naslednje module: | Supply and installation of a modular address control panel in the CJP-1 designation, e.g. SINTESO FC2060-AA, SIEMENS, supply of modules for 6x FDnet address loops, max 1512 address elements. Possibility of connecting the control panel to the FCnet network. Memory for 2000 events. Ethernet RJ45 connector. Possibility of remote access and management of the system via the Ethernet network. Integration into security monitoring systems via the BACnet protocol. The control panel also contains the following modules: |  |  | kpl | 1 |  | 0
| - upravljalna prikazovalna enota ( grafični LCD display z 8 vrsticami ) | - control display unit ( graphic LCD display with 8 lines ) | kos | 1
| - napajalnik 24V/150W, FP2005-A1 | - power supply 24V/150W, FP2005-A1 | kos | 1
| - linijska kartica ( FDnet ), FCL2001-A1 | - line card ( FDnet ), FCL2001-A1 | kos | 5
| - komunikacijski vmesnik SAFEDLINK, FN2001-A1, | - sAFEDLINK communication interface, FN2001-A1, | kos | 1
| - akumulatorska baterija ( 2x12V/45Ah ), FA2007-A1, | - rechargeable battery ( 2x12V/45Ah ), FA2007-A1, | kos | 1
| - dodatno ohišje za akumulatorsko baterijo, FH2004-A1, | - additional battery case, FH2004-A1, | kos | 1
| - akumulatorska baterija v dodatnem ohišju ( 2x12V/65Ah ), FA2008-A1, | - rechargeable battery in additional housing ( 2x12V/65Ah ), FA2008-A1, | kos | 1
| - licenčni ključ, S2 | - licence key, S2 | kos | 1
| - priključitev centrale na napajanje. | - connecting the control panel to the power supply. | kos | 1
| - Ethernet switch, kot naprimer: FN2012-A1, skupaj z modulom za SM optično povezavo, kot naprimer: VN2003-A1 | - Ethernet switch, e.g. FN2012-A1, together with an SM fibre module, e.g. VN2003-A1 | kos | 1
| - Montažni komplet za Ethernet switch, kot naprimer: FHA2029-A1 | - Mounting kit for Ethernet switch, e.g. FHA2029-A1 | kos | 1
| Namestiti je potrebno vse potrebne module, da bo centrala delovala kot celota, Akumulatorska baterija mora zagotavljat 72 urno delovanje sistema in 0,5 ure pod obremenitvijo (alarmno stanje). | All the necessary modules must be installed for the control panel to work as a complete unit, The battery must provide 72 hours of system operation and 0.5 hours under load (alarm state).
1.2 | Dobava in montaža modularne adresne centralne naprave v oznaki CJP-2 kot naprimer: SINTESO FC2060-AA, SIEMENS, dobava modulov za 6x FDnet adresni zanki, max.1512 adresnih elementov. Možnost povezave centralne naprave v mrežo central FCnet. Spomin za 2000 dogodkov. Ethernet priključek RJ45. Možnost oddaljenega dostopa in upravljanja sistema preko Ethernet mreže. Integracija na varnostne nadzorne sisteme preko BACnet protokola. Centrala vsebuje še naslednje module: | Supply and installation of a modular address control panel in the CJP-2 designation, e.g. SINTESO FC2060-AA, SIEMENS, supply of modules for 6x FDnet address loops, max 1512 address elements. Possibility of connecting the control panel to the FCnet network. Memory for 2000 events. Ethernet RJ45 connector. Possibility of remote access and management of the system via the Ethernet network. Integration into security monitoring systems via the BACnet protocol. The control panel also contains the following modules: |  |  | kpl | 1 |  | 0
| - upravljalna prikazovalna enota ( grafični LCD display z 8 vrsticami ) | - control display unit ( graphic LCD display with 8 lines ) | kos | 1
| - napajalnik 24V/150W, FP2005-A1 | - power supply 24V/150W, FP2005-A1 | kos | 1
| - linijska kartica ( FDnet ), FCL2001-A1 | - line card ( FDnet ), FCL2001-A1 | kos | 5
| - akumulatorska baterija ( 2x12V/45Ah ), FA2007-A1, | - rechargeable battery ( 2x12V/45Ah ), FA2007-A1, | kos | 1
| - dodatno ohišje za akumulatorsko baterijo, FH2004-A1, | - additional battery case, FH2004-A1, | kos | 1
| - akumulatorska baterija v dodatnem ohišju ( 2x12V/65Ah ), FA2008-A1, | - rechargeable battery in additional housing ( 2x12V/65Ah ), FA2008-A1, | kos | 1
| - licenčni ključ, S2 | - licence key, S2 | kos | 1
| - priključitev centrale na napajanje. | - connecting the control panel to the power supply. | kos | 1
| - Ethernet switch, kot naprimer: FN2012-A1, skupaj z modulom za SM optično povezavo, kot naprimer: VN2003-A1 | - Ethernet switch, e.g. FN2012-A1, together with an SM fibre module, e.g. VN2003-A1 | kos | 1
| - Montažni komplet za Ethernet switch, kot naprimer: FHA2029-A1 | - Mounting kit for Ethernet switch, e.g. FHA2029-A1 | kos | 1
| Namestiti je potrebno vse potrebne module, da bo centrala delovala kot celota, Akumulatorska baterija mora zagotavljat 72 urno delovanje sistema in 0,5 ure pod obremenitvijo (alarmno stanje). | All the necessary modules must be installed for the control panel to work as a complete unit, The battery must provide 72 hours of system operation and 0.5 hours under load (alarm state).
1.3 | Dobava in montaža posluževalnega terminala v TSV vratarnica v oznaki TBL1, kot naprimer: FT2040, SIEMENS, za upravljanje in nadzor posamezne centralne naprave ali celotnega sistema. Možnost povezave v mrežo FCnet. Ethernet priključek. S posluževalnim terminalom se dobavi in vgradi naslednja oprema: | Supply and installation of a listening terminal in a TSV door control room with the TBL1 code, e.g. FT2040, SIEMENS, for the management and control of a single central device or the entire system. Possibility of connection to the FCnet network. Ethernet connection. The following equipment is supplied and installed with the listening terminal: |  |  | kpl | 1 |  | 0
| - upravljalna prikazovalna enota ( grafični LCD display z 8 vrsticami ) | - control display unit ( graphic LCD display with 8 lines ) | kos | 1
| - akumulatorska baterija ( 2x12V/7Ah ) | - rechargeable battery ( 2x12V/7Ah ) | kos | 1
| - prazno eko ohišje v velikosti posluževalnega terminala, kot napprimer OH-BFFH2001-A1, dimenzij 430 x 398 x 80mm | - empty eco-enclosure in the size of a business terminal, e.g. OH-BFFH2001-A1, dimensions 430 x 398 x 80mm | kos | 1
| - priključitev centrale na napajanje prek centrale CJP-2 | - connecting the control panel to the power supply via the CJP-2 control panel | kos | 1
| - Ethernet switch, kot naprimer: FN2012-A1, skupaj z modulom za SM optično povezavo, kot naprimer: VN2003-A1 | - Ethernet switch, e.g. FN2012-A1, together with an SM fibre module, e.g. VN2003-A1 | kos | 1
| - Montažni komplet za Ethernet switch, kot naprimer: FHA2029-A1 | - Mounting kit for Ethernet switch, e.g. FHA2029-A1 | kos | 1
| Namestiti je potrebno vse potrebne module, da bo centrala delovala kot celota, Akumulatorska baterija mora zagotavljat 72 urno delovanje sistema in 0,5 ure pod obremenitvijo (alarmno stanje). | All the necessary modules must be installed for the control panel to work as a complete unit, The battery must provide 72 hours of system operation and 0.5 hours under load (alarm state).
1.4 | Dobava in montaža modularne adresne centralne naprave v oznaki CJP-CO kot naprimer: SINTESO FC2020-AA, SIEMENS. V centralu javljanja požara se dobavi in vgradi naslednja oprema: | Supply and installation of a modular address control panel in the CJP-CO code, e.g. SINTESO FC2020-AA, SIEMENS. The following equipment shall be supplied and installed in the fire alarm control panel: |  |  | kpl | 1 |  | 0
| - upravljalna prikazovalna enota ( grafični LCD display z 8 vrsticami ) | - control display unit ( graphic LCD display with 8 lines ) | kos | 1
| - napajalnik 24V/150W, FP2004-A1 | - power supply 24V/150W, FP2004-A1 | kos | 1
| - akumulatorska baterija ( 2x12V/25Ah ), | - rechargeable battery ( 2x12V/25Ah ), | kos | 1
| - dodatno ohišje za akumulatorsko baterijo, FH2004-A1 | - additional battery case, FH2004-A1 | kos | 1
| - akumulatorska baterija v dodatnem ohišju ( 2x12V/17Ah ), | - rechargeable battery in additional housing ( 2x12V/17Ah ), | kos | 1
| - licenčni ključ, S2 | - licence key, S2 | kos | 1
| - priključitev centrale na napajanje. | - connecting the control panel to the power supply. | kos | 1
| - Ethernet switch, kot naprimer: FN2012-A1, skupaj z modulom za SM optično povezavo, kot naprimer: VN2003-A1 | - Ethernet switch, e.g. FN2012-A1, together with an SM fibre module, e.g. VN2003-A1 | kos | 1
| - Montažni komplet za Ethernet switch, kot naprimer: FHA2029-A1 | - Mounting kit for Ethernet switch, e.g. FHA2029-A1 | kos | 1
| Namestiti je potrebno vse potrebne module, da bo centrala delovala kot celota, Akumulatorska baterija mora zagotavljat 72 urno delovanje sistema in 0,5 ure pod obremenitvijo (alarmno stanje). | All the necessary modules must be installed for the control panel to work as a complete unit, The battery must provide 72 hours of system operation and 0.5 hours under load (alarm state).
1.5 | Dobava in montaža modularne adresne centralne naprave v oznaki CJP-šprinkler kot naprimer: SINTESO FC2020-AA, SIEMENS. V centralu javljanja požara se dobavi in vgradi naslednja oprema: | Supply and installation of a modular addressable control panel in the CJP-Sprinkler code, e.g. SINTESO FC2020-AA, SIEMENS. The following equipment shall be supplied and installed in the fire alarm control panel: |  |  | kpl | 1 |  | 0
| - upravljalna prikazovalna enota ( grafični LCD display z 8 vrsticami ) | - control display unit ( graphic LCD display with 8 lines ) | kos | 1
| - napajalnik 24V/150W, FP2004-A1 | - power supply 24V/150W, FP2004-A1 | kos | 1
| - akumulatorska baterija ( 2x12V/25Ah ), | - rechargeable battery ( 2x12V/25Ah ), | kos | 1
| - dodatno ohišje za akumulatorsko baterijo, FH2004-A1 | - additional battery case, FH2004-A1 | kos | 1
| - akumulatorska baterija v dodatnem ohišju ( 2x12V/17Ah ), | - rechargeable battery in additional housing ( 2x12V/17Ah ), | kos | 1
| - licenčni ključ, S2 | - licence key, S2 | kos | 1
| - priključitev centrale na napajanje. | - connecting the control panel to the power supply. | kos | 1
| - Ethernet switch, kot naprimer: FN2012-A1, skupaj z modulom za SM optično povezavo, kot naprimer: VN2003-A1 | - Ethernet switch, e.g. FN2012-A1, together with an SM fibre module, e.g. VN2003-A1 | kos | 1
| - Montažni komplet za Ethernet switch, kot naprimer: FHA2029-A1 | - Mounting kit for Ethernet switch, e.g. FHA2029-A1 | kos | 1
| Namestiti je potrebno vse potrebne module, da bo centrala delovala kot celota, Akumulatorska baterija mora zagotavljat 72 urno delovanje sistema in 0,5 ure pod obremenitvijo (alarmno stanje). | All the necessary modules must be installed for the control panel to work as a complete unit, The battery must provide 72 hours of system operation and 0.5 hours under load (alarm state).
1.6 | 'Dobava in montaža adresabilnega kombiniranega termično / optičnega javljalnika dima z vgrajeno ASA tehnologijo, kot naprimer: FDOOT241-A, vgrajen izolator zanke, komplet z vso potrebno dodatno opremo (podnožje FDB221 in FDB291, (nastavitev za običajno okolje), tesnila, napisna ploščico FDBZ291, montažni in inštalacijski material, ...). Sinteso S-LINE, Siemens. | Supply and installation of an addressable combined thermal/optical smoke detector with integrated ASA technology, such as FDOOT241-A, integrated loop isolator, complete with all necessary accessories (base FDB221 and FDB291, (setup for normal environment), gaskets, nameplate FDBZ291, mounting and installation material, ...). Sinteso S-LINE, Siemens. |  |  | kos | 1530 |  | 0
1.7 | Dobava in montaža adresabilnega ročnega javljalnika požara, kot naprimer FDM223, rdeče barve, komplet z luminiscenčno ploščo z napisom '' ROČNI JAVLJALNIK'' in vso potrebno dodatno opremo (elektronika javljalnika FDME223, ohišje FDMH293-R, zaščita DMZ1197-AC, montažni in inštalacijski material, ...). Sinteso, Siemens. | Supply and installation of an addressable manual fire detector, such as the FDM223, red, complete with luminescent panel with the inscription ''HAND HAND HAND DETECTOR'' and all necessary accessories (detector electronics FDME223, housing FDMH293-R, protection DMZ1197-AC, mounting and installation material, etc.). Sinteso, Siemens. |  |  | kos | 105 |  | 0
1.8 | Dobava in montaža adresabilnega kombiniranega termično/optičnega javljalnika dima z vgrajeno ASA tehnologijo, kot naprimer: FDOOT241-A na skupno kombinirano podnožje s sireno FDSB291, napisno ploščico FDBZ291, komplet z vso potrebno dodatno opremo. Sinteso, Siemens. | Supply and installation of an addressable combined thermal/optical smoke alarm with ASA technology, such as FDOOT241-A on a common combined base with siren FDSB291, nameplate FDBZ291, complete with all necessary accessories. Sinteso, Siemens. |  |  | kos | 165 |  | 0
1.9 | Dobava in montaža adresebilne alarmne sirene rdeče barve z bliskavko rdeče barve, kot naprimer Siemens Sinteso FDS226-RR, IP65, s dozo FDB227-R. | Supply and installation of a red addressable alarm siren with red flash, such as Siemens Sinteso FDS226-RR, IP65, with FDB227-R dock. |  |  | kos | 45 |  | 0
1.10 | Dobava in montaža adresebilne alarmne sirene rdeče barve, kot naprimer Siemens Sinteso FDS226-R, povezava v FD net s podnožjem FDB226-R in luminiscenčno ploščo z napisom ''SIRENA'' izdelana skladno s SIST 1013 | Supply and installation of a red-coloured addressable alarm siren, such as Siemens Sinteso FDS226-R, connection to the FD net with FDB226-R base and luminescent panel with the word "SIRENA", manufactured in accordance with SIST 1013 |  |  | kos | 115 |  | 0
1.11 | Dobava in montaža vhodno/izhodnega modula, kot naprimer Siemens Sinteso, FDCIO222, (4x vhod+4x izhod), 4x relejski izhod, 4x vhod za brezpotencialni kontakt, komunikacija FDnet, napajanje preko komunikacije z ohišjem FDCH221. | Supply and installation of I/O module, such as Siemens Sinteso, FDCIO222, (4x input+4x output), 4x relay output, 4x potential-free contact input, FDnet communication, power supply via communication with FDCH221 housing. |  |  | kos | 127 |  | 0
1.12 | Dobava in montaža vhodno/izhodnega modula, kot naprimer Siemens Sinteso, FDCIO221, (1x vhod+1xizhod), komunikacija FDnet, napajanje preko komunikacije z ohišjem FDCH221. | Supply and installation of an I/O module, such as Siemens Sinteso, FDCIO221, (1x input+1xoutput), FDnet communication, power supply via communication with FDCH221 housing. |  |  | kos | 109 |  | 0
1.13 | Dobava in montaža vhodnega modula, kot naprimer Siemens Sinteso, FDCI222, (4x vhod), komunikacija FDnet, napajanje preko komunikacije z ohišjem FDCH221. | Supply and installation of an input module, such as Siemens Sinteso, FDCI222, (4x input), FDnet communication, power supply via communication with FDCH221 housing. |  |  | kos | 8 |  | 0
1.14 | Dobava in montaža detektorja zemeljskega plina (prisotnost plina) kot na primer CH4-I Tevel, ter relejskega vmesnika za omenjeni detektor za signalizacijo prisotnosti plina preko adresnega vmesnika na centralo javljanja požara, 25V DC. Z vso potrebno dodatno opremo (montažni in inštalacijski material, ...). | Supply and installation of a natural gas detector (presence of gas), such as CH4-I Tevel, and a relay interface for the detector to signal the presence of gas via an address interface to the fire alarm control panel, 25V DC. With all necessary accessories (mounting and installation materials, etc.). |  |  | kos | 4 |  | 0
1.15 | 'Dobava in montaža adresabilnega kombiniranega termično / optičnega javljalnika dima z vgrajeno ASA tehnologijo v spuščenem stropu, kot naprimer: FDOOT241-A, vgrajen izolator zanke, komplet z vso potrebno dodatno opremo (podnožje FDB221 in FDB291, (nastavitev za običajno okolje), tesnila, napisna ploščico FDBZ291, montažni in inštalacijski material, ...). Sinteso S-LINE, Siemens. | Supply and installation of an addressable combined thermal/optical smoke detector with integrated ASA technology in a dropped ceiling, such as FDOOT241-A, integrated loop isolator, complete with all necessary accessories (base FDB221 and FDB291, (setup for normal environment), gaskets, nameplate FDBZ291, mounting and installation material, ...). Sinteso S-LINE, Siemens. |  |  | kos | 80 |  | 0
1.16 | Dobava in montaža paralelnega svetlobnega indikatorja, kot naprimer: FDAI92 za javljalnike v spuščenem stropu, komplet z vso potrebno dodatno opremo (podnožje, napisna ploščica, tesnila, montažni in inštalacijski material, ...)..Sinteso, Siemens.. | Supply and installation of a parallel light indicator, such as the FDAI92 for beacons in dropped ceilings, complete with all necessary accessories (base, nameplate, gaskets, mounting and installation materials, ...)... Sinteso, Siemens... |  |  | kos | 80 |  | 0
1.17 | Dobava in montaža adresabilnega CO javljalnika kot naprimer FDOOTC241 z vgrajeno ASA tehnologijo, komplet z vso potrebno dodatno opremo (podnožje FDB221 (nastavitev za običajno okolje), tesnila, montažni in inštalacijski material, ...). Sinteso S-LINE, Siemens. | Supply and installation of an addressable CO detector such as the FDOOTC241 with integrated ASA technology, complete with all necessary accessories (FDB221 base (setting for normal environment), seals, mounting and installation materials, etc.). Sinteso S-LINE, Siemens. |  |  | kos | 55 |  | 0
1.18 | Dobava in montaža dvostranskega svetlobnega tabloja z vgrajeno piskavko, dimenzij 320x140x95mm, IP40. Svetlobni tablo predviden za montažo na nosilno vrvico v kleti in medetaži. Kot naprimer: AVD FJ/BF | Supply and installation of a double-sided light board with integrated beeper, dimensions 320x140x95mm, IP40. The light board is intended for mounting on a support cord in the basement and mezzanine. For example: AVD FJ/BF |  |  | kos | 55 |  | 0
1.19 | Dobava in montaža adresabilnega kombiniranega javljalnika požara kot naprimer FDOOT241-A z vgrajeno ASA tehnologijo in vzorčno komoro FDBZ290, komplet z vso potrebno dodatno opremo (podnožje FDB222, cevjo 600mm FDBZ290-AA, tesnila, montažni in inštalacijski material, ...). Sinteso C-LINE, Siemens. | Supply and installation of an addressable combined fire detector such as FDOOT241-A with ASA technology and FDBZ290 sample chamber, complete with all necessary accessories (FDB222 base, 600mm FDBZ290-AA hose, seals, mounting and installation materials, etc.). Sinteso C-LINE, Siemens. |  |  | kos | 45 |  | 0
1.20 | Dobava in montaža adresabilnega termično/optičnega javljalnika za EX okolje z vgrajeno ASA tehnologijo in vgrajenim izolatorjem zanke; ima vgrajen dvojni optični, dvojni termični senzor, povezava preko FDnet EX line galvanskega ločilnika ; primeren za Ex cone: Gas 1 in 2, kot naprimer: FDOOT241-A-Ex, komplet z vso potrebno dodatno opremo (podnožjem FDB291, dodatnim podnožjem FDB221, napisna ploščico FDBZ291 montažni in inštalacijski material, ...). Sinteso, Siemens. | Supply and installation of an addressable thermal/optical alarm device for EX environment with integrated ASA technology and integrated loop isolator; has integrated double optical, double thermal sensor, connection via FDnet EX line galvanic isolator ; suitable for Ex zones: Gas 1 and 2, such as FDOOT241-A-Ex, complete with all necessary accessories (FDB291 base, additional FDB221 base, FDBZ291 nameplate, mounting and installation material, ...). Sinteso, Siemens. |  |  | kos | 4 |  | 0
1.21 | Dobava in montaža varnostnega galvanskega ločilnika za EX okolje (barijere), za povezavo preko FDne/C-NET adresne zanke, deluje na stub liniji ali adresni zanki, LED indikatorji, kot naprimer: FDCL221-Ex, Siemens, komplet z vso potrebno dodatno opremo: (ohišjem FDCH222, nosilna letev TS35_122 in uvodnico M20-Exi, napisna ploščico FDBZ291, ter z montažnim in inštalacijskim materialom, ...). Sinteso, Siemens. | Supply and installation of a safety galvanic isolator for EX environment (barrier), for connection via FDne/C-NET address loop, operating on a stub line or address loop, LED indicators, such as FDCL221-Ex, Siemens, complete with all necessary accessories: (FDCH222 housing, TS35_122 support rail and M20-Exi grommet, FDBZ291 nameplate, as well as mounting and installation materials, ...). Sinteso, Siemens. |  |  | kos | 2 |  | 0
1.22 | Električni prijemnik vrat | Electric door closer |  |  | kos | 9 |  | 0
1.23 | Dobava in montaža kamer za detekcijo požara kot naprimer FDV202, komplet z vso potrebno dodatno opremo (nosilec…). Sinteso, Siemens. | Supply and installation of fire detection cameras such as FDV202, complete with all necessary accessories (bracket...). Sinteso, Siemens. |  |  | kos | 4 |  | 0
1.24 | Priključna vodotesna doza IP67, kot naprimer: Protectowire ZB-4-QC-MP. Vodotesna doza za priključitev termičnega kabla na vmesnik, komplet z uvodnicami in sponkami | IP67 watertight dock connector, e.g. Protectowire ZB-4-QC-MP. Watertight dock for connecting a thermal cable to an interface, complete with glands and clips |  |  | kos | 1 |  | 0
1.25 | Zaključna vodotesna doza IP67, kot naprimer: Protectowire ZB-4-QC-MP. vodotesna doza za zaključek termičnega kabla z zaključnim uporom, komplet z uvodnico, sponkami in uporom. | IP67 watertight dock termination, e.g. Protectowire ZB-4-QC-MP. watertight thermocouple termination dock with termination resistor, complete with gland, clips and resistor. |  |  | kos | 1 |  | 0
1.26 | Dobava in polaganje ognje-odpornih kablov tipa JE-H(St)H Bd FE180/E30, rdeče barve, na kabelske police in v zaščitne cevi. certifikat o ustreznostie (kabel mora biti posebej namenjen za javljanje požara). Kot naprimer (LAPPKABEL, alternativa (enakovredne tehnične lastnosti) TKD, Helukabel) | Supply and installation of fire-resistant cables type JE-H(St)H Bd FE180/E30, red, on cable racks and in protective tubes. Certificate of suitability (the cable must be specifically designed for fire alarm). As for example (LAPPKABEL, alternative (equivalent technical characteristics) TKD, Helukabel)
| JE-H(St)H Bd 1x2x0,8 mm FE180/E30 - rdeče barve | JE-H(St)H Bd 1x2x0,8 mm FE180/E30 - red |  |  | m | 27000 |  | 0
| JE-H(St)H Bd 2x2x0,8 mm FE180/E30 - rdeče barve | JE-H(St)H Bd 2x2x0,8 mm FE180/E30 - red |  |  | m | 3500 |  | 0
1.27 | Dobava in polaganje ognje-odpornih napajlnih kablov NHXH FE180/E30 na kabelske police in v zaščitne cevi. Pri polaganju mora biti uporabljen poseben pribor, ki je predviden za ognje-odporene kable (police, cevi, obešala, ...) in način polaganja, certifikat o ustreznosti. Kot naprimer (LAPPKABEL, alternativa (enakovredne tehnične lastnosti) TKD, Helukabel | Supply and installation of NHXH FE180/E30 flame-resistant power cables on cable racks and in protective tubes. The installation must be carried out using the specific accessories provided for flame-resistant cables (racks, tubes, hangers, etc.) and the method of installation, certificate of suitability. For example (LAPPKABEL, alternative (equivalent technical characteristics) TKD, Helukabel)
| NHXH-J 3x1,5 mm2 FE180/E30 | NHXH-J 3x1,5 mm2 FE180/E30 |  |  | m | 500 |  | 0
| NHXH-O 2x2,5 mm2 FE180/E30 | NHXH-O 2x2,5 mm2 FE180/E30 |  |  | m | 100 |  | 0
1.28 | Termični detekcijski kabel za namen hladilnice Protectowire, PHSC, izolacija, temperatura detekcije 57°C, največja priporočena temperatura prostora 38°C. | Thermal detection cable for Protectowire refrigeration, PHSC, insulation, detection temperature 57°C, maximum recommended ambient temperature 38°C.
| - PHSC-135-XLT (57°C), kot na primer: Protectowire | - PHSC-135-XLT (57°C), such as Protectowire |  |  | m | 4 |  | 0
| - Pritrdilni element za temperaturne kable, razmik 1,5m, kot na primer: JD-1, Protectowire | - Fixing element for temperature cables, spacing 1.5 m, e.g. JD-1, Protectowire |  |  | kos | 2 |  | 0
1.29 | Sistem SB-ES, BETAfixss, E30/E90, razmik med objemkami < 800mm. Ob montaži upoštevati navodila proizvajalca: | System SB-ES, BETAfixss, E30/E90, clamp spacing < 800mm. Follow manufacturer's instructions for installation:
| ESM 6-8 M6 enostavna objemka | ESM 6-8 M6 single clamp |  |  | kos | 31000 |  | 0
| zidni vložek FNA M6x45 | fNA wall insert M6x45 |  |  | kos | 31000 |  | 0
1.30 | Dobava in montaža ognjevarnih kabelskih polic kot naprimer: BAKS E90, skupaj s obešalnim priborom, objemkami za kable, koleni, s pokrovi, spojnim materialom in višinskimi prehodi | Supply and installation of fire-resistant cable racks, e.g. BAKS E90, including hanging accessories, cable clamps, elbows, covers, fasteners and height transitions
| 50/60 mm (KFL50H60/3) | 50/60 mm (KFL50H60/3) |  |  | m | 400 |  | 0
1.31 | Dobava in montaža zaščitnih ognjevarnih cevi za zaščito kablov, skupaj s priborom po standardu DIN 4102-12: | Supply and installation of fire-resistant protective hoses for cable protection, including accessories according to DIN 4102-12:
| ognjevarne zaščitne cevi fi 16 mm z objemkami, po standardu DIN 4102-12 oz. TSG. | fire-resistant protective tubes 16 mm fi with clamps, according to DIN 4102-12 or TSG. |  |  | m | 5500 |  | 0
| ognjevarne zaščitne cevi fi 23 mm z objemkami, po standardu DIN 4102-12 oz. TSG. | 23 mm fire-resistant protective tubes with clamps, according to DIN 4102-12 or TSG. |  |  | m | 1800 |  | 0
1.32 | Ozemljitve in izenačevanje potencialov: dobava in polaganje Cu vrvi za ozemljitev kabelskih polic, itd. | Earthing and equipotential bonding: supply and installation of Cu ropes for earthing of cable racks, etc.
| - Cu vrv 16 mm2 | - Cu rope 16 mm2 |  |  | m | 60 |  | 0
1.33 | Izvedba povezave požarne centrale preko adresnih vmesnikov na šprinkler sistem v objektu (kontrolo pretoka, stanje ventilov, ...). | Connection of the fire panel to the sprinkler system in the building via address interfaces (flow control, valve status, etc.). |  |  | kos | 125 |  | 0
1.34 | Izvedba povezave požarne centrale preko adresnih vmesnikov na dvigala (požarno krmiljenje dvigal) | Connection of fire panels via address interfaces to lifts (fire control of lifts) |  |  | kos | 9 |  | 0
1.35 | Izvedba povezave protipožarnih loput preko adresnega vmesnika na požarno centralo ter izvedba požarnega krmiljenja. | Connection of fire dampers via address interface to the fire panel and fire control. |  |  | kos | 250 |  | 0
1.36 | Povezava krmilnikov klimata preko adresnega vmesnika na požarno centralo ter izvedba krmiljenja v primeru požara. | Connecting the climate controllers via the address interface to the fire panel and implementing the control in case of fire. |  |  | kos | 16 |  | 0
1.37 | Izvedba povezave požarne centrale preko adresnih vmesnikov na enoto za upravljanje kupol za odvod dima in toplote. | Connection of the fire panel via address interfaces to the smoke and heat dome management unit. |  |  | kos | 5 |  | 0
1.38 | Izvedba povezave požarne centrale preko adresnih vmesnikov na sisteme evakuacijskega ozvočenja. | Connection of the fire panel to the evacuation public address systems via address interfaces. |  |  | kos | 10 |  | 0
1.39 | Izvedba povezave požarne centrale preko adresnih vmesnikov na glavno omaro zasilne razsvetljave. | Connection of the fire panel via address interfaces to the main emergency lighting cabinet. |  |  | kos | 1 |  | 0
1.40 | Izvedba povezave požarne centrale preko adresnih vmesnikov na kamere za detekcijo požara | Connecting the fire panel to the fire detection cameras via address interfaces |  |  | kos | 4 |  | 0
1.41 | Dobava in namestitev programske aplikacije MM8000 za upravljanje sistemov javljanje požara in varnostnih sistemov na PC komplet z licencami. Integracija central CJP-1, CJP-2, CJP-CO in CJP-šprinkler na glavni nadzorni računalnik: | Supply and installation of the MM8000 software application for the management of fire alarm and security systems on a PC complete with licences. Integration of the CJP-1, CJP-2, CJP-CO and CJP-Sprinkler control panels on the main control computer: |  |  | kpl | 1 |  | 0
| - izdelava grafičnega nadzornega sistema (GNC) na lokaciji, finalno parametriranje, testiranje sistema; | - development of the on-site graphical control system (GNC), final parameterisation, testing of the system; | kos | 1
| - vnos tlorisov v GNC (Acad), prilagoditev velikosti Acad-ovih tlorisov na resolucijo GNC-ja, monitorja in vnos v grafični del SCADA; | - input of floor plans into GNC (Acad), adjustment of the size of Acad floor plans to the resolution of GNC, monitor and input into the graphic part of SCADA; | št. tlorisov | 7
| - Vnos točk v GNC (javljalniki, vmesniki, itd). Prenos podatkov iz konfiguracijske datoteke požarne centrale na grafične podlage za GNC, ki vključuje: -razdelitev javljalnikov in adresnih vmesnikov po posameznih etažah, -določitev atributov vsakega javljalnika posebej, ki omogočajo ustrezno barvanje za ponazoritev stanja točke (rdeča, rumena, oranžna, zelena, modra) v odvisnosti od dogodka, ki ga vsaka točka lahko generira (alarm, izklop, napaka, normalno stanje, nealarmni dogodek), -določitev in vnos tekstovnih in številčnih oznak za vsak prikazan javljalnik ali adresni vmesnik, -natančno razporeditev javljalnikov in vmesnikov po posameznih prostorih na grafičnem tlorisu, -vnos vseh nadzornih elementov ( požarne lopute, PP vrata, kupole, klima naprave, AMS in RMS...), -postavitev ukaznih gumbov za pošiljanje ukazov v požarni sistem za omogočanje upravljanja, -definiranje klientov in njihov dostop do baze dogodkov. | - GNC entry points (beacons, interfaces, etc.). Transfer of data from the fire panel configuration file to the GNC graphics, including: -the distribution of beacons and address interfaces on each floor, -defining attributes for each beacon separately, allowing the appropriate colouring to represent the state of the point (red, yellow, orange, green, blue) depending on the event that each point can generate (alarm, trip, fault, normal, non-alarm event), -define and enter text and numeric codes for each displayed annunciator or address interface, -the precise arrangement of beacons and interfaces in each room on the graphical floor plan, -input of all control elements ( fire dampers, PP doors, domes, air conditioning, AMS and RMS...), -setting up command buttons to send commands to the fire system to enable management, -defining clients and their access to the event database. | kos | 2536
| Detajlno konfiguracijo grafičnega nadzornega sistema je potrebno uskladiti z zahtevami investirorja in študije požarne varnosti, pri tem je potrebno upoštavati, da mora sistem javljanja požara funkcionalno in varno delovati. | The detailed configuration of the graphic control system must be coordinated with the investor's requirements and the fire safety study, bearing in mind that the fire detection system must be functional and safe.
1.42 | Integracija centrale stabilne gasilne naprave na GNC javljanje požara. Komplet z vsemi potrebnimi vmesniki (MODBUS) in integratorjem. | Integration of the Stable Fire Extinguisher Control Panel into the GNC fire alarm system. Complete with all necessary interfaces (MODBUS) and integrator. |  |  | kpl | 1 |  | 0
1.43 | Dobava in polaganje izolacijskih cevi in inšalacijskih kanalov: | Supply and installation of insulation pipes and ducts:
| Trde izolacijske cevi fi 13,5-29, PN, komplet z obešalnim priborom. | Rigid insulation pipes fi 13,5-29, PN, complete with hanger fittings. |  |  | m | 4000 |  | 0
| Gibljive zaščitne cevi fi 16-48, RBT, | Flexible protection tubes fi 16-48, RBT, |  |  | m | 3000 |  | 0
1.44 | Dobava in polaganje optičnega kabla od glavne centrale javljanja požara CJP-1 do centrale javljanja požara CJP-2 | Supply and installation of fibre optic cable from the main fire panel CJP-1 to the fire panel CJP-2 |  |  | m | 2 |  | 0
| - optični kabel FO SM (4 vlaken), 9/125um OS1, kot naprimer: Leviton | - fO SM (4 fibre), 9/125um OS1 fibre optic cable, e.g. Leviton
1.45 | Dobava in polaganje optičnega kabla od centrale javljanja požara CJP-2 do prikazovalnega terminala TBL1 | Supply and installation of a fibre optic cable from the fire alarm control panel CJP-2 to the display terminal TBL1 |  |  | m | 20 |  | 0
| - optični kabel FO SM (4 vlaken), 9/125um OS1, kot naprimer: Leviton | - fO SM (4 fibre), 9/125um OS1 fibre optic cable, e.g. Leviton
1.46 | Dobava in polaganje optičnega kabla od prikazovalnega terminala TBL1 do centrale javljanja plina CO CJP-CO | Supply and installation of a fibre optic cable from the TBL1 display terminal to the CO CJP-CO gas reporting control panel |  |  | m | 120 |  | 0
| - optični kabel FO SM (4 vlaken), 9/125um OS1, kot naprimer: Leviton | - fO SM (4 fibre), 9/125um OS1 fibre optic cable, e.g. Leviton
1.47 | Dobava in polaganje optičnega kabla od centrale javljanja plina CO do centrale javljanja požara za šprinkler CJP-šprinkler | Supply and installation of a fibre optic cable from the CO gas alarm control panel to the fire alarm control panel for the CJP sprinkler system |  |  | m | 140 |  | 0
| - optični kabel FO SM (4 vlaken), 9/125um OS1, kot naprimer: Leviton | - fO SM (4 fibre), 9/125um OS1 fibre optic cable, e.g. Leviton
1.48 | Dobava in polaganje optičnega kabla od centrale javljanja požara za šprinkler CJP-šprinkler do glavne centrale javljanja požara CJP-1 | Supply and installation of a fibre optic cable from the fire alarm control panel for the CJP sprinkler to the main fire alarm control panel CJP-1 |  |  | m | 170 |  | 0
| - optični kabel FO SM (4 vlaken), 9/125um OS1, kot naprimer: Leviton | - fO SM (4 fibre), 9/125um OS1 fibre optic cable, e.g. Leviton
1.49 | Izdelava povezav in naslednjih priključitev: | Making the connections and following connections: |  |  | kpl | 1 |  | 0
| - od glavne centrale javljanja požara CJP-1 do CJP-2 | - from the main fire panel CJP-1 to CJP-2
| - od CJP-2 do TBL1 | - cJP-2 to TBL1
| - od TBL1 do CJP-CO | - from TBL1 to CJP-CO
| - od CJP-CO do CJP-šprinkler | - from CJP-CO to CJP-Sprinkler
| - od CJP-šprinkler do CJP-1 | - from CJP-Sprinkler to CJP-1
1.50 | Programiranje požarne centrale | Programming the fire panel |  |  | kpl | 5 |  | 0
1.51 | Pregled sistema avtomatskega javljanja požara s strani pooblaščene inštitucije in sodelovanje serviserja pri pregledu in pridobitev pozitivnega potrdila pooblaščene inštitucije: | Inspection of the automatic fire detection system by an approved institution and participation of the technician in the inspection and obtaining a positive certificate from an approved institution: |  |  | kpl | 1 |  | 0
| - avtomatskega javljanja požara, | - automatic fire detection,
| - za delovanje strojniških naparav, vključno s požarnimi loputami in ostalimi napravami v okviru javljanja požara. | - for the operation of machinery installations, including fire dampers and other fire detection devices.
1.52 | Izobraževanje uporabnikov in vzdrževalcev | User and maintenance training |  |  | kpl | 1 |  | 0
| AKTIVNI SISTEMI PROTIPOŽARNE ZAŠČITE | ACTIVE FIRE PROTECTION SYSTEMS | [5 empty] | 0

## 3.9.2_ODT
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.9 | ELEKTRO DELA | ELECTRICAL WORKS
3.9.2 | ODVOD DIMA IN TOPLOTE | SMOKE AND HEAT EXTRACTION |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
2 | ODVOD DIMA IN TOPLOTE | SMOKE AND HEAT EXTRACTION
2.1 | Dobava in montaža comfort enote za upravljanje napajanja, 3.4A, za eno alarmno skupino in eno prezračevalno enoto.Barva: oranžna RAL 2011 Samodejno preklapljanje iz omrežja v baterijo. V nujnih primerih, z baterijo 24 V, je sistemska avtonomija zagotovljena vsaj 72 ur.Spredaj je nadzorna plošča za alarm:- gumb za ročno aktiviranje alarma, tipko za ponastavitev in LED indikacijo "alarm", "pri delu" in "napaka"- dva okrogla gumba za osvetljevanje motorja za "odprto" prezračevanje; "Close"Širina: 140 mm; Višina: 248 mm; Globina: 85 mm, kot naprimer GEZE THZ Šifra izdelka 140900. | Supply and installation of comfort power management unit, 3.4A, for one alarm group and one ventilation unit.Colour: orange RAL 2011 Automatic switchover from mains to battery. In case of emergency, with a 24 V battery, system autonomy is guaranteed for at least 72 hours.Front alarm control panel:- Manual alarm activation button, reset button and LED indication "alarm", "in operation" and "fault"- Two round buttons to illuminate the motor for "open" ventilation; "close "Width: 140 mm; Height: 248 mm; Depth: 85 mm, such as for example GEZE THZ Product code 140900. | kos | 5 |  | 0
2.2 | Dobava in montaža požarne tipke / tipkalo, kot naprimer GEZE FT- 4, 24V DC, VdS, Grey RAL 7035. Šifra izdelka 106382. | Supply and installation of fire push buttons / keyswitches, e.g. GEZE FT- 4, 24V DC, VdS, Grey RAL 7035. Product code 106382. | kpl | 10 |  | 0
2.3 | Dobava in montaža stikala za dnevno prezračevanje/ventilacijo, kot naprimer: GEZE LTA-24 AZ, funkcije odpiranja / zapiranja, z LED signalizacijo. Šifra izdelka 129393. | Supply and installation of day ventilation/ventilation switches, e.g. GEZE LTA-24 AZ, opening/closing function, with LED signalling. Product code 129393. | kos | 5 |  | 0
2.4 | Priklop ODT na vmesnik požarne centrale (Požar, napaka, alarm …). | Connecting the ODT to the fire panel interface (Fire, fault, alarm, etc.). | kos | 5 |  | 0
2.5 | Dobava in polaganje ognje-odpornih kablov tipa JE-H(St)H Bd FE180/E30, rdeče barve, halogen free, na kabelske police in v zaščitne cevi. Pri polaganju mora biti uporabljen poseben pribor, ki je predviden za ognje-odporene kable (police, cevi, obešala, ...) in način polaganja na kabelske police in v zaščitne cevi, certifikat o ustreznostie (kabel mora biti posebej namenjen za javljanje požara). | Supply and installation of fire-resistant cables type JE-H(St)H Bd FE180/E30, red, halogen free, on cable racks and in protective tubes. The installation must be carried out using the special accessories provided for fire-resistant cables (racks, hoses, hangers, etc.) and the method of installation on the cable racks and in the protective tubes must be certified (the cable must be specially designed for fire detection).
| JE-H(St)H 4x2x0,8 mm FE180/E30 - rdeče barve | JE-H(St)H 4x2x0,8 mm FE180/E30 - red | m | 250 |  | 0
2.6 | Dobava in polaganje ognje-odpornih napajlnih kablov N2XH FE180/E30 na kabelske police in v zaščitne cevi. Pri polaganju mora biti uporabljen poseben pribor, ki je predviden za ognje-odporene kable (police, cevi, obešala, ...) in način polaganja, certifikat o ustreznosti. Kabel se uporablja za napajanje centrale ODT ter za pogon kupole | Supply and installation of N2XH FE180/E30 flame-resistant power cables on cable racks and in protective tubes. The installation must be carried out using the special accessories provided for flame-resistant cables (racks, tubes, hangers, etc.) and the method of installation, certificate of suitability. The cable is used to power the ODT control panel and to drive the dome
| - NHXH-J 3x1,5 mm2 FE180/E30 | - NHXH-J 3x1,5 mm2 FE180/E30 | m | 150 |  | 0
| - NHXH-J 3x2,5 mm2 FE180/E30 | - NHXH-J 3x2,5 mm2 FE180/E30 | m | 75 |  | 0
2.7 | Sistem SB-ES, BETAfixss, E30/E90, razmik med objemkami < 800mm. Ob montaži upoštevati navodila proizvajalca: | System SB-ES, BETAfixss, E30/E90, clamp spacing < 800mm. Follow manufacturer's instructions for installation:
| - ESM 6-8 M6 enostavna objemka | - ESM 6-8 M6 single clamp | kos | 70 |  | 0
| - zidni vložek FNA M6x45 | - fNA wall insert M6x45 | kos | 70 |  | 0
2.8 | Dobava in polaganje izolacijskih cevi in inšalacijskih kanalov: | Supply and installation of insulation pipes and ducts:
| - Gibljive zaščitne cevi fi 13,5-23 mm, RBT, | - Flexible protection tubes fi 13,5-23 mm, RBT, | m | 150 |  | 0
2.9 | Pregled sistema odvoda dima in toplote s strani pooblaščene inštitucije in sodelovanje serviserja pri pregledu in pridobitev pozitivnega potrdila pooblaščene inštitucije: | Inspection of the smoke and heat extraction system by an approved institution and participation of the technician in the inspection and obtaining a positive certificate from an approved institution: | kpl | 1 |  | 0
| ODVOD DIMA IN TOPLOTE | SMOKE AND HEAT EXTRACTION |  |  |  | 0

## 3.9.3_JPLINA
Investitor: | UNIVERZA V LJUBLJANI | UNIVERZA V LJUBLJANI
Gradnja: | Fakulteta za strojništvo | Fakulteta za strojništvo
Objekt: | STAVBA FAKULTETE | STAVBA FAKULTETE
3.9 | ELEKTRO DELA | ELECTRICAL WORKS
3.9.3 | JAVLJANJE PLINA | GAS REPORTING | [5 empty] | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description |  |  | EM | Količina | Cena/EM | Cena
3 | JAVLJANJE PLINA | GAS REPORTING
3.1 | Dobava in montaža centrale javljana plinov +CJPL-P-1 v naslednjem sestavu: | Supply and installation of a gas control panel +CJPL-P-1 in the following configuration: |  |  | kpl | 1 |  | 0
| Dimenzije omare so: višina 2000 mm, širina 1000 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Omara ima dvokrilna vrata po celi višini spredaj, uvod kablov zgoraj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1000 mm and depth 400 mm. The whole cabinet stands on a base height of 200 mm. The cabinet has a full-height double-leaf door at the front, a cable entry at the top, a comfort handle and a key-operated double-hinged closure.
| OPOMBA: Na vratih se izvede odprtina za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira svetilka za razsvetljavo omare, servisna vtičnica in predal za dokumentacijo | NOTE: A ventilation opening shall be made in the door and air filters shall be fitted. A luminaire for cabinet lighting, a service socket and a drawer for documentation shall be installed inside the cabinet
| - ohišje iz jeklene pločevine v barvi RAL 7035, dimenzij (šxvxg) 1000x2000x400mm, podstavek višine 200mm, dvokrilna vrata, odpiranje vrat 120°, IP55, IK10, ročka za odpiranje, cilindrični vložek, torba za načrte A4, svetilka LED s stikalom, vtičnico in priključnim kablom, 230V, 50Hz, končno stikalo s povezovalnim kablom, termostat, ventilator s filtrom, vgrajen na zgornjem delu kovinskih vrat, priključni kabel, filterska rešetka vgrajena na spodnjem delu kovinskih vrat, vtičnica 230VAC/16A, 50Hz, L, N, PE za montažo na DIN letev, vtičnica 2xRJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omari. Uvod kablov zgoraj. Kot na primer omara PanelSeT SFN, tip: Nsysfn221060, Schneider. | - ohišje iz jeklene pločevine v barvi RAL 7035, dimenzij (šxvxg) 1000x2000x400mm, podstavek višine 200mm, dvokrilna vrata, odpiranje vrat 120°, IP55, IK10, ročka za odpiranje, cilindrični vložek, torba za načrte A4, svetilka LED s stikalom, vtičnico in priključnim kablom, 230V, 50Hz, končno stikalo s povezovalnim kablom, termostat, ventilator s filtrom, vgrajen na zgornjem delu kovinskih vrat, priključni kabel, filterska rešetka vgrajena na spodnjem delu kovinskih vrat, vtičnica 230VAC/16A, 50Hz, L, N, PE za montažo na DIN letev, vtičnica 2xRJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omari. Uvod kablov zgoraj. Such as the PanelSeT SFN cabinet, type: Nsysfn221060, Schneider. | kos | 1
| V omaro se vgradi naslednja elektro oprema: | The following electrical equipment shall be installed in the cabinet:
| - glavno stikalo za montažo na vrata omare (In=32A), Schneider | - main switch for mounting on cabinet doors (In=32A), Schneider | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 1
| - rdeča kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM4+ZBZ32, Schneider | - red LED signal lamp, Ø 22, 230 to 240 V, as for example type:XB4BVM4+ZBZ32, Schneider | kos | 2
| - oranžna kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM5+ZBZ32, Schneider | - orange complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM5+ZBZ32, Schneider | kos | 1
| - tipka za vgradnjo na ohišje omare, za kvintiranje alarma, s LED osvetlitvijo, rdeče barve, Ø 22, 24V, Schneider | - pushbutton for mounting on cabinet enclosure, for quintillating alarm, LED illuminated, red, Ø 22, 24V, Schneider | kos | 1
| - prenapetostni odvodnik DEHNguard, DG M TN 275, 2-polni, 20 kA, Class II; | - dEHNguard surge arrester, DG M TN 275, 2-pole, 20 kA, Class II; |  | 1
| '- enopolni inštalacijski odklopnik 4 A, C karakteristika, 15 kA, Schneider. | - Single pole circuit breaker 4 A, C characteristic, 15 kA, Schneider. | kos | 8
| '- enopolni inštalacijski odklopnik 6 A, C karakteristika, 15 kA, Schneider. | - Single pole circuit breaker 6 A, C characteristic, 15 kA, Schneider. | kos | 5
| '- enopolni inštalacijski odklopnik 10 A, C karakteristika, 15 kA, Schneider. | - Single pole circuit breaker 10 A, C characteristic, 15 kA, Schneider. | kos | 5
| '- enopolni inštalacijski odklopnik 16 A, C karakteristika, 15 kA, Schneider. | - Single pole circuit breaker 16 A, C characteristic, 15 kA, Schneider. | kos | 3
| - dvopolni inštalacijski odklopnik 10 A, C karakteristika, DC, 15 kA, Schneider. | - 10 A, C characteristic, DC, 15 kA, Schneider, double-pole circuit breaker. | kos | 3
| Alarmna centrala s kapaciteto za priklop do 12 detektorjev s pripadajočimi relejskimi izhodi in možnostjo kasnejše nadgradnje, kot na primer Tevel, MX7, v sestavi: Na vratih se izvede odprtina za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira svetilka za razsvetljavo omare, servisna vtičnica in predal za dokumentacijo | Alarm control panel with capacity for connecting up to 12 detectors with associated relay outputs and the possibility of later upgrading, e.g. Tevel, MX7, in the assembly: A ventilation opening shall be made in the door and air filters shall be fitted. A luminaire for cabinet lighting, a service socket and a drawer for documentation shall be installed inside the cabinet
| - Galaxy MX7 CPU modul z povezavo analognih in digitalnih vhodnih, izhodnih modulov, prikazovalnika, TEVEL; | - Galaxy MX7 CPU module with connection of analogue and digital input, output modules, display, TEVEL; | kos | 1
| - Galaxy MX7 Ai modul z 12 vhodi za priklop 4-20mA detektorjev, TEVEL; | - Galaxy MX7 Ai module with 12 inputs for connecting 4-20mA detectors, TEVEL; | kos | 1
| - Galaxy MX7 Dio modul z kapaciteto 12 vhodov in 12 izhodov, TEVEL; | - Galaxy MX7 Dio module with 12 inputs and 12 outputs, TEVEL; | kos | 4
| - Galaxy MX7 Komunikacijski RS485 modul , TEVEL; | - Galaxy MX7 Communication RS485 module , TEVEL; | kos | 1
| '- Galaxy MX7 Touchscreen prikazovalno posluževalni panel, TEVEL; | - Galaxy MX7 Touchscreen display and operating panel, TEVEL; | kos | 1
| - Quint Napajalnik 230V AC / 24V DC / 10A (TRIO-PS-2G/1AC/24DC/20) ; Phoenix Contact; | - Quint Power supply 230V AC / 24V DC / 10A (TRIO-PS-2G/1AC/24DC/20) ; Phoenix Contact; | kos | 1
| - Quint UPS modul za napajalnik; (QUINT4-UPS 24DC/24DC/20/PN), Phoenix Contact; | - Quint UPS module for power supply; (QUINT4-UPS 24DC/24DC/20/PN), Phoenix Contact; | kos | 1
| - Akumulatorsko rezervno napajanje, akomulator 12V/12Ah, UPS-BAT/PB/24DC/20AH; Phoenix Contact; | - Battery backup power supply, accumulator 12V/12Ah, UPS-BAT/PB/24DC/20AH; Phoenix Contact; | kos | 4
| - Mrežni delilnik za daljinski nadzor sistema, Ethernet switch, 6GK5005-0GA00-1AB2; Siemens; | - Network splitter for remote system monitoring, Ethernet switch, 6GK5005-0GA00-1AB2; Siemens; | kos | 1
| - rele-sponka Phoenix Contact, PLC-RSC-24UC/21-21, 24VAC/DC (2x CO preklopni kontakt); | - relay-coupler Phoenix Contact, PLC-RSC-24UC/21-21, 24VAC/DC (2x CO switching contact); | kos | 25
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 1
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 1
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 1
| - sponke, kot naprimer: Phoenix Contact, MTK-P/P; | - terminals such as Phoenix Contact, MTK-P/P; | kos | 120
| - sponke z varovalko 0,315 A, kot naprimer: Phoenix Contact,UK 5-HESI; | - terminals with a fuse of 0,315 A, such as Phoenix Contact,UK 5-HESI; | kos | 21
| Namestiti je potrebno vse potrebne module, da bo centrala delovala kot celota; | All the necessary modules must be installed to make the control panel work as a complete unit;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, din letvijo, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, kovinskimi uvodnicami. itd. | Complete with all necessary electrical installation and fixing materials, din moulding, wiring, equipotential bonding, cable marking, nameplates, metallic lead-ins, etc. | kpl | 1
| Opomba: Delavniške risbe centrale za javljane plina mora izdelati izbrani dobavitelj. | Remark: Shop drawings of the gas control panel shall be made by the selected supplier.
3.2 | Dobava in montaža centrale javljana plinov +CJPL-P-2 v naslednjem sestavu: | Supply and installation of a gas control panel +CJPL-P-2 in the following configuration: |  |  | kpl | 1 |  | 0
| Dimenzije omare so: višina 2000 mm, širina 1200 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Omara ima dvokrilna vrata po celi višini spredaj, uvod kablov zgoraj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1200 mm and depth 400 mm. The whole cabinet stands on a base height of 200 mm. The cabinet has a full-height double-leaf door at the front, a cable entry at the top, a comfort handle and a key-operated double-hinged closure.
| OPOMBA: Na vratih se izvede odprtina za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira svetilka za razsvetljavo omare, servisna vtičnica in predal za dokumentacijo | NOTE: A ventilation opening shall be made in the door and air filters shall be fitted. A luminaire for cabinet lighting, a service socket and a drawer for documentation shall be installed inside the cabinet
| - ohišje iz jeklene pločevine v barvi RAL 7035, dimenzij (šxvxg) 1200x2000x400mm, podstavek višine 200mm, dvokrilna vrata, odpiranje vrat 120°, IP55, IK10, ročka za odpiranje, cilindrični vložek, torba za načrte A4, svetilka LED s stikalom, vtičnico in priključnim kablom, 230V, 50Hz, končno stikalo s povezovalnim kablom, termostat, ventilator s filtrom, vgrajen na zgornjem delu kovinskih vrat, priključni kabel, filterska rešetka vgrajena na spodnjem delu kovinskih vrat, vtičnica 230VAC/16A, 50Hz, L, N, PE za montažo na DIN letev, vtičnica 2xRJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omari. Uvod kablov zgoraj. Kot na primer omara PanelSeT SFN, tip: NSYSM2012402DP, Schneider. | - ohišje iz jeklene pločevine v barvi RAL 7035, dimenzij (šxvxg) 1200x2000x400mm, podstavek višine 200mm, dvokrilna vrata, odpiranje vrat 120°, IP55, IK10, ročka za odpiranje, cilindrični vložek, torba za načrte A4, svetilka LED s stikalom, vtičnico in priključnim kablom, 230V, 50Hz, končno stikalo s povezovalnim kablom, termostat, ventilator s filtrom, vgrajen na zgornjem delu kovinskih vrat, priključni kabel, filterska rešetka vgrajena na spodnjem delu kovinskih vrat, vtičnica 230VAC/16A, 50Hz, L, N, PE za montažo na DIN letev, vtičnica 2xRJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omari. Uvod kablov zgoraj. Such as the PanelSeT SFN cabinet, type: NSYSM2012402DP, Schneider. | kos | 1
| V omaro se vgradi naslednja elektro oprema: | The following electrical equipment shall be installed in the cabinet:
| - glavno stikalo za montažo na vrata omare (In=32A), Schneider | - main switch for mounting on cabinet doors (In=32A), Schneider | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 1
| - rdeča kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM4+ZBZ32, Schneider | - red LED signal lamp, Ø 22, 230 to 240 V, as for example type:XB4BVM4+ZBZ32, Schneider | kos | 2
| - oranžna kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM5+ZBZ32, Schneider | - orange complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM5+ZBZ32, Schneider | kos | 1
| - tipka za vgradnjo na ohišje omare, za kvintiranje alarma, s LED osvetlitvijo, rdeče barve, Ø 22, 24V, Schneider | - pushbutton for mounting on cabinet enclosure, for quintillating alarm, LED illuminated, red, Ø 22, 24V, Schneider | kos | 1
| - prenapetostni odvodnik DEHNguard, DG M TN 275, 2-polni, 20 kA, Class II; | - dEHNguard surge arrester, DG M TN 275, 2-pole, 20 kA, Class II; |  | 1
| '- enopolni inštalacijski odklopnik 4 A, C karakteristika, 15 kA, Schneider. | - Single-pole circuit breaker 4 A, C characteristic, 15 kA, Schneider. | kos | 12
| '- enopolni inštalacijski odklopnik 6 A, C karakteristika, 15 kA, Schneider. | - Single-pole circuit breaker 6 A, C characteristic, 15 kA, Schneider. | kos | 5
| '- enopolni inštalacijski odklopnik 10 A, C karakteristika, 15 kA, Schneider. | - Single-pole circuit breaker 10 A, C characteristic, 15 kA, Schneider. | kos | 5
| '- enopolni inštalacijski odklopnik 16 A, C karakteristika, 15 kA, Schneider. | - Single pole circuit breaker 16 A, C characteristic, 15 kA, Schneider. | kos | 3
| - dvopolni inštalacijski odklopnik 10 A, C karakteristika, DC, 15 kA, Schneider. | - 10 A, C characteristic, DC, 15 kA, Schneider, double-pole circuit breaker. | kos | 3
| Alarmna centrala s kapaciteto za priklop do 12 detektorjev s pripadajočimi relejskimi izhodi in možnostjo kasnejše nadgradnje, kot na primer Tevel, MX7, v sestavi: Na vratih se izvede odprtina za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira svetilka za razsvetljavo omare, servisna vtičnica in predal za dokumentacijo | Alarm control panel with capacity for connecting up to 12 detectors with associated relay outputs and the possibility of later upgrading, e.g. Tevel, MX7, in the assembly: A ventilation opening shall be made in the door and air filters shall be fitted. A luminaire for cabinet lighting, a service socket and a drawer for documentation shall be installed inside the cabinet
| - Galaxy MX7 CPU modul z povezavo analognih in digitalnih vhodnih, izhodnih modulov, prikazovalnika, TEVEL; | - Galaxy MX7 CPU module with connection of analogue and digital input, output modules, display, TEVEL; | kos | 1
| - Galaxy MX7 Ai modul z 12 vhodi za priklop 4-20mA detektorjev, TEVEL; | - Galaxy MX7 Ai module with 12 inputs for connecting 4-20mA detectors, TEVEL; | kos | 2
| - Galaxy MX7 Dio modul z kapaciteto 12 vhodov in 12 izhodov, TEVEL; | - Galaxy MX7 Dio module with 12 inputs and 12 outputs, TEVEL; | kos | 5
| - Galaxy MX7 Komunikacijski RS485 modul , TEVEL; | - Galaxy MX7 Communication RS485 module , TEVEL; | kos | 1
| '- Galaxy MX7 Touchscreen prikazovalno posluževalni panel, TEVEL; | - Galaxy MX7 Touchscreen display and operating panel, TEVEL; | kos | 1
| - Quint Napajalnik 230V AC / 24V DC / 10A (TRIO-PS-2G/1AC/24DC/20) ; Phoenix Contact; | - Quint Power supply 230V AC / 24V DC / 10A (TRIO-PS-2G/1AC/24DC/20) ; Phoenix Contact; | kos | 1
| - Quint UPS modul za napajalnik; (QUINT4-UPS 24DC/24DC/20/PN), Phoenix Contact; | - Quint UPS module for power supply; (QUINT4-UPS 24DC/24DC/20/PN), Phoenix Contact; | kos | 1
| - Akumulatorsko rezervno napajanje, akomulator 12V/12Ah, UPS-BAT/PB/24DC/20AH; Phoenix Contact; | - Battery backup power supply, accumulator 12V/12Ah, UPS-BAT/PB/24DC/20AH; Phoenix Contact; | kos | 4
| - Mrežni delilnik za daljinski nadzor sistema, Ethernet switch, 6GK5005-0GA00-1AB2; Siemens; | - Network splitter for remote system monitoring, Ethernet switch, 6GK5005-0GA00-1AB2; Siemens; | kos | 1
| - rele-sponka Phoenix Contact, PLC-RSC-24UC/21-21, 24VAC/DC (2x CO preklopni kontakt); | - relay-coupler Phoenix Contact, PLC-RSC-24UC/21-21, 24VAC/DC (2x CO switching contact); | kos | 31
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 1
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 1
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 1
| - sponke, kot naprimer: Phoenix Contact, MTK-P/P; | - terminals such as Phoenix Contact, MTK-P/P; | kos | 152
| - sponke z varovalko 0,315 A, kot naprimer: Phoenix Contact,UK 5-HESI; | - terminals with a fuse of 0,315 A, such as Phoenix Contact,UK 5-HESI; | kos | 35
| Namestiti je potrebno vse potrebne module, da bo centrala delovala kot celota; | All the necessary modules must be installed to make the control panel work as a complete unit;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, din letvijo, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, kovinskimi uvodnicami. itd. | Complete with all necessary electrical installation and fixing materials, din moulding, wiring, equipotential bonding, cable marking, nameplates, metallic lead-ins, etc. | kpl | 1
| Opomba: Delavniške risbe centrale za javljane plina mora izdelati izbrani dobavitelj. | Remark: Shop drawings of the gas control panel shall be made by the selected supplier.
3.3 | Dobava in montaža centrale javljana plinov +CJPL-P-3 v naslednjem sestavu: | Supply and installation of a gas control panel +CJPL-P-3 in the following configuration: |  |  | kpl | 1 |  | 0
| Dimenzije omare so: višina 2000 mm, širina 1200 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Omara ima dvokrilna vrata po celi višini spredaj, uvod kablov zgoraj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1200 mm and depth 400 mm. The whole cabinet stands on a base height of 200 mm. The cabinet has a full-height double-leaf door at the front, a cable entry at the top, a comfort handle and a key-operated double-hinged closure.
| OPOMBA: Na vratih se izvede odprtina za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira svetilka za razsvetljavo omare, servisna vtičnica in predal za dokumentacijo | NOTE: A ventilation opening shall be made in the door and air filters shall be fitted. A luminaire for cabinet lighting, a service socket and a drawer for documentation shall be installed inside the cabinet
| - ohišje iz jeklene pločevine v barvi RAL 7035, dimenzij (šxvxg) 1200x2000x400mm, podstavek višine 200mm, dvokrilna vrata, odpiranje vrat 120°, IP55, IK10, ročka za odpiranje, cilindrični vložek, torba za načrte A4, svetilka LED s stikalom, vtičnico in priključnim kablom, 230V, 50Hz, končno stikalo s povezovalnim kablom, termostat, ventilator s filtrom, vgrajen na zgornjem delu kovinskih vrat, priključni kabel, filterska rešetka vgrajena na spodnjem delu kovinskih vrat, vtičnica 230VAC/16A, 50Hz, L, N, PE za montažo na DIN letev, vtičnica 2xRJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omari. Uvod kablov zgoraj. Kot na primer omara PanelSeT SFN, tip: NSYSM2012402DP, Schneider. | - ohišje iz jeklene pločevine v barvi RAL 7035, dimenzij (šxvxg) 1200x2000x400mm, podstavek višine 200mm, dvokrilna vrata, odpiranje vrat 120°, IP55, IK10, ročka za odpiranje, cilindrični vložek, torba za načrte A4, svetilka LED s stikalom, vtičnico in priključnim kablom, 230V, 50Hz, končno stikalo s povezovalnim kablom, termostat, ventilator s filtrom, vgrajen na zgornjem delu kovinskih vrat, priključni kabel, filterska rešetka vgrajena na spodnjem delu kovinskih vrat, vtičnica 230VAC/16A, 50Hz, L, N, PE za montažo na DIN letev, vtičnica 2xRJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omari. Uvod kablov zgoraj. Such as the PanelSeT SFN cabinet, type: NSYSM2012402DP, Schneider. | kos | 1
| V omaro se vgradi naslednja elektro oprema: | The following electrical equipment shall be installed in the cabinet:
| - glavno stikalo za montažo na vrata omare (In=32A), Schneider | - main switch for mounting on cabinet doors (In=32A), Schneider | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 1
| - rdeča kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM4+ZBZ32, Schneider | - red LED signal lamp, Ø 22, 230 to 240 V, as for example type:XB4BVM4+ZBZ32, Schneider | kos | 2
| - oranžna kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM5+ZBZ32, Schneider | - orange complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM5+ZBZ32, Schneider | kos | 1
| - tipka za vgradnjo na ohišje omare, za kvintiranje alarma, s LED osvetlitvijo, rdeče barve, Ø 22, 24V, Schneider | - pushbutton for mounting on cabinet enclosure, for quintillating alarm, LED illuminated, red, Ø 22, 24V, Schneider | kos | 1
| - prenapetostni odvodnik DEHNguard, DG M TN 275, 2-polni, 20 kA, Class II; | - dEHNguard surge arrester, DG M TN 275, 2-pole, 20 kA, Class II; |  | 1
| '- enopolni inštalacijski odklopnik 4 A, C karakteristika, 15 kA, Schneider. | - Single pole circuit breaker 4 A, C characteristic, 15 kA, Schneider. | kos | 16
| '- enopolni inštalacijski odklopnik 6 A, C karakteristika, 15 kA, Schneider. | - Single pole circuit breaker 6 A, C characteristic, 15 kA, Schneider. | kos | 5
| '- enopolni inštalacijski odklopnik 10 A, C karakteristika, 15 kA, Schneider. | - Single pole circuit breaker 10 A, C characteristic, 15 kA, Schneider. | kos | 5
| '- enopolni inštalacijski odklopnik 16 A, C karakteristika, 15 kA, Schneider. | - Single pole circuit breaker 16 A, C characteristic, 15 kA, Schneider. | kos | 3
| - dvopolni inštalacijski odklopnik 10 A, C karakteristika, DC, 15 kA, Schneider. | - 10 A, C characteristic, DC, 15 kA, Schneider, double-pole circuit breaker. | kos | 3
| Alarmna centrala s kapaciteto za priklop do 12 detektorjev s pripadajočimi relejskimi izhodi in možnostjo kasnejše nadgradnje, kot na primer Tevel, MX7, v sestavi: Na vratih se izvede odprtina za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira svetilka za razsvetljavo omare, servisna vtičnica in predal za dokumentacijo | Alarm control panel with capacity for connecting up to 12 detectors with associated relay outputs and the possibility of later upgrading, e.g. Tevel, MX7, in the assembly: A ventilation opening shall be made in the door and air filters shall be fitted. A luminaire for cabinet lighting, a service socket and a drawer for documentation shall be installed inside the cabinet
| - Galaxy MX7 CPU modul z povezavo analognih in digitalnih vhodnih, izhodnih modulov, prikazovalnika, TEVEL; | - Galaxy MX7 CPU module with connection of analogue and digital input, output modules, display, TEVEL; | kos | 1
| - Galaxy MX7 Ai modul z 12 vhodi za priklop 4-20mA detektorjev, TEVEL; | - Galaxy MX7 Ai module with 12 inputs for connecting 4-20mA detectors, TEVEL; | kos | 2
| - Galaxy MX7 Dio modul z kapaciteto 12 vhodov in 12 izhodov, TEVEL; | - Galaxy MX7 Dio module with 12 inputs and 12 outputs, TEVEL; | kos | 4
| - Galaxy MX7 Komunikacijski RS485 modul , TEVEL; | - Galaxy MX7 Communication RS485 module , TEVEL; | kos | 1
| '- Galaxy MX7 Touchscreen prikazovalno posluževalni panel, TEVEL; | - Galaxy MX7 Touchscreen display and operating panel, TEVEL; | kos | 1
| - Quint Napajalnik 230V AC / 24V DC / 10A (TRIO-PS-2G/1AC/24DC/20) ; Phoenix Contact; | - Quint Power supply 230V AC / 24V DC / 10A (TRIO-PS-2G/1AC/24DC/20) ; Phoenix Contact; | kos | 1
| - Quint UPS modul za napajalnik; (QUINT4-UPS 24DC/24DC/20/PN), Phoenix Contact; | - Quint UPS module for power supply; (QUINT4-UPS 24DC/24DC/20/PN), Phoenix Contact; | kos | 1
| - Akumulatorsko rezervno napajanje, akomulator 12V/12Ah, UPS-BAT/PB/24DC/20AH; Phoenix Contact; | - Battery backup power supply, accumulator 12V/12Ah, UPS-BAT/PB/24DC/20AH; Phoenix Contact; | kos | 4
| - Mrežni delilnik za daljinski nadzor sistema, Ethernet switch, 6GK5005-0GA00-1AB2; Siemens; | - Network splitter for remote system monitoring, Ethernet switch, 6GK5005-0GA00-1AB2; Siemens; | kos | 1
| - rele-sponka Phoenix Contact, PLC-RSC-24UC/21-21, 24VAC/DC (2x CO preklopni kontakt); | - relay-coupler Phoenix Contact, PLC-RSC-24UC/21-21, 24VAC/DC (2x CO switching contact); | kos | 35
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 1
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 1
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 1
| - sponke, kot naprimer: Phoenix Contact, MTK-P/P; | - terminals such as Phoenix Contact, MTK-P/P; | kos | 168
| - sponke z varovalko 0,315 A, kot naprimer: Phoenix Contact,UK 5-HESI; | - terminals with a fuse of 0,315 A, such as Phoenix Contact,UK 5-HESI; | kos | 51
| Namestiti je potrebno vse potrebne module, da bo centrala delovala kot celota; | All the necessary modules must be installed to make the control panel work as a complete unit;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, din letvijo, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, kovinskimi uvodnicami. itd. | Complete with all necessary electrical installation and fixing materials, din moulding, wiring, equipotential bonding, cable marking, nameplates, metallic lead-ins, etc. | kpl | 1
| Opomba: Delavniške risbe centrale za javljane plina mora izdelati izbrani dobavitelj. | Remark: Shop drawings of the gas control panel shall be made by the selected supplier.
3.4 | Dobava in montaža centrale javljana plinov +CJPL-P-4 v naslednjem sestavu: | Supply and installation of a gas control panel +CJPL-P-4 in the following configuration: |  |  | kpl | 1 |  | 0
| Dimenzije omare so: višina 2000 mm, širina 1200 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Omara ima dvokrilna vrata po celi višini spredaj, uvod kablov zgoraj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1200 mm and depth 400 mm. The whole cabinet stands on a base height of 200 mm. The cabinet has a full-height double-leaf door at the front, a cable entry at the top, a comfort handle and a key-operated double-hinged closure.
| OPOMBA: Na vratih se izvede odprtina za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira svetilka za razsvetljavo omare, servisna vtičnica in predal za dokumentacijo | NOTE: A ventilation opening shall be made in the door and air filters shall be fitted. A luminaire for cabinet lighting, a service socket and a drawer for documentation shall be installed inside the cabinet
| - ohišje iz jeklene pločevine v barvi RAL 7035, dimenzij (šxvxg) 1200x2000x400mm, podstavek višine 200mm, dvokrilna vrata, odpiranje vrat 120°, IP55, IK10, ročka za odpiranje, cilindrični vložek, torba za načrte A4, svetilka LED s stikalom, vtičnico in priključnim kablom, 230V, 50Hz, končno stikalo s povezovalnim kablom, termostat, ventilator s filtrom, vgrajen na zgornjem delu kovinskih vrat, priključni kabel, filterska rešetka vgrajena na spodnjem delu kovinskih vrat, vtičnica 230VAC/16A, 50Hz, L, N, PE za montažo na DIN letev, vtičnica 2xRJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omari. Uvod kablov zgoraj. Kot na primer omara PanelSeT SFN, tip: NSYSM2012402DP, Schneider. | - ohišje iz jeklene pločevine v barvi RAL 7035, dimenzij (šxvxg) 1200x2000x400mm, podstavek višine 200mm, dvokrilna vrata, odpiranje vrat 120°, IP55, IK10, ročka za odpiranje, cilindrični vložek, torba za načrte A4, svetilka LED s stikalom, vtičnico in priključnim kablom, 230V, 50Hz, končno stikalo s povezovalnim kablom, termostat, ventilator s filtrom, vgrajen na zgornjem delu kovinskih vrat, priključni kabel, filterska rešetka vgrajena na spodnjem delu kovinskih vrat, vtičnica 230VAC/16A, 50Hz, L, N, PE za montažo na DIN letev, vtičnica 2xRJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omari. Uvod kablov zgoraj. Such as the PanelSeT SFN cabinet, type: NSYSM2012402DP, Schneider. | kos | 1
| V omaro se vgradi naslednja elektro oprema: | The following electrical equipment shall be installed in the cabinet:
| - glavno stikalo za montažo na vrata omare (In=32A), Schneider | - main switch for mounting on cabinet doors (In=32A), Schneider | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 1
| - rdeča kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM4+ZBZ32, Schneider | - red LED signal lamp, Ø 22, 230 to 240 V, as for example type:XB4BVM4+ZBZ32, Schneider | kos | 2
| - oranžna kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM5+ZBZ32, Schneider | - orange complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM5+ZBZ32, Schneider | kos | 1
| - tipka za vgradnjo na ohišje omare, za kvintiranje alarma, s LED osvetlitvijo, rdeče barve, Ø 22, 24V, Schneider | - pushbutton for mounting on cabinet enclosure, for quintillating alarm, LED illuminated, red, Ø 22, 24V, Schneider | kos | 1
| - prenapetostni odvodnik DEHNguard, DG M TN 275, 2-polni, 20 kA, Class II; | - dEHNguard surge arrester, DG M TN 275, 2-pole, 20 kA, Class II; |  | 1
| '- enopolni inštalacijski odklopnik 4 A, C karakteristika, 15 kA, Schneider. | - Single pole circuit breaker 4 A, C characteristic, 15 kA, Schneider. | kos | 22
| '- enopolni inštalacijski odklopnik 6 A, C karakteristika, 15 kA, Schneider. | - Single-pole circuit breaker 6 A, C characteristic, 15 kA, Schneider. | kos | 5
| '- enopolni inštalacijski odklopnik 10 A, C karakteristika, 15 kA, Schneider. | - Single-pole circuit breaker 10 A, C characteristic, 15 kA, Schneider. | kos | 5
| '- enopolni inštalacijski odklopnik 16 A, C karakteristika, 15 kA, Schneider. | - Single pole circuit breaker 16 A, C characteristic, 15 kA, Schneider. | kos | 3
| - dvopolni inštalacijski odklopnik 10 A, C karakteristika, DC, 15 kA, Schneider. | - 10 A, C characteristic, DC, 15 kA, Schneider, double-pole circuit breaker. | kos | 3
| Alarmna centrala s kapaciteto za priklop do 12 detektorjev s pripadajočimi relejskimi izhodi in možnostjo kasnejše nadgradnje, kot na primer Tevel, MX7, v sestavi: Na vratih se izvede odprtina za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira svetilka za razsvetljavo omare, servisna vtičnica in predal za dokumentacijo | Alarm control panel with capacity for connecting up to 12 detectors with associated relay outputs and the possibility of later upgrading, e.g. Tevel, MX7, in the assembly: A ventilation opening shall be made in the door and air filters shall be fitted. A luminaire for cabinet lighting, a service socket and a drawer for documentation shall be installed inside the cabinet
| - Galaxy MX7 CPU modul z povezavo analognih in digitalnih vhodnih, izhodnih modulov, prikazovalnika, TEVEL; | - Galaxy MX7 CPU module with connection of analogue and digital input, output modules, display, TEVEL; | kos | 1
| - Galaxy MX7 Ai modul z 12 vhodi za priklop 4-20mA detektorjev, TEVEL; | - Galaxy MX7 Ai module with 12 inputs for connecting 4-20mA detectors, TEVEL; | kos | 3
| - Galaxy MX7 Dio modul z kapaciteto 12 vhodov in 12 izhodov, TEVEL; | - Galaxy MX7 Dio module with 12 inputs and 12 outputs, TEVEL; | kos | 5
| - Galaxy MX7 Komunikacijski RS485 modul , TEVEL; | - Galaxy MX7 Communication RS485 module , TEVEL; | kos | 1
| '- Galaxy MX7 Touchscreen prikazovalno posluževalni panel, TEVEL; | - Galaxy MX7 Touchscreen display and operating panel, TEVEL; | kos | 1
| - Quint Napajalnik 230V AC / 24V DC / 10A (TRIO-PS-2G/1AC/24DC/20) ; Phoenix Contact; | - Quint Power supply 230V AC / 24V DC / 10A (TRIO-PS-2G/1AC/24DC/20) ; Phoenix Contact; | kos | 1
| - Quint UPS modul za napajalnik; (QUINT4-UPS 24DC/24DC/20/PN), Phoenix Contact; | - Quint UPS module for power supply; (QUINT4-UPS 24DC/24DC/20/PN), Phoenix Contact; | kos | 1
| - Akumulatorsko rezervno napajanje, akomulator 12V/12Ah, UPS-BAT/PB/24DC/20AH; Phoenix Contact; | - Battery backup power supply, accumulator 12V/12Ah, UPS-BAT/PB/24DC/20AH; Phoenix Contact; | kos | 4
| - Mrežni delilnik za daljinski nadzor sistema, Ethernet switch, 6GK5005-0GA00-1AB2; Siemens; | - Network splitter for remote system monitoring, Ethernet switch, 6GK5005-0GA00-1AB2; Siemens; | kos | 1
| - rele-sponka Phoenix Contact, PLC-RSC-24UC/21-21, 24VAC/DC (2x CO preklopni kontakt); | - relay-coupler Phoenix Contact, PLC-RSC-24UC/21-21, 24VAC/DC (2x CO switching contact); | kos | 35
| - Zener bariera Z728, 24VDC, PEPPERL+FUCHS; | - Zener barrier Z728, 24VDC, PEPPERL+FUCHS; | kos | 12
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 1
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 1
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 1
| - sponke, kot naprimer: Phoenix Contact, MTK-P/P; | - terminals such as Phoenix Contact, MTK-P/P; | kos | 168
| - sponke z varovalko 0,315 A, kot naprimer: Phoenix Contact,UK 5-HESI; | - terminals with a fuse of 0,315 A, such as Phoenix Contact,UK 5-HESI; | kos | 51
| Namestiti je potrebno vse potrebne module, da bo centrala delovala kot celota; | All the necessary modules must be installed to make the control panel work as a complete unit;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, din letvijo, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, kovinskimi uvodnicami. itd. | Complete with all necessary electrical installation and fixing materials, din moulding, wiring, equipotential bonding, cable marking, nameplates, metallic lead-ins, etc. | kpl | 1
| Opomba: Delavniške risbe centrale za javljane plina mora izdelati izbrani dobavitelj. | Remark: Shop drawings of the gas control panel shall be made by the selected supplier.
3.5 | Dobava in montaža centrale javljana plinov +CJPL-2N-1 v naslednjem sestavu: | Supply and installation of a gas control panel +CJPL-2N-1 in the following configuration: |  |  | kpl | 1 |  | 0
| Dimenzije omare so: višina 2000 mm, širina 1000 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Omara ima dvokrilna vrata po celi višini spredaj, uvod kablov zgoraj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1000 mm and depth 400 mm. The whole cabinet stands on a base height of 200 mm. The cabinet has a full-height double-leaf door at the front, a cable entry at the top, a comfort handle and a key-operated double-hinged closure.
| OPOMBA: Na vratih se izvede odprtina za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira svetilka za razsvetljavo omare, servisna vtičnica in predal za dokumentacijo | NOTE: A ventilation opening shall be made in the door and air filters shall be fitted. A luminaire for cabinet lighting, a service socket and a drawer for documentation shall be installed inside the cabinet
| - ohišje iz jeklene pločevine v barvi RAL 7035, dimenzij (šxvxg) 1000x2000x400mm, podstavek višine 200mm, dvokrilna vrata, odpiranje vrat 120°, IP55, IK10, ročka za odpiranje, cilindrični vložek, torba za načrte A4, svetilka LED s stikalom, vtičnico in priključnim kablom, 230V, 50Hz, končno stikalo s povezovalnim kablom, termostat, ventilator s filtrom, vgrajen na zgornjem delu kovinskih vrat, priključni kabel, filterska rešetka vgrajena na spodnjem delu kovinskih vrat, vtičnica 230VAC/16A, 50Hz, L, N, PE za montažo na DIN letev, vtičnica 2xRJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omari. Uvod kablov zgoraj. Kot na primer omara PanelSeT SFN, tip: Nsysfn221060, Schneider. | - ohišje iz jeklene pločevine v barvi RAL 7035, dimenzij (šxvxg) 1000x2000x400mm, podstavek višine 200mm, dvokrilna vrata, odpiranje vrat 120°, IP55, IK10, ročka za odpiranje, cilindrični vložek, torba za načrte A4, svetilka LED s stikalom, vtičnico in priključnim kablom, 230V, 50Hz, končno stikalo s povezovalnim kablom, termostat, ventilator s filtrom, vgrajen na zgornjem delu kovinskih vrat, priključni kabel, filterska rešetka vgrajena na spodnjem delu kovinskih vrat, vtičnica 230VAC/16A, 50Hz, L, N, PE za montažo na DIN letev, vtičnica 2xRJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omari. Uvod kablov zgoraj. Such as the PanelSeT SFN cabinet, type: Nsysfn221060, Schneider. | kos | 1
| V omaro se vgradi naslednja elektro oprema: | The following electrical equipment shall be installed in the cabinet:
| - glavno stikalo za montažo na vrata omare (In=32A), Schneider | - main switch for mounting on cabinet doors (In=32A), Schneider | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 1
| - rdeča kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM4+ZBZ32, Schneider | - red LED signal lamp, Ø 22, 230 to 240 V, as for example type:XB4BVM4+ZBZ32, Schneider | kos | 2
| - oranžna kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM5+ZBZ32, Schneider | - orange complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM5+ZBZ32, Schneider | kos | 1
| - tipka za vgradnjo na ohišje omare, za kvintiranje alarma, s LED osvetlitvijo, rdeče barve, Ø 22, 24V, Schneider | - pushbutton for mounting on cabinet enclosure, for quintillating alarm, LED illuminated, red, Ø 22, 24V, Schneider | kos | 1
| - prenapetostni odvodnik DEHNguard, DG M TN 275, 2-polni, 20 kA, Class II; | - dEHNguard surge arrester, DG M TN 275, 2-pole, 20 kA, Class II; |  | 1
| '- enopolni inštalacijski odklopnik 4 A, C karakteristika, 15 kA, Schneider. | - Single pole circuit breaker 4 A, C characteristic, 15 kA, Schneider. | kos | 8
| '- enopolni inštalacijski odklopnik 6 A, C karakteristika, 15 kA, Schneider. | - Single pole circuit breaker 6 A, C characteristic, 15 kA, Schneider. | kos | 5
| '- enopolni inštalacijski odklopnik 10 A, C karakteristika, 15 kA, Schneider. | - Single pole circuit breaker 10 A, C characteristic, 15 kA, Schneider. | kos | 5
| '- enopolni inštalacijski odklopnik 16 A, C karakteristika, 15 kA, Schneider. | - Single pole circuit breaker 16 A, C characteristic, 15 kA, Schneider. | kos | 3
| - dvopolni inštalacijski odklopnik 10 A, C karakteristika, DC, 15 kA, Schneider. | - 10 A, C characteristic, DC, 15 kA, Schneider, double-pole circuit breaker. | kos | 3
| Alarmna centrala s kapaciteto za priklop do 12 detektorjev s pripadajočimi relejskimi izhodi in možnostjo kasnejše nadgradnje, kot na primer Tevel, MX7, v sestavi: Na vratih se izvede odprtina za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira svetilka za razsvetljavo omare, servisna vtičnica in predal za dokumentacijo | Alarm control panel with capacity for connecting up to 12 detectors with associated relay outputs and the possibility of later upgrading, e.g. Tevel, MX7, in the assembly: A ventilation opening shall be made in the door and air filters shall be fitted. A luminaire for cabinet lighting, a service socket and a drawer for documentation shall be installed inside the cabinet
| - Galaxy MX7 CPU modul z povezavo analognih in digitalnih vhodnih, izhodnih modulov, prikazovalnika, TEVEL; | - Galaxy MX7 CPU module with connection of analogue and digital input, output modules, display, TEVEL; | kos | 1
| - Galaxy MX7 Ai modul z 12 vhodi za priklop 4-20mA detektorjev, TEVEL; | - Galaxy MX7 Ai module with 12 inputs for connecting 4-20mA detectors, TEVEL; | kos | 1
| - Galaxy MX7 Dio modul z kapaciteto 12 vhodov in 12 izhodov, TEVEL; | - Galaxy MX7 Dio module with 12 inputs and 12 outputs, TEVEL; | kos | 3
| - Galaxy MX7 Komunikacijski RS485 modul , TEVEL; | - Galaxy MX7 Communication RS485 module , TEVEL; | kos | 1
| '- Galaxy MX7 Touchscreen prikazovalno posluževalni panel, TEVEL; | - Galaxy MX7 Touchscreen display and operating panel, TEVEL; | kos | 1
| - Quint Napajalnik 230V AC / 24V DC / 10A (TRIO-PS-2G/1AC/24DC/20) ; Phoenix Contact; | - Quint Power supply 230V AC / 24V DC / 10A (TRIO-PS-2G/1AC/24DC/20) ; Phoenix Contact; | kos | 1
| - Quint UPS modul za napajalnik; (QUINT4-UPS 24DC/24DC/20/PN), Phoenix Contact; | - Quint UPS module for power supply; (QUINT4-UPS 24DC/24DC/20/PN), Phoenix Contact; | kos | 1
| - Akumulatorsko rezervno napajanje, akomulator 12V/12Ah, UPS-BAT/PB/24DC/20AH; Phoenix Contact; | - Battery backup power supply, accumulator 12V/12Ah, UPS-BAT/PB/24DC/20AH; Phoenix Contact; | kos | 4
| - Mrežni delilnik za daljinski nadzor sistema, Ethernet switch, 6GK5005-0GA00-1AB2; Siemens; | - Network splitter for remote system monitoring, Ethernet switch, 6GK5005-0GA00-1AB2; Siemens; | kos | 1
| - rele-sponka Phoenix Contact, PLC-RSC-24UC/21-21, 24VAC/DC (2x CO preklopni kontakt); | - relay-coupler Phoenix Contact, PLC-RSC-24UC/21-21, 24VAC/DC (2x CO switching contact); | kos | 35
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 1
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 1
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 1
| - sponke, kot naprimer: Phoenix Contact, MTK-P/P; | - terminals such as Phoenix Contact, MTK-P/P; | kos | 120
| - sponke z varovalko 0,315 A, kot naprimer: Phoenix Contact,UK 5-HESI; | - terminals with a fuse of 0,315 A, such as Phoenix Contact,UK 5-HESI; | kos | 21
| Namestiti je potrebno vse potrebne module, da bo centrala delovala kot celota; | All the necessary modules must be installed to make the control panel work as a complete unit;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, din letvijo, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, kovinskimi uvodnicami. itd. | Complete with all necessary electrical installation and fixing materials, din moulding, wiring, equipotential bonding, cable marking, nameplates, metallic lead-ins, etc. | kpl | 1
| Opomba: Delavniške risbe centrale za javljane plina mora izdelati izbrani dobavitelj. | Remark: Shop drawings of the gas control panel shall be made by the selected supplier.
3.6 | Dobava in montaža centrale javljana plinov +CJPL-2N-2 v naslednjem sestavu: | Supply and installation of a gas control panel +CJPL-2N-2 in the following configuration: |  |  | kpl | 1 |  | 0
| Dimenzije omare so: višina 2000 mm, širina 1000 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Omara ima dvokrilna vrata po celi višini spredaj, uvod kablov zgoraj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1000 mm and depth 400 mm. The whole cabinet stands on a base height of 200 mm. The cabinet has a full-height double-leaf door at the front, a cable entry at the top, a comfort handle and a key-operated double-hinged closure.
| OPOMBA: Na vratih se izvede odprtina za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira svetilka za razsvetljavo omare, servisna vtičnica in predal za dokumentacijo | NOTE: A ventilation opening shall be made in the door and air filters shall be fitted. A luminaire for cabinet lighting, a service socket and a drawer for documentation shall be installed inside the cabinet
| - ohišje iz jeklene pločevine v barvi RAL 7035, dimenzij (šxvxg) 1000x2000x400mm, podstavek višine 200mm, dvokrilna vrata, odpiranje vrat 120°, IP55, IK10, ročka za odpiranje, cilindrični vložek, torba za načrte A4, svetilka LED s stikalom, vtičnico in priključnim kablom, 230V, 50Hz, končno stikalo s povezovalnim kablom, termostat, ventilator s filtrom, vgrajen na zgornjem delu kovinskih vrat, priključni kabel, filterska rešetka vgrajena na spodnjem delu kovinskih vrat, vtičnica 230VAC/16A, 50Hz, L, N, PE za montažo na DIN letev, vtičnica 2xRJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omari. Uvod kablov zgoraj. Kot na primer omara PanelSeT SFN, tip: Nsysfn221060, Schneider. | - ohišje iz jeklene pločevine v barvi RAL 7035, dimenzij (šxvxg) 1000x2000x400mm, podstavek višine 200mm, dvokrilna vrata, odpiranje vrat 120°, IP55, IK10, ročka za odpiranje, cilindrični vložek, torba za načrte A4, svetilka LED s stikalom, vtičnico in priključnim kablom, 230V, 50Hz, končno stikalo s povezovalnim kablom, termostat, ventilator s filtrom, vgrajen na zgornjem delu kovinskih vrat, priključni kabel, filterska rešetka vgrajena na spodnjem delu kovinskih vrat, vtičnica 230VAC/16A, 50Hz, L, N, PE za montažo na DIN letev, vtičnica 2xRJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omari. Uvod kablov zgoraj. Such as the PanelSeT SFN cabinet, type: Nsysfn221060, Schneider. | kos | 1
| V omaro se vgradi naslednja elektro oprema: | The following electrical equipment shall be installed in the cabinet:
| - glavno stikalo za montažo na vrata omare (In=32A), Schneider | - main switch for mounting on cabinet doors (In=32A), Schneider | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 1
| - rdeča kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM4+ZBZ32, Schneider | - red LED signal lamp, Ø 22, 230 to 240 V, as for example type:XB4BVM4+ZBZ32, Schneider | kos | 2
| - oranžna kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM5+ZBZ32, Schneider | - orange complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM5+ZBZ32, Schneider | kos | 1
| - tipka za vgradnjo na ohišje omare, za kvintiranje alarma, s LED osvetlitvijo, rdeče barve, Ø 22, 24V, Schneider | - pushbutton for mounting on cabinet enclosure, for quintillating alarm, LED illuminated, red, Ø 22, 24V, Schneider | kos | 1
| - prenapetostni odvodnik DEHNguard, DG M TN 275, 2-polni, 20 kA, Class II; | - dEHNguard surge arrester, DG M TN 275, 2-pole, 20 kA, Class II; |  | 1
| '- enopolni inštalacijski odklopnik 4 A, C karakteristika, 15 kA, Schneider. | - Single-pole circuit breaker 4 A, C characteristic, 15 kA, Schneider. | kos | 8
| '- enopolni inštalacijski odklopnik 6 A, C karakteristika, 15 kA, Schneider. | - Single pole circuit breaker 6 A, C characteristic, 15 kA, Schneider. | kos | 5
| '- enopolni inštalacijski odklopnik 10 A, C karakteristika, 15 kA, Schneider. | - Single pole circuit breaker 10 A, C characteristic, 15 kA, Schneider. | kos | 5
| '- enopolni inštalacijski odklopnik 16 A, C karakteristika, 15 kA, Schneider. | - Single pole circuit breaker 16 A, C characteristic, 15 kA, Schneider. | kos | 3
| - dvopolni inštalacijski odklopnik 10 A, C karakteristika, DC, 15 kA, Schneider. | - 10 A, C characteristic, DC, 15 kA, Schneider, double-pole circuit breaker. | kos | 3
| Alarmna centrala s kapaciteto za priklop do 12 detektorjev s pripadajočimi relejskimi izhodi in možnostjo kasnejše nadgradnje, kot na primer Tevel, MX7, v sestavi: Na vratih se izvede odprtina za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira svetilka za razsvetljavo omare, servisna vtičnica in predal za dokumentacijo | Alarm control panel with capacity for connecting up to 12 detectors with associated relay outputs and the possibility of later upgrading, e.g. Tevel, MX7, in the assembly: A ventilation opening shall be made in the door and air filters shall be fitted. A luminaire for cabinet lighting, a service socket and a drawer for documentation shall be installed inside the cabinet
| - Galaxy MX7 CPU modul z povezavo analognih in digitalnih vhodnih, izhodnih modulov, prikazovalnika, TEVEL; | - Galaxy MX7 CPU module with connection of analogue and digital input, output modules, display, TEVEL; | kos | 1
| - Galaxy MX7 Ai modul z 12 vhodi za priklop 4-20mA detektorjev, TEVEL; | - Galaxy MX7 Ai module with 12 inputs for connecting 4-20mA detectors, TEVEL; | kos | 1
| - Galaxy MX7 Dio modul z kapaciteto 12 vhodov in 12 izhodov, TEVEL; | - Galaxy MX7 Dio module with 12 inputs and 12 outputs, TEVEL; | kos | 4
| - Galaxy MX7 Komunikacijski RS485 modul , TEVEL; | - Galaxy MX7 Communication RS485 module , TEVEL; | kos | 1
| '- Galaxy MX7 Touchscreen prikazovalno posluževalni panel, TEVEL; | - Galaxy MX7 Touchscreen display and operating panel, TEVEL; | kos | 1
| - Quint Napajalnik 230V AC / 24V DC / 10A (TRIO-PS-2G/1AC/24DC/20) ; Phoenix Contact; | - Quint Power supply 230V AC / 24V DC / 10A (TRIO-PS-2G/1AC/24DC/20) ; Phoenix Contact; | kos | 1
| - Quint UPS modul za napajalnik; (QUINT4-UPS 24DC/24DC/20/PN), Phoenix Contact; | - Quint UPS module for power supply; (QUINT4-UPS 24DC/24DC/20/PN), Phoenix Contact; | kos | 1
| - Akumulatorsko rezervno napajanje, akomulator 12V/12Ah, UPS-BAT/PB/24DC/20AH; Phoenix Contact; | - Battery backup power supply, accumulator 12V/12Ah, UPS-BAT/PB/24DC/20AH; Phoenix Contact; | kos | 4
| - Mrežni delilnik za daljinski nadzor sistema, Ethernet switch, 6GK5005-0GA00-1AB2; Siemens; | - Network splitter for remote system monitoring, Ethernet switch, 6GK5005-0GA00-1AB2; Siemens; | kos | 1
| - rele-sponka Phoenix Contact, PLC-RSC-24UC/21-21, 24VAC/DC (2x CO preklopni kontakt); | - relay-coupler Phoenix Contact, PLC-RSC-24UC/21-21, 24VAC/DC (2x CO switching contact); | kos | 35
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 1
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 1
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 1
| - sponke, kot naprimer: Phoenix Contact, MTK-P/P; | - terminals such as Phoenix Contact, MTK-P/P; | kos | 120
| - sponke z varovalko 0,315 A, kot naprimer: Phoenix Contact,UK 5-HESI; | - terminals with a fuse of 0,315 A, such as Phoenix Contact,UK 5-HESI; | kos | 21
| Namestiti je potrebno vse potrebne module, da bo centrala delovala kot celota; | All the necessary modules must be installed to make the control panel work as a complete unit;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, din letvijo, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, kovinskimi uvodnicami. itd. | Complete with all necessary electrical installation and fixing materials, din moulding, wiring, equipotential bonding, cable marking, nameplates, metallic lead-ins, etc. | kpl | 1
| Opomba: Delavniške risbe centrale za javljane plina mora izdelati izbrani dobavitelj. | Remark: Shop drawings of the gas control panel shall be made by the selected supplier.
3.7 | Dobava in montaža centrale javljana plinov +CJPL-2N-3 v naslednjem sestavu: | Supply and installation of a gas control panel +CJPL-2N-3 in the following configuration: |  |  | kpl | 1 |  | 0
| Dimenzije omare so: višina 2000 mm, širina 1200 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Omara ima dvokrilna vrata po celi višini spredaj, uvod kablov zgoraj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1200 mm and depth 400 mm. The whole cabinet stands on a base height of 200 mm. The cabinet has a full-height double-leaf door at the front, a cable entry at the top, a comfort handle and a key-operated double-hinged closure.
| OPOMBA: Na vratih se izvede odprtina za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira svetilka za razsvetljavo omare, servisna vtičnica in predal za dokumentacijo | NOTE: A ventilation opening shall be made in the door and air filters shall be fitted. A luminaire for cabinet lighting, a service socket and a drawer for documentation shall be installed inside the cabinet
| - ohišje iz jeklene pločevine v barvi RAL 7035, dimenzij (šxvxg) 1200x2000x400mm, podstavek višine 200mm, dvokrilna vrata, odpiranje vrat 120°, IP55, IK10, ročka za odpiranje, cilindrični vložek, torba za načrte A4, svetilka LED s stikalom, vtičnico in priključnim kablom, 230V, 50Hz, končno stikalo s povezovalnim kablom, termostat, ventilator s filtrom, vgrajen na zgornjem delu kovinskih vrat, priključni kabel, filterska rešetka vgrajena na spodnjem delu kovinskih vrat, vtičnica 230VAC/16A, 50Hz, L, N, PE za montažo na DIN letev, vtičnica 2xRJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omari. Uvod kablov zgoraj. Kot na primer omara PanelSeT SFN, tip: NSYSM2012402DP, Schneider. | - ohišje iz jeklene pločevine v barvi RAL 7035, dimenzij (šxvxg) 1200x2000x400mm, podstavek višine 200mm, dvokrilna vrata, odpiranje vrat 120°, IP55, IK10, ročka za odpiranje, cilindrični vložek, torba za načrte A4, svetilka LED s stikalom, vtičnico in priključnim kablom, 230V, 50Hz, končno stikalo s povezovalnim kablom, termostat, ventilator s filtrom, vgrajen na zgornjem delu kovinskih vrat, priključni kabel, filterska rešetka vgrajena na spodnjem delu kovinskih vrat, vtičnica 230VAC/16A, 50Hz, L, N, PE za montažo na DIN letev, vtičnica 2xRJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omari. Uvod kablov zgoraj. Such as the PanelSeT SFN cabinet, type: NSYSM2012402DP, Schneider. | kos | 1
| V omaro se vgradi naslednja elektro oprema: | The following electrical equipment shall be installed in the cabinet:
| - glavno stikalo za montažo na vrata omare (In=32A), Schneider | - main switch for mounting on cabinet doors (In=32A), Schneider | kos | 1
| - bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM1+ZBZ32, Schneider | - white complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM1+ZBZ32, Schneider | kos | 1
| - rdeča kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM4+ZBZ32, Schneider | - red LED signal lamp, Ø 22, 230 to 240 V, as for example type:XB4BVM4+ZBZ32, Schneider | kos | 2
| - oranžna kompletna signalna svetilka LED, Ø 22, 230 do 240 V, kot naprimer tip:XB4BVM5+ZBZ32, Schneider | - orange complete LED signal luminaire, Ø 22, 230 to 240 V, as for example type:XB4BVM5+ZBZ32, Schneider | kos | 1
| - tipka za vgradnjo na ohišje omare, za kvintiranje alarma, s LED osvetlitvijo, rdeče barve, Ø 22, 24V, Schneider | - pushbutton for mounting on cabinet enclosure, for quintillating alarm, LED illuminated, red, Ø 22, 24V, Schneider | kos | 1
| - prenapetostni odvodnik DEHNguard, DG M TN 275, 2-polni, 20 kA, Class II; | - dEHNguard surge arrester, DG M TN 275, 2-pole, 20 kA, Class II; |  | 1
| '- enopolni inštalacijski odklopnik 4 A, C karakteristika, 15 kA, Schneider. | - Single pole circuit breaker 4 A, C characteristic, 15 kA, Schneider. | kos | 8
| '- enopolni inštalacijski odklopnik 6 A, C karakteristika, 15 kA, Schneider. | - Single pole circuit breaker 6 A, C characteristic, 15 kA, Schneider. | kos | 5
| '- enopolni inštalacijski odklopnik 10 A, C karakteristika, 15 kA, Schneider. | - Single pole circuit breaker 10 A, C characteristic, 15 kA, Schneider. | kos | 5
| '- enopolni inštalacijski odklopnik 16 A, C karakteristika, 15 kA, Schneider. | - Single pole circuit breaker 16 A, C characteristic, 15 kA, Schneider. | kos | 3
| - dvopolni inštalacijski odklopnik 10 A, C karakteristika, DC, 15 kA, Schneider. | - 10 A, C characteristic, DC, 15 kA, Schneider, double-pole circuit breaker. | kos | 3
| Alarmna centrala s kapaciteto za priklop do 12 detektorjev s pripadajočimi relejskimi izhodi in možnostjo kasnejše nadgradnje, kot na primer Tevel, MX7, v sestavi: Na vratih se izvede odprtina za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira svetilka za razsvetljavo omare, servisna vtičnica in predal za dokumentacijo | Alarm control panel with capacity for connecting up to 12 detectors with associated relay outputs and the possibility of later upgrading, e.g. Tevel, MX7, as a set: A ventilation opening shall be made in the door and air filters shall be fitted. A luminaire for cabinet lighting, a service socket and a drawer for documentation shall be installed inside the cabinet
| - Galaxy MX7 CPU modul z povezavo analognih in digitalnih vhodnih, izhodnih modulov, prikazovalnika, TEVEL; | - Galaxy MX7 CPU module with connection of analogue and digital input, output modules, display, TEVEL; | kos | 1
| - Galaxy MX7 Ai modul z 12 vhodi za priklop 4-20mA detektorjev, TEVEL; | - Galaxy MX7 Ai module with 12 inputs for connecting 4-20mA detectors, TEVEL; | kos | 2
| - Galaxy MX7 Dio modul z kapaciteto 12 vhodov in 12 izhodov, TEVEL; | - Galaxy MX7 Dio module with 12 inputs and 12 outputs, TEVEL; | kos | 3
| - Galaxy MX7 Komunikacijski RS485 modul , TEVEL; | - Galaxy MX7 Communication RS485 module , TEVEL; | kos | 1
| '- Galaxy MX7 Touchscreen prikazovalno posluževalni panel, TEVEL; | - Galaxy MX7 Touchscreen display and operating panel, TEVEL; | kos | 1
| - Quint Napajalnik 230V AC / 24V DC / 10A (TRIO-PS-2G/1AC/24DC/20) ; Phoenix Contact; | - Quint Power supply 230V AC / 24V DC / 10A (TRIO-PS-2G/1AC/24DC/20) ; Phoenix Contact; | kos | 1
| - Quint UPS modul za napajalnik; (QUINT4-UPS 24DC/24DC/20/PN), Phoenix Contact; | - Quint UPS module for power supply; (QUINT4-UPS 24DC/24DC/20/PN), Phoenix Contact; | kos | 1
| - Akumulatorsko rezervno napajanje, akomulator 12V/12Ah, UPS-BAT/PB/24DC/20AH; Phoenix Contact; | - Battery backup power supply, accumulator 12V/12Ah, UPS-BAT/PB/24DC/20AH; Phoenix Contact; | kos | 4
| - Mrežni delilnik za daljinski nadzor sistema, Ethernet switch, 6GK5005-0GA00-1AB2; Siemens; | - Network splitter for remote system monitoring, Ethernet switch, 6GK5005-0GA00-1AB2; Siemens; | kos | 1
| - rele-sponka Phoenix Contact, PLC-RSC-24UC/21-21, 24VAC/DC (2x CO preklopni kontakt); | - relay-coupler Phoenix Contact, PLC-RSC-24UC/21-21, 24VAC/DC (2x CO switching contact); | kos | 35
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 1
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 1
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 1
| - sponke, kot naprimer: Phoenix Contact, MTK-P/P; | - terminals such as Phoenix Contact, MTK-P/P; | kos | 120
| - sponke z varovalko 0,315 A, kot naprimer: Phoenix Contact,UK 5-HESI; | - terminals with a fuse of 0,315 A, such as Phoenix Contact,UK 5-HESI; | kos | 21
| Namestiti je potrebno vse potrebne module, da bo centrala delovala kot celota; | All the necessary modules must be installed to make the control panel work as a complete unit;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, din letvijo, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, kovinskimi uvodnicami. itd. | Complete with all necessary electrical installation and fixing materials, din moulding, wiring, equipotential bonding, cable marking, nameplates, metallic lead-ins, etc. | kpl | 1
| Opomba: Delavniške risbe centrale za javljane plina mora izdelati izbrani dobavitelj. | Remark: Shop drawings of the gas control panel shall be made by the selected supplier.
3.8 | Dobava in montaža detektorjev kisika O2 zaradi prisotnosti dušika N2, helija He, argona Ar. | Supply and installation of O2 detectors for nitrogen N2, helium He, argon Ar. |  |  | kpl | 115 |  | 0
| kot na primer: DTG-2/IR/O2, merilno območje 0-25% O2, IP66 Tevel | such as DTG-2/IR/O2, measuring range 0-25% O2, IP66 Tevel
3.9 | Dobava in montaža detektorjev kisika O2. | Supply and installation of O2 detectors. |  |  | kpl | 16 |  | 0
| kot na primer: DTG-2/IR/O2, merilno območje 0-25% O2, IP66 Tevel | such as DTG-2/IR/O2, measuring range 0-25% O2, IP66 Tevel
3.8 | Dobava in montaža detektorjev vodika H2 | Supply and installation of H2 detectors |  |  | kpl | 17 |  | 0
| kot na primer: CTX300, 0-2000 ppm, Tevel, | such as CTX300, 0-2000 ppm, Tevel,
| komplet s priborom za montažo. | complete with mounting accessories.
3.11 | Dobava in montaža detektorja metana CH4 | Supply and installation of a CH4 methane detector |  |  | kpl | 15 |  | 0
| kot na primer: CO-I, 0-50% SME, IP66, Tevel | such as CO-I, 0-50% SME, IP66, Tevel
3.12 | Dobava in montaža detektorja amoniaka NH3 | Supply and installation of an NH3 ammonia detector |  |  | kpl | 15 |  | 0
| kot na primer: CTX300, 0-1000 ppm, IP66, Tevel | such as CTX300, 0-1000 ppm, IP66, Tevel
| komplet s priborom za montažo. | complete with mounting accessories.
3.13 | Dobava in montaža detektorja monoksida CO | Supply and installation of CO |  |  | kpl | 5 |  | 0
| kot na primer: CO-I, 0-250ppm, IP66, Tevel | such as CO-I, 0-250ppm, IP66, Tevel
3.13 | Dobava in montaža detektorjev kisika CO2. | Supply and installation of CO2 oxygen detectors. |  |  | kpl | 26 |  | 0
| kot na primer: DTG-2(R)/IR/CO2, merilno območje 0-5% CO2, IP66 Tevel | such as DTG-2(R)/IR/CO2, measuring range 0-5% CO2, IP66 Tevel
3.15 | Dobava in montaža detektorja acitelena C2H2 | Supply and installation of an acitelene C2H2 detector |  |  | kpl | 2 |  | 0
| Tevel | Tevel
3.14 | Dobava in montaža detektorja zemeljskega plina ZP | Supply and installation of a ZP natural gas detector |  |  | kpl | 8 |  | 0
| kot na primer: S-JP/K , merilno območje 0-60% SME CO2, IP65, Tevel | such as: e.g. S-JP/K , measuring range 0-60% SME CO2, IP65, Tevel
| komplet s priborom za montažo. | complete with mounting accessories.
3.17 | Dobava in montaža modularnega semaforja, sestavljen iz 2x svetlobni modul, 1x sirena, premera cca. 60mm, 24V AC/DC, IP65, s priborm za montažo na strop prostora, v naslednji sestavi: | Supply and installation of a modular traffic light, consisting of 2x light module, 1x siren, approx. 60mm diameter, 24V AC/DC, IP65, with fittings for ceiling mounting, as follows: |  |  | kpl | 74 |  | 0
| - osvetlitvena enota, oranžna barva | - illumination unit, orange | kos | 1
| - osvetlitvena enota, oranžna barva | - illumination unit, orange | kos | 1
| - zvočno-alarmna enota, 100 dB | - sound-alarm unit, 100 dB | kos | 1
| - baza s stebričkom, komplet s priborom za montažo na strop prostora | - base with column, complete with accessories for mounting on the ceiling of the room | kos | 1
| kot na primer: Signalna bliskavica s hupo, TWS HS/02,IP65, Tevel | such as: signal flash with horn, TWS HS/02,IP65, Tevel
3.18 | Dobava in montaža alarmne sirene za zvočno in svetlobno signalizacijo, zgrajena iz ohišja iz poliestra, piskača in bliskavice, napajanje 12-24VDC, IP65, komplet s priborom za montažo. kot na primer: ASB12-24, Tevel. | Supply and installation of an alarm siren for sound and light signalling, made of polyester housing, beeper and flash, power supply 12-24VDC, IP65, complete with mounting accessories. such as ASB12-24, Tevel. |  |  | kos | 39 |  | 0
3.19 | Dobava in montaža enostranskega svetlobnega tabloja z napisom (POZOR PLIN ZAPUSTI PROSTOR), 12-24VDC, komplet s priborom za montažo, kot na primer: Opozorilni tablor 12/24VDC, Tevel | Supply and installation of a single-sided light board with the inscription (CAUTION GAS LEAVE THE ROOM), 12-24VDC, complete with mounting accessories, such as: 12/24VDC warning lamp, Tevel |  |  | kpl | 84 |  | 0
3.20 | Dobava in montaža enostranskega svetlobnega tabloja z napisom (POZOR PLIN NE VSTOPAJ), 12-24VDC, komplet s priborom za montažo, kot na primer: Opozorilni tablor 12/24VDC, Tevel | Supply and installation of a single-sided light board with the inscription (WARNING GAS DO NOT ENTER), 12-24VDC, complete with mounting accessories, such as: 12/24VDC warning lamp, Tevel |  |  | kpl | 97 |  | 0
3.21 | Dobava in montaža tipke za izklop v sili, ohišje s steklenim delom pokrova, tipkalom in dvema kontaktoma za fazno krmiljenje, rumene barve, IP55, s priborm za montažo, namenjen za zapiranje ventila na dovodu zemeljskega plina, kot na primer: Tipkalo za izklop v sili 42201, Tevel. | Supply and installation of emergency stop button, housing with glass cover, push button and two contacts for phase control, yellow, IP55, with mounting accessories, designed to close the valve on the natural gas inlet, such as: emergency stop button 42201, Tevel. |  |  | kpl | 8 |  | 0
3.22 | Dobava in polaganje krmilno-signalni kabla na kabelske police in delno uvlačenje v cevi, vključno z označevalnimi ploščicami, razvodnicami ter drobnim in spojnim materialom, Odziv na ogenj vsaj Cca s1 d2 a1. Kabli brez halogena. | Supply and installation of control-signalling cables on cable racks and partial insertion into conduits, including marker plates, conduit, and small and jointing materials, Fire-resistance rating not less than Cca s1 d2 a1. Cables shall be halogen-free.
| - LiHCH 5x1,5 mm2 | - LiHCH 5x1,5 mm2 |  |  | m | 6500 |  | 0
| - LiHCH 4x1,5 mm2 | - LiHCH 4x1,5 mm2 |  |  | m | 450 |  | 0
| - LiHCH 3x1,5 mm2 | - LiHCH 3x1,5 mm2 |  |  | m | 4650 |  | 0
3.23 | 'Dobava in polaganje na kabelske police oz. uvlečenje v inštalacijske cevi, vključno z označevalnimi ploščicami, razvodnicami ter drobnim in spojnim materialom: | Supply and installation on cable racks or insertion into conduits, including marker plates, conduit boxes, small and jointing materials:
| -F/FTP-Category 6A, 4x2x23 AWG, brezhalogenski, kot naprimer: Leviton | -F/FTP-Category 6A, 4x2x23 AWG, halogen-free, such as Leviton |  |  | m | 630 |  | 0
3.24 | Dobava in polaganje na kabelske police oz. uvlečenje v inštalacijske cevi, vključno z označevalnimi ploščicami, razvodnicami ter drobnim in spojnim materialom, odziv na ogenj vsaj Cca s1 d2 a1. Kabli brez halogena. | Supply and installation on cable racks or insertion into conduits, including marker plates, conduit boxes, fittings and joints, reaction to fire not less than Cca s1 d2 a1. Cables shall be halogen-free.
| -N2XH-J 3x4 mm² | -N2XH-J 3x4 mm² |  |  | m | 750 |  | 0
| -N2XH-J 4x1,5 mm² | -N2XH-J 4x1,5 mm² |  |  | m | 5200 |  | 0
| -N2XH-J 3x1,5 mm² | -N2XH-J 3x1,5 mm² |  |  | m | 850 |  | 0
3.25 | Priključitev elektromagnetnega ventila na dovodu helija He na nadzorno centralo javljanja plinov. | Connection of the solenoid valve on the helium He inlet to the gas monitoring control panel. |  |  | kos | 8 |  | 0
3.26 | Priključitev elektromagnetnega ventila na dovodu argona Ar na nadzorno centralo javljanja plinov. | Connection of the solenoid valve on the Ar argon inlet to the gas monitoring control panel. |  |  | kos | 22 |  | 0
3.27 | Priključitev elektromagnetnega ventila na dovodu kisika O2 na nadzorno centralo javljanja plinov. | Connecting the solenoid valve on the O2 inlet to the gas monitoring control panel. |  |  | kos | 15 |  | 0
3.28 | Priključitev elektromagnetnega ventila na dovodu dušika N2 na nadzorno centralo javljanja plinov. | Connection of the solenoid valve on the N2 nitrogen inlet to the gas monitoring control panel. |  |  | kos | 25 |  | 0
3.29 | Priključitev elektromagnetnega ventila na dovodu vodika H2 na nadzorno centralo javljanja plinov. | Connection of the solenoid valve at the H2 hydrogen inlet to the gas monitoring control panel. |  |  | kos | 7 |  | 0
3.30 | Priključitev elektromagnetnega ventila na dovodu ogljikovega dioksida CO2 na nadzorno centralo javljanja plinov. | Connecting the solenoid valve at the CO2 inlet to the gas monitoring control panel. |  |  | kos | 12 |  | 0
3.31 | Priključitev elektromagnetnega ventila na dovodu dušikovega oksidula N2O na nadzorno centralo javljanja plinov. | Connecting the solenoid valve on the N2O inlet to the gas monitoring control panel. |  |  | kos | 3 |  | 0
3.32 | Priključitev elektromagnetnega ventila na dovodu zemeljskega plina ZP na nadzorno centralo javljanja plinov. | Connection of the solenoid valve at the ZP natural gas inlet to the gas monitoring control panel. |  |  | kos | 5 |  | 0
3.33 | Priključitev elektromagnetnega ventila na dovodu amonjaka NH3 na nadzorno centralo javljanja plinov. | Connecting the solenoid valve on the NH3 ammonia inlet to the gas monitoring control panel. |  |  | kos | 4 |  | 0
3.34 | Priključitev elektromagnetnega ventila na dovodu ogljikovega monoksida CO na nadzorno centralo javljanja plinov. | Connection of the solenoid valve at the CO inlet to the gas monitoring control panel. |  |  | kos | 3 |  | 0
3.35 | Priključitev elektromagnetnega ventila na dovodu metana CH4 na nadzorno centralo javljanja plinov. | Connecting the solenoid valve on the CH4 methane inlet to the gas monitoring control panel. |  |  | kos | 4 |  | 0
3.36 | Umerjenje merilnih glav za javljanje kisika O2 s strani proizvajalca ozi. serviserja. | Calibration of O2 sensing heads by the manufacturer or service technician. |  |  | kpl | 131 |  | 0
3.37 | Umerjenje merilnih glav za javljanje vodika H2 s strani proizvajalca ozi. serviserja. | Calibration of hydrogen H2 sensing heads by the manufacturer or service technician. |  |  | kpl | 17 |  | 0
3.38 | Umerjenje merilnih glav za javljanje ogljikovega dioksida CO2 s strani proizvajalca ozi. serviserja. | Calibration of CO2 measuring heads by the manufacturer or service technician. |  |  | kpl | 26 |  | 0
3.39 | Umerjenje merilnih glav za javljanje zemeljskega pliina ZP s strani proizvajalca ozi. serviserja. | Calibration of the measuring heads for ground tide ZP by the manufacturer or repairer. |  |  | kpl | 8 |  | 0
3.40 | Umerjenje merilnih glav za javljanje amonjaka NH3 s strani proizvajalca ozi. serviserja. | Calibration of NH3 ammonia detection measuring heads by the manufacturer or service technician. |  |  | kpl | 15 |  | 0
3.41 | Umerjenje merilnih glav za javljanje ogljikovega monoksida CO s strani proizvajalca ozi. serviserja. | Calibration of the carbon monoxide CO detector heads by the manufacturer or service technician. |  |  | kpl | 5 |  | 0
3.42 | Umerjenje merilnih glav za javljanje metana CH4 s strani proizvajalca ozi. serviserja. | Calibration of CH4 methane detection measuring heads by the manufacturer or service technician. |  |  | kpl | 15 |  | 0
3.43 | Umerjenje merilnih glav za javljanje acetilina C2H2 s strani proizvajalca ozi. serviserja. | Calibration of C2H2 acetylene reporting heads by the manufacturer or repairer. |  |  | kpl | 2 |  | 0
3.43 | Označevanje javljalnikov plina. | Marking of gas detectors. |  |  | kpl | 219 |  | 0
3.45 | Dobava in polaganje izolacijskih cevi in inšalacijskih kanalov: | Supply and installation of insulation pipes and ducts:
| -Zaščitna PVC PN cev za notranje elektroinštalacije, fi 13,5-29, vključno z drobnim montažnim materialom | -PVC PN protective hose for indoor electrical installations, fi 13,5-29, including small installation materials |  |  | m | 850 |  | 0
| -Zaščitna PVC RB cev za notranje elektroinštalacije, fi 16-48, | -PVC RB shielding pipe for indoor electrical installations, fi 16-48, |  |  | m | 520 |  | 0
| - Nerjaveče kovinske zaščitne cevi INOX fi 25-70, komplet z pritrdilnim priborom | - Stainless metal protective tubes INOX fi 25-70, complete with fittings |  |  | m | 100 |  | 0
3.46 | Izdelava priključkov na signalnih elementih. | Making connections at signal elements. |  |  | kos | 302 |  | 0
3.47 | Izdelava priključkov na elementih v coni 2 eksplozivne ogroženosti. | Making connections to elements in explosion hazard zone 2. |  |  | kos | 5 |  | 0
3.48 | Priklop centrale javljanja plina preko vmesnikov (5 stanj) na centralo javljanja požara. | Connection of the gas alarm control panel via interfaces (5 states) to the fire alarm control panel. |  |  | kpl | 7 |  | 0
3.49 | Izdelava programske opreme na glavnem nadzornem računalniku za nadzor nad sistemom javljanja plinov na lokaciji v obsegu: | Development of software on the main control computer to control the on-site gas detection system in the following scope: |  |  | kpl | 1 |  | 0
| -izdelava grafičnega nadzornega sistema na lokaciji, finalno parametriranje, testiranje sistema; | -development of a graphical on-site control system, final parameterisation, testing of the system; | kpl | 1
| - vnos tlorisov v grafični del SCADA; | - entering floor plans into the graphical part of SCADA; | št.t. | 3
| -vnos točk (javljalniki, semaforji, hupe, tipke, ...); | -entry points (beacons, traffic lights, horns, keys, etc.); | kpl | 1
| -prenos podatkov iz konfiguracijske datoteke plinske centrale na grafične podlage, ki vključuje: | -transfer of data from the gas plant configuration file to graphical bases, including: | kpl | 1
| -razdelitev javljalnikov po posameznih etažah, | -the distribution of beacons on each floor, | kpl | 1
| -določitev atributov vsakega javljalnika, ki omogočajo ustrezno barvanje za ponazoritev stanja točke (rdeča, rumena, oranžna, zelena, modra) v odvisnosti od dogodka, ki ga vsaka točka lahko generira (alarm, izklop, napaka, normalno stanje, nealarmni dogodek), | -defining the attributes of each annunciator to allow appropriate colouring to represent the state of the point (red, yellow, orange, green, blue) depending on the event that each point can generate (alarm, trip, fault, normal, non-alarm), | kpl | 1
| -natančno razporeditev javljalnikov po posameznih prostorih na grafičnem tlorisu, | -the exact arrangement of the beacons in each room on a graphical floor plan, | kpl | 1
| -definiranje klientov in njihov dostop do baze dogodkov itd.... | -defining clients and their access to the event database etc.... | kpl | 1
3.50 | Izdelava tesnenja prehodov kablov in kabelskih inštalacij skozi požarne sektorje, ki ga z ustreznimi materiali izvede izvajalec z licenco ter na koncu izda ustrezni certifikat (izvedba in uporabljen material v skladu s standardom). | Sealing of cable penetrations and cable installations through fire sectors, carried out by a licensed contractor using appropriate materials and finally certified (execution and material used in accordance with the standard). |  |  | kos | 10 |  | 0
3.51 | Vrtanje odprtin v stenah in ploščah do fi 60 mm | Drilling holes in walls and panels up to 60 mm fi |  |  | kos | 10 |  | 0
3.52 | Programiranje centrale, meritve, označevanje javljalnikov, nastavitve in spuščanje sistema za javljanje hlapov v obratovanje, izdelava kalibracijskih listov in poročila o zagonu | Control panel programming, measurements, marking of detectors, setting up and commissioning of the vapour detection system, production of calibration sheets and commissioning reports |  |  | kpl | 1 |  | 0
3.53 | Povezava krmilnikov klimata v sistem javljanja plina ter izvedba krmiljenja v primeru alarma. | Connection of climate controllers to the gas detection system and control in the event of an alarm. |  |  | kpl | 1 |  | 0
3.54 | Programiranje centrale, meritve, označevanje javljalnikov, nastavitve in spuščanje sistema za javljanje hlapov v obratovanje, izdelava kalibracijskih listov in poročila o zagonu | Control panel programming, measurements, marking of detectors, setting up and commissioning of the vapour detection system, production of calibration sheets and commissioning reports |  |  | kpl | 1 |  | 0
3.55 | Pregled in preizkus vgrajenega sistema javljanja hlapov s pridobitvijo pozitivnega potrdila pooblaščene inštituicje | Inspection and test of the installed vapour detection system with positive certification by an approved body |  |  | kpl | 1 |  | 0
3.56 | Izdelava zbirne dokumentacije certifikatov ATEX in izjav o skladnosti, za opremo izvedeno v protieksplozijski zaščiti, 1 izvod | Preparation of summary documentation of ATEX certificates and declarations of conformity for explosion-proof equipment, 1 copy |  |  | kpl | 1 |  | 0
3.57 | Prisotnost serviserjev pri pregledu aktivne protiplinske zaščite | Presence of technicians at the inspection of the active gas protection system |  |  | kpl | 1 |  | 0
3.58 | Priprava seznama in predaja certifikatov in izjav vgrajene opreme | Listing and handing over of certificates and declarations of installed equipment |  |  | kpl | 1 |  | 0
3.59 | Izobraževanje uporabnikov in vzdrževalcev | User and maintenance training |  |  | kpl | 1 |  | 0
| JAVLJANJE PLINA | GAS REPORTING | [5 empty] | 0

## 3.9.4_Ostalo
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.9 | ELEKTRO DELA | ELECTRICAL WORKS
3.9.4 | OSTALO | OTHER |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
4 | OSTALO | OTHER
4.1 | Priprava podlog za izdelavo PID projekta. Vnos sprememb, do katerih pride med izvedbo, v en izvod PZI projekta. | Preparation of the basis for the PID project. Entry of changes that occur during implementation in one copy of the PID project. | kpl | 1 |  | 0
4.2 | Integracija centralne naprave za javljanje požara na osnovno nadzorno postajo: | Integration of the central fire detection and fire alarm system into the basic control station:
| - IQ in OQ izvedba testiranja varnostnega nadzornega sistema vključno s pripravo kvalifikacijske dokumentacije | - IQ and OQ testing of the security control system including preparation of qualification documentation | kpl | 2 |  | 0
4.3 | Izvedba OQ testa slišnosti požarnih siren ob sodelovanju nadzornika in SVZD po celotnem objektu. V primeru nezadostne slišnosti akustičnega signala je potrebno ustrezno povečati število siren. | Carry out an OQ test of the audibility of the fire sirens with the participation of the supervisor and the SAWS throughout the building. In case of insufficient audibility of the acoustic signal, the number of sirens should be increased accordingly. | kpl | 1 |  | 0
4.4 | Navodila za obratovanje in vzdrževanje. Izdelana natančna obratovalna navodila glede posameznih stikalnih manipulacij in komunikacij za zagotavljanje rezervnega napajanja in ponovne vzpostavitve normalnega napajanja. | Operating and maintenance instructions. Detailed operating instructions on individual switching manipulations and communications to ensure back-up power and restoration of normal power supply. | kpl | 1 |  | 0
4.5 | Pozitivne ocene, atesti, certifikati in potrdila ustreznih inštitucij za dokazovanje primerne kakovosti vgrajenih naprav, napeljav, materialov in montažnih del (EIMV, IVD, ZAG, SIQ in podobno). | Positive evaluations, attestations, certificates and attestations of the relevant institutions to prove the adequate quality of the installed devices, installations, materials and assembly works (EIMV, IVD, ZAG, SIQ, etc.). | kpl | 1 |  | 0
| Opomba: | Remark:
| Dobavitelj opreme prilagodi projekt za izvedbo PZI na izbrano oziroma ponujeno opremo! | The equipment supplier adapts the PZI project to the equipment selected or offered!
| OSTALO | OTHER |  |  |  | 0