## 0_Naslovnica
OPOZORILO! Vsi prevodi v angleščino so strojno izdelani in zgolj informativne narave. V primeru kakršnekoli nejasnosti ali dvoma izključno velja izvirno besedilo v slovenščini. WARNING! All translations into English have been produced by machine translation and are provided for informational purposes only. In the event of any ambiguity or uncertainty, the original Slovenian text shall prevail exclusively.
| / | / | [5 empty] | /
| Sprem./Rev.: | Opis spremembe/Description of Changes: | [5 empty] | Datum/Date: | Podpis/Signature:
| Investitor/Investor: |  |  |  |  | Gradnja/Facility
|  |  | Univerza v Ljubljani Kongresni trg 12 1000 Ljubljana, Slovenija |  |  | Fakulteta za strojništvo/Faculty of Mechanical Engineering
| Projektant/Design Engineer: |  |  |  |  | Del objekta/sistem/Building/System:
|  |  | IBE, svetovanje, projektiranje in inženiring Ljubljana, Slovenija |  |  | STAVBA FAKULTETE/FACULTY BUILDING
| Projektant/Design Engineer: |  |  |  |  | Vrsta načrta/Documentation:
3 NAČRT S PODROČJA ELEKTROTEHNIKE/ DOC. IN THE FIELD OF ELECTRICAL ENGINEERING
|  | Ime in priimek/Name and Surname: |  |  | Id. št./Id. No: | Vsebina risbe (dokumenta)/Document Title:
| Vodja proj./ Des. Manager: | Boštjan Vuga, univ. dipl. inž. arh., grad. dip. (AA) |  |  | ZAPS 0035 PA PPN | PR. POPIS ELEKTRO DEL/BOQ OF ELEC. WORKS 3/10 Tehnično varovanje in pristopna kontrola/Technical Security and Access Control
| Poobl. strok./ Cert. Profess.: | Klemen Kavčič, univ. dipl. inž. el. |  |  | IZS E-1713
| Poobl. strok./ Cert. Profess.: |  |  |  |  | Št. proj./ Proj. No.: | 362-19 |  | Vrsta dokument./ Document. Type: | DZR
| Izdelal/ Creator: | Robert Stavar el. teh energ. Enis Rokša, mag. inž. el. |  |  |  | Klas. ozn./ Class. No.: | -- |  | Stran/ Page: | 1/*
| Datum/ Date: | maj/May 2026 |  | Merilo/ Scale: | / | Ident. ozn./ Id. No: | JULFS--6E9462P

## 0_Osebe
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
POOBLAŠČENI STROKOVNJAKI, ODGOVORNI ZA IZDELAVO PROJEKTANTSKEGA POPISA:
Id. št. ZAPS/IZS | Pooblaščeni strokovnjak | Strokovno področje
IZS E-1713 | Klemen Kavčič, univ. dipl. inž. el. | Električne inštalacije
SODELAVCI PRI IZDELAVI PROJEKTANTSKEGA POPISA:
/ | Robert Stavar el. teh energ. | Električne inštalacije - tehnično varovanje
CERTIFIED EXPERTS RESPONSIBLE FOR ELABORATING THE BILL OF QUANTITIES:
Id. No ZAPS/IZS | Certified Expert | Area of Expertise
IZS E-1713 | Klemen Kavčič, univ. dipl. inž. el. | Electrical installations
COLABORATORS IN THE ELABORATING THE BILL OF QUANTITIES:
/ | Robert Stavar el. teh energ. | Electrical installations - technical protection

## 0.1_Uvod-STP
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
0.1 | SPLOŠNI TEHNIČNI POGOJI | GENERAL TECHNICAL CONDITIONS
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic operator with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
0.1.1 | Izvajalec se obveže, da bo upošteval veljavno zakonodajo, ki ureja graditev objektov v Republiki Sloveniji, vključno s povezanimi podzakonskimi akti, predpisi, tehničnimi smernicami, standardi, pravili stroke in dobro gradbeno prakso. Prav tako mora izvajalec upoštevati vse zahteve izdanega integralnega gradbenega dovoljenja in vsa dela izvesti skladno s projektno dokumentacijo ter ostalimi pogoji, objavljenimi v razpisni dokumentaciji. | The Contractor undertakes to comply with the applicable legislation governing the construction of buildings in the Republic of Slovenia, including related by-laws, regulations, technical guidelines, standards, professional rules and good construction practice. The Contractor shall also comply with all the requirements of the integral building permit issued and shall carry out all works in accordance with the project documentation and other conditions published in the tender documentation.
0.1.2 | Dela lahko izvaja samo izvajalec, ki je registriran za opravljanje gradbene dejavnosti in ima za tovrstna dela ustrezno zavarovanje za škodo, certifikate, tehnično izobražen kader, sredstva ter je usposobljen za samostojno pripravo in izvedbo del. | The work may only be carried out by a contractor who is registered to carry out construction work and who has the appropriate insurance for such work, certificates, technically trained staff, resources and is qualified to prepare and carry out the work independently.
0.1.3 | Izvajalec odgovarja za kakovost izvedbe vseh del. | The Contractor shall be responsible for the quality of the execution of all works.
0.1.4 | Izvajalec nosi vso odgovornost za nesreče in škodo, ki nastane na objektu ali v okolici zaradi njegovega dela. | The Contractor shall bear all liability for accidents and damage to the installation or the surrounding area caused by his work.
0.1.5 | Pred oddajo ponudbe se je izvajalec dolžan seznaniti z območjem predvidenim za gradnjo in temu prilagoditi vsa potrebna dela, kar mora biti zajeto v ponudbi. V neposredni bližini predvidene gradnje se nahajajo stavbe, v katerih potekajo izobraževalni in raziskovalni procesi. Zato bo izvajalec moral izvajati kontrolo hrupa in kontrolo vibracij. Dela, ki so hrupna in dela, ki povzročajo vibracije bo izvajalec moral preprečiti oziroma jih izvesti na način, da povzročajo minimalne vplive. Tehnologijo rušenja, pilotiranja in tehnologijo izvedbe ostalih del bo izvajalec moral prilagoditi tako, da bo vpliv minimalen. Izvajalec mora preprečiti in zmanjšati emisije delcev iz gradbišča na najmanjšo možno mero. | Before submitting a tender, the contractor is obliged to familiarise himself with the area to be constructed and to adapt any necessary works accordingly, which must be included in the tender. In the immediate vicinity of the proposed construction, there are buildings in which educational and research processes take place. The contractor will therefore be required to carry out noise and vibration control. Noise and vibration works will have to be avoided or carried out in such a way as to minimise the impact. Demolition, piling and other works will have to be adapted to minimise the impact. The contractor must avoid and minimise the emission of particulates emitted from the construction site as far as is reasonably practicable.
0.1.6 | Izvajalec je pred oddajo ponudbe dolžan pregledati projektno dokumentacijo in ostale pogoje, ki so del razpisne dokumentacije V primeru morebitnih napak in neskladij je izvajalec dolžan na to opozoriti naročnika pred oddajo ponudbe. | The Contractor is obliged to review the project documentation and other conditions forming part of the tender documentation before submitting the tender In case of any errors or inconsistencies, the Contractor is obliged to bring these to the attention of the Contracting Authority before submitting the tender.
0.1.7 | Pred oddajo ponudbe je izvajalec dolžan preveriti ustreznost popisov del in količin v teh popisih ter njihovo skladnost z ostalimi dokumenti projektne dokumentacije, ki so del razpisne dokumentacije. Prav tako je izvajalec dolžan preveriti vse detajle in sheme. Vse izmere je potrebno preveriti po posameznih projektih oz. načrtih, ki sestavljajo razpisno dokumentacijo. V primeru ugotovljenih neskladij je v času priprave ponudbe obvezan o tem obvestiti naročnika. | Before submitting a tender, the Contractor shall check the adequacy of the inventories of works and quantities in these Bills of Quantities and their conformity with the other documents of the project documentation forming part of the tender documentation. The Contractor shall also check all details and diagrams. All measurements shall be checked against the individual projects or plans forming part of the tender documentation. In the event of any discrepancies, the Contractor shall inform the Contracting Authority at the time of preparing the tender.
0.1.8 | Pred oddajo ponudbe je izvajalec dolžan v tem popisu preveriti zmnožke in seštevke ter prenose le-teh v rekapitulacijo. Izvajalec se s pripravo ponudbe obvezuje, da je prebral vse celice in elemente celotnega popisa, vključno z vsemi postavkami in splošnimi navodili ali določili in je preveril pravilnost preračuna ter s tem zagotavlja ponudbeno vrednost. | Before submitting a tender, the Contractor is required to check the products and totals in this Bill of Quantities (BoQ) and their transfer to the recapitulation. The Contractor undertakes, by preparing a tender, to have read all the cells and elements of the complete BoQ, including all headings and general instructions or provisions, and to have checked the correctness of the conversion, thereby guaranteeing the value of the tender.
0.1.9 | Dela bo izvajalec moral izvajati po predloženi projektni dokumentaciji, detajlih in z upoštevanjem navodil in potrditev projektanta, nadzornika in investitorja. Vso potrebno delavniško dokumentacijo zagotovi izvajalec del v okviru ponujene cene. | The Contractor shall carry out the works in accordance with the submitted design documents, details and subject to the instructions and approvals of the Designer, the Supervisor and the Investor. All necessary workshop documentation shall be provided by the Contractor within the scope of the price quoted.
0.1.10 | Pred izvedbo posameznih del je izvajalec dolžan pregledati projektno dokumentacijo za izvedbo gradnje (PZI) in elaborate. Na morebitne napake v dokumentaciji ali neskladja med posameznimi načrti ali deli načrtov (popisi del, tehnična poročila, lokacijski in tehnični prikazi) izvajalec opozori nadzornika in projektanta, in se z njima pravočasno uskladi. | The Contractor shall review the Detailed Design documentation (PZI) and the studies before carrying out the individual works. The Contractor shall draw the attention of the Supervisor and the Designer to any errors in the documentation or discrepancies between the individual designs or parts of designs (BoQ, technical reports, location and technical drawings) and shall coordinate with them in good time.
0.1.11 | Tehnični opisi, prikazi, detajli, sheme ter ostali dokumenti v PZI dokumentaciji predstavljajo dodaten opis popisnih postavk gradbeno obrtniških in inštalacijskih del ter jih je potrebno dosledno upoštevati skupaj s popisom del. | The technical descriptions, illustrations, details, diagrams and other documents in the Detailed Design documentation (PZI) are additional descriptions of the BoQ inventory items of the building, construction and installation works and must be strictly followed together with the BoQ.
0.1.12 | Specifikacije in zahteve, navedene v popisu, se ne smejo upoštevati kot edine zahteve. Izvajalec je dolžan v ceni zajeti in dobaviti vse elemente opreme ter opraviti dela in storitve, ki niso eksplicitno navedeni, a so bistvenega pomena za funkcionalnost, skladnost s predpisi ter kontinuirano, zanesljivo in varno obratovanje opreme. | The specifications and requirements set out in the BoQ shall not be taken as the only requirements. The Contractor shall be obliged to include in the price and supply all items of equipment and to carry out works and services which are not expressly mentioned but which are essential for the functionality, regulatory compliance and continuous, reliable and safe operation of the equipment.
0.1.13 | Vsa dela morajo biti izvedena kvalitetno in iz materialov z zahtevanimi lastnostmi, izvedena skladno z veljavno zakonodajo in z upoštevanjem navodil za vgradnjo za izbrane materiale in opremo, s predložitvijo predpisanih izjav o lastnostih in/ali certifikatov. Vsi gradbeni proizvodi (GP) morajo biti označeni s CE oznako. | All work shall be of good quality and be executed with materials of the required characteristics, in accordance with the applicable legislation and in compliance with the installation instructions for the materials and equipment selected, and shall be accompanied by the prescribed declarations of performance and/or certificates. All construction products (GP) shall bear the CE marking.
0.1.14 | Za vsako opisano delo v popisu je potrebno upoštevati celotno potrebno delo, ves osnovni in pomožni material, prevoz materiala in orodja na objekt, notranje transporte, delovne in pomožne odre, zaključno čiščenje in odstranitev odpadkov po dovršenem delu. | For each work described in the inventory, the total work required, all basic and ancillary materials, the transport of materials and tools to the site, internal transports, working and ancillary scaffolding, final cleaning and the disposal of waste after the work has been completed must be taken into account.
0.1.15 | Vsa delovna sredstva, organizacija in koordinacija del, pripravljalna, spremljajoča in zaključna dela, potrebni montažni in tesnilni materiali ter podkonstrukcije so sestavni del posameznih postavk. | All labour, organisation and coordination of the works, preparatory, accompanying and finishing works, necessary prefabrication and sealing materials and substructures are part of the individual items.
0.1.16 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - načrt organizacije gradbišča s podrobnim terminskim planom in izvedba vseh pripravljalnih del, postavitev, organizacija, zaščita in prijava gradbišča, gradbiščnih objektov, ureditev začasnih deponij, tekoče vzdrževanje, skupaj s plačilom splošnih stroškov pristojbin in davkov upravnih organov, pridobivanju raznih dovoljenj in soglasij za izvedbo, ograditev gradbišča in postavitev gradbene table in prometne signalizacije, zagotavljanje ustrezne varnosti na gradbišču, tekoče vzdrževanje in končna odstranitev gradbišča; - zagotovitev potrebnih začasnih površin za transportne poti in gradnjo izven območja gradbišča s plačilom stroškov za sanacijo in vzpostavitev okoliških zemljišč in objektov v prvotno stanje (soglasja, odškodnine, itd.); - začasni odvoz, deponiranje in vračanje izkopanega materiala, ki ga ne bo možno deponirati na gradbišču; - odvoz in zagotovitev odstranjevanja odpadnega gradbenega materiala skladno z zakonodajo na področju ravnanja z odpadki (odvoz na urejene deponije s plačilom komunalnih prispevkov in taks itd.); - oteženi izkop v mokrem terenu, izkop v vodi, odvod meteorne vode iz gradbene jame in vode, ki se izceja iz bočnih strani izkopov; - ustrezno varovanje izkopa gradbene jame za objekt in ostalih manjših posameznih izkopov za izvedbo komunalne infrastrukture brez posegov na sosednja zemljišča; - ustrezno varovanje obstoječih objektov, infrastrukture in okolice v času gradnje ter dokumentiranje vseh morebitnih škodnih dogodkov; - pripravljalna, spremljajoča in zaključna dela (zakoličbe, zagotovitev potrebnih komunalnih priključkov za potrebe izvajanja gradnje, izvedba začasnih inštalacij, označevanje podzemnih vodov, postavljanje in vzdrževanje zakoličbenih profilov, izvedba in označevanje novih in starih križanj ter morebitna zaščita križanj komunalnih vodov, geodetski posnetki in izdajanje vmesnih posnetkov izvedene infrastrukture naročniku, izdelava zbirnih kart, itd.), v kolikor ni to drugače določeno; - pridobivanje soglasij in izvedba morebitnih zapor na vseh cestah s plačilom stroškov, nadomestil in pristojbin; - zagotovitev oz. postavitev in končna odstranitev po zaključku gradnje začasnih skladišč in začasnega pisarniškega kontejnerskega objekta vključno z opremo za dve delovni mesti in za skupne operativne sestanke vel. ca. 40 m2 za potrebe naročnika, s tekočim vzdrževanjem in čiščenjem. | The following must also be included or taken into account in the uniform prices for individual items: - a construction site organisation plan with a detailed timetable and the execution of all preparatory works, the setting-up, organisation, protection and registration of the construction site, site facilities, the arrangement of temporary storage facilities, ongoing maintenance, including the payment of general costs of fees and taxes of the administrative authorities, the obtaining of various permits and consents for the execution, the fencing of the site and the erection of construction signs and traffic signals, the provision of adequate security on the site, ongoing maintenance and the final dismantling of the construction site; - provision of the necessary temporary areas for transport routes and off-site construction, with costs for restoration and reinstatement of surrounding land and buildings (consents, compensation, etc.); - temporary removal, storage and return of excavated material that cannot be stored on site; - removing and disposing of waste building materials in accordance with waste management legislation (removal to regulated landfill sites with payment of municipal fees and charges, etc.); - difficult excavation in wet ground, excavation in water, drainage of rainwater from the construction pit and water draining from the sides of excavations; - adequate protection of the excavation of the construction pit for the building and other small individual excavations for the implementation of the utility infrastructure without encroaching on neighbouring land; - adequate protection of existing facilities, infrastructure and the surrounding area during construction, and documentation of any damage incidents; - preparatory, accompanying and finishing works (stake-out, provision of the necessary utility connections for the needs of construction, execution of temporary installations, marking of underground lines, installation and maintenance of stake-out profiles, execution and marking of new and old crossings and possible protection of crossings of utility lines, geodetic surveys and issuing of intermediate images of the completed infrastructure to the client, production of summary maps, etc.), unless otherwise specified; - obtaining consents and implementing any road closures, with costs, compensation and fees; - provision or erection and final removal on completion of construction of temporary storage and temporary office container building including equipment for two workstations and for joint operational meetings of approx. 40 m2 for the needs of the client, with ongoing maintenance and cleaning.
0.1.17 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - izdelava montažne tehnične dokumentacije, detajlov izvedbe in vse druge potrebne delavniške dokumentacije (s področja arhitekture, gradbeništva, elektrotehnike, strojništva in zunanje ter krajinske ureditve) ter pridobitev obvezne potrditve s strani projektanta, nadzornika in investitorja; - odprava vseh vrst inštalacijskih kolizij z izvajanjem potrebnih premikov inštalacij in njihovim usklajevanjem na mestu montaže, vse v obsegu, ki ne vpliva na projektirano rešitev ali tip inštalacij oz. opreme; - zagotavljanje kompletnosti elektro-instalacijskih sistemov s področja avtomatike za doseganje njihove popolne funkcionalnosti delovanja; - stroški za nadzor in koordinacijo izvedbe vseh elektro napeljav, ki so predmet končne instalacije proizvoda (senčila, vrata, okna,…); - izdelava montažnih skic in detajlov za izvedbo v dogovoru z vodjo gradnje in nadzornikom; - izdelava in predstavitev vzorcev v ustrezni velikosti za potrditev projektanta, nadzornika in investitorja; - zagotavljanje varnosti in zdravja pri delu, zlasti izvajanje vseh del, ki izhajajo in ukrepov, ki izhajajo iz določil veljavnih predpisov varstva pri delu in zahtev Varnostnega načrta;- stroški garancij, ki jih mora izvajalec predložiti naročniku. | The following must also be included or taken into account in the uniform prices for individual items: - preparation of prefabricated technical documentation, construction details and all other necessary workshop documentation (architectural, civil, electrical, mechanical, exterior and landscaping) and obtaining the mandatory approval of the designer, the supervisor and the investor; - elimination of all types of installation conflicts by carrying out the necessary relocation of installations and their coordination at the installation site, all to the extent that it does not affect the design solution or the type of installation or equipment; - ensuring the completeness of electrical installation systems in the automation sector to achieve their full operational functionality; - the cost of supervising and coordinating the installation of all the electrical installations that are the subject of the final installation of the product (blinds, doors, windows, etc.); - preparation of erection drawings and details for implementation in agreement with the construction manager and supervisor; - production and presentation of samples in appropriate sizes for the approval of the designer, the supervisor and the investor; - ensuring health and safety at work, in particular the implementation of all the works arising from and the measures resulting from the provisions of the applicable occupational safety regulations and the requirements of the Safety Plan; - the cost of the guarantees to be provided by the contractor to the client.
0.1.18 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - strošek vodje del glavnega izvajalca, ki bo izvajal tudi koordinacijo s podizvajalci in z drugimi izvajalci, ki jih bo izbral naročnik in bo opravljal delo vodje gradbišča; - koordinacija del z ostalimi izvajalci oz. podizvajalci del, projektantom, nadzornikom in investitorjem pri medsebojnem usklajevanju organizacije gradbišča in časovnega načrta del ter pri usklajevanju izdelave plana montaže, potrjenih s strani vseh udeležencev gradnje; - stroški koordinacije, sodelovanja in usklajevanja z dobavitelji tehnološke, laboratorijske, eksperimentalne in vse ostale pohištvene ter multimedijske opreme ter z vsemi ostalimi dobavitelji oz. podizvajalci na objektu; - stroški izdelave situacij; - stroški zavarovanja objekta v času izvedbe del in delavcev ter materiala na gradbišču v času izvajanja del, od začetka del do pridobitve uporabnega dovoljenja za objekt. Zavarovanje mora biti sklenjeno pri ustrezni zavarovalni družbi najmanj v višini pogodbene vrednosti ali v zakonsko predpisani vrednosti (v kolikor zavarovanje v višini pogodbene vrednosti presega zakonsko dovoljeno), za ves čas trajanja izvedbe del do uspešne primopredaje objekta; - preizkušanje kvalitete materiala, ki se vgrajuje in dokazovanje kvalitete s certifikati oz. tehničnimi soglasji; - izvedba vseh zahtevanih testov in preizkusov (npr. tlačni preizkusi, termografski pregledi, meritve elektromagnetnega sevanja, hrupa, itd.), poskusnega obratovanja celotnega objekta s poudarkom na vseh inštalacijah ter izvajanje predpisanega monitoringa v skladu s Poročilom o vplivih na okolje (pred gradnjo, med gradnjo in po končani gradnji); - izdelava izkaza požarne varnosti, vključno s sprotnim spremljanjem gradnje in izvajanjem požarnovarnostnih zahtev ter izdelava Požarnega reda z obveznimi prilogami; - izdelava Izkaza zaščite pred hrupom v stavbah; - izdelava Izkaza energijskih lastnosti stavbe in energetske izkaznice; - sodelovanje z izvajalci gradbenega in projektantskega nadzora in investitorjem za izvedbo tehničnega pregleda in priprava primopredaje, ki mora vsebovati vso zahtevano dokumentacijo, predvsem pa: izjave o skladnosti, požarni izkaz in ostale izkaze ter obvezne tabele, dokazilo o zanesljivosti objekta (DZO), certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo in vzdrževanje ter vse ostale dokumente v skladu s predpisi in pogodbenimi določili. | The following must also be included or taken into account in the uniform prices of the individual items: - the cost of a works manager for the main contractor, who will also coordinate with subcontractors and other contractors selected by the client and act as site manager; - coordination of the works with other contractors or subcontractors, the designer, the supervisor and the investor in coordinating the organisation of the construction site and the timetable for the works, and in coordinating the production of an installation plan approved by all the participants in the construction; - the costs of coordination, cooperation and coordination with suppliers of technological, laboratory, experimental and all other furniture and multimedia equipment, as well as with all other suppliers or subcontractors on the site; - the cost of drawing up situations; - the cost of insuring the building during the execution of the works and the workers and materials on site during the execution of the works, from the start of the works until the building has been licensed for occupation. The insurance must be taken out with a suitable insurance company for at least the contract value or the legal value (if the insurance for the contract value exceeds the legal value), for the entire duration of the works until the successful handover of the building; - testing the quality of the material to be installed and proving it with certificates or technical approvals; - carrying out all required tests and trials (e.g. pressure tests, thermographic inspections, electromagnetic radiation measurements, noise measurements, etc.), trial operation of the entire building, with emphasis on all installations, and carrying out the required monitoring in accordance with the Environmental Impact Assessment Report (before, during and after construction); - preparation of a fire safety statement, including ongoing monitoring of construction and implementation of fire safety requirements, and preparation of a Fire Safety Order with mandatory annexes; - preparation of a Noise Protection Statement for buildings; - preparation of the Building Energy Performance Report and Energy Performance Certificate; - cooperation with the construction and design supervision contractors and the investor to carry out the technical inspection and prepare the handover, which must include all the required documentation, in particular: declarations of conformity, fire and other statements and mandatory tables, proof of reliability of the building (DZO), certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use and maintenance, and all other documents in accordance with the regulations and the contractual provisions.
0.1.19 | V enotnih cenah posameznih postavk, ki se nanašajo na opremo in posamezne sisteme, mora biti zajeto oz. upoštevano tudi naslednje: - dobava oz. transport, - stroški za vse delovne stroje za dvigovanje bremen in delovne košare za dostope do delovišč; - morebitni stroški povzročeni upravljavcem GJI, ki bi nastali v zvezi s predmetno gradnjo; - montaža, vključno s pomožnim montažnim materialom (vezni, tesnilni in pritrdilni material, sidra, nosilni profili, podkonstrukcije in podobno) in navodili proizvajalca, - odprava vseh kolizij sistemov s stenami in med sistemi, - izvedba vseh potrebnih tesnjenj, - priključitev in nastavitve, vključno z morebitnim kalibriranjem, - zagon, testiranje in meritve, vključno s poročili, - šolanje uporabnikov oz. vzdrževalnega osebja za uporabo in vzdrževanje sistemov, - navodila za obratovanje in vzdrževanje, - vsi potrebni certifikati, izjave o skladnosti oz. potrdila ter - vsa druga pomožna dela in material, da se zagotovi funkcionalnost posamezne postavke popisa. | The following must also be included or taken into account in the uniform prices for individual items relating to equipment and individual systems: - delivery/transport, - the cost of all lifting machines and work baskets for access to work sites; - any costs incurred to the operators of utility infrastructure (GJI) in connection with the subject construction; - installation, including ancillary installation materials (bonding, sealing and fixing materials, anchors, support profiles, substructures, etc.) and manufacturer's instructions, - eliminating all system-to-wall and system-to-system collisions, - all necessary sealing work, - connection and set-up, including calibration if necessary, - commissioning, testing and measurements, including reports, - training users or maintenance staff in the use and maintenance of the systems, - operating and maintenance instructions, - any necessary certificates, declarations of conformity or attestations; and - all other ancillary works and materials to ensure the functionality of each inventory item.
0.1.20 | Vsi odri morajo biti upoštevani v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All scaffolding must be included in the uniform prices of the items listed, except where specifically mentioned.
0.1.21 | Vsi delovni in pomožni odri, lestve in ostala potrebna pomožna sredstva, kot tudi čiščenje vseh elementov po končanih delih, mora biti upoštevano v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All working and auxiliary scaffolding, ladders and other necessary ancillaries, as well as the cleaning of all elements after completion of the works, shall be included in the uniform prices of the items listed, except those specifically mentioned.
0.1.22 | Delavniško dokumentacijo za vse nosilne jeklene konstrukcije in podkonstrukcije izdela izvajalec, strošek izdelave delavniške dokumentacije se upošteva v ponujenih cenah in se ne obračuna posebej. | The cost of the shop drawings for all steelwork and substructures shall be included in the prices quoted and shall not be charged separately.
0.1.23 | V enotnih cenah postavk mora biti vključeno tudi vgrajevanje vseh instalacijskih razvodov v opaže armirano betonskih elementov in izdelava prehodov inštalacij ter dodatno izrezovanje utorov in prebojev v kamnite, zidane ali armirano-betonske stene, ponovno demontiranje in montiranje vseh vrst montažnih sten, vsa dodatna dela za zagotavljanje primernih križanj med posameznimi instalacijskimi vodi, izdelava vseh vrst ojačitev konstrukcij in podobna dela, ki zagotavljajo kakovostno vgradnjo vseh vrst instalacijskih vodov in niso posebej navedena v popisu GOI del. V ponudbi morajo biti upoštevana vsa drobna strojna in elektro instalacijska dela in transporti. | The installation of all installation ducts in the formwork of reinforced concrete elements and the construction of installation penetrations, as well as the additional cutting of grooves and penetrations in stone, masonry or reinforced concrete walls, the reassembly and reinstallation of all types of prefabricated walls, all additional work to ensure adequate crossings between individual installation ducts, the construction of all types of structural reinforcement and similar work to ensure the quality installation of all types of installation ducts and not specifically mentioned in the BoQ of the Construction, installation and finishing works (GOI) shall also be included in the uniform prices of the items. The tender shall take into account all minor mechanical and electrical installation work and transport.
0.1.24 | Vsi kovinski elementi in konstrukcije, ki bi lahko bili izpostavljeni atmosferskim in ostalim korozijskim vplivom, morajo biti ustrezno protikorozijsko zaščiteni. | All metallic elements and structures that could be exposed to atmospheric and other corrosive influences must be adequately protected against corrosion.
0.1.25 | Za vse večje jeklene dele se skladno s predpisi, izdelajo ustrezne ozemljitve, nevidno pritrjene in speljane na splošno ozemljitev objekta. | For all major steel parts, appropriate earth connections shall be made in accordance with the regulations, invisibly attached and connected to the general earth of the building.
0.1.26 | Za vse vidne elemente in serijske elemente je obvezna predhodna uskladitev obdelav, barv in materialov s projektantom na podlagi dostavljenih vzorcev v ustrezni velikosti. Obvezna je preveritev dejanskih mer na licu mesta in posledična prilagoditev elementov in njihove montaže. | For all visible elements and serial elements, it is mandatory to coordinate the finishes, colours and materials with the designer beforehand on the basis of the supplied samples in the appropriate size. It is mandatory to check the actual dimensions on site and to adjust the elements and their installation accordingly.
0.1.27 | Dimenzije obrtniških izdelkov in količine je potrebno pred naročanjem preveriti na objektu. Potrebna je uskladitev vseh elementov (kljuke, okovje, detajlne konstrukcije in obdelave, itd.) s projektantom, nadzornikom in investitorjem. Izvajalec je dolžan pred izdelavo predložiti projektantu v potrditev ustrezne delavniške načrte in detajle. | The dimensions of the workmanship and quantities must be checked on site before ordering. All elements (hooks, fittings, detailed construction and finishes, etc.) must be coordinated with the designer, the supervisor and the investor. The contractor is obliged to submit the relevant workshop plans and details to the designer for approval before manufacture.
0.1.28 | V posameznih postavkah popisa so navedeni proizvajalci in/ali tipi posameznih sistemov, materialov ali opreme, s čimer so zgolj natančno opredeljene zahtevane tehnične lastnosti. Izvajalec del lahko ponudi nadomesten sistem, material ali opremo drugega proizvajalca in tipa, pri čemer morajo biti tehnične lastnosti ponujenega sistema, materiala ali opreme enakovredne ali boljše od opredeljenih v popisu, dimenzijsko pa ne smejo presegati projektiranih dimenzij. Vse funkcijske in tehnične karakteristike nadomestnih sistemov, materialov ali opreme mora izvajalec dokazati z ustrezno dokumentacijo. Vse morebitne posledice zaradi spremembe sistemov, materialov ali opreme vključno z morebitnimi spremembami oz. dopolnitvami BIM modelov in projektne dokumentacije, stroškovno in časovno bremenijo izvajalca. | The individual items of the Inventory shall specify the manufacturers and/or types of the individual systems, materials or equipment, thereby merely specifying the required technical characteristics. The Contractor may offer a substitute system, material or equipment of a different manufacturer and type, provided that the technical characteristics of the offered system, material or equipment shall be equivalent to or better than those specified in the BoQ, and shall not exceed the design dimensions. All functional and technical characteristics of the substitute systems, materials or equipment shall be demonstrated by the Contractor with appropriate documentation. Any consequences resulting from changes to systems, materials or equipment, including any changes or additions to the BIM models and project documentation, shall be borne by the Contractor in terms of cost and time.
0.1.29 | Vsako zamenjavo, uporabo in končni izbor nadomestnih sistemov, materialov, proizvodov in opreme morajo obvezno in pravočasno (pred dobavo in vgradnjo) pisno potrditi projektant (vseh sodelujočih strok), nadzornik in investitor. | Any replacement, use and final selection of alternative systems, materials, products and equipment must be approved in writing by the designer (of all disciplines involved), the supervisor and the investor in a timely manner (prior to delivery and installation).
0.1.30 | Izvajalec mora v ponudbeno ceno vključiti tudi: - ves čas gradnje sprotno beleženje sprememb oz. odstopanj od PZI dokumentacije, vključno z izdelavo tekstualnega opisa sprememb, - pripravo podlog na nivoju PZI, ki so potrebne za posodobitev oz. uskladitev BIM modela z izvedenim stanjem (LOD 500) in izdelavo projektne dokumentacije izvedenih del (PID), - mesečno predajanje potrjenih sprememb opreme in materiala, ki vplivajo na BIM model, v formatu IFC, - vzdrževanje in uporabljanje pri izvedbi zadnje veljavne revizije PZI dokumentacije, vključno z dopolnitvami PZI načrtov, ki so nastali zaradi sprememb med gradnjo. | The contractor must also include in the tender price: - keeping a record of changes or deviations from the construction documentation (PZI) throughout construction, including a textual description of the changes, - preparation of the Detailed Design (PZI) level documents required to update or align the BIM model with the as-built condition (LOD 500) and the preparation of the as-built project documentation for the works (PID), - monthly submission of approved equipment and material changes affecting the BIM model in IFC format, - maintenance and use in the execution of the last valid revision of the construction documentation (PZI), including additions to the construction design documentation (PZI) resulting from changes during construction.

## 0.2_Uvod-DGNB
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
0.2 | SPLOŠNI TEHNIČNI POGOJI ZA PODROČJE DGNB CERTIFICIRANJA | GENERAL TECHNICAL CONDITIONS FOR DGNB CERTIFICATION
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic entity with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
| Splošni pogoji za področje DGNB certificiranja predstavljajo dopolnilo splošnim tehničnim pogojem in ne odpravljajo drugih obveznosti in odgovornosti, ki jih ima izvajalec v skladu s predpisi in pogodbo. | The General Conditions for DGNB Certification are complementary to the General Technical Conditions and do not exclude other obligations and responsibilities that the Contractor has under the Regulations and the Contract.
0.2.1 | Izvajalec mora v svojih ponudbah upoštevati, da se bo objekt certificiral v skladu z zahtevami DGNB sistema certificiranja trajnostne gradnje, ter pravočasno (vsaj 60 dni pred vgradnjo posameznega produkta) dostaviti vso ustrezno dokumentacijo za vse v ponudbi zajete materiale, elemente in opremo. Zahtevana je uporaba materialov, elementov ali opreme, ki so okolju in ljudem prijazni, energetsko učinkoviti in obenem ustrezajo zahtevam DGNB sistema. Zahtevan nivo certifikata je: ZLATI CERTIFIKAT | The Contractor shall take into account in its tenders that the building will be certified in accordance with the requirements of the DGNB Sustainable Building Certification Scheme and shall deliver all relevant documentation for all materials, elements and equipment included in the tender in a timely manner (at least 60 days before the installation of each product). The use of materials, elements or equipment that are environmentally and human friendly, energy efficient and at the same time meet the requirements of the DGNB system is required. The required level of certification is: GOLD CERTIFICATE
0.2.2 | Podrobnejši opis DGNB sistema in navodila za posamezne kriterije so dostopna v dokumentu"DGNB Criteria Set New Construction Buildings, Version 2020 International", ki je na voljo na DGNB spletni strani https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria | A more detailed description of the DGNB system and guidance on the individual criteria is available in the document "DGNB Criteria Set New Construction Buildings, Version 2020 International", available on the DGNB website https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria
0.2.3 | Izvajalec mora v svojih ponudbah upoštevati, da je potrebno skladno z določili DGNB certifikacijskega sistema, pravočasno (pred pričetkom gradnje) dostaviti vso ustrezno dokumentacijo, za vse v ponudbi zajete materiale, elemente in opremo (tehnični list, varnostni list, izjava o lastnostih, tehnična navodila za ravnanje, servisiranje, vzdrževanje,...) v slovenskem jeziku. Vgradnja kakršnihkoli materialov, elementov ali opreme, se izvede zgolj na podlagi predhodne preveritve posredovane dokumentacije in obenem potrditve s strani nadzornika. | The Contractor must take into account in its tenders that, in accordance with the provisions of the DGNB certification system, all relevant documentation for all materials, elements and equipment included in the tender (technical data sheet, safety data sheet, declaration of properties, technical instructions for handling, servicing, maintenance,...) must be delivered on time (prior to the start of construction) in the Slovene language (in accordance with the provisions of the DGNB certification system). The installation of any materials, elements or equipment shall be subject to prior checking of the submitted documentation and, at the same time, to the approval of the Supervisor.
0.2.4 | Izbrani materiali, elementi, naprave, sistemi in oprema morajo prispevati k večji trajnosti stavbe v smeri zagotavljanja energetske učinkovitosti, ekonomičnega in enostavnega vzdrževanja ter čiščenja, dolge življenjske dobe, uporabe okolju prijaznih materialov ipd. | The materials, elements, appliances, systems and equipment chosen must contribute to the sustainability of the building in terms of energy efficiency, economic and easy maintenance and cleaning, long lifetime, use of environmentally friendly materials, etc.
0.2.5 | Predloženi dokumenti za vse uporabljene materiale, elemente in opremo morajo izpolnjevati zahteve najmanj kakovostne stopnje QS3 (zaželeno QS4), iz dokumenta: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001) | The documents submitted for all materials, components and equipment used shall meet the requirements of at least quality level QS3 (preferably QS4) of the document DGNB Quality Grades for Materials, Components and Equipment (JULFS--7X9001)
0.2.6 | V kolikor izbrani materiali oz. elementi, navedeni v posameznih postavkah, ne ustrezajo vsaj kakovostni stopnji QS3 iz seznama: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), je izvajalec dolžan na to opozoriti projektanta, nadzor in investitorja ter podati predlog ustreznega materiala oz. elementa. | If the selected materials or elements listed in the individual items do not meet at least quality level QS3 of the list of DGNB quality classes for materials, elements and equipment (JULFS--7X9001), the Contractor shall draw this to the attention of the Designer, the Supervisor and the Investor, and shall make a proposal for a suitable material or element.
0.2.7 | Izvajalec lahko v svoji ponudbi predlaga alternativne produkte in rešitve glede na predvidene s projektom, pod pogojem, da le-te prav tako izpolnjujejo vse navedene zahteve. Pri morebitnih predlaganih alternativnih produktih oz. rešitvah je potrebno upoštevati najmanj enake ali boljše lastnosti v smislu življenjske dobe, obstojnosti, ter enostavnosti in stroška čiščenja ter vzdrževanja v primerjavi s projektom predpisanimi rešitvami. Za alternativne rešitve izvajalec pridobi soglasje projektanta, nadzornika in investitorja pred pričetkom gradnje. | The Contractor may propose alternative products and solutions to those envisaged by the project in its tender, provided that they also meet all the requirements set out above. Any alternative products or solutions proposed shall have at least the same or better characteristics in terms of service life, durability, and ease and cost of cleaning and maintenance compared to the solutions envisaged by the project. For alternative solutions, the contractor shall obtain the agreement of the designer, the supervisor and the investor before starting construction.
0.2.8 | Izvajalec med gradnjo dnevno beleži vsa eventualna odstopanja od PZI projektne dokumentacije ter podatke pravočasno posreduje naročniku, nadzoru in projektantu. Potrjene spremembe vnese v podlage za izdelavo PID in posodobitev BIM modelov. | During construction, the Contractor shall record on a daily basis any deviations from the Detailed Design documentation (PZI) and shall provide the information to the Client, Supervision and the Designer in a timely manner. Confirmed changes shall be entered into the basis for the As-built documentation (PID) and BIM model updates.
0.2.9 | Izvajalec med gradnjo sproti izpolnjuje Seznam vseh konstrukcijskih sestav s pripadajočimi vgrajenimi gradbenimi materiali in dokumentira naslednje podatke o vgrajenih materialih (v slovenskem jeziku): - Varnostni list - Tehnični list - Izjavo o lastnostih (če je relevantno) - Izkazovanje morebiti obstoječega okoljskega certifikata (Tip I - okoljski znak ali Tip III - okoljska produktna deklaracija /EPD) - Izjavo proizvajalca ali dobavitelja, da produkt ustreza zahtevam ENV1.2 - Tehnična navodila za ravnanje, servisiranje, vzdrževanje oziroma ostale, z zakonom predpisane dokumente in dokumentacijo. | During construction, the Contractor shall keep a List of all structural assemblies with their associated construction materials and document the following information on the materials installed (in Slovene language): - Safety Data Sheet - Technical Data Sheet - Declaration of performance (if applicable) - Demonstration of any existing environmental certification (Type I - Ecolabel or Type III - Environmental Product Declaration /EPD) - A declaration by the manufacturer or supplier that the product complies with the requirements of ENV1.2 - Technical instructions for handling, servicing, maintenance or other documents and documentation required by law.
0.2.10 | Za vse vgrajene bistvene tehnične sisteme mora izvajalec zagotoviti obstoj pooblaščenega servisa, ki deluje na območju Republike Slovenije, da ima investitor možnost skleniti ustrezno pogodbo o vzdrževanju. Med bistvene tehnične sisteme sodijo npr.: sistemi ogrevanja in hlajenja, priprava tehnoloških medijev, prezračevanje in klimatizacija, sistemi detekcije in gašenja požara, sistemi tehničnega varovanja, BMS in CNS sistemi upravljanja stavbe, razsvetljava, komunikacijski in WI-FI sistemi,... | For all installed essential technical systems, the contractor must ensure the existence of an authorised service centre operating in the territory of the Republic of Slovenia, so that the investor has the possibility of concluding an appropriate maintenance contract. The essential technical systems include, for example: heating and cooling systems, technological media preparation, ventilation and air conditioning, fire detection and extinguishing systems, technical security systems, BMS and CNS building management systems, lighting, communication and WI-FI systems,...
0.2.11 | Zaželeno je, da imajo uporabljeni elementi in materiali okoljsko oznako Tip I. (kot npr. ENCODE, BLUE ANGEL, ipd...). | It is preferable that the elements and materials used have a Type I environmental label (such as ENCODE, BLUE ANGEL, etc...).
0.2.12 | Izvajalec bo za elemente iz lesa moral dokazovati izvor z navedbo izvorne države in tipa lesa, FSC / PEFC certifikat z dodatnim pripadajočim potrdilom Chain of custody-trgovski certifikat dobavitelja - ta se dokazuje z dobavnicami, računi ali enakovredno. Za izdelke iz naravnega kamna iz EU držav je potrebna deklaracija, da je izvor in procesiranje teh izdelkov v celoti v EU državah. Za izdelke iz naravnega kamna, ki prihajajo iz držav izven EU, je potrebno predložiti dokazilo o izpolnjevanju ILO konvencije 182, ki vključuje neodvisna inšpekcijska poročila. | For wood elements, the contractor will be required to provide proof of origin, indicating the country of origin and the type of wood, FSC/PEFC certification with an additional Chain of Custody certificate - the supplier's trade certificate - this shall be evidenced by delivery notes, invoices or equivalent. For natural stone products from EU countries, a declaration that the sourcing and processing of these products is entirely in EU countries is required. For natural stone products from non-EU countries, proof of compliance with ILO Convention 182, including independent inspection reports, is required.
0.2.13 | Izobraževanje udeležencev pri gradnji Izvajalec je dolžan vse udeležence pri gradnji podrobneje seznaniti tudi z relevantnimi koncepti, študijami, elaborati, ki opredelujejo trajnostni način gradnje za naslednja področja: - zaščita pred hrupom (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)) - zaščita pred prašenjem - zaščita tal in podzemne vode (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)), Analiza tveganja za onesnaženje vodnega telesa podzemne vode št. 0346-023/2023, maj 2023 (Geološko projektiranje d.o.o.)) - ravnanje z gradbenimi odpadki (Načrt gospodarjenja z gradbenimi odpadki) Izobraževanja se izvajajo skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.1 1.2, 2.2, 3.2 in 4.2 Training for the parties implementing the construction work | Training of construction participants The contractor is also obliged to inform all construction participants in detail about relevant concepts, studies, elaborations defining sustainable construction methods for the following areas: - noise protection (Environmental Impact Assessment Report No 100123-11523, dated 11.5.2023, supplemented on 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.)) - dust protection - protection of soil and groundwater (Environmental Impact Assessment Report No. 100123-11523, dated 11.5.2023, supplemented 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.), Risk analysis for contamination of the groundwater No. 0346-023/2023, May 2023 (Geološko projektiranje d.o.o.)) - construction waste management (Construction Waste Management Plan) The training shall be carried out in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.1 1.2, 2.2, 3.2 and 4.2 Training for the parties implementing the construction work
0.2.14 | Navodila za obratovanje in vzdrževanje objekta Izvajalec pripravi Navodila za obratovanje in vzdrževanje objekta skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilih: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual | Instructions for the operation and maintenance of the facility The Contractor shall prepare the Operation and Maintenance Instructions for the Facility in accordance with the applicable Slovenian legislation and the DGNB System Instructions specified in the Criteria: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual
0.2.15 | Meritve kontrole kakovosti gradnje Izvajalec mora upoštevati, da se bodo po koncu gradnje izvedle naslednje meritve: - meritve zrakotesnosti - meritve s termokamero (termografija) - meritve akustike - meritve zvočne zaščite ovoja stavbe - meritve zvočne zaščite ločilnih elementov med posameznimi prostori različnih namembnosti - meritve udarnega zvoka - meritve vlažnosti vgrajenih elementov, pred vgradnjo finalnih tlakov - test odvoda dima in toplote Meritve morajo opraviti ustrezno usposobljeni preskusni organi ali strokovnjaki ter rezultate oceniti in primerjati z zahtevami. Obseg opravljenih meritev mora biti sorazmeren z velikostjo zgradbe in mora ustrezno odražati cilj preverjanja kakovosti zgradbe. Smiselno je, da izvajalec del tekom gradnje za sprotno kontrolo kakovosti vgrajenih materialov, elementov in opreme, sam izvaja meritve. Končne meritve (ob primopredaji) izvede tretja oseba kot neodvisna potrditev doseganja zahtev. Meritve se izvajajo skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 2. Quality control measurements | Construction quality control measurements The contractor must take into account that the following measurements will be carried out after completion of the construction: - airtightness measurements - thermal camera measurements (thermography) - acoustics measurements - measurements of the sound insulation of the building envelope - measurements of the sound insulation of the separating elements between different rooms of different uses - impact sound measurements - moisture measurements of the installed elements, prior to the installation of the final flooring - smoke and heat extraction test The measurements shall be carried out by suitably qualified test bodies or experts and the results evaluated and compared with the requirements. The extent of the measurements carried out shall be proportionate to the size of the building and shall adequately reflect the objective of the building quality verification. It is reasonable for the contractor to carry out his own measurements during construction to check the quality of the materials, elements and equipment installed. Final measurements (at handover) are carried out by a third party as an independent confirmation of compliance with the requirements. The measurements shall be carried out in accordance with the applicable Slovenian legislation and the DGNB system instructions specified in the benchmark: PRO 2.2 2. Quality control measurements
0.2.16 | Zagotavljanje kakovosti za uporabljene gradbene proizvode Izvajalec mora zagotavljati izvajanje primerjav med definiranim in dejansko uporabljenim materialom, elementom ali opremo skladno seznamom: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), vključno z dokazno dokumentacijo ugotovitev primerjav ter skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 3.1 Quality assurance for the used construction products | Quality assurance for the construction products used The Contractor shall ensure that comparisons are made between the defined and the actual material, element or equipment used in accordance with the list: DGNB Quality Grades of Installed Materials, Elements and Equipment (JULFS--7X9001), including supporting documentation of the findings of the comparisons, and in accordance with the DGNB system instructions defined in the Criterion: PRO 2.2 3.1 Quality assurance for the used construction products
0.2.17 | Zaščita pred vlago Izvajalec predloži dokumentacijo, ki dokazuje, da je bil izveden program prezračevanja, prilagojen stavbi, s čimer se zagotovi pogoje, da so vgrajeni gradbeni elementi ustrezno suhi, skladno z navodili DGNB opredeljenimi v merilu: PRO 2.2 4.1 Mould prevention | Protection against moisture The Contractor shall provide documentation demonstrating that a building-specific ventilation programme has been implemented to ensure that the building elements installed are adequately dry, in accordance with the DGNB guidelines specified in the criteria: PRO 2.2 4.1 Mould prevention
0.2.18 | Preizkusi delovanja sistemov Izvajalec sodeluje pri izvedbi predhodnega in končnega preizkusa delovanja vseh bistvenih tehničnih komponent stavbe in pripravi ustrezne dokazne dokumentacije ter pri usposabljanju vzdrževalcev/upravljalcev stavbe, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators | System performance tests The Contractor shall be involved in the performance of the preliminary and final performance tests of all essential technical components of the building and the preparation of the relevant supporting documentation, as well as in the training of the maintenance/management staff of the building, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators
0.2.19 | Poročilo o zagonu objekta Izvajalec sodeluje pri pripravi končnega poročila o zagonu objekta, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 5.1 Creation of a detailed final report | Commissioning report The Contractor shall be involved in the preparation of the final commissioning report, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 5.1 Creation of a detailed final report
0.2.20 | Koncept celovitega delovanja sistemov v stavbi Izvajalec sodeluje pri procesu implementiranja stalnega nadzora in nastavitev delovanja stavbe ter usposabljanju vzdrževalcev/upravljalcev stavbe. Navedeno se izvede v skladu z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 6.1 Creation and handover of an integral operating concept | The concept of integrated building systems The contractor is involved in the process of implementing the building's continuous monitoring and settings and training the building's maintenance/management staff. This shall be done in accordance with the DGNB system instructions defined in the benchmark: PRO 2.3 6.1 Creation and handover of an integral operating concept
0.2.21 | Prilagoditev nastavitev sistemov po začetni fazi uporabe objekta Izvajalec sodeluje pri ponovnem pregledu delovanja vseh bistvenih tehničnih sistemov ter eventualni ponovni prilagoditvi teh sistemov s strani strokovnjaka oz. (neodvisne) tretje osebe. Postopek se izvede po približno 10–14 mesecih po zaključku gradnje, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 7.1 Readjustment of the system following initial operating phase | Adjusting system settings after the initial phase of use of the building The Contractor shall be involved in the re-examination of the functioning of all essential technical systems and the possible re-adjustment of these systems by an expert or (independent) third party. The procedure shall be carried out approximately 10-14 months after completion of construction, in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.3 7.1 Readjustment of the system following initial operating phase

## 3.10.0_Rekapitulacija
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
| REKAPITULACIJA STROŠKOV ELEKTRO DEL | COST SUMMARY OF ELECTRICAL WORKS
| 3 NAČRT S PODROČJA ELEKTROTEHNIKE | 3 DOCUMENTATION IN THE FIELD OF ELECTRICAL ENGINEERING
| 3/10 Tehnično varovanje in pristopna kontrola | 3/10 Technical Security and Access Control
3.10 | ELEKTRO DELA | ELECTRICAL WORKS
3.10.1 | SISTEM JAVLJANJE VLOMA | BURGLAR ALARM SYSTEM | 0
3.10.2 | SISTEM VIDEO NADZORA | VIDEO SURVEILLANCE SYSTEM | 0
3.10.3 | KONTROLA PRISTOPA | ACCESS CONTROL | 0
3.10.4 | OSTALO | OTHER | 0
0
0 | NEPREDVIDENA DELA | UNFORSEEN WORKS | 0
| SKUPAJ ELEKTRO DELA | TOTAL ELECTRICAL WORKS | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT

## 3.10.1_Javljanje vloma
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.10 | ELEKTRO DELA | ELECTRICAL WORKS
3.10.1 | SISTEM JAVLJANJE VLOMA | BURGLAR ALARM SYSTEM |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
1 | SISTEM JAVLJANJE VLOMA | BURGLAR ALARM SYSTEM
1.1 | Dobava in montaža alarmne centrale, 8 osnovnih področij, max. 192 področij, z vgrajenim napajalnikom 2,5A, 999 uporabniških gesel, možnost oddaljenega programiranja, akumulator 1X 7Ah (MB7.2Ah-12V), v ohišju s ključavnico in protisabotažnim mikrostikalom z transformatorjem 80VA (BOX80), SIST EN 50131 Grade 3, kot npr. PARADOX EVOHD+/PCB ali enakovredno | Supply and installation of alarm control panel, 8 basic zones, max. 192 zones, with built-in 2.5A power supply, 999 user passwords, remote programming, 1X 7Ah battery (MB7.2Ah-12V), in housing with lock and anti-tamper microswitch with 80VA transformer (BOX80), SIST EN 50131 Grade 3, e.g. PARADOX EVOHD+/PCB or equivalent | kos | 2 |  | 0
1.2 | Dobava in montaža komunikacijskega vmesnika Ethernet, za priklop alarmne centrale na omrežje Ethernet, podpora HTTPS, LAN/VAN/Internet, možnost lokalnega / oddaljenega programiranja, kompatibilnost z alarmno centralo, kot npr. PARADOX IP180 ali enakovredno | Supply and installation of an Ethernet communication interface for connecting the control panel to an Ethernet network, HTTPS support, LAN/VAN/Internet, local/remote programming capability, compatibility with an alarm control panel such as PARADOX IP180 or equivalent | kos | 2 |  | 0
1.3 | Dobava in montaža komunikacijskega modula LTE/2G/ GSM kot npr. PARADOX PCS265V7 ali enakovredno | Supply and installation of LTE/2G/ GSM communication module such as PARADOX PCS265V7 or equivalent | kos | 2 |  | 0
1.4 | Dobava in montaža razširitvenega modula, za 8 dodatnih področij, v ohišju s ključavnico, protisabotažna zaščita z mikrostikalom, kompatibilnost z alarmno centralo, SIS EN50131-3 Grade 3, kot npr. PARADOX ZX82 ali enakovredno | Supply and installation of an expansion module, for 8 additional areas, in a housing with lock, anti-tamper protection with microstrip, compatibility with alarm control panel, SIS EN50131-3 Grade 3, such as PARADOX ZX82 or equivalent | kos | 19 |  | 0
1.5 | Dobava in montaža dodatnega napajalnika 75W 100-240 Vac ali 13.8 Vdc Baterija ali 15 Vdc, AC 110 Vac do 240 Vac, 75W skupna moč, 15 Vdc 4.0A, s plinotesno baterijo 7Ah (MB7.2Ah-12V), polni nadzor, standalone delovanje ali nadzor centrale preko BUS povezave, ohišje s ključavnico, protisabotažna zaščita z mikrostikalom, kompatibilnost z alarmno centralo, kot npr. PARADOX PS45 ali enakovredno | Supply and installation of additional power supply 75W 100-240 Vac or 13.8 Vdc Battery or 15 Vdc, AC 110 Vac to 240 Vac, 75W total power, 15 Vdc 4.0A, with 7Ah gas-operated battery (MB7.2Ah-12V), full control, standalone operation or control of the control panel via BUS connection, housing with lock, anti-tamper protection with microswitch, compatibility with control panel such as PARADOX PS45 or equivalent | kos | 19 |  | 0
1.6 | Dobava in montaža LCD šifratorja v energetski objekt, za vklop/izklop sistema, nov dizajn z modrim LCD zaslonom z možnostjo prikaza do 32 znakov, Ena adresabilna cona, 1 x PGM izhod, tri panik tipke za EVO192 in EVOHD V beli barvi, SIST EN 50131 Grade 3, kot npr. PARADOX K641+ ali enakovredno | Supply and installation of an LCD encoder in the energy facility, for system on/off, new design with blue LCD display with the possibility of displaying up to 32 characters, One addressable zone, 1 x PGM output, three panic keys for EVO192 and EVOHD In white, SIST EN 50131 Grade 3, such as PARADOX K641+ or equivalent | kos | 13 |  | 0
1.7 | Dobava in montaža senzorja gibanja dvojne tehnologije, IR+MW, antimasking, pokritje 15x15m, napajanje 9.5-14.5V, poraba max. 100mA, SIST EN 50131 Grade 3, kot npr. PARADOX NVX80 ali enakovredno. | Supply and installation of dual technology motion sensor, IR+MW, anti-masking, 15x15m coverage, 9.5-14.5V power supply, 100mA max. power consumption, SIST EN 50131 Grade 3, such as PARADOX NVX80 or equivalent. | kos | 47 |  | 0
1.8 | Magnetno mikrostikalo, za kovinska vrata, priključni kabel, montažni komplet, zaključek priključnega kabla v standardni p/o dozi 60mm pri zgornjem robu podboja nad ostalo električno opremo prehoda oz. v spuščenem stropu, kot npr. ASSA ABLOY 10365 ali enakovredno | Magnetic microswitch, for metal doors, connecting cable, mounting kit, termination of the connecting cable in a standard 60mm p/o socket at the top edge of the soffit above other electrical equipment in the passageway or in the dropped ceiling, e.g. ASSA ABLOY 10365 or equivalent | kos | 49 |  | 0
1.9 | Dobava in montaža alarmne sirene za zunanjo uporabo, z vgrajeno bliskavko (rdečo), 109dB piskač, z akomulatorjem, kompatibilnost z alarmno centralo, SIST EN 50131 Grade 2, kot npr. Texecom Odyssey5E ali enakovredno | Supply and installation of an alarm siren for outdoor use, with built-in flash (red), 109dB beeper, with accouulator, compatibility with alarm control panel, SIST EN 50131 Grade 2, such as Texecom Odyssey5E or equivalent | kos | 11 |  | 0
1.10 | Dobava in montaža alarmne sirene za notranjo uporabo, z vgrajeno bliskavko (rdečo), 109dB piskač, z akomulatorjem, kompatibilnost z alarmno centralo, SIST EN 50131 Grade 2, kot npr. Texecom Odyssey5E ali enakovredno | Supply and installation of an alarm siren for indoor use, with built-in flash (red), 109dB beeper, with accouulator, compatibility with alarm control panel, SIST EN 50131 Grade 2, such as Texecom Odyssey5E or equivalent | kos | 3 |  | 0
1.11 | Dobava in montaža kamer (ko objekt ne obratuje delujejo kot protivlomne kamere) so specificirane v popisu video nadzora. | The supply and installation of cameras (when the building is not in operation they act as burglar cameras) are specified in the video surveillance inventory.
1.12 | Dobava in polaganje na kabelske police oz. uvlečenje v inštalacijske cevi, vključno z označevalnimi ploščicami, razvodnicami ter drobnim in spojnim materialom: | Supply and installation on cable racks or insertion into conduit pipes, including marker plates, conduit boxes, small and jointing materials:
| -Signalni alarmni kabel za dajalnike alarmnih stanj, LiYHCy 2x0,5 + 4x0,22mm2, brezhalogenski , Odziv na ogenj Eca kot naprimer Lappkabel: | -Alarm signal cable for alarm encoders, LiYHCy 2x0,5 + 4x0,22mm2, halogen-free, Eca fire response as for example Lappkabel: | m | 6100 |  | 0
1.13 | Dobava in polaganje na kabelske police oz. uvlečenje v inštalacijske cevi, vključno z označevalnimi ploščicami, razvodnicami ter drobnim in spojnim materialom: | Supply and installation on cable racks or insertion into conduit pipes, including marker plates, conduit boxes, small and jointing materials:
| -Komunikacijski kabel za povezave ražiritvenih modulov in tipkovnic, I-YH(St)Y 3x2x0,8mm, brezhalogenski, odziv na ogenj Eca kot naprimer Lappkabel: | -Communication cable for connection of control modules and keypads, I-YH(St)Y 3x2x0,8mm, halogen-free, Eca fire response as for example Lappkabel: | m | 1300 |  | 0
1.14 | Dobava in polaganje na kabelske police oz. uvlečenje v inštalacijske cevi, vključno z označevalnimi ploščicami, razvodnicami ter drobnim in spojnim materialom: | Supply and installation on cable racks or insertion into conduit pipes, including marker plates, conduit boxes, small and jointing materials:
| -F/FTP-Category 6A, 4x2x23 AWG, brezhalogenski, odziv na ogenj Eca. Kot naprimer Leviton: | -F/FTP-Category 6A, 4x2x23 AWG, halogen-free, reaction to fire Eca. As for example Leviton: | m | 90 |  | 0
1.15 | Dobava in polaganje na kabelske police oz. uvlečenje v inštalacijske cevi, vključno z označevalnimi ploščicami, razvodnicami ter drobnim in spojnim materialom, odziv na ogenj Eca. | Supply and installation on cable racks or insertion into conduits, including marker plates, conduit boxes and small and jointing materials, response to fire Eca.
| -Napajalni kabel NYM-J 3x1,5 mm², kot naprimer Lappkabel: | -Power cable NYM-J 3x1.5 mm², such as Lappkabel: | m | 750 |  | 0
1.16 | Sestavljanje, montaža in povezovanje vseh naprav alarmnega sistema | Assembling, installing and connecting all alarm system devices | kos | 167 |  | 0
1.17 | Povezovanje vseh kamer (ko objekt ne obratuje delujejo kot protivlomne kamere) na sistem javljanja vloma | Connection of all cameras (when the building is not in operation they act as burglar alarm cameras) to the intruder detection system | kos | 28 |  | 0
1.18 | Zagon sistema in programiranje obeh alarmnih central, programske opreme, vnos uporabnikov, nastavitev pravic, nastavitev režimov itd.. | System commissioning and programming of both control panels, software, user entry, rights settings, mode settings, etc. | kpl | 1 |  | 0
1.19 | Priklop videonadzora na sistem za javljanje vloma; sodelovanje dobavitelja / izvajalca | Connection of CCTV to intruder detection system; supplier/contractor involvement | kpl | 1 |  | 0
1.20 | Integracija obeh central, uvoz tlorisov, vnos vseh elementov, parametriranje elementov, programiranje interakcij med sistemi, izdelava / razvoj / prilagoditev komunikacijskih aplikacij | Integration of both control panels, import of floor plans, input of all elements, parameterisation of elements, programming of interactions between systems, creation / development / customisation of communication applications | kpl | 1 |  | 0
1.21 | Preizkus delovanja protivlomnega sistema | Burglar alarm system function test | kpl | 1 |  | 0
1.22 | Izobraževanje uporabnikov in vzdrževalcev | User and maintenance training | kpl | 1 |  | 0
1.23 | Uporabniška navodila za uporabo, obratovanje in vzdrževanje | User instructions for use, operation and maintenance | kpl | 1 |  | 0
1.24 | Pomožne nosilne konstrukcije kabelskega razvoda - hladno cinkano, ki jih ni možno izdelati s tipskimi elementi ( Hilti profili, navojne palice, obdelano profilno železo, itd. ). | Auxiliary cable support structures - cold galvanised, which cannot be manufactured with standard elements ( Hilti profiles, threaded rods, machined profile iron, etc.). | kg | 250 |  | 0
1.25 | Dobava in polaganje izolacijskih cevi in inšalacijskih kanalov: | Supply and installation of insulation pipes and ducts:
| -Zaščitna PVC RB cev za notranje elektroinštalacije, fi 16-48, | -PVC RB shielding pipe for indoor electrical installations, fi 16-48, | m | 1830 |  | 0
| -Zaščitna PVC PN cev za notranje elektroinštalacije, fi 13,5-29, vključno z drobnim montažnim materialom | -PVC PN protective hose for indoor electrical installations, fi 13,5-29, including small installation materials | m | 240 |  | 0
| SISTEM JAVLJANJE VLOMA | BURGLAR ALARM SYSTEM |  |  |  | 0

## 3.10.2_Video nadzor
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.10 | ELEKTRO DELA | ELECTRICAL WORKS
3.10.2 | SISTEM VIDEO NADZORA | VIDEO SURVEILLANCE SYSTEM | [5 empty] | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description |  |  | EM | Količina | Cena/EM | Cena
2 | SISTEM VIDEO NADZORA | VIDEO SURVEILLANCE SYSTEM
2.1 | Dobava in montaža prostostoječe kovinske omare za potrebe video nadzora z oznako +VN-P1 Omara dimenzije: 2200 mm x 800 mm x 800 mm (VxŠXG), 47U na podstavku višine 100 mm. Omara ima enokrilna steklena vrata po celi višini spredaj in kovinsko zadaj, uvod kablov zgoraj. Rittal, VX IT. Sestava omare je naslednja: | Supply and installation of a freestanding metal cabinet for video surveillance purposes, marked +VN-P1 Cabinet dimensions: 2200 mm x 800 mm x 800 mm (HxWxD), 47U on a 100 mm high base. The cabinet has a full-height single-leaf glass door at the front and a metal door at the rear, cable entry at the top. Rittal, VX IT. The wardrobe is composed as follows: |  |  | kpl | 1 |  | 0
| - omara video nadzora, Rittal, VX 5312.124 | - video surveillance cabinet, Rittal, VX 5312.124 | kos | 1
| - steklena vrata spredaj, VX IT 5051.215 | - glass door at front, VX IT 5051.215 | kos | 1
| - kovinska vrata zadaj, VX IT 5051.223 | - metal rear door, VX IT 5051.223 | kos | 1
| - stranska stena omare, VX 8128.245 | - side wall of cabinet, VX 8128.245 | kos | 2
| - standardni 19" montažni profil 47HE (sprednji) VX IT 5302.108 | - standard 19" mounting profile 47HE (front) VX IT 5302.108 | kos | 2
| - standardni 19" montažni profil 47HE (zadnji) VX IT 5302.109 | - standard 19" mounting profile 47HE (rear) VX IT 5302.109 | kos | 2
| - montažni nosilec 800 MM standardni, VX IT 5302.167 | - mounting bracket 800 MM standard, VX IT 5302.167 | kpl | 2
| - montažni nosilec 800 MM, VX IT 5302.169 | - mounting bracket 800 MM, VX IT 5302.169 | kos | 8
| - montažna letev 17x64 MM, 800 MM, VX 8617.040 | - mounting bar 17x64 MM, 800 MM, VX 8617.040 | kos | 2
| - ojačitveni kotnik za 19 profile 800 MM, IT 5302.124 | - reinforcement angle for 19 profiles 800 MM, IT 5302.124 | kpl | 1
| - streha, SV 9681.688 | - roof, SV 9681.688 | kos | 1
| - podstavek kotni element s ploščo spredaj/zadaj, 100 mm, VX 8640.003 | - pedestal corner element with front/rear panel, 100 mm, VX 8640.003 | kos | 2
| '- podstavek stranska zapiralna plošča, 100 mm, VX 8640.034 | - pedestal side closing plate, 100 mm, VX 8640.034 | kos | 2
| - vertikalni urejevalnik kablov, DK 5302.053 | - vertical cable cutter, DK 5302.053 | kos | 2
| - konfortna ročka za odpiranje, VX 8618.201, | - comfort opening handle, VX 8618.201, | kos | 1
| - cilinder vložek (Sistemski ključ LEK) TS8611.180 | - cylinder insert (LEK system key) TS8611.180 | kos | 1
| - ščetinasta zaščita uvoda kablov 2x1m, DK 7825.375 | - bristle cable entry protector 2x1m, DK 7825.375 | kos | 1
| - polica, DK 5501.665 | - shelf, DK 5501.665 | kos | 2
| - ventilator s filtrom, vgrajen na zgornjem delu kovinske stranice priključni kabel…, ventilator priklopljen preko svoje varovalke, SK 3239.108 | - fan with filter, mounted on the upper part of the metal side, connecting cable..., fan connected via its own fuse, SK 3239.108 | kos | 1
| - filterska rešetka vgrajena na spodnjem delu kovinske stranice, SK 3239.208 | - filter grate mounted on the lower part of the metal side, SK 3239.208 | kos | 1
| - končno stikalo SZ 4127.010 | - limit switch SZ 4127.010 | kos | 1
| - termostat, DK 19, 1HE, temperaturni prikazovalnik, SK 5302.041 | - thermostat, DK 19, 1HE, temperature display, SK 5302.041 | kos | 1
| - VT IT kotnik za vratno stikalo VX 5302.351 | - VT IT angle for door switch VX 5302.351 | kos | 1
| - predal za dokumentacijo, SZ 2514.000 | - documentation drawer, SZ 2514.000 | kos | 1
| - vtična razdelilna letev s 9 ''schuko'' vtičnicami, z vgrajeno prenapetostno zaščito tretje stopnje, DK 7240.330 | - plug-in distribution board with 9 "schuko" sockets, with built-in surge protector of third level, DK 7240.330 | kos | 2
| - enofazna nadometna vtičnica 230V, 16A, DK 7280.100 | - single-phase 230V, 16A, DK 7280.100 | kos | 2
| - v omaro so vgrajeni 19" okvirji (profili) za montažo ethernet stikala in ostale aktivne in pasivne opreme. | - 19" frames (profiles) for mounting Ethernet switches and other active and passive equipment are built into the cabinet.
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc.
| V video omaro +VN-P1 se dobavi in vgradi naslednja pasivna in aktivna oprema: | The following passive and active equipment shall be supplied and installed in the +VN-P1 video cabinet:
| - omrežno stikalo za potrebe video nadzora, 24x priključek LAN PoE (60W na izhod), 4xSFP multimode kot naprimer HP, CISCO. OPREMO DOBAVI IZVAJALEC VIDEO NADZORA | - network switch for video surveillance, 24x LAN PoE connector (60W per output), 4xSFP multimode such as HP, CISCO. EQUIPMENT SUPPLIED BY VIDEO CONTROL CONTRACTOR | kos | 1
| - urejevalnik kablov (organiser) 19”, kot naprimer Leviton tip: 1U Rack Mounted - 5 ring, (koda: MMCACCCM001) | - 19" cable manager (organiser), such as Leviton type: 1U Rack Mounted - 5 ring, (code: MMCACCCM001) | kos | 2
| - oprema specificirana pod pozicijo: 3.10.2.25, 3.10.2.24 | - equipment specified under headings: 3.10.2.25, 3.10.2.24 | kpl | 1
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, … | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc
2.2 | Dobava in montaža opreme v komunikacijsko omaro TK_P1_1- (Security) za sistem video nadzora. | Supply and installation of equipment in the TK_P1_1- (Security) communication cabinet for the video surveillance system. |  |  | kpl | 1 |  | 0
| - omrežno stikalo za potrebe video nadzora, 24x priključek LAN PoE (60W na izhod), kot naprimer HP, CISCO. OPREMO DOBAVI IZVAJALEC VIDEO NADZORA | - network switch for video surveillance, 24x LAN PoE connector (60W per output), such as HP, CISCO. SUPPLIED BY VIDEO CONTROL CONTRACTOR | kos | 2
| - urejevalnik kablov (organiser) 19”, kot naprimer Leviton tip: 1U Rack Mounted - 5 ring, (koda: MMCACCCM001) | - 19" cable manager (organiser), such as Leviton type: 1U Rack Mounted - 5 ring, (code: MMCACCCM001) | kos | 2
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, … | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc
2.3 | Dobava in montaža opreme v komunikacijsko omaro TK_P1_2- (Security) za sistem video nadzora. | Supply and installation of equipment in the TK_P1_2- (Security) communication cabinet for the video surveillance system. |  |  | kpl | 1 |  | 0
| - omrežno stikalo za potrebe video nadzora, 24x priključek LAN PoE (60W na izhod), kot naprimer HP, CISCO. OPREMO DOBAVI IZVAJALEC VIDEO NADZORA | - network switch for video surveillance, 24x LAN PoE connector (60W per output), such as HP, CISCO. SUPPLIED BY VIDEO CONTROL CONTRACTOR | kos | 1
| - urejevalnik kablov (organiser) 19”, kot naprimer Leviton tip: 1U Rack Mounted - 5 ring, (koda: MMCACCCM001) | - 19" cable manager (organiser), such as Leviton type: 1U Rack Mounted - 5 ring, (code: MMCACCCM001) | kos | 1
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, … | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc
2.4 | Dobava in montaža opreme v komunikacijsko omaro TK_P1_3- (Security) za sistem video nadzora. | Supply and installation of equipment in the TK_P1_3- (Security) communication cabinet for the video surveillance system. |  |  | kpl | 1 |  | 0
| - omrežno stikalo za potrebe video nadzora, 24x priključek LAN PoE (60W na izhod), kot naprimer HP, CISCO. OPREMO DOBAVI IZVAJALEC VIDEO NADZORA | - network switch for video surveillance, 24x LAN PoE connector (60W per output), such as HP, CISCO. SUPPLIED BY VIDEO CONTROL CONTRACTOR | kos | 2
| - urejevalnik kablov (organiser) 19”, kot naprimer Leviton tip: 1U Rack Mounted - 5 ring, (koda: MMCACCCM001) | - 19" cable manager (organiser), such as Leviton type: 1U Rack Mounted - 5 ring, (code: MMCACCCM001) | kos | 2
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, … | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc
2.5 | Dobava in montaža opreme v komunikacijsko omaro TK_P1_4- (Security) za sistem video nadzora. | Supply and installation of equipment in the TK_P1_4- (Security) communication cabinet for the video surveillance system. |  |  | kpl | 1 |  | 0
| - omrežno stikalo za potrebe video nadzora, 24x priključek LAN PoE (60W na izhod), kot naprimer HP, CISCO. OPREMO DOBAVI IZVAJALEC VIDEO NADZORA | - network switch for video surveillance, 24x LAN PoE connector (60W per output), such as HP, CISCO. SUPPLIED BY VIDEO CONTROL CONTRACTOR | kos | 2
| - urejevalnik kablov (organiser) 19”, kot naprimer Leviton tip: 1U Rack Mounted - 5 ring, (koda: MMCACCCM001) | - 19" cable manager (organiser), such as Leviton type: 1U Rack Mounted - 5 ring, (code: MMCACCCM001) | kos | 2
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, … | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc
2.6 | Dobava in montaža opreme v komunikacijsko omaro TK_P1_5- (Security) za sistem video nadzora. | Supply and installation of equipment in the TK_P1_5- (Security) communication cabinet for the video surveillance system. |  |  | kpl | 1 |  | 0
| - omrežno stikalo za potrebe video nadzora, 24x priključek LAN PoE (60W na izhod), kot naprimer HP, CISCO. OPREMO DOBAVI IZVAJALEC VIDEO NADZORA | - network switch for video surveillance, 24x LAN PoE connector (60W per output), such as HP, CISCO. SUPPLIED BY VIDEO CONTROL CONTRACTOR | kos | 1
| - urejevalnik kablov (organiser) 19”, kot naprimer Leviton tip: 1U Rack Mounted - 5 ring, (koda: MMCACCCM001) | - 19" cable manager (organiser), such as Leviton type: 1U Rack Mounted - 5 ring, (code: MMCACCCM001) | kos | 1
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, … | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc
2.7 | Dobava in montaža opreme v komunikacijsko omaro TK_P1_6- (Security) za sistem video nadzora. | Supply and installation of equipment in the TK_P1_6- (Security) communication cabinet for the video surveillance system. |  |  | kpl | 1 |  | 0
| - omrežno stikalo za potrebe video nadzora, 24x priključek LAN PoE (60W na izhod), kot naprimer HP, CISCO. OPREMO DOBAVI IZVAJALEC VIDEO NADZORA | - network switch for video surveillance, 24x LAN PoE connector (60W per output), such as HP, CISCO. SUPPLIED BY VIDEO CONTROL CONTRACTOR | kos | 1
| - urejevalnik kablov (organiser) 19”, kot naprimer Leviton tip: 1U Rack Mounted - 5 ring, (koda: MMCACCCM001) | - 19" cable manager (organiser), such as Leviton type: 1U Rack Mounted - 5 ring, (code: MMCACCCM001) | kos | 1
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, … | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc
2.8 | Dobava in montaža opreme v komunikacijsko omaro TK_N2_1- (Security) za sistem video nadzora. | Supply and installation of equipment in the TK_N2_1- (Security) communication cabinet for the video surveillance system. |  |  | kpl | 1 |  | 0
| - omrežno stikalo za potrebe video nadzora, 24x priključek LAN PoE (60W na izhod), kot naprimer HP, CISCO. OPREMO DOBAVI IZVAJALEC VIDEO NADZORA | - network switch for video surveillance, 24x LAN PoE connector (60W per output), such as HP, CISCO. SUPPLIED BY VIDEO CONTROL CONTRACTOR | kos | 2
| - urejevalnik kablov (organiser) 19”, kot naprimer Leviton tip: 1U Rack Mounted - 5 ring, (koda: MMCACCCM001) | - 19" cable manager (organiser), such as Leviton type: 1U Rack Mounted - 5 ring, (code: MMCACCCM001) | kos | 2
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, … | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc
2.9 | Dobava in montaža opreme v komunikacijsko omaro TK_N2_2- (Security) za sistem video nadzora. | Supply and installation of equipment in the TK_N2_2- (Security) communication cabinet for the video surveillance system. |  |  | kpl | 1 |  | 0
| - omrežno stikalo za potrebe video nadzora, 24x priključek LAN PoE (60W na izhod), kot naprimer HP, CISCO. OPREMO DOBAVI IZVAJALEC VIDEO NADZORA | - network switch for video surveillance, 24x LAN PoE connector (60W per output), such as HP, CISCO. SUPPLIED BY VIDEO CONTROL CONTRACTOR | kos | 1
| - urejevalnik kablov (organiser) 19”, kot naprimer Leviton tip: 1U Rack Mounted - 5 ring, (koda: MMCACCCM001) | - 19" cable manager (organiser), such as Leviton type: 1U Rack Mounted - 5 ring, (code: MMCACCCM001) | kos | 1
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, … | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc
2.10 | Dobava in montaža opreme v komunikacijsko omaro TK_N2_3- (Security) za sistem video nadzora. | Supply and installation of equipment in the TK_N2_3- (Security) communication cabinet for the video surveillance system. |  |  | kpl | 1 |  | 0
| - omrežno stikalo za potrebe video nadzora, 24x priključek LAN PoE (60W na izhod), kot naprimer HP, CISCO. OPREMO DOBAVI IZVAJALEC VIDEO NADZORA | - network switch for video surveillance, 24x LAN PoE connector (60W per output), such as HP, CISCO. SUPPLIED BY VIDEO CONTROL CONTRACTOR | kos | 1
| - urejevalnik kablov (organiser) 19”, kot naprimer Leviton tip: 1U Rack Mounted - 5 ring, (koda: MMCACCCM001) | - 19" cable manager (organiser), such as Leviton type: 1U Rack Mounted - 5 ring, (code: MMCACCCM001) | kos | 1
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, … | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc
2.11 | Dobava in montaža opreme v komunikacijsko omaro TK_N2_4- (Security) za sistem video nadzora. | Supply and installation of equipment in the TK_N2_4- (Security) communication cabinet for the video surveillance system. |  |  | kpl | 1 |  | 0
| - omrežno stikalo za potrebe video nadzora, 24x priključek LAN PoE (60W na izhod), kot naprimer HP, CISCO. OPREMO DOBAVI IZVAJALEC VIDEO NADZORA | - network switch for video surveillance, 24x LAN PoE connector (60W per output), such as HP, CISCO. SUPPLIED BY VIDEO CONTROL CONTRACTOR | kos | 1
| - urejevalnik kablov (organiser) 19”, kot naprimer Leviton tip: 1U Rack Mounted - 5 ring, (koda: MMCACCCM001) | - 19" cable manager (organiser), such as Leviton type: 1U Rack Mounted - 5 ring, (code: MMCACCCM001) | kos | 1
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, … | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc
2.12 | Dobava in montaža digitalne IP notranje, IR video kamere za montažo na strop nadometno, dan/noč, 8MP, napajanje preko PoE kot naprimer Avigilon . | Supply and installation of digital IP indoor, IR video cameras for ceiling mounting, day/night, 8MP, PoE power supply like Avigilon. |  |  | kpl | 100 |  | 0
| - Notranja nadometna dome kamera 8.0C-H6A-D1-IR | - Indoor dome camera 8.0C-H6A-D1-IR | kos | 1
2.13 | Dobava in montaža digitalne IP notranje, IR video kamere za montažo na steno komplet z adapterjem in nosilcem, dan/noč, 8MP, napajanje preko PoE kot naprimer Avigilon . | Supply and installation of digital IP indoor, IR video camera for wall mounting complete with adapter and bracket, day/night, 8MP, PoE power supply like Avigilon. |  |  | kpl | 64 |  | 0
| - Notranja nadometna dome kamera 8.0C-H6A-D1-IR | - Indoor dome camera 8.0C-H6A-D1-IR | kos | 1
| - Adapter H6A-MT-NPTA1 | - Adapter H6A-MT-NPTA1 | kos | 1
| - Stenski nosilec WLMT-1021 | - Wall bracket WLMT-1021 | kos | 1
2.14 | Dobava in montaža digitalne IP zunanje, IR video kamere za montažo na strop nadometno, dan/noč, 360°, IP66, 8MP, napajanje preko PoE kot naprimer Avigilon . | Supply and installation of digital IP outdoor, IR video camera for ceiling mounting, day/night, 360°, IP66, 8MP, PoE power supply like Avigilon. |  |  | kpl | 2 |  | 0
| - Nadometna fisheye kamera 8.0C-H5A-FE-DO1-IR | - Overhead fisheye camera 8.0C-H5A-FE-DO1-IR | kos | 1
2.15 | Dobava in montaža digitalne IP notranje, IR video kamere za montažo na strop nadometno, dan/noč, 360°, 8MP, napajanje preko PoE kot naprimer Avigilon . | Supply and installation of digital IP indoor, IR video cameras for ceiling mounting, day/night, 360°, 8MP, PoE power supply like Avigilon. |  |  | kpl | 18 |  | 0
| - Nadometna fisheye kamera 8.0C-H5A-FE-DO1-IR | - Overhead fisheye camera 8.0C-H5A-FE-DO1-IR | kos | 1
2.16 | Dobava in montaža digitalne IP zunanje, IR kamera, komplet z priključno dozo, dan/noč, v termostatskem ogrevanem zaščitnem ohišju, montaža na strop, 8MP, napajanje preko PoE, kot naprimer Avigilon . | Supply and installation of digital IP outdoor, IR camera, complete with dock, day/night, in thermostatic heated protective housing, ceiling mounting, 8MP, PoE power supply, like Avigilon. |  |  | kpl | 42 |  | 0
| - Zunanja bullet kamera 8.0C-H6X-BO1-IR | - Outdoor bullet camera 8.0C-H6X-BO1-IR | kos | 1
| - Priključna doza H4-BO-JBOX1 | - H4-BO-JBOX1 dock connector | kos | 1
2.17 | Dobava in montaža digitalne IP notranje, IR video kamere za montažo na strop nadometno, dan/noč, 8MP, ko objekt ne obratuje deluje kod protivlomna kamera, prenos alarma preko relejnega kontakta na protivlomno centralo, napajanje preko PoE kot naprimer Avigilon . | Supply and installation of a digital IP indoor, IR video camera for ceiling mounting, day/night, 8MP, when the building is not in operation it operates as a burglar alarm camera, alarm transmission via relay contact to the burglar alarm control panel, power supply via PoE as for example Avigilon. |  |  | kpl | 6 |  | 0
| - Notranja nadometna dome kamera 8.0C-H6A-D1-IR | - Indoor dome camera 8.0C-H6A-D1-IR | kos | 1
2.18 | Dobava in montaža digitalne IP notranje, IR video kamere za montažo na steno komplet z adapterjem in nosilcem, dan/noč, 8MP, ko objekt ne obratuje deluje kod protivlomna kamera, prenos alarma preko relejnega kontakta na protivlomno centralo, napajanje preko PoE kot naprimer Avigilon . | Supply and installation of digital IP indoor, IR video camera for wall mounting complete with adapter and bracket, day/night, 8MP, when the building is not in operation it operates as a burglar alarm camera, alarm transmission via relay contact to the burglar alarm control panel, power supply via PoE as for example Avigilon. |  |  | kpl | 4 |  | 0
| - Notranja nadometna dome kamera 8.0C-H6A-D1-IR | - Indoor dome camera 8.0C-H6A-D1-IR | kos | 1
| - Adapter H6A-MT-NPTA1 | - Adapter H6A-MT-NPTA1 | kos | 1
| - Stenski nosilec WLMT-1021 | - Wall bracket WLMT-1021 | kos | 1
2.19 | Dobava in montaža digitalne IP zunanje, IR kamera, komplet z priključno dozo, dan/noč, v termostatskem ogrevanem zaščitnem ohišju, montaža na strop, 8MP, ko objekt ne obratuje deluje kod protivlomna kamera, prenos alarma preko relejnega kontakta na protivlomno centralo, napajanje preko PoE, kot naprimer Avigilon . | Supply and installation of digital IP outdoor, IR camera, complete with dock, day/night, in thermostatic heated protective housing, ceiling mounting, 8MP, when the building is not in operation it operates as a burglar alarm camera, alarm transmission via relay contact to the burglar alarm control panel, power supply via PoE, such as Avigilon. |  |  | kpl | 16 |  | 0
| - Zunanja bullet kamera 8.0C-H6X-BO1-IR | - Outdoor bullet camera 8.0C-H6X-BO1-IR | kos | 1
| - Priključna doza H4-BO-JBOX1 | - H4-BO-JBOX1 dock connector | kos | 1
2.20 | Dobava in polaganje na kabelske police oz. uvlečenje v inštalacijske cevi, vključno z označevalnimi ploščicami, razvodnicami ter drobnim in spojnim materialom: | Supply and installation on cable racks or insertion into conduits, including marker plates, conduit boxes, small and jointing materials:
| -F/FTP-Category 6A, 4x2x23 AWG, brezhalogenski, odziv na ogenj Eca. Kot naprimer Leviton: | -F/FTP-Category 6A, 4x2x23 AWG, halogen-free, reaction to fire Eca. As for example Leviton: |  |  | m | 16200 |  | 0
2.21 | Dobava in montaža prenapetostne zaščite za potrebe zunanjih video kamer montaža v komunikacijsko vozlišče, DEHN, DPA M CLE RJ45B 48. | Supply and installation of surge protectors for external video cameras, installation in communication hub, DEHN, DPA M CLE RJ45B 48. |  |  | kos | 60 |  | 0
2.22 | Priključitev prenapetostne zaščite na patch panel z ustreznim ranžirnim "patch" kabelom, 2x Snap-In konektor, F/FTP cat 6A, RJ-45 to RJ-45, Leviton. | Connection of the surge protector to the patch panel with a suitable patch cable, 2x Snap-In connector, F/FTP cat 6A, RJ-45 to RJ-45, Leviton. |  |  | kos | 60 |  | 0
2.23 | Priključitev kamer s kablom F/FTP, komplet z Snap-In konektorji RJ45 Cat 6A, z predpripravo kabla in z vsemi potrebnimi inštalacijskim materialom (ohišje konektorja…) | Connection of cameras with F/FTP cable, complete with RJ45 Cat 6A Snap-In connectors, with cable pre-preparation and all necessary installation materials (connector housing...) |  |  | kos | 252 |  | 0
2.24 | Zaključitev F/FTP kabla na patch panelih oziroma prenapetostni zaščiti komplet z Snap-In konektorji RJ45 Cat 6A v komunikacijskih vozliščih oziroma omarici. Komplet z vsem potrebnim inštalacijskim materalom | Termination of the F/FTP cable on patch panels or surge protectors complete with RJ45 Cat 6A Snap-In connectors in the communication hubs or cabinet. Complete with all necessary installation materials |  |  | kos | 252 |  | 0
2.25 | Dobava in namestitev v omaro +VN-P1 pregledovalno delovno postajo z licenčno programsko opremo za upravljanje in nadzor IP video kamer v sestavi: video strežnik z grafičnim vmesnikom, mrežna kartica, video zajemalna kartica, podpora za 6HDMI, 8TB SATA HDD kompletu s tipkovnico in miško kot naprimer Avigilon Workstation | Supply and installation in a cabinet of a +VN-P1 review workstation with licensed software for management and control of IP video cameras, comprising: video server with graphic interface, network card, video capture card, support for 6HDMI, 8TB SATA HDD complete with keyboard and mouse such as Avigilon Workstation |  |  | kpl | 1 |  | 0
2.26 | Dobava in namestitev 34'' LCD monitorja 4k kakovostjo kot naprimer HP, Dell, Samsung | Supply and installation of 34'' LCD monitor with 4k quality such as HP, Dell, Samsung |  |  | kos | 2 |  | 0
2.27 | Dobava in namestitev v omaro +VN-P1 digitalne snemalne naprave za hranjenje posnetkov 249. kamer za obdobje 2. mesecev, kot naprimer Avigilon video archive, 1.5PB, (Dolžino shranjevanja posnetkov in kapaciteta shranjevalnega diska se določi z investitorjem oziroma uporabnikom). | Supply and installation in +VN-P1 cabinet of a digital recording device for storing 249. camera recordings for a period of 2 months, such as Avigilon video archive, 1.5PB, (The length of the storage of recordings and the capacity of the storage disk to be agreed with the investor or user). |  |  | kpl | 1 |  | 0
2.28 | Programska oprema za zajem, distribucijo, preklapljanje, spremljanje in arhiviranje video zapisa (252 kamer), z vsemi potrebnimi licencami za IP kamere video nadzornega sistema AVIGILON - po posameznih tipih | Software for video capture, distribution, switching, monitoring and archiving (252 cameras), with all necessary licences for IP cameras of the AVIGILON video surveillance system - by type
| -ACC7-ENT | -ACC7-ENT |  |  | kpl | 1 |  | 0
2.29 | Izvajalec inštalacij informacijskega komunikacijskega sistema mora biti usposobljen za izvedbo telekomunikacijskih kabelskih sistemov za kategorijo 6a (CAT 6a). Pri izvedbi univerzalnega kabliranja oz. TK kabelskih sistemov, mora izvajalec inštalacij upoštavati zahteve podane v standardu SIST EN 50173 za kategorijo 6a (CAT 6a). | The contractor for the installation of the information communication system shall be qualified for the installation of Category 6a (CAT 6a) telecommunication cabling systems. When installing universal cabling or TK cable systems, the installer must comply with the requirements of the SIST EN 50173 standard for category 6a (CAT 6a). |  |  | kpl | 1 |  | 0
2.30 | Meritve informacijskega komunikacijskega sistema (linka) v skladu s standardi in spuščanje v pogon (252 priključkov). Izvajalec informacijskega komunikacijskega sistema je dolžan dostaviti rezultate meritev, opravljenih z ustreznim instrumentom, potrjenim s strani proizvajalca pasivne opreme. Rezultati morajo biti (tudi) v originalnem formatu instrumenta. | Measurement of the information communication system (link) according to standards and commissioning (252 connections). The contractor of the information communication system shall deliver the results of the measurements made with a suitable instrument validated by the manufacturer of the passive equipment. The results shall (also) be in the original format of the instrument. |  |  | kpl | 1 |  | 0
2.31 | Parametriranje kamer in sistema, vnos v tlorise, nastavitve ter zagon video nadzornega sistema vključno z izdelavo ustreznih zapisnikov in poročil | Camera and system parameterisation, floor plan entry, setup and commissioning of the video surveillance system, including production of relevant records and reports |  |  | kpl | 1 |  | 0
2.32 | Izobraževanje uporabnikov in vzdrževalcev. | User and maintenance training. |  |  | kpl | 1 |  | 0
2.33 | Uporabniška navodila za uporabo, obratovanje in vzdrževanje | User instructions for use, operation and maintenance |  |  | kpl | 1 |  | 0
2.34 | Pomožne nosilne konstrukcije kabelskega razvoda - hladno cinkano, ki jih ni možno izdelati s tipskimi elementi ( Hilti profili, navojne palice, obdelano profilno železo, itd. ). | Auxiliary cable support structures - cold galvanised, which cannot be manufactured with standard elements ( Hilti profiles, threaded rods, machined profile iron, etc.). |  |  | kg | 300 |  | 0
2.35 | Vrtanje odprtin v stenah in ploščah ter njihovo tesnenje, premer x dolžina lukenj (mm): 50x150 | Drilling and sealing of holes in walls and panels, diameter x length of holes (mm): 50x150 |  |  | kos | 30 |  | 0
2.36 | Vrtanje odprtin v stenah in ploščah do fi 120 mm | Drilling holes in walls and panels up to 120 mm fi |  |  | kos | 35 |  | 0
2.37 | Dobava in polaganje izolacijskih cevi in inšalacijskih kanalov: | Supply and installation of insulation pipes and ducts:
| -Zaščitna PVC RB cev za notranje elektroinštalacije, fi 16-48, | -PVC RB shielding pipe for indoor electrical installations, fi 16-48, |  |  | m | 2400 |  | 0
| -Zaščitna PVC PN cev za notranje elektroinštalacije, fi 13,5-29, vključno z drobnim montažnim materialom | -PVC PN protective hose for indoor electrical installations, fi 13,5-29, including small installation materials |  |  | m | 650 |  | 0
| SISTEM VIDEO NADZORA | VIDEO SURVEILLANCE SYSTEM | [5 empty] | 0

## 3.10.3_Kontrola Pristopa
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.10 | ELEKTRO DELA | ELECTRICAL WORKS
3.10.3 | KONTROLA PRISTOPA | ACCESS CONTROL | [5 empty] | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description |  |  | EM | Količina | Cena/EM | Cena
3 | KONTROLA PRISTOPA | ACCESS CONTROL
3.1 | Dobava in montaža stenske kovinske omare za kontrolo pristopa z oznako +RKP1, kot na primer: Schneider Electric, tip NSYS3D6420P, dimenzije: 600 mm x 400 mm x 200 mm (VxŠXG) vključno z DIN letvami (NSYMD64) | Supply and installation of a wall-mounted metal access control cabinet with code +RKP1, such as Schneider Electric, type NSYS3D6420P, dimensions: 600 mm x 400 mm x 200 mm (HxWxDxL) including DIN mouldings (NSYMD64) |  |  | kpl | 1 |  | 0
| V omaro +RKP1 se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in +RKP1:
| -Inteligentni krmilnik za kontrolo pristopa, ki lahko krmili do 32 vhodno/izhodnih naprav, kot naprimer Spica, Zone Wing krmilnik, tip:TSTZ1W-2 | -Intelligent access control controller for controlling up to 32 I/O devices, e.g. Spica, Zone Wing controller, type:TSTZ1W-2 | kos | 1
| -Vhodno/izhodna enota, ki krmili čitalce, releje in alarme, kot naprimer Spica, Zone Door I/O naprava, tip: TSTZ1D | -Input/output unit controlling readers, relays and alarms, e.g. Spica, Zone Door I/O device, type: TSTZ1D | kos | 8
| - Napajalnik kot naprimer Spica, tip: TDR60-12VK | - Power supply like Spica, type: TDR60-12VK | kos | 1
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 2
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 2
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 2
| - uvodnice LAPP: | - lAPP introducer:
| + za kable fi 4,5 - 10mm | + for cables fi 4,5 - 10 mm | kos | 35
| Namestiti je potrebno vse potrebne module, da bo kontrola pristopa delovala kot celota; | All the necessary modules must be installed for the access control to work as a complete system;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc. | kpl | 1
| Priključitev napajalnika kontrole pristopa na za to pripravljeni vir napajanja (kabelski fiksni priključek, 230 VAC, UPS napajanje). | Connection of the access control power supply to a ready-to-use power source (cable fixed connection, 230 VAC, UPS power supply).
3.2 | Dobava in montaža stenske kovinske omare za kontrolo pristopa z oznako +RKP1.1, kot na primer: Schneider Electric, tip NSYS3D6620P, dimenzije: 600 mm x 600 mm x 200 mm (VxŠXG) vključno z DIN letvami (NSYMD66) | Supply and installation of a wall-mounted metal access control cabinet with code +RKP1.1, such as Schneider Electric, type NSYS3D6620P, dimensions: 600 mm x 600 mm x 200 mm (HxWxDxL) including DIN mouldings (NSYMD66) |  |  | kpl | 1 |  | 0
| V omaro +RKP1.1 se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in +RKP1.1:
| -Vhodno/izhodna enota, ki krmili čitalce, releje in alarme, kot naprimer Spica, Zone Door I/O naprava, tip: TSTZ1D | -Input/output unit controlling readers, relays and alarms, e.g. Spica, Zone Door I/O device, type: TSTZ1D | kos | 16
| - Napajalnik kot naprimer Spica, tip: TDR60-12VK | - Power supply like Spica, type: TDR60-12VK | kos | 1
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 2
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 2
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 2
| - uvodnice LAPP: | - lAPP introducer:
| + za kable fi 4,5 - 10mm | + for cables fi 4,5 - 10 mm | kos | 66
| Namestiti je potrebno vse potrebne module, da bo kontrola pristopa delovala kot celota; | All the necessary modules must be installed for the access control to work as a complete system;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc. | kpl | 1
| Priključitev napajalnika kontrole pristopa na za to pripravljeni vir napajanja (kabelski fiksni priključek, 230 VAC, UPS napajanje). | Connection of the access control power supply to a ready-to-use power source (cable fixed connection, 230 VAC, UPS power supply).
3.3 | Dobava in montaža stenske kovinske omare za kontrolo pristopa z oznako +RKP2, kot na primer: Schneider Electric, tip NSYS3D6620P, dimenzije: 600 mm x 600 mm x 200 mm (VxŠXG) vključno z DIN letvami (NSYMD66) | Supply and installation of a wall-mounted metal access control cabinet with code +RKP2, such as Schneider Electric, type NSYS3D6620P, dimensions: 600 mm x 600 mm x 200 mm (HxWxDxL) including DIN mouldings (NSYMD66) |  |  | kpl | 1 |  | 0
| V omaro +RKP2 se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in +RKP2:
| -Inteligentni krmilnik za kontrolo pristopa, ki lahko krmili do 32 vhodno/izhodnih naprav, kot naprimer Spica, Zone Wing krmilnik, tip:TSTZ1W-2 | -Intelligent access control controller for controlling up to 32 I/O devices, e.g. Spica, Zone Wing controller, type:TSTZ1W-2 | kos | 1
| -Vhodno/izhodna enota, ki krmili čitalce, releje in alarme, kot naprimer Spica, Zone Door I/O naprava, tip: TSTZ1D | -Input/output unit controlling readers, relays and alarms, e.g. Spica, Zone Door I/O device, type: TSTZ1D | kos | 9
| - Napajalnik kot naprimer Spica, tip: TDR60-12VK | - Power supply like Spica, type: TDR60-12VK | kos | 1
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 2
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 2
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 2
| - uvodnice LAPP: | - lAPP introducer:
| + za kable fi 4,5 - 10mm | + for cables fi 4,5 - 10 mm | kos | 40
| Namestiti je potrebno vse potrebne module, da bo kontrola pristopa delovala kot celota; | All the necessary modules must be installed for the access control to work as a complete system;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc. | kpl | 1
| Priključitev napajalnika kontrole pristopa na za to pripravljeni vir napajanja (kabelski fiksni priključek, 230 VAC, UPS napajanje). | Connection of the access control power supply to a ready-to-use power source (cable fixed connection, 230 VAC, UPS power supply).
3.4 | Dobava in montaža stenske kovinske omare za kontrolo pristopa z oznako +RKP2.1, kot na primer: Schneider Electric, tip NSYS3D6620P, dimenzije: 600 mm x 600 mm x 200 mm (VxŠXG) vključno z DIN letvami (NSYMD66) | Supply and installation of a wall-mounted metal access control cabinet with code +RKP2.1, such as Schneider Electric, type NSYS3D6620P, dimensions 600 mm x 600 mm x 200 mm (HxWxDxWxD) including DIN mouldings (NSYMD66) |  |  | kpl | 1 |  | 0
| V omaro +RKP2.1 se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in +RKP2.1:
| -Vhodno/izhodna enota, ki krmili čitalce, releje in alarme, kot naprimer Spica, Zone Door I/O naprava, tip: TSTZ1D | -Input/output unit controlling readers, relays and alarms, e.g. Spica, Zone Door I/O device, type: TSTZ1D | kos | 15
| - Napajalnik kot naprimer Spica, tip: TDR60-12VK | - Power supply like Spica, type: TDR60-12VK | kos | 1
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 2
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 2
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 2
| - uvodnice LAPP: | - lAPP introducer:
| + za kable fi 4,5 - 10mm | + for cables fi 4,5 - 10 mm | kos | 62
| Namestiti je potrebno vse potrebne module, da bo kontrola pristopa delovala kot celota; | All the necessary modules must be installed for the access control to work as a complete system;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc. | kpl | 1
| Priključitev napajalnika kontrole pristopa na za to pripravljeni vir napajanja (kabelski fiksni priključek, 230 VAC, UPS napajanje). | Connection of the access control power supply to a ready-to-use power source (cable fixed connection, 230 VAC, UPS power supply).
3.5 | Dobava in montaža stenske kovinske omare za kontrolo pristopa z oznako +RKP3, kot na primer: Schneider Electric, tip NSYS3D6420P, dimenzije: 600 mm x 400 mm x 200 mm (VxŠXG) vključno z DIN letvami (NSYMD64) | Supply and installation of a wall-mounted metal access control cabinet with code +RKP3, such as Schneider Electric, type NSYS3D6420P, dimensions: 600 mm x 400 mm x 200 mm (HxWxDxL) including DIN mouldings (NSYMD64) |  |  | kpl | 1 |  | 0
| V omaro +RKP3 se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in +RKP3:
| -Inteligentni krmilnik za kontrolo pristopa, ki lahko krmili do 32 vhodno/izhodnih naprav, kot naprimer Spica, Zone Wing krmilnik, tip:TSTZ1W-2 | -Intelligent access control controller for controlling up to 32 I/O devices, e.g. Spica, Zone Wing controller, type:TSTZ1W-2 | kos | 1
| -Vhodno/izhodna enota, ki krmili čitalce, releje in alarme, kot naprimer Spica, Zone Door I/O naprava, tip: TSTZ1D | -Input/output unit controlling readers, relays and alarms, e.g. Spica, Zone Door I/O device, type: TSTZ1D | kos | 6
| - Napajalnik kot naprimer Spica, tip: TDR60-12VK | - Power supply like Spica, type: TDR60-12VK | kos | 1
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 2
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 2
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 2
| - uvodnice LAPP: | - lAPP introducer:
| + za kable fi 4,5 - 10mm | + for cables fi 4,5 - 10 mm | kos | 27
| Namestiti je potrebno vse potrebne module, da bo kontrola pristopa delovala kot celota; | All the necessary modules must be installed for the access control to work as a complete system;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc. | kpl | 1
| Priključitev napajalnika kontrole pristopa na za to pripravljeni vir napajanja (kabelski fiksni priključek, 230 VAC, UPS napajanje). | Connection of the access control power supply to a ready-to-use power source (cable fixed connection, 230 VAC, UPS power supply).
3.6 | Dobava in montaža stenske kovinske omare za kontrolo pristopa z oznako +RKP3.1, kot na primer: Schneider Electric, tip NSYS3D6420P, dimenzije: 600 mm x 400 mm x 200 mm (VxŠXG) vključno z DIN letvami (NSYMD64) | Supply and installation of a wall-mounted metal access control cabinet with code +RKP3.1, such as Schneider Electric, type NSYS3D6420P, dimensions 600 mm x 400 mm x 200 mm (HxWxDxWxD) including DIN mouldings (NSYMD64) |  |  | kpl | 1 |  | 0
| V omaro +RKP3.1 se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in +RKP3.1:
| -Vhodno/izhodna enota, ki krmili čitalce, releje in alarme, kot naprimer Spica, Zone Door I/O naprava, tip: TSTZ1D | -Input/output unit controlling readers, relays and alarms, e.g. Spica, Zone Door I/O device, type: TSTZ1D | kos | 10
| - Napajalnik kot naprimer Spica, tip: TDR60-12VK | - Power supply like Spica, type: TDR60-12VK | kos | 1
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 2
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 2
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 2
| - uvodnice LAPP: | - lAPP introducer:
| + za kable fi 4,5 - 10mm | + for cables fi 4,5 - 10 mm | kos | 42
| Namestiti je potrebno vse potrebne module, da bo kontrola pristopa delovala kot celota; | All the necessary modules must be installed for the access control to work as a complete system;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc. | kpl | 1
| Priključitev napajalnika kontrole pristopa na za to pripravljeni vir napajanja (kabelski fiksni priključek, 230 VAC, UPS napajanje). | Connection of the access control power supply to a ready-to-use power source (cable fixed connection, 230 VAC, UPS power supply).
3.7 | Dobava in montaža stenske kovinske omare za kontrolo pristopa z oznako +RKP4, kot na primer: Schneider Electric, tip NSYS3D6420P, dimenzije: 600 mm x 400 mm x 200 mm (VxŠXG) vključno z DIN letvami (NSYMD64) | Supply and installation of a wall-mounted metal access control cabinet with code +RKP4, such as Schneider Electric, type NSYS3D6420P, dimensions: 600 mm x 400 mm x 200 mm (HxWxDxL) including DIN mouldings (NSYMD64) |  |  | kpl | 1 |  | 0
| V omaro +RKP4 se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in +RKP4:
| -Inteligentni krmilnik za kontrolo pristopa, ki lahko krmili do 32 vhodno/izhodnih naprav, kot naprimer Spica, Zone Wing krmilnik, tip:TSTZ1W-2 | -Intelligent access control controller for controlling up to 32 I/O devices, e.g. Spica, Zone Wing controller, type:TSTZ1W-2 | kos | 1
| -Vhodno/izhodna enota, ki krmili čitalce, releje in alarme, kot naprimer Spica, Zone Door I/O naprava, tip: TSTZ1D | -Input/output unit controlling readers, relays and alarms, e.g. Spica, Zone Door I/O device, type: TSTZ1D | kos | 4
| - Napajalnik kot naprimer Spica, tip: TDR60-12VK | - Power supply like Spica, type: TDR60-12VK | kos | 1
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 2
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 2
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 2
| - uvodnice LAPP: | - lAPP introducer:
| + za kable fi 4,5 - 10mm | + for cables fi 4,5 - 10 mm | kos | 20
| Namestiti je potrebno vse potrebne module, da bo kontrola pristopa delovala kot celota; | All the necessary modules must be installed for the access control to work as a complete system;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc. | kpl | 1
| Priključitev napajalnika kontrole pristopa na za to pripravljeni vir napajanja (kabelski fiksni priključek, 230 VAC, UPS napajanje). | Connection of the access control power supply to a ready-to-use power source (cable fixed connection, 230 VAC, UPS power supply).
3.8 | Dobava in montaža stenske kovinske omare za kontrolo pristopa z oznako +RKP4.1, kot na primer: Schneider Electric, tip NSYS3D6620P, dimenzije: 600 mm x 600 mm x 200 mm (VxŠXG) vključno z DIN letvami (NSYMD66) | Supply and installation of a wall-mounted metal access control cabinet with code +RKP4.1, such as Schneider Electric, type NSYS3D6620P, dimensions: 600 mm x 600 mm x 200 mm (HxWxDxL) including DIN mouldings (NSYMD66) |  |  | kpl | 1 |  | 0
| V omaro +RKP4.1 se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in +RKP4.1:
| -Vhodno/izhodna enota, ki krmili čitalce, releje in alarme, kot naprimer Spica, Zone Door I/O naprava, tip: TSTZ1D | -Input/output unit controlling readers, relays and alarms, e.g. Spica, Zone Door I/O device, type: TSTZ1D | kos | 12
| - Napajalnik kot naprimer Spica, tip: TDR60-12VK | - Power supply like Spica, type: TDR60-12VK | kos | 1
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 2
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 2
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 2
| - uvodnice LAPP: | - lAPP introducer:
| + za kable fi 4,5 - 10mm | + for cables fi 4,5 - 10 mm | kos | 50
| Namestiti je potrebno vse potrebne module, da bo kontrola pristopa delovala kot celota; | All the necessary modules must be installed for the access control to work as a complete system;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc. | kpl | 1
| Priključitev napajalnika kontrole pristopa na za to pripravljeni vir napajanja (kabelski fiksni priključek, 230 VAC, UPS napajanje). | Connection of the access control power supply to a ready-to-use power source (cable fixed connection, 230 VAC, UPS power supply).
3.9 | Dobava in montaža stenske kovinske omare za kontrolo pristopa z oznako +RKP5, kot na primer: Schneider Electric, tip NSYS3D6620P, dimenzije: 600 mm x 600 mm x 200 mm (VxŠXG) vključno z DIN letvami (NSYMD66) | Supply and installation of a wall-mounted metal access control cabinet with code +RKP5, such as Schneider Electric, type NSYS3D6620P, dimensions: 600 mm x 600 mm x 200 mm (HxWxDxL) including DIN mouldings (NSYMD66) |  |  | kpl | 1 |  | 0
| V omaro +RKP5 se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in +RKP5:
| -Inteligentni krmilnik za kontrolo pristopa, ki lahko krmili do 32 vhodno/izhodnih naprav, kot naprimer Spica, Zone Wing krmilnik, tip:TSTZ1W-2 | -Intelligent access control controller for controlling up to 32 I/O devices, e.g. Spica, Zone Wing controller, type:TSTZ1W-2 | kos | 1
| -Vhodno/izhodna enota, ki krmili čitalce, releje in alarme, kot naprimer Spica, Zone Door I/O naprava, tip: TSTZ1D | -Input/output unit controlling readers, relays and alarms, e.g. Spica, Zone Door I/O device, type: TSTZ1D | kos | 13
| - Napajalnik kot naprimer Spica, tip: TDR60-12VK | - Power supply like Spica, type: TDR60-12VK | kos | 1
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 2
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 2
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 2
| - uvodnice LAPP: | - lAPP introducer:
| + za kable fi 4,5 - 10mm | + for cables fi 4,5 - 10 mm | kos | 55
| Namestiti je potrebno vse potrebne module, da bo kontrola pristopa delovala kot celota; | All the necessary modules must be installed for the access control to work as a complete system;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc. | kpl | 1
| Priključitev napajalnika kontrole pristopa na za to pripravljeni vir napajanja (kabelski fiksni priključek, 230 VAC, UPS napajanje). | Connection of the access control power supply to a ready-to-use power source (cable fixed connection, 230 VAC, UPS power supply).
3.10 | Dobava in montaža stenske kovinske omare za kontrolo pristopa z oznako +RKP11, kot na primer: Schneider Electric, tip NSYS3D8620P, dimenzije: 800 mm x 600 mm x 200 mm (VxŠXG) vključno z DIN letvami (NSYMD86) | Supply and installation of a wall-mounted metal access control cabinet with code +RKP11, such as Schneider Electric, type NSYS3D8620P, dimensions: 800 mm x 600 mm x 200 mm (HxWxDxL) including DIN mouldings (NSYMD86) |  |  | kpl | 1 |  | 0
| V omaro +RKP11 se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in cabinet +RKP11:
| -Inteligentni krmilnik za kontrolo pristopa, ki lahko krmili do 32 vhodno/izhodnih naprav, kot naprimer Spica, Zone Wing krmilnik, tip:TSTZ1W-2 | -Intelligent access control controller for controlling up to 32 I/O devices, e.g. Spica, Zone Wing controller, type:TSTZ1W-2 | kos | 1
| -Vhodno/izhodna enota, ki krmili čitalce, releje in alarme, kot naprimer Spica, Zone Door I/O naprava, tip: TSTZ1D | -Input/output unit controlling readers, relays and alarms, e.g. Spica, Zone Door I/O device, type: TSTZ1D | kos | 23
| - Napajalnik kot naprimer Spica, tip: TDR60-12VK | - Power supply like Spica, type: TDR60-12VK | kos | 1
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 2
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 2
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 2
| - uvodnice LAPP: | - lAPP introducer:
| + za kable fi 4,5 - 10mm | + for cables fi 4,5 - 10 mm | kos | 95
| Namestiti je potrebno vse potrebne module, da bo kontrola pristopa delovala kot celota; | All the necessary modules must be installed for the access control to work as a complete system;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc. | kpl | 1
| Priključitev napajalnika kontrole pristopa na za to pripravljeni vir napajanja (kabelski fiksni priključek, 230 VAC, UPS napajanje). | Connection of the access control power supply to a ready-to-use power source (cable fixed connection, 230 VAC, UPS power supply).
3.11 | Dobava in montaža stenske kovinske omare za kontrolo pristopa z oznako +RKP6, kot na primer: Schneider Electric, tip NSYS3D6420P, dimenzije: 600 mm x 400 mm x 200 mm (VxŠXG) vključno z DIN letvami (NSYMD64) | Supply and installation of a wall-mounted metal access control cabinet with code +RKP6, such as Schneider Electric, type NSYS3D6420P, dimensions: 600 mm x 400 mm x 200 mm (HxWxDxL) including DIN mouldings (NSYMD64) |  |  | kpl | 1 |  | 0
| V omaro +RKP6 se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in +RKP6:
| -Inteligentni krmilnik za kontrolo pristopa, ki lahko krmili do 32 vhodno/izhodnih naprav, kot naprimer Spica, Zone Wing krmilnik, tip:TSTZ1W-2 | -Intelligent access control controller for controlling up to 32 I/O devices, e.g. Spica, Zone Wing controller, type:TSTZ1W-2 | kos | 1
| -Vhodno/izhodna enota, ki krmili čitalce, releje in alarme, kot naprimer Spica, Zone Door I/O naprava, tip: TSTZ1D | -Input/output unit controlling readers, relays and alarms, e.g. Spica, Zone Door I/O device, type: TSTZ1D | kos | 7
| - Napajalnik kot naprimer Spica, tip: TDR60-12VK | - Power supply like Spica, type: TDR60-12VK | kos | 1
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 2
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 2
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 2
| - uvodnice LAPP: | - lAPP introducer:
| + za kable fi 4,5 - 10mm | + for cables fi 4,5 - 10 mm | kos | 31
| Namestiti je potrebno vse potrebne module, da bo kontrola pristopa delovala kot celota; | All the necessary modules must be installed for the access control to work as a complete system;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc. | kpl | 1
| Priključitev napajalnika kontrole pristopa na za to pripravljeni vir napajanja (kabelski fiksni priključek, 230 VAC, UPS napajanje). | Connection of the access control power supply to a ready-to-use power source (cable fixed connection, 230 VAC, UPS power supply).
3.12 | Dobava in montaža stenske kovinske omare za kontrolo pristopa z oznako +RKP6.1, kot na primer: Schneider Electric, tip NSYS3D6420P, dimenzije: 600 mm x 400 mm x 200 mm (VxŠXG) vključno z DIN letvami (NSYMD64) | Supply and installation of a wall-mounted metal access control cabinet with code +RKP6.1, such as Schneider Electric, type NSYS3D6420P, dimensions 600 mm x 400 mm x 200 mm (HxWxDxWxD) including DIN mouldings (NSYMD64) |  |  | kpl | 1 |  | 0
| V omaro +RKP6.1 se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in +RKP6.1:
| -Vhodno/izhodna enota, ki krmili čitalce, releje in alarme, kot naprimer Spica, Zone Door I/O naprava, tip: TSTZ1D | -Input/output unit controlling readers, relays and alarms, e.g. Spica, Zone Door I/O device, type: TSTZ1D | kos | 10
| - Napajalnik kot naprimer Spica, tip: TDR60-12VK | - Power supply like Spica, type: TDR60-12VK | kos | 1
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 2
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 2
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 2
| - uvodnice LAPP: | - lAPP introducer:
| + za kable fi 4,5 - 10mm | + for cables fi 4,5 - 10 mm | kos | 42
| Namestiti je potrebno vse potrebne module, da bo kontrola pristopa delovala kot celota; | All the necessary modules must be installed for the access control to work as a complete system;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc. | kpl | 1
| Priključitev napajalnika kontrole pristopa na za to pripravljeni vir napajanja (kabelski fiksni priključek, 230 VAC, UPS napajanje). | Connection of the access control power supply to a ready-to-use power source (cable fixed connection, 230 VAC, UPS power supply).
3.13 | Dobava in montaža stenske kovinske omare za kontrolo pristopa z oznako +RKP7, kot na primer: Schneider Electric, tip NSYS3D8620P, dimenzije: 800 mm x 600 mm x 200 mm (VxŠXG) vključno z DIN letvami (NSYMD86) | Supply and installation of a wall-mounted metal access control cabinet with code +RKP7, such as Schneider Electric, type NSYS3D8620P, dimensions: 800 mm x 600 mm x 200 mm (HxWxDxL) including DIN mouldings (NSYMD86) |  |  | kpl | 1 |  | 0
| V omaro +RKP7 se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in +RKP7:
| -Inteligentni krmilnik za kontrolo pristopa, ki lahko krmili do 32 vhodno/izhodnih naprav, kot naprimer Spica, Zone Wing krmilnik, tip:TSTZ1W-2 | -Intelligent access control controller for controlling up to 32 I/O devices, e.g. Spica, Zone Wing controller, type:TSTZ1W-2 | kos | 1
| -Vhodno/izhodna enota, ki krmili čitalce, releje in alarme, kot naprimer Spica, Zone Door I/O naprava, tip: TSTZ1D | -Input/output unit controlling readers, relays and alarms, e.g. Spica, Zone Door I/O device, type: TSTZ1D | kos | 26
| - Napajalnik kot naprimer Spica, tip: TDR60-12VK | - Power supply like Spica, type: TDR60-12VK | kos | 1
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 2
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 2
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 2
| - uvodnice LAPP: | - lAPP introducer:
| + za kable fi 4,5 - 10mm | + for cables fi 4,5 - 10 mm | kos | 107
| Namestiti je potrebno vse potrebne module, da bo kontrola pristopa delovala kot celota; | All the necessary modules must be installed for the access control to work as a complete system;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc. | kpl | 1
| Priključitev napajalnika kontrole pristopa na za to pripravljeni vir napajanja (kabelski fiksni priključek, 230 VAC, UPS napajanje). | Connection of the access control power supply to a ready-to-use power source (cable fixed connection, 230 VAC, UPS power supply).
3.14 | Dobava in montaža stenske kovinske omare za kontrolo pristopa z oznako +RKP8, kot na primer: Schneider Electric, tip NSYS3D6620P, dimenzije: 600 mm x 600 mm x 200 mm (VxŠXG) vključno z DIN letvami (NSYMD66) | Supply and installation of a wall-mounted metal access control cabinet with code +RKP8, such as Schneider Electric, type NSYS3D6620P, dimensions: 600 mm x 600 mm x 200 mm (HxWxDxL) including DIN mouldings (NSYMD66) |  |  | kpl | 1 |  | 0
| V omaro +RKP8 se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in +RKP8:
| -Inteligentni krmilnik za kontrolo pristopa, ki lahko krmili do 32 vhodno/izhodnih naprav, kot naprimer Spica, Zone Wing krmilnik, tip:TSTZ1W-2 | -Intelligent access control controller for controlling up to 32 I/O devices, e.g. Spica, Zone Wing controller, type:TSTZ1W-2 | kos | 1
| -Vhodno/izhodna enota, ki krmili čitalce, releje in alarme, kot naprimer Spica, Zone Door I/O naprava, tip: TSTZ1D | -Input/output unit controlling readers, relays and alarms, e.g. Spica, Zone Door I/O device, type: TSTZ1D | kos | 15
| - Napajalnik kot naprimer Spica, tip: TDR60-12VK | - Power supply like Spica, type: TDR60-12VK | kos | 1
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 2
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 2
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 2
| - uvodnice LAPP: | - lAPP introducer:
| + za kable fi 4,5 - 10mm | + for cables fi 4,5 - 10mm | kos | 63
| Namestiti je potrebno vse potrebne module, da bo kontrola pristopa delovala kot celota; | All the necessary modules must be installed for the access control to work as a complete system;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc. | kpl | 1
| Priključitev napajalnika kontrole pristopa na za to pripravljeni vir napajanja (kabelski fiksni priključek, 230 VAC, UPS napajanje). | Connection of the access control power supply to a ready-to-use power source (cable fixed connection, 230 VAC, UPS power supply).
3.15 | Dobava in montaža stenske kovinske omare za kontrolo pristopa z oznako +RKP8.1, kot na primer: Schneider Electric, tip NSYS3D6420P, dimenzije: 600 mm x 400 mm x 200 mm (VxŠXG) vključno z DIN letvami (NSYMD64) | Supply and installation of a wall-mounted metal access control cabinet with code +RKP8.1, such as Schneider Electric, type NSYS3D6420P, dimensions 600 mm x 400 mm x 200 mm (HxWxDxWxD) including DIN mouldings (NSYMD64) |  |  | kpl | 1 |  | 0
| V omaro +RKP8.1 se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in +RKP8.1:
| -Vhodno/izhodna enota, ki krmili čitalce, releje in alarme, kot naprimer Spica, Zone Door I/O naprava, tip: TSTZ1D | -Input/output unit controlling readers, relays and alarms, e.g. Spica, Zone Door I/O device, type: TSTZ1D | kos | 10
| - Napajalnik kot naprimer Spica, tip: TDR60-12VK | - Power supply like Spica, type: TDR60-12VK | kos | 1
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 2
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 2
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 2
| - uvodnice LAPP: | - lAPP introducer:
| + za kable fi 4,5 - 10mm | + for cables fi 4,5 - 10 mm | kos | 42
| Namestiti je potrebno vse potrebne module, da bo kontrola pristopa delovala kot celota; | All the necessary modules must be installed for the access control to work as a complete system;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc. | kpl | 1
| Priključitev napajalnika kontrole pristopa na za to pripravljeni vir napajanja (kabelski fiksni priključek, 230 VAC, UPS napajanje). | Connection of the access control power supply to a ready-to-use power source (cable fixed connection, 230 VAC, UPS power supply).
3.16 | Dobava in montaža stenske kovinske omare za kontrolo pristopa z oznako +RKP9, kot na primer: Schneider Electric, tip NSYS3D8620P, dimenzije: 800 mm x 600 mm x 200 mm (VxŠXG) vključno z DIN letvami (NSYMD86) | Supply and installation of a wall-mounted metal access control cabinet with code +RKP9, such as Schneider Electric, type NSYS3D8620P, dimensions: 800 mm x 600 mm x 200 mm (HxWxDxL) including DIN mouldings (NSYMD86) |  |  | kpl | 1 |  | 0
| V omaro +RKP9 se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in cabinet +RKP9:
| -Inteligentni krmilnik za kontrolo pristopa, ki lahko krmili do 32 vhodno/izhodnih naprav, kot naprimer Spica, Zone Wing krmilnik, tip:TSTZ1W-2 | -Intelligent access control controller for controlling up to 32 I/O devices, e.g. Spica, Zone Wing controller, type:TSTZ1W-2 | kos | 1
| -Vhodno/izhodna enota, ki krmili čitalce, releje in alarme, kot naprimer Spica, Zone Door I/O naprava, tip: TSTZ1D | -Input/output unit controlling readers, relays and alarms, e.g. Spica, Zone Door I/O device, type: TSTZ1D | kos | 24
| - Napajalnik kot naprimer Spica, tip: TDR60-12VK | - Power supply like Spica, type: TDR60-12VK | kos | 1
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 2
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 2
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 2
| - uvodnice LAPP: | - lAPP introducer:
| + za kable fi 4,5 - 10mm | + for cables fi 4,5 - 10 mm | kos | 100
| Namestiti je potrebno vse potrebne module, da bo kontrola pristopa delovala kot celota; | All the necessary modules must be installed for the access control to work as a complete system;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc. | kpl | 1
| Priključitev napajalnika kontrole pristopa na za to pripravljeni vir napajanja (kabelski fiksni priključek, 230 VAC, UPS napajanje). | Connection of the access control power supply to a ready-to-use power source (cable fixed connection, 230 VAC, UPS power supply).
3.17 | Dobava in montaža stenske kovinske omare za kontrolo pristopa z oznako +RKP10, kot na primer: Schneider Electric, tip NSYS3D8620P, dimenzije: 800 mm x 600 mm x 200 mm (VxŠXG) vključno z DIN letvami (NSYMD86) | Supply and installation of a wall-mounted metal access control cabinet with code +RKP10, such as Schneider Electric, type NSYS3D8620P, dimensions: 800 mm x 600 mm x 200 mm (HxWxDxL) including DIN mouldings (NSYMD86) |  |  | kpl | 1 |  | 0
| V omaro +RKP10 se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in +RKP10:
| -Inteligentni krmilnik za kontrolo pristopa, ki lahko krmili do 32 vhodno/izhodnih naprav, kot naprimer Spica, Zone Wing krmilnik, tip:TSTZ1W-2 | -Intelligent access control controller for controlling up to 32 I/O devices, e.g. Spica, Zone Wing controller, type:TSTZ1W-2 | kos | 1
| -Vhodno/izhodna enota, ki krmili čitalce, releje in alarme, kot naprimer Spica, Zone Door I/O naprava, tip: TSTZ1D | -Input/output unit controlling readers, relays and alarms, e.g. Spica, Zone Door I/O device, type: TSTZ1D | kos | 22
| - Napajalnik kot naprimer Spica, tip: TDR60-12VK | - Power supply like Spica, type: TDR60-12VK | kos | 1
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 2
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 2
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 2
| - uvodnice LAPP: | - lAPP introducer:
| + za kable fi 4,5 - 10mm | + for cables fi 4,5 - 10 mm | kos | 95
| Namestiti je potrebno vse potrebne module, da bo kontrola pristopa delovala kot celota; | All the necessary modules must be installed for the access control to work as a complete system;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc. | kpl | 1
| Priključitev napajalnika kontrole pristopa na za to pripravljeni vir napajanja (kabelski fiksni priključek, 230 VAC, UPS napajanje). | Connection of the access control power supply to a ready-to-use power source (cable fixed connection, 230 VAC, UPS power supply).
3.18 | Dobava in montaža stenske kovinske omare za kontrolo pristopa z oznako +RKP12, kot na primer: Schneider Electric, tip NSYS3D8620P, dimenzije: 600 mm x 600 mm x 200 mm (VxŠXG) vključno z DIN letvami (NSYMD86) | Supply and installation of a wall-mounted metal access control cabinet with code +RKP12, such as Schneider Electric, type NSYS3D8620P, dimensions: 600 mm x 600 mm x 200 mm (HxWxDxL) including DIN mouldings (NSYMD86) |  |  | kpl | 1 |  | 0
| V omaro +RKP12 se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in +RKP12:
| -Inteligentni krmilnik za kontrolo pristopa, ki lahko krmili do 32 vhodno/izhodnih naprav, kot naprimer Spica, Zone Wing krmilnik, tip:TSTZ1W-2 | -Intelligent access control controller for controlling up to 32 I/O devices, e.g. Spica, Zone Wing controller, type:TSTZ1W-2 | kos | 1
| -Vhodno/izhodna enota, ki krmili čitalce, releje in alarme, kot naprimer Spica, Zone Door I/O naprava, tip: TSTZ1D | -Input/output unit controlling readers, relays and alarms, e.g. Spica, Zone Door I/O device, type: TSTZ1D | kos | 11
| - Napajalnik kot naprimer Spica, tip: TDR60-12VK | - Power supply like Spica, type: TDR60-12VK | kos | 1
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 2
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 2
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 2
| - uvodnice LAPP: | - lAPP introducer:
| + za kable fi 4,5 - 10mm | + for cables fi 4,5 - 10 mm | kos | 47
| Namestiti je potrebno vse potrebne module, da bo kontrola pristopa delovala kot celota; | All the necessary modules must be installed for the access control to work as a complete system;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc. | kpl | 1
| Priključitev napajalnika kontrole pristopa na za to pripravljeni vir napajanja (kabelski fiksni priključek, 230 VAC, UPS napajanje). | Connection of the access control power supply to a ready-to-use power source (cable fixed connection, 230 VAC, UPS power supply).
3.19 | Dobava in montaža stenske kovinske omare za kontrolo pristopa z oznako +RKP13, kot na primer: Schneider Electric, tip NSYS3D3320P, dimenzije: 300 mm x 300 mm x 200 mm (VxŠXG) vključno z DIN letvami (NSYMD33) | Supply and installation of a wall-mounted metal access control cabinet with code +RKP13, such as Schneider Electric, type NSYS3D3320P, dimensions: 300 mm x 300 mm x 200 mm (HxWxDxWxD) including DIN mouldings (NSYMD33) |  |  | kpl | 1 |  | 0
| V omaro +RKP13 se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in cabinet +RKP13:
| -Inteligentni krmilnik za kontrolo pristopa, ki lahko krmili do 32 vhodno/izhodnih naprav, kot naprimer Spica, Zone Wing krmilnik, tip:TSTZ1W-2 | -Intelligent access control controller for controlling up to 32 I/O devices, e.g. Spica, Zone Wing controller, type:TSTZ1W-2 | kos | 1
| -Vhodno/izhodna enota, ki krmili čitalce, releje in alarme, kot naprimer Spica, Zone Door I/O naprava, tip: TSTZ1D | -Input/output unit controlling readers, relays and alarms, e.g. Spica, Zone Door I/O device, type: TSTZ1D | kos | 3
| - Napajalnik kot naprimer Spica, tip: TDR60-12VK | - Power supply like Spica, type: TDR60-12VK | kos | 1
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 2
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 2
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 2
| - uvodnice LAPP: | - lAPP introducer:
| + za kable fi 4,5 - 10mm | + for cables fi 4,5 - 10 mm | kos | 15
| Namestiti je potrebno vse potrebne module, da bo kontrola pristopa delovala kot celota; | All the necessary modules must be installed for the access control to work as a complete system;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc. | kpl | 1
| Priključitev napajalnika kontrole pristopa na za to pripravljeni vir napajanja (kabelski fiksni priključek, 230 VAC, UPS napajanje). | Connection of the access control power supply to a ready-to-use power source (cable fixed connection, 230 VAC, UPS power supply).
3.20 | Dobava in montaža stenske kovinske omare za kontrolo pristopa z oznako +RKP13.1, kot na primer: Schneider Electric, tip NSYS3D3320P, dimenzije: 300 mm x 300 mm x 200 mm (VxŠXG) vključno z DIN letvami (NSYMD33) | Supply and installation of a wall-mounted metal access control cabinet with code +RKP13.1, such as Schneider Electric, type NSYS3D3320P, dimensions: 300 mm x 300 mm x 200 mm (HxWxDxWxD) including DIN mouldings (NSYMD33) |  |  | kpl | 1 |  | 0
| V omaro +RKP13.1 se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in cabinet +RKP13.1:
| -Vhodno/izhodna enota, ki krmili čitalce, releje in alarme, kot naprimer Spica, Zone Door I/O naprava, tip: TSTZ1D | -Input/output unit controlling readers, relays and alarms, e.g. Spica, Zone Door I/O device, type: TSTZ1D | kos | 2
| - Napajalnik kot naprimer Spica, tip: TDR60-12VK | - Power supply like Spica, type: TDR60-12VK | kos | 1
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 2
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 2
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 2
| - uvodnice LAPP: | - lAPP introducer:
| + za kable fi 4,5 - 10mm | + for cables fi 4,5 - 10 mm | kos | 10
| Namestiti je potrebno vse potrebne module, da bo kontrola pristopa delovala kot celota; | All the necessary modules must be installed for the access control to work as a complete system;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc. | kpl | 1
| Priključitev napajalnika kontrole pristopa na za to pripravljeni vir napajanja (kabelski fiksni priključek, 230 VAC, UPS napajanje). | Connection of the access control power supply to a ready-to-use power source (cable fixed connection, 230 VAC, UPS power supply).
3.21 | Dobava in montaža stenske kovinske omare za kontrolo pristopa z oznako +RKP13.2, kot na primer: Schneider Electric, tip NSYS3D3320P, dimenzije: 300 mm x 300 mm x 200 mm (VxŠXG) vključno z DIN letvami (NSYMD33) | Supply and installation of a wall-mounted metal access control cabinet with code +RKP13.2, such as Schneider Electric, type NSYS3D3320P, dimensions: 300 mm x 300 mm x 200 mm (HxWxDxWxD) including DIN mouldings (NSYMD33) |  |  | kpl | 1 |  | 0
| V omaro +RKP13.2 se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in cabinet +RKP13.2:
| -Vhodno/izhodna enota, ki krmili čitalce, releje in alarme, kot naprimer Spica, Zone Door I/O naprava, tip: TSTZ1D | -Input/output unit controlling readers, relays and alarms, e.g. Spica, Zone Door I/O device, type: TSTZ1D | kos | 3
| - Napajalnik kot naprimer Spica, tip: TDR60-12VK | - Power supply like Spica, type: TDR60-12VK | kos | 1
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 2
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 2
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 2
| - uvodnice LAPP: | - lAPP introducer:
| + za kable fi 4,5 - 10mm | + for cables fi 4,5 - 10 mm | kos | 15
| Namestiti je potrebno vse potrebne module, da bo kontrola pristopa delovala kot celota; | All the necessary modules must be installed for the access control to work as a complete system;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc. | kpl | 1
| Priključitev napajalnika kontrole pristopa na za to pripravljeni vir napajanja (kabelski fiksni priključek, 230 VAC, UPS napajanje). | Connection of the access control power supply to a ready-to-use power source (cable fixed connection, 230 VAC, UPS power supply).
3.22 | Dobava in montaža stenske kovinske omare za kontrolo pristopa z oznako +RKP14, kot na primer: Schneider Electric, tip NSYS3D3320P, dimenzije: 300 mm x 300 mm x 200 mm (VxŠXG) vključno z DIN letvami (NSYMD33) | Supply and installation of a wall-mounted metal access control cabinet with code +RKP14, such as Schneider Electric, type NSYS3D3320P, dimensions: 300 mm x 300 mm x 200 mm (HxWxDxL) including DIN mouldings (NSYMD33) |  |  | kpl | 1 |  | 0
| V omaro +RKP14 se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in +RKP14:
| -Inteligentni krmilnik za kontrolo pristopa, ki lahko krmili do 32 vhodno/izhodnih naprav, kot naprimer Spica, Zone Wing krmilnik, tip:TSTZ1W-2 | -Intelligent access control controller for controlling up to 32 I/O devices, e.g. Spica, Zone Wing controller, type:TSTZ1W-2 | kos | 1
| -Vhodno/izhodna enota, ki krmili čitalce, releje in alarme, kot naprimer Spica, Zone Door I/O naprava, tip: TSTZ1D | -Input/output unit controlling readers, relays and alarms, e.g. Spica, Zone Door I/O device, type: TSTZ1D | kos | 2
| - Napajalnik kot naprimer Spica, tip: TDR60-12VK | - Power supply like Spica, type: TDR60-12VK | kos | 1
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 2
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 2
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 2
| - uvodnice LAPP: | - lAPP introducer:
| + za kable fi 4,5 - 10mm | + for cables fi 4,5 - 10 mm | kos | 12
| Namestiti je potrebno vse potrebne module, da bo kontrola pristopa delovala kot celota; | All the necessary modules must be installed for the access control to work as a complete system;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc. | kpl | 1
| Priključitev napajalnika kontrole pristopa na za to pripravljeni vir napajanja (kabelski fiksni priključek, 230 VAC, UPS napajanje). | Connection of the access control power supply to a ready-to-use power source (cable fixed connection, 230 VAC, UPS power supply).
3.23 | Dobava in montaža stenske kovinske omare za kontrolo pristopa z oznako +RKP14.1, kot na primer: Schneider Electric, tip NSYS3D3320P, dimenzije: 300 mm x 300 mm x 200 mm (VxŠXG) vključno z DIN letvami (NSYMD33) | Supply and installation of a wall-mounted metal access control cabinet with code +RKP14.1, such as Schneider Electric, type NSYS3D3320P, dimensions: 300 mm x 300 mm x 200 mm (HxWxDxWxD) including DIN mouldings (NSYMD33) |  |  | kpl | 1 |  | 0
| V omaro +RKP14.1 se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in +RKP14.1:
| -Vhodno/izhodna enota, ki krmili čitalce, releje in alarme, kot naprimer Spica, Zone Door I/O naprava, tip: TSTZ1D | -Input/output unit controlling readers, relays and alarms, e.g. Spica, Zone Door I/O device, type: TSTZ1D | kos | 3
| - Napajalnik kot naprimer Spica, tip: TDR60-12VK | - Power supply like Spica, type: TDR60-12VK | kos | 1
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 2
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 2
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 2
| - uvodnice LAPP: | - lAPP introducer:
| + za kable fi 4,5 - 10mm | + for cables fi 4,5 - 10 mm | kos | 15
| Namestiti je potrebno vse potrebne module, da bo kontrola pristopa delovala kot celota; | All the necessary modules must be installed for the access control to work as a complete system;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc. | kpl | 1
| Priključitev napajalnika kontrole pristopa na za to pripravljeni vir napajanja (kabelski fiksni priključek, 230 VAC, UPS napajanje). | Connection of the access control power supply to a ready-to-use power source (cable fixed connection, 230 VAC, UPS power supply).
3.24 | Dobava in montaža stenske kovinske omare za kontrolo pristopa z oznako +RKP14.2, kot na primer: Schneider Electric, tip NSYS3D3320P, dimenzije: 300 mm x 300 mm x 200 mm (VxŠXG) vključno z DIN letvami (NSYMD33) | Supply and installation of a wall-mounted metal access control cabinet with code +RKP14.2, such as Schneider Electric, type NSYS3D3320P, dimensions: 300 mm x 300 mm x 200 mm (HxWxDxWxD) including DIN mouldings (NSYMD33) |  |  | kpl | 1 |  | 0
| V omaro +RKP14.2 se dobavi in vgradi naslednja oprema: | The following equipment shall be supplied and installed in +RKP14.2:
| -Vhodno/izhodna enota, ki krmili čitalce, releje in alarme, kot naprimer Spica, Zone Door I/O naprava, tip: TSTZ1D | -Input/output unit controlling readers, relays and alarms, e.g. Spica, Zone Door I/O device, type: TSTZ1D | kos | 3
| - Napajalnik kot naprimer Spica, tip: TDR60-12VK | - Power supply like Spica, type: TDR60-12VK | kos | 1
| - sponke Phoenix Contact, UT 4 | - terminals Phoenix Contact, UT 4 | kos | 2
| - sponke Phoenix Contact, UT 4-PE | - terminals Phoenix Contact, UT 4-PE | kos | 2
| - sponke Phoenix Contact, UT 4-BU | - terminals Phoenix Contact, UT 4-BU | kos | 2
| - uvodnice LAPP: | - lAPP introducer:
| + za kable fi 4,5 - 10mm | + for cables fi 4,5 - 10 mm | kos | 15
| Namestiti je potrebno vse potrebne module, da bo kontrola pristopa delovala kot celota; | All the necessary modules must be installed for the access control to work as a complete system;
| Komplet z vsem potrebnim elektro inštalacijskim in pritrdilnim materialom, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami. itd. | Complete with all necessary electrical installation and fixing materials, wiring, equipotential bonding, cable marking, nameplates, etc. | kpl | 1
| Priključitev napajalnika kontrole pristopa na za to pripravljeni vir napajanja (kabelski fiksni priključek, 230 VAC, UPS napajanje). | Connection of the access control power supply to a ready-to-use power source (cable fixed connection, 230 VAC, UPS power supply).
3.25 | Dobava in montaža na steno (na višini 130 cm od tal) vhodnega čitalnika ID kartic KP, kot naprimer: Spica, tip IXR10SE. Priključitev na pripadajočo vhodno/izhodnu enotu (izhodnega čitalnika ne potrebujemo, ker je predviden izhod s kljuko). | Supply and installation on the wall (at a height of 130 cm from the floor) of a KP ID card input reader, such as Spica, type IXR10SE. Connection to the associated input/output unit (no output reader is required as a hook output is provided). |  |  | kos | 510 |  | 0
3.26 | Dobava in montaža na steno (na višini 130 cm od tal) vhodnega čitalnika ID kartic KP za zunanji del (zalit z epoksi smolo), kot naprimer: Spica, tip IXR10SE. Priključitev na pripadajočo vhodno/izhodnu enotu (izhodnega čitalnika ne potrebujemo, ker je predviden izhod s kljuko). | Supply and installation on the wall (at a height of 130 cm from the floor) of a KP ID card input reader for the external part (epoxy-coated), such as Spica, type IXR10SE. Connection to the associated input/output unit (no output reader is required, as a hook output is provided). |  |  | kos | 2 |  | 0
3.27 | Dobava in montaža na steno (na višini 160 cm od tal) registratora delovnega časa na brezkontaktne kartice, kot naprimer: Spica, Zone Touch; tip TSTZ1T. | Supply and installation on the wall (at a height of 160 cm from the floor) of a time and attendance recorder for contactless cards, e.g. Spica, Zone Touch; type TSTZ1T. |  |  | kos | 9 |  | 0
3.28 | Izvedba, nastavitve in spuščanje v pogon Ethernet povezave med predvidenim Ethernet omrežnim stikalom in posameznim krmilnikom za kontrolo pristopa (Zone Wing). | Implementation, setup and commissioning of the Ethernet connection between the intended Ethernet network switch and the individual Zone Wing controller. |  |  | kos | 14 |  | 0
3.29 | Izvedba, nastavitve in spuščanje v pogon Ethernet povezave med predvidenim Ethernet omrežnim stikalom in registratorem delovnega časa (Zone Touch) | Implementation, setup and commissioning of the Ethernet connection between the intended Ethernet network switch and the time and attendance recorder (Zone Touch) |  |  | kos | 9 |  | 0
3.30 | Dobava brezkontaktnih kartic, število uskladiti s potrebami investitorja | Supply of contactless cards, number to be adjusted to investor's needs |  |  | kos | 0 |  | 0
3.31 | Električne ključavnice se dobavijo skupaj z vrati in so zajeto v načrtu arhitekture | Electric locks are supplied with the door and are included in the architectural plan |  |  | kos | 0 |  | 0
3.32 | Inštalacija, nastavitev, testiranje in spuščanje v pogon informacijske programske opreme za evidenco delovnega časa in kontrolo pristopa za X uporabnikov (TSSTAAC). Programska oprema kontrole pristopa se namesti na server računalnik, ki je lociran v strežniškem prostoru. Programska oprema naj deluje na spletnem brskalniku (Internet Explorer, ...). | Installation, set-up, testing and commissioning of the Time and Attendance and Access Control software for X users (TSSTAAC). The access control software is to be installed on a server computer located in the server room. The software is to run on a web browser (Internet Explorer, etc.). |  |  | kpl | 1 |  | 0
3.33 | Dobava in polaganje na kabelske police oz. uvlečenje v inštalacijske cevi, vključno z označevalnimi ploščicami, razvodnicami ter drobnim in spojnim materialom: | Supply and installation on cable racks or insertion into conduit pipes, including marker plates, conduit boxes, small and jointing materials:
| -F/FTP-Category 6A, 4x2, 24AWG, brezhalogenski; | -F/FTP-Category 6A, 4x2, 24AWG, halogen-free; |  |  | m | 19000 |  | 0
3.34 | Dobava in polaganje na kabelske police oz. uvlečenje v inštalacijske cevi, vključno z označevalnimi ploščicami, razvodnicami ter drobnim in spojnim materialom: | Supply and installation on cable racks or insertion into conduit pipes, including marker plates, conduit boxes, small and jointing materials:
| -Napajalni kabel N2XH-J 3x1,5 mm², brezhalogenski, Lappkabel: | -Power cable N2XH-J 3x1,5 mm², halogen-free, Lappkabel: |  |  | m | 800 |  | 0
3.35 | Dobava in polaganje na kabelske police oz. uvlečenje v inštalacijske cevi, vključno z označevalnimi ploščicami, razvodnicami ter drobnim in spojnim materialom: | Supply and installation on cable racks or insertion into conduit pipes, including marker plates, conduit boxes, small and jointing materials:
| -Napajalni kabel N2XH-J 3x2,5 mm², brezhalogenski, Lappkabel: | -Power cable N2XH-J 3x2,5 mm², halogen-free, Lappkabel: |  |  | m | 200 |  | 0
3.36 | Dobava in polaganje na kabelske police oz. uvlečenje v inštalacijske cevi, vključno z označevalnimi ploščicami, razvodnicami ter drobnim in spojnim materialom: | Supply and installation on cable racks or insertion into conduit pipes, including marker plates, conduit boxes, small and jointing materials:
| -Signalni oz. alarmni kabel za povezave vhodno/izhodnih enot in električnih prijemnikov, LSZH 2x0,5+8x0,22 mm², brezhalogenski, Lappkabel: | -Signalling/alarm cable for connection of I/O units and electrical receivers, LSZH 2x0,5+8x0,22 mm², halogen-free, Lappkabel: |  |  | m | 16000 |  | 0
3.37 | Dobava in polaganje izolacijskih cevi in inšalacijskih kanalov: | Supply and installation of insulation pipes and ducts:
| Trde izolacijske cevi fi 13,5-29, PN, komplet z obešalnim priborom. | Rigid insulation pipes fi 13,5-29, PN, complete with hanger fittings. |  |  | m | 5000 |  | 0
| Gibljive zaščitne cevi fi 16-48, RBT, | Flexible protection tubes fi 16-48, RBT, |  |  | m | 5000 |  | 0
3.38 | Izobraževanje uporabnikov in vzdrževalcev | User and maintenance training |  |  | kpl | 1 |  | 0
| KONTROLA PRISTOPA | ACCESS CONTROL | [5 empty] | 0

## 3.10.4_Ostalo
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.10 | ELEKTRO DELA | ELECTRICAL WORKS
3.10.4 | OSTALO | OTHER |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
4 | OSTALO | OTHER
4.1 | IQ in OQ izvedba testiranja sistemov tehničnega varovanja vključno s pripravo kvalifikacijske dokumentacije | IQ and OQ testing of technical security systems including preparation of qualification documentation | kpl | 1 |  | 0
4.2 | Navodila za obratovanje in vzdrževanje. Izdelana natančna obratovalna navodila glede posameznih stikalnih manipulacij in komunikacij za zagotavljanje rezervnega napajanja in ponovne vzpostavitve normalnega napajanja. | Operating and maintenance instructions. Detailed operating instructions on individual switching manipulations and communications to ensure back-up power and restoration of normal power supply. | kpl | 1 |  | 0
4.3 | Pozitivne ocene, atesti, certifikati in potrdila za vgrajene naprave, napeljave, materiale in montažna dela: -Dokumentacija, izdana s strani priznanih inštitucij (npr. EIMV, IVD, ZAG, SIQ ali enakovredne), ki potrjuje kakovost, skladnost in varnost vgrajene opreme ter izvedenih del. -Vključuje atestne liste, certifikate skladnosti, poročila preizkusov in druga potrdila, ki dokazujejo, da so materiali, naprave in montaža izvedeni po veljavnih standardih in tehničnih predpisih. -Namenjena za prevzemno dokumentacijo, notranje kontrole in dokazovanje skladnosti z zakonodajo ter tehničnimi normativi. Dokumenti izdanih priznanih laboratorijev in inštitucij, kot so naprimer: -EIMV – testiranje in certifikacija elektroinštalacij. -IVD – požarna preizkušanja in certifikacija. -ZAG – preizkušanje gradbenih materialov in konstrukcij. -SIQ – certifikacija, testiranja in nadzor kakovosti. In druge priznane institucije po veljavnih standardih. | Positive assessments, attestations, certificates and approvals for installed appliances, fixtures, materials and installation work: -Documentation issued by recognised institutions (e.g. EIMV, IVD, ZAG, SIQ or equivalent) certifying the quality, conformity and safety of the equipment installed and the work carried out. -It includes certificates of attestation, certificates of conformity, test reports and other certificates proving that the materials, installations and assembly have been carried out in accordance with the applicable standards and technical regulations. -Designed for acceptance documentation, internal controls and demonstrating compliance with legislation and technical standards. Documents issued by recognised laboratories and institutions, such as: -EIMV - Electrical Installation Testing and Certification. -IVD - Fire Testing and Certification. -ZAG - Testing of building materials and structures. -SIQ - certification, testing and quality control. And other recognised institutions according to the applicable standards. | kpl | 1 |  | 0
| OSTALO | OTHER |  |  |  | 0