## 0_Naslovnica
OPOZORILO! Vsi prevodi v angleščino so strojno izdelani in zgolj informativne narave. V primeru kakršnekoli nejasnosti ali dvoma izključno velja izvirno besedilo v slovenščini. WARNING! All translations into English have been produced by machine translation and are provided for informational purposes only. In the event of any ambiguity or uncertainty, the original Slovenian text shall prevail exclusively.
| / | / | [5 empty] | /
| Sprem./Rev.: | Opis spremembe/Description of Changes: | [5 empty] | Datum/Date: | Podpis/Signature:
| Investitor/Investor: |  |  |  |  | Gradnja/Facility
|  |  | Univerza v Ljubljani Kongresni trg 12 1000 Ljubljana, Slovenija |  |  | Fakulteta za strojništvo/Faculty of Mechanical Engineering
| Projektant/Design Engineer: |  |  |  |  | Del objekta/sistem/Building/System:
|  |  | IBE, svetovanje, projektiranje in inženiring Ljubljana, Slovenija |  |  | STAVBA FAKULTETE/FACULTY BUILDING
| Projektant/Design Engineer: |  |  |  |  | Vrsta načrta/Documentation:
3 NAČRT S PODROČJA ELEKTROTEHNIKE/ DOC. IN THE FIELD OF ELECTRICAL ENGINEERING
|  | Ime in priimek/Name and Surname: |  |  | Id. št./Id. No: | Vsebina risbe (dokumenta)/Document Title:
| Vodja proj./ Des. Manager: | Boštjan Vuga, univ. dipl. inž. arh., grad. dip. (AA) |  |  | ZAPS 0035 PA PPN | PR. POPIS ELEKTRO DEL/BOQ OF ELEC. WORKS 3/13 Avtomatizacija zgradbe - BMS in CNS/Building Automation - BMS and CMS
| Poobl. strok./ Cert. Profess.: | Robert Bobovnik, dipl.inž.el. |  |  | IZS E-2380
| Poobl. strok./ Cert. Profess.: |  |  |  |  | Št. proj./ Proj. No.: | 362-19 |  | Vrsta dokument./ Document. Type: | DZR
| Izdelal/ Creator: | Rok Brenkuš, dipl.inž.el. |  |  |  | Klas. ozn./ Class. No.: | -- |  | Stran/ Page: | 1/*
| Datum/ Date: | maj/May 2026 |  | Merilo/ Scale: | / | Ident. ozn./ Id. No: | JULFS--6E9602P

## 0_Osebe
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
POOBLAŠČENI STROKOVNJAKI, ODGOVORNI ZA IZDELAVO PROJEKTANTSKEGA POPISA:
Id. št. ZAPS/IZS | Pooblaščeni strokovnjak | Strokovno področje
IZS E-2380 | Robert Bobovnik, dipl. inž. el. | Električne inštalacije
SODELAVCI PRI IZDELAVI PROJEKTANTSKEGA POPISA:
/ | Rok Brenkuš, dipl. inž. el. | Električne inštalacije
CERTIFIED EXPERTS RESPONSIBLE FOR ELABORATING THE BILL OF QUANTITIES:
Id. No ZAPS/IZS | Certified Expert | Area of Expertise
IZS E-2380 | Robert Bobovnik, dipl. inž. el. | Electrical installations
COLABORATORS IN THE ELABORATING THE BILL OF QUANTITIES:
/ | Rok Brenkuš, dipl. inž. el. | Electrical installations

## 0.1_Uvod-STP
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
0.1 | SPLOŠNI TEHNIČNI POGOJI | GENERAL TECHNICAL CONDITIONS
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic operator with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
0.1.1 | Izvajalec se obveže, da bo upošteval veljavno zakonodajo, ki ureja graditev objektov v Republiki Sloveniji, vključno s povezanimi podzakonskimi akti, predpisi, tehničnimi smernicami, standardi, pravili stroke in dobro gradbeno prakso. Prav tako mora izvajalec upoštevati vse zahteve izdanega integralnega gradbenega dovoljenja in vsa dela izvesti skladno s projektno dokumentacijo ter ostalimi pogoji, objavljenimi v razpisni dokumentaciji. | The Contractor undertakes to comply with the applicable legislation governing the construction of buildings in the Republic of Slovenia, including related by-laws, regulations, technical guidelines, standards, professional rules and good construction practice. The Contractor shall also comply with all the requirements of the integral building permit issued and shall carry out all works in accordance with the project documentation and other conditions published in the tender documentation.
0.1.2 | Dela lahko izvaja samo izvajalec, ki je registriran za opravljanje gradbene dejavnosti in ima za tovrstna dela ustrezno zavarovanje za škodo, certifikate, tehnično izobražen kader, sredstva ter je usposobljen za samostojno pripravo in izvedbo del. | The work may only be carried out by a contractor who is registered to carry out construction work and who has the appropriate insurance for such work, certificates, technically trained staff, resources and is qualified to prepare and carry out the work independently.
0.1.3 | Izvajalec odgovarja za kakovost izvedbe vseh del. | The Contractor shall be responsible for the quality of the execution of all works.
0.1.4 | Izvajalec nosi vso odgovornost za nesreče in škodo, ki nastane na objektu ali v okolici zaradi njegovega dela. | The Contractor shall bear all liability for accidents and damage to the installation or the surrounding area caused by his work.
0.1.5 | Pred oddajo ponudbe se je izvajalec dolžan seznaniti z območjem predvidenim za gradnjo in temu prilagoditi vsa potrebna dela, kar mora biti zajeto v ponudbi. V neposredni bližini predvidene gradnje se nahajajo stavbe, v katerih potekajo izobraževalni in raziskovalni procesi. Zato bo izvajalec moral izvajati kontrolo hrupa in kontrolo vibracij. Dela, ki so hrupna in dela, ki povzročajo vibracije bo izvajalec moral preprečiti oziroma jih izvesti na način, da povzročajo minimalne vplive. Tehnologijo rušenja, pilotiranja in tehnologijo izvedbe ostalih del bo izvajalec moral prilagoditi tako, da bo vpliv minimalen. Izvajalec mora preprečiti in zmanjšati emisije delcev iz gradbišča na najmanjšo možno mero. | Before submitting a tender, the contractor is obliged to familiarise himself with the area to be constructed and to adapt any necessary works accordingly, which must be included in the tender. In the immediate vicinity of the proposed construction, there are buildings in which educational and research processes take place. The contractor will therefore be required to carry out noise and vibration control. Noise and vibration works will have to be avoided or carried out in such a way as to minimise the impact. Demolition, piling and other works will have to be adapted to minimise the impact. The contractor must avoid and minimise the emission of particulates emitted from the construction site as far as is reasonably practicable.
0.1.6 | Izvajalec je pred oddajo ponudbe dolžan pregledati projektno dokumentacijo in ostale pogoje, ki so del razpisne dokumentacije V primeru morebitnih napak in neskladij je izvajalec dolžan na to opozoriti naročnika pred oddajo ponudbe. | The Contractor is obliged to review the project documentation and other conditions forming part of the tender documentation before submitting the tender In case of any errors or inconsistencies, the Contractor is obliged to bring these to the attention of the Contracting Authority before submitting the tender.
0.1.7 | Pred oddajo ponudbe je izvajalec dolžan preveriti ustreznost popisov del in količin v teh popisih ter njihovo skladnost z ostalimi dokumenti projektne dokumentacije, ki so del razpisne dokumentacije. Prav tako je izvajalec dolžan preveriti vse detajle in sheme. Vse izmere je potrebno preveriti po posameznih projektih oz. načrtih, ki sestavljajo razpisno dokumentacijo. V primeru ugotovljenih neskladij je v času priprave ponudbe obvezan o tem obvestiti naročnika. | Before submitting a tender, the Contractor shall check the adequacy of the inventories of works and quantities in these Bills of Quantities and their conformity with the other documents of the project documentation forming part of the tender documentation. The Contractor shall also check all details and diagrams. All measurements shall be checked against the individual projects or plans forming part of the tender documentation. In the event of any discrepancies, the Contractor shall inform the Contracting Authority at the time of preparing the tender.
0.1.8 | Pred oddajo ponudbe je izvajalec dolžan v tem popisu preveriti zmnožke in seštevke ter prenose le-teh v rekapitulacijo. Izvajalec se s pripravo ponudbe obvezuje, da je prebral vse celice in elemente celotnega popisa, vključno z vsemi postavkami in splošnimi navodili ali določili in je preveril pravilnost preračuna ter s tem zagotavlja ponudbeno vrednost. | Before submitting a tender, the Contractor is required to check the products and totals in this Bill of Quantities (BoQ) and their transfer to the recapitulation. The Contractor undertakes, by preparing a tender, to have read all the cells and elements of the complete BoQ, including all headings and general instructions or provisions, and to have checked the correctness of the conversion, thereby guaranteeing the value of the tender.
0.1.9 | Dela bo izvajalec moral izvajati po predloženi projektni dokumentaciji, detajlih in z upoštevanjem navodil in potrditev projektanta, nadzornika in investitorja. Vso potrebno delavniško dokumentacijo zagotovi izvajalec del v okviru ponujene cene. | The Contractor shall carry out the works in accordance with the submitted design documents, details and subject to the instructions and approvals of the Designer, the Supervisor and the Investor. All necessary workshop documentation shall be provided by the Contractor within the scope of the price quoted.
0.1.10 | Pred izvedbo posameznih del je izvajalec dolžan pregledati projektno dokumentacijo za izvedbo gradnje (PZI) in elaborate. Na morebitne napake v dokumentaciji ali neskladja med posameznimi načrti ali deli načrtov (popisi del, tehnična poročila, lokacijski in tehnični prikazi) izvajalec opozori nadzornika in projektanta, in se z njima pravočasno uskladi. | The Contractor shall review the Detailed Design documentation (PZI) and the studies before carrying out the individual works. The Contractor shall draw the attention of the Supervisor and the Designer to any errors in the documentation or discrepancies between the individual designs or parts of designs (BoQ, technical reports, location and technical drawings) and shall coordinate with them in good time.
0.1.11 | Tehnični opisi, prikazi, detajli, sheme ter ostali dokumenti v PZI dokumentaciji predstavljajo dodaten opis popisnih postavk gradbeno obrtniških in inštalacijskih del ter jih je potrebno dosledno upoštevati skupaj s popisom del. | The technical descriptions, illustrations, details, diagrams and other documents in the Detailed Design documentation (PZI) are additional descriptions of the BoQ inventory items of the building, construction and installation works and must be strictly followed together with the BoQ.
0.1.12 | Specifikacije in zahteve, navedene v popisu, se ne smejo upoštevati kot edine zahteve. Izvajalec je dolžan v ceni zajeti in dobaviti vse elemente opreme ter opraviti dela in storitve, ki niso eksplicitno navedeni, a so bistvenega pomena za funkcionalnost, skladnost s predpisi ter kontinuirano, zanesljivo in varno obratovanje opreme. | The specifications and requirements set out in the BoQ shall not be taken as the only requirements. The Contractor shall be obliged to include in the price and supply all items of equipment and to carry out works and services which are not expressly mentioned but which are essential for the functionality, regulatory compliance and continuous, reliable and safe operation of the equipment.
0.1.13 | Vsa dela morajo biti izvedena kvalitetno in iz materialov z zahtevanimi lastnostmi, izvedena skladno z veljavno zakonodajo in z upoštevanjem navodil za vgradnjo za izbrane materiale in opremo, s predložitvijo predpisanih izjav o lastnostih in/ali certifikatov. Vsi gradbeni proizvodi (GP) morajo biti označeni s CE oznako. | All work shall be of good quality and be executed with materials of the required characteristics, in accordance with the applicable legislation and in compliance with the installation instructions for the materials and equipment selected, and shall be accompanied by the prescribed declarations of performance and/or certificates. All construction products (GP) shall bear the CE marking.
0.1.14 | Za vsako opisano delo v popisu je potrebno upoštevati celotno potrebno delo, ves osnovni in pomožni material, prevoz materiala in orodja na objekt, notranje transporte, delovne in pomožne odre, zaključno čiščenje in odstranitev odpadkov po dovršenem delu. | For each work described in the inventory, the total work required, all basic and ancillary materials, the transport of materials and tools to the site, internal transports, working and ancillary scaffolding, final cleaning and the disposal of waste after the work has been completed must be taken into account.
0.1.15 | Vsa delovna sredstva, organizacija in koordinacija del, pripravljalna, spremljajoča in zaključna dela, potrebni montažni in tesnilni materiali ter podkonstrukcije so sestavni del posameznih postavk. | All labour, organisation and coordination of the works, preparatory, accompanying and finishing works, necessary prefabrication and sealing materials and substructures are part of the individual items.
0.1.16 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - načrt organizacije gradbišča s podrobnim terminskim planom in izvedba vseh pripravljalnih del, postavitev, organizacija, zaščita in prijava gradbišča, gradbiščnih objektov, ureditev začasnih deponij, tekoče vzdrževanje, skupaj s plačilom splošnih stroškov pristojbin in davkov upravnih organov, pridobivanju raznih dovoljenj in soglasij za izvedbo, ograditev gradbišča in postavitev gradbene table in prometne signalizacije, zagotavljanje ustrezne varnosti na gradbišču, tekoče vzdrževanje in končna odstranitev gradbišča; - zagotovitev potrebnih začasnih površin za transportne poti in gradnjo izven območja gradbišča s plačilom stroškov za sanacijo in vzpostavitev okoliških zemljišč in objektov v prvotno stanje (soglasja, odškodnine, itd.); - začasni odvoz, deponiranje in vračanje izkopanega materiala, ki ga ne bo možno deponirati na gradbišču; - odvoz in zagotovitev odstranjevanja odpadnega gradbenega materiala skladno z zakonodajo na področju ravnanja z odpadki (odvoz na urejene deponije s plačilom komunalnih prispevkov in taks itd.); - oteženi izkop v mokrem terenu, izkop v vodi, odvod meteorne vode iz gradbene jame in vode, ki se izceja iz bočnih strani izkopov; - ustrezno varovanje izkopa gradbene jame za objekt in ostalih manjših posameznih izkopov za izvedbo komunalne infrastrukture brez posegov na sosednja zemljišča; - ustrezno varovanje obstoječih objektov, infrastrukture in okolice v času gradnje ter dokumentiranje vseh morebitnih škodnih dogodkov; - pripravljalna, spremljajoča in zaključna dela (zakoličbe, zagotovitev potrebnih komunalnih priključkov za potrebe izvajanja gradnje, izvedba začasnih inštalacij, označevanje podzemnih vodov, postavljanje in vzdrževanje zakoličbenih profilov, izvedba in označevanje novih in starih križanj ter morebitna zaščita križanj komunalnih vodov, geodetski posnetki in izdajanje vmesnih posnetkov izvedene infrastrukture naročniku, izdelava zbirnih kart, itd.), v kolikor ni to drugače določeno; - pridobivanje soglasij in izvedba morebitnih zapor na vseh cestah s plačilom stroškov, nadomestil in pristojbin; - zagotovitev oz. postavitev in končna odstranitev po zaključku gradnje začasnih skladišč in začasnega pisarniškega kontejnerskega objekta vključno z opremo za dve delovni mesti in za skupne operativne sestanke vel. ca. 40 m2 za potrebe naročnika, s tekočim vzdrževanjem in čiščenjem. | The following must also be included or taken into account in the uniform prices for individual items: - a construction site organisation plan with a detailed timetable and the execution of all preparatory works, the setting-up, organisation, protection and registration of the construction site, site facilities, the arrangement of temporary storage facilities, ongoing maintenance, including the payment of general costs of fees and taxes of the administrative authorities, the obtaining of various permits and consents for the execution, the fencing of the site and the erection of construction signs and traffic signals, the provision of adequate security on the site, ongoing maintenance and the final dismantling of the construction site; - provision of the necessary temporary areas for transport routes and off-site construction, with costs for restoration and reinstatement of surrounding land and buildings (consents, compensation, etc.); - temporary removal, storage and return of excavated material that cannot be stored on site; - removing and disposing of waste building materials in accordance with waste management legislation (removal to regulated landfill sites with payment of municipal fees and charges, etc.); - difficult excavation in wet ground, excavation in water, drainage of rainwater from the construction pit and water draining from the sides of excavations; - adequate protection of the excavation of the construction pit for the building and other small individual excavations for the implementation of the utility infrastructure without encroaching on neighbouring land; - adequate protection of existing facilities, infrastructure and the surrounding area during construction, and documentation of any damage incidents; - preparatory, accompanying and finishing works (stake-out, provision of the necessary utility connections for the needs of construction, execution of temporary installations, marking of underground lines, installation and maintenance of stake-out profiles, execution and marking of new and old crossings and possible protection of crossings of utility lines, geodetic surveys and issuing of intermediate images of the completed infrastructure to the client, production of summary maps, etc.), unless otherwise specified; - obtaining consents and implementing any road closures, with costs, compensation and fees; - provision or erection and final removal on completion of construction of temporary storage and temporary office container building including equipment for two workstations and for joint operational meetings of approx. 40 m2 for the needs of the client, with ongoing maintenance and cleaning.
0.1.17 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - izdelava montažne tehnične dokumentacije, detajlov izvedbe in vse druge potrebne delavniške dokumentacije (s področja arhitekture, gradbeništva, elektrotehnike, strojništva in zunanje ter krajinske ureditve) ter pridobitev obvezne potrditve s strani projektanta, nadzornika in investitorja; - odprava vseh vrst inštalacijskih kolizij z izvajanjem potrebnih premikov inštalacij in njihovim usklajevanjem na mestu montaže, vse v obsegu, ki ne vpliva na projektirano rešitev ali tip inštalacij oz. opreme; - zagotavljanje kompletnosti elektro-instalacijskih sistemov s področja avtomatike za doseganje njihove popolne funkcionalnosti delovanja; - stroški za nadzor in koordinacijo izvedbe vseh elektro napeljav, ki so predmet končne instalacije proizvoda (senčila, vrata, okna,…); - izdelava montažnih skic in detajlov za izvedbo v dogovoru z vodjo gradnje in nadzornikom; - izdelava in predstavitev vzorcev v ustrezni velikosti za potrditev projektanta, nadzornika in investitorja; - zagotavljanje varnosti in zdravja pri delu, zlasti izvajanje vseh del, ki izhajajo in ukrepov, ki izhajajo iz določil veljavnih predpisov varstva pri delu in zahtev Varnostnega načrta;- stroški garancij, ki jih mora izvajalec predložiti naročniku. | The following must also be included or taken into account in the uniform prices for individual items: - preparation of prefabricated technical documentation, construction details and all other necessary workshop documentation (architectural, civil, electrical, mechanical, exterior and landscaping) and obtaining the mandatory approval of the designer, the supervisor and the investor; - elimination of all types of installation conflicts by carrying out the necessary relocation of installations and their coordination at the installation site, all to the extent that it does not affect the design solution or the type of installation or equipment; - ensuring the completeness of electrical installation systems in the automation sector to achieve their full operational functionality; - the cost of supervising and coordinating the installation of all the electrical installations that are the subject of the final installation of the product (blinds, doors, windows, etc.); - preparation of erection drawings and details for implementation in agreement with the construction manager and supervisor; - production and presentation of samples in appropriate sizes for the approval of the designer, the supervisor and the investor; - ensuring health and safety at work, in particular the implementation of all the works arising from and the measures resulting from the provisions of the applicable occupational safety regulations and the requirements of the Safety Plan; - the cost of the guarantees to be provided by the contractor to the client.
0.1.18 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - strošek vodje del glavnega izvajalca, ki bo izvajal tudi koordinacijo s podizvajalci in z drugimi izvajalci, ki jih bo izbral naročnik in bo opravljal delo vodje gradbišča; - koordinacija del z ostalimi izvajalci oz. podizvajalci del, projektantom, nadzornikom in investitorjem pri medsebojnem usklajevanju organizacije gradbišča in časovnega načrta del ter pri usklajevanju izdelave plana montaže, potrjenih s strani vseh udeležencev gradnje; - stroški koordinacije, sodelovanja in usklajevanja z dobavitelji tehnološke, laboratorijske, eksperimentalne in vse ostale pohištvene ter multimedijske opreme ter z vsemi ostalimi dobavitelji oz. podizvajalci na objektu; - stroški izdelave situacij; - stroški zavarovanja objekta v času izvedbe del in delavcev ter materiala na gradbišču v času izvajanja del, od začetka del do pridobitve uporabnega dovoljenja za objekt. Zavarovanje mora biti sklenjeno pri ustrezni zavarovalni družbi najmanj v višini pogodbene vrednosti ali v zakonsko predpisani vrednosti (v kolikor zavarovanje v višini pogodbene vrednosti presega zakonsko dovoljeno), za ves čas trajanja izvedbe del do uspešne primopredaje objekta; - preizkušanje kvalitete materiala, ki se vgrajuje in dokazovanje kvalitete s certifikati oz. tehničnimi soglasji; - izvedba vseh zahtevanih testov in preizkusov (npr. tlačni preizkusi, termografski pregledi, meritve elektromagnetnega sevanja, hrupa, itd.), poskusnega obratovanja celotnega objekta s poudarkom na vseh inštalacijah ter izvajanje predpisanega monitoringa v skladu s Poročilom o vplivih na okolje (pred gradnjo, med gradnjo in po končani gradnji); - izdelava izkaza požarne varnosti, vključno s sprotnim spremljanjem gradnje in izvajanjem požarnovarnostnih zahtev ter izdelava Požarnega reda z obveznimi prilogami; - izdelava Izkaza zaščite pred hrupom v stavbah; - izdelava Izkaza energijskih lastnosti stavbe in energetske izkaznice; - sodelovanje z izvajalci gradbenega in projektantskega nadzora in investitorjem za izvedbo tehničnega pregleda in priprava primopredaje, ki mora vsebovati vso zahtevano dokumentacijo, predvsem pa: izjave o skladnosti, požarni izkaz in ostale izkaze ter obvezne tabele, dokazilo o zanesljivosti objekta (DZO), certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo in vzdrževanje ter vse ostale dokumente v skladu s predpisi in pogodbenimi določili. | The following must also be included or taken into account in the uniform prices of the individual items: - the cost of a works manager for the main contractor, who will also coordinate with subcontractors and other contractors selected by the client and act as site manager; - coordination of the works with other contractors or subcontractors, the designer, the supervisor and the investor in coordinating the organisation of the construction site and the timetable for the works, and in coordinating the production of an installation plan approved by all the participants in the construction; - the costs of coordination, cooperation and coordination with suppliers of technological, laboratory, experimental and all other furniture and multimedia equipment, as well as with all other suppliers or subcontractors on the site; - the cost of drawing up situations; - the cost of insuring the building during the execution of the works and the workers and materials on site during the execution of the works, from the start of the works until the building has been licensed for occupation. The insurance must be taken out with a suitable insurance company for at least the contract value or the legal value (if the insurance for the contract value exceeds the legal value), for the entire duration of the works until the successful handover of the building; - testing the quality of the material to be installed and proving it with certificates or technical approvals; - carrying out all required tests and trials (e.g. pressure tests, thermographic inspections, electromagnetic radiation measurements, noise measurements, etc.), trial operation of the entire building, with emphasis on all installations, and carrying out the required monitoring in accordance with the Environmental Impact Assessment Report (before, during and after construction); - preparation of a fire safety statement, including ongoing monitoring of construction and implementation of fire safety requirements, and preparation of a Fire Safety Order with mandatory annexes; - preparation of a Noise Protection Statement for buildings; - preparation of the Building Energy Performance Report and Energy Performance Certificate; - cooperation with the construction and design supervision contractors and the investor to carry out the technical inspection and prepare the handover, which must include all the required documentation, in particular: declarations of conformity, fire and other statements and mandatory tables, proof of reliability of the building (DZO), certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use and maintenance, and all other documents in accordance with the regulations and the contractual provisions.
0.1.19 | V enotnih cenah posameznih postavk, ki se nanašajo na opremo in posamezne sisteme, mora biti zajeto oz. upoštevano tudi naslednje: - dobava oz. transport, - stroški za vse delovne stroje za dvigovanje bremen in delovne košare za dostope do delovišč; - morebitni stroški povzročeni upravljavcem GJI, ki bi nastali v zvezi s predmetno gradnjo; - montaža, vključno s pomožnim montažnim materialom (vezni, tesnilni in pritrdilni material, sidra, nosilni profili, podkonstrukcije in podobno) in navodili proizvajalca, - odprava vseh kolizij sistemov s stenami in med sistemi, - izvedba vseh potrebnih tesnjenj, - priključitev in nastavitve, vključno z morebitnim kalibriranjem, - zagon, testiranje in meritve, vključno s poročili, - šolanje uporabnikov oz. vzdrževalnega osebja za uporabo in vzdrževanje sistemov, - navodila za obratovanje in vzdrževanje, - vsi potrebni certifikati, izjave o skladnosti oz. potrdila ter - vsa druga pomožna dela in material, da se zagotovi funkcionalnost posamezne postavke popisa. | The following must also be included or taken into account in the uniform prices for individual items relating to equipment and individual systems: - delivery/transport, - the cost of all lifting machines and work baskets for access to work sites; - any costs incurred to the operators of utility infrastructure (GJI) in connection with the subject construction; - installation, including ancillary installation materials (bonding, sealing and fixing materials, anchors, support profiles, substructures, etc.) and manufacturer's instructions, - eliminating all system-to-wall and system-to-system collisions, - all necessary sealing work, - connection and set-up, including calibration if necessary, - commissioning, testing and measurements, including reports, - training users or maintenance staff in the use and maintenance of the systems, - operating and maintenance instructions, - any necessary certificates, declarations of conformity or attestations; and - all other ancillary works and materials to ensure the functionality of each inventory item.
0.1.20 | Vsi odri morajo biti upoštevani v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All scaffolding must be included in the uniform prices of the items listed, except where specifically mentioned.
0.1.21 | Vsi delovni in pomožni odri, lestve in ostala potrebna pomožna sredstva, kot tudi čiščenje vseh elementov po končanih delih, mora biti upoštevano v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All working and auxiliary scaffolding, ladders and other necessary ancillaries, as well as the cleaning of all elements after completion of the works, shall be included in the uniform prices of the items listed, except those specifically mentioned.
0.1.22 | Delavniško dokumentacijo za vse nosilne jeklene konstrukcije in podkonstrukcije izdela izvajalec, strošek izdelave delavniške dokumentacije se upošteva v ponujenih cenah in se ne obračuna posebej. | The cost of the shop drawings for all steelwork and substructures shall be included in the prices quoted and shall not be charged separately.
0.1.23 | V enotnih cenah postavk mora biti vključeno tudi vgrajevanje vseh instalacijskih razvodov v opaže armirano betonskih elementov in izdelava prehodov inštalacij ter dodatno izrezovanje utorov in prebojev v kamnite, zidane ali armirano-betonske stene, ponovno demontiranje in montiranje vseh vrst montažnih sten, vsa dodatna dela za zagotavljanje primernih križanj med posameznimi instalacijskimi vodi, izdelava vseh vrst ojačitev konstrukcij in podobna dela, ki zagotavljajo kakovostno vgradnjo vseh vrst instalacijskih vodov in niso posebej navedena v popisu GOI del. V ponudbi morajo biti upoštevana vsa drobna strojna in elektro instalacijska dela in transporti. | The installation of all installation ducts in the formwork of reinforced concrete elements and the construction of installation penetrations, as well as the additional cutting of grooves and penetrations in stone, masonry or reinforced concrete walls, the reassembly and reinstallation of all types of prefabricated walls, all additional work to ensure adequate crossings between individual installation ducts, the construction of all types of structural reinforcement and similar work to ensure the quality installation of all types of installation ducts and not specifically mentioned in the BoQ of the Construction, installation and finishing works (GOI) shall also be included in the uniform prices of the items. The tender shall take into account all minor mechanical and electrical installation work and transport.
0.1.24 | Vsi kovinski elementi in konstrukcije, ki bi lahko bili izpostavljeni atmosferskim in ostalim korozijskim vplivom, morajo biti ustrezno protikorozijsko zaščiteni. | All metallic elements and structures that could be exposed to atmospheric and other corrosive influences must be adequately protected against corrosion.
0.1.25 | Za vse večje jeklene dele se skladno s predpisi, izdelajo ustrezne ozemljitve, nevidno pritrjene in speljane na splošno ozemljitev objekta. | For all major steel parts, appropriate earth connections shall be made in accordance with the regulations, invisibly attached and connected to the general earth of the building.
0.1.26 | Za vse vidne elemente in serijske elemente je obvezna predhodna uskladitev obdelav, barv in materialov s projektantom na podlagi dostavljenih vzorcev v ustrezni velikosti. Obvezna je preveritev dejanskih mer na licu mesta in posledična prilagoditev elementov in njihove montaže. | For all visible elements and serial elements, it is mandatory to coordinate the finishes, colours and materials with the designer beforehand on the basis of the supplied samples in the appropriate size. It is mandatory to check the actual dimensions on site and to adjust the elements and their installation accordingly.
0.1.27 | Dimenzije obrtniških izdelkov in količine je potrebno pred naročanjem preveriti na objektu. Potrebna je uskladitev vseh elementov (kljuke, okovje, detajlne konstrukcije in obdelave, itd.) s projektantom, nadzornikom in investitorjem. Izvajalec je dolžan pred izdelavo predložiti projektantu v potrditev ustrezne delavniške načrte in detajle. | The dimensions of the workmanship and quantities must be checked on site before ordering. All elements (hooks, fittings, detailed construction and finishes, etc.) must be coordinated with the designer, the supervisor and the investor. The contractor is obliged to submit the relevant workshop plans and details to the designer for approval before manufacture.
0.1.28 | V posameznih postavkah popisa so navedeni proizvajalci in/ali tipi posameznih sistemov, materialov ali opreme, s čimer so zgolj natančno opredeljene zahtevane tehnične lastnosti. Izvajalec del lahko ponudi nadomesten sistem, material ali opremo drugega proizvajalca in tipa, pri čemer morajo biti tehnične lastnosti ponujenega sistema, materiala ali opreme enakovredne ali boljše od opredeljenih v popisu, dimenzijsko pa ne smejo presegati projektiranih dimenzij. Vse funkcijske in tehnične karakteristike nadomestnih sistemov, materialov ali opreme mora izvajalec dokazati z ustrezno dokumentacijo. Vse morebitne posledice zaradi spremembe sistemov, materialov ali opreme vključno z morebitnimi spremembami oz. dopolnitvami BIM modelov in projektne dokumentacije, stroškovno in časovno bremenijo izvajalca. | The individual items of the Inventory shall specify the manufacturers and/or types of the individual systems, materials or equipment, thereby merely specifying the required technical characteristics. The Contractor may offer a substitute system, material or equipment of a different manufacturer and type, provided that the technical characteristics of the offered system, material or equipment shall be equivalent to or better than those specified in the BoQ, and shall not exceed the design dimensions. All functional and technical characteristics of the substitute systems, materials or equipment shall be demonstrated by the Contractor with appropriate documentation. Any consequences resulting from changes to systems, materials or equipment, including any changes or additions to the BIM models and project documentation, shall be borne by the Contractor in terms of cost and time.
0.1.29 | Vsako zamenjavo, uporabo in končni izbor nadomestnih sistemov, materialov, proizvodov in opreme morajo obvezno in pravočasno (pred dobavo in vgradnjo) pisno potrditi projektant (vseh sodelujočih strok), nadzornik in investitor. | Any replacement, use and final selection of alternative systems, materials, products and equipment must be approved in writing by the designer (of all disciplines involved), the supervisor and the investor in a timely manner (prior to delivery and installation).
0.1.30 | Izvajalec mora v ponudbeno ceno vključiti tudi: - ves čas gradnje sprotno beleženje sprememb oz. odstopanj od PZI dokumentacije, vključno z izdelavo tekstualnega opisa sprememb, - pripravo podlog na nivoju PZI, ki so potrebne za posodobitev oz. uskladitev BIM modela z izvedenim stanjem (LOD 500) in izdelavo projektne dokumentacije izvedenih del (PID), - mesečno predajanje potrjenih sprememb opreme in materiala, ki vplivajo na BIM model, v formatu IFC, - vzdrževanje in uporabljanje pri izvedbi zadnje veljavne revizije PZI dokumentacije, vključno z dopolnitvami PZI načrtov, ki so nastali zaradi sprememb med gradnjo. | The contractor must also include in the tender price: - keeping a record of changes or deviations from the construction documentation (PZI) throughout construction, including a textual description of the changes, - preparation of the Detailed Design (PZI) level documents required to update or align the BIM model with the as-built condition (LOD 500) and the preparation of the as-built project documentation for the works (PID), - monthly submission of approved equipment and material changes affecting the BIM model in IFC format, - maintenance and use in the execution of the last valid revision of the construction documentation (PZI), including additions to the construction design documentation (PZI) resulting from changes during construction.

## 0.2_Uvod-DGNB
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
0.2 | SPLOŠNI TEHNIČNI POGOJI ZA PODROČJE DGNB CERTIFICIRANJA | GENERAL TECHNICAL CONDITIONS FOR DGNB CERTIFICATION
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic entity with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
| Splošni pogoji za področje DGNB certificiranja predstavljajo dopolnilo splošnim tehničnim pogojem in ne odpravljajo drugih obveznosti in odgovornosti, ki jih ima izvajalec v skladu s predpisi in pogodbo. | The General Conditions for DGNB Certification are complementary to the General Technical Conditions and do not exclude other obligations and responsibilities that the Contractor has under the Regulations and the Contract.
0.2.1 | Izvajalec mora v svojih ponudbah upoštevati, da se bo objekt certificiral v skladu z zahtevami DGNB sistema certificiranja trajnostne gradnje, ter pravočasno (vsaj 60 dni pred vgradnjo posameznega produkta) dostaviti vso ustrezno dokumentacijo za vse v ponudbi zajete materiale, elemente in opremo. Zahtevana je uporaba materialov, elementov ali opreme, ki so okolju in ljudem prijazni, energetsko učinkoviti in obenem ustrezajo zahtevam DGNB sistema. Zahtevan nivo certifikata je: ZLATI CERTIFIKAT | The Contractor shall take into account in its tenders that the building will be certified in accordance with the requirements of the DGNB Sustainable Building Certification Scheme and shall deliver all relevant documentation for all materials, elements and equipment included in the tender in a timely manner (at least 60 days before the installation of each product). The use of materials, elements or equipment that are environmentally and human friendly, energy efficient and at the same time meet the requirements of the DGNB system is required. The required level of certification is: GOLD CERTIFICATE
0.2.2 | Podrobnejši opis DGNB sistema in navodila za posamezne kriterije so dostopna v dokumentu"DGNB Criteria Set New Construction Buildings, Version 2020 International", ki je na voljo na DGNB spletni strani https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria | A more detailed description of the DGNB system and guidance on the individual criteria is available in the document "DGNB Criteria Set New Construction Buildings, Version 2020 International", available on the DGNB website https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria
0.2.3 | Izvajalec mora v svojih ponudbah upoštevati, da je potrebno skladno z določili DGNB certifikacijskega sistema, pravočasno (pred pričetkom gradnje) dostaviti vso ustrezno dokumentacijo, za vse v ponudbi zajete materiale, elemente in opremo (tehnični list, varnostni list, izjava o lastnostih, tehnična navodila za ravnanje, servisiranje, vzdrževanje,...) v slovenskem jeziku. Vgradnja kakršnihkoli materialov, elementov ali opreme, se izvede zgolj na podlagi predhodne preveritve posredovane dokumentacije in obenem potrditve s strani nadzornika. | The Contractor must take into account in its tenders that, in accordance with the provisions of the DGNB certification system, all relevant documentation for all materials, elements and equipment included in the tender (technical data sheet, safety data sheet, declaration of properties, technical instructions for handling, servicing, maintenance,...) must be delivered on time (prior to the start of construction) in the Slovene language (in accordance with the provisions of the DGNB certification system). The installation of any materials, elements or equipment shall be subject to prior checking of the submitted documentation and, at the same time, to the approval of the Supervisor.
0.2.4 | Izbrani materiali, elementi, naprave, sistemi in oprema morajo prispevati k večji trajnosti stavbe v smeri zagotavljanja energetske učinkovitosti, ekonomičnega in enostavnega vzdrževanja ter čiščenja, dolge življenjske dobe, uporabe okolju prijaznih materialov ipd. | The materials, elements, appliances, systems and equipment chosen must contribute to the sustainability of the building in terms of energy efficiency, economic and easy maintenance and cleaning, long lifetime, use of environmentally friendly materials, etc.
0.2.5 | Predloženi dokumenti za vse uporabljene materiale, elemente in opremo morajo izpolnjevati zahteve najmanj kakovostne stopnje QS3 (zaželeno QS4), iz dokumenta: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001) | The documents submitted for all materials, components and equipment used shall meet the requirements of at least quality level QS3 (preferably QS4) of the document DGNB Quality Grades for Materials, Components and Equipment (JULFS--7X9001)
0.2.6 | V kolikor izbrani materiali oz. elementi, navedeni v posameznih postavkah, ne ustrezajo vsaj kakovostni stopnji QS3 iz seznama: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), je izvajalec dolžan na to opozoriti projektanta, nadzor in investitorja ter podati predlog ustreznega materiala oz. elementa. | If the selected materials or elements listed in the individual items do not meet at least quality level QS3 of the list of DGNB quality classes for materials, elements and equipment (JULFS--7X9001), the Contractor shall draw this to the attention of the Designer, the Supervisor and the Investor, and shall make a proposal for a suitable material or element.
0.2.7 | Izvajalec lahko v svoji ponudbi predlaga alternativne produkte in rešitve glede na predvidene s projektom, pod pogojem, da le-te prav tako izpolnjujejo vse navedene zahteve. Pri morebitnih predlaganih alternativnih produktih oz. rešitvah je potrebno upoštevati najmanj enake ali boljše lastnosti v smislu življenjske dobe, obstojnosti, ter enostavnosti in stroška čiščenja ter vzdrževanja v primerjavi s projektom predpisanimi rešitvami. Za alternativne rešitve izvajalec pridobi soglasje projektanta, nadzornika in investitorja pred pričetkom gradnje. | The Contractor may propose alternative products and solutions to those envisaged by the project in its tender, provided that they also meet all the requirements set out above. Any alternative products or solutions proposed shall have at least the same or better characteristics in terms of service life, durability, and ease and cost of cleaning and maintenance compared to the solutions envisaged by the project. For alternative solutions, the contractor shall obtain the agreement of the designer, the supervisor and the investor before starting construction.
0.2.8 | Izvajalec med gradnjo dnevno beleži vsa eventualna odstopanja od PZI projektne dokumentacije ter podatke pravočasno posreduje naročniku, nadzoru in projektantu. Potrjene spremembe vnese v podlage za izdelavo PID in posodobitev BIM modelov. | During construction, the Contractor shall record on a daily basis any deviations from the Detailed Design documentation (PZI) and shall provide the information to the Client, Supervision and the Designer in a timely manner. Confirmed changes shall be entered into the basis for the As-built documentation (PID) and BIM model updates.
0.2.9 | Izvajalec med gradnjo sproti izpolnjuje Seznam vseh konstrukcijskih sestav s pripadajočimi vgrajenimi gradbenimi materiali in dokumentira naslednje podatke o vgrajenih materialih (v slovenskem jeziku): - Varnostni list - Tehnični list - Izjavo o lastnostih (če je relevantno) - Izkazovanje morebiti obstoječega okoljskega certifikata (Tip I - okoljski znak ali Tip III - okoljska produktna deklaracija /EPD) - Izjavo proizvajalca ali dobavitelja, da produkt ustreza zahtevam ENV1.2 - Tehnična navodila za ravnanje, servisiranje, vzdrževanje oziroma ostale, z zakonom predpisane dokumente in dokumentacijo. | During construction, the Contractor shall keep a List of all structural assemblies with their associated construction materials and document the following information on the materials installed (in Slovene language): - Safety Data Sheet - Technical Data Sheet - Declaration of performance (if applicable) - Demonstration of any existing environmental certification (Type I - Ecolabel or Type III - Environmental Product Declaration /EPD) - A declaration by the manufacturer or supplier that the product complies with the requirements of ENV1.2 - Technical instructions for handling, servicing, maintenance or other documents and documentation required by law.
0.2.10 | Za vse vgrajene bistvene tehnične sisteme mora izvajalec zagotoviti obstoj pooblaščenega servisa, ki deluje na območju Republike Slovenije, da ima investitor možnost skleniti ustrezno pogodbo o vzdrževanju. Med bistvene tehnične sisteme sodijo npr.: sistemi ogrevanja in hlajenja, priprava tehnoloških medijev, prezračevanje in klimatizacija, sistemi detekcije in gašenja požara, sistemi tehničnega varovanja, BMS in CNS sistemi upravljanja stavbe, razsvetljava, komunikacijski in WI-FI sistemi,... | For all installed essential technical systems, the contractor must ensure the existence of an authorised service centre operating in the territory of the Republic of Slovenia, so that the investor has the possibility of concluding an appropriate maintenance contract. The essential technical systems include, for example: heating and cooling systems, technological media preparation, ventilation and air conditioning, fire detection and extinguishing systems, technical security systems, BMS and CNS building management systems, lighting, communication and WI-FI systems,...
0.2.11 | Zaželeno je, da imajo uporabljeni elementi in materiali okoljsko oznako Tip I. (kot npr. ENCODE, BLUE ANGEL, ipd...). | It is preferable that the elements and materials used have a Type I environmental label (such as ENCODE, BLUE ANGEL, etc...).
0.2.12 | Izvajalec bo za elemente iz lesa moral dokazovati izvor z navedbo izvorne države in tipa lesa, FSC / PEFC certifikat z dodatnim pripadajočim potrdilom Chain of custody-trgovski certifikat dobavitelja - ta se dokazuje z dobavnicami, računi ali enakovredno. Za izdelke iz naravnega kamna iz EU držav je potrebna deklaracija, da je izvor in procesiranje teh izdelkov v celoti v EU državah. Za izdelke iz naravnega kamna, ki prihajajo iz držav izven EU, je potrebno predložiti dokazilo o izpolnjevanju ILO konvencije 182, ki vključuje neodvisna inšpekcijska poročila. | For wood elements, the contractor will be required to provide proof of origin, indicating the country of origin and the type of wood, FSC/PEFC certification with an additional Chain of Custody certificate - the supplier's trade certificate - this shall be evidenced by delivery notes, invoices or equivalent. For natural stone products from EU countries, a declaration that the sourcing and processing of these products is entirely in EU countries is required. For natural stone products from non-EU countries, proof of compliance with ILO Convention 182, including independent inspection reports, is required.
0.2.13 | Izobraževanje udeležencev pri gradnji Izvajalec je dolžan vse udeležence pri gradnji podrobneje seznaniti tudi z relevantnimi koncepti, študijami, elaborati, ki opredelujejo trajnostni način gradnje za naslednja področja: - zaščita pred hrupom (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)) - zaščita pred prašenjem - zaščita tal in podzemne vode (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)), Analiza tveganja za onesnaženje vodnega telesa podzemne vode št. 0346-023/2023, maj 2023 (Geološko projektiranje d.o.o.)) - ravnanje z gradbenimi odpadki (Načrt gospodarjenja z gradbenimi odpadki) Izobraževanja se izvajajo skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.1 1.2, 2.2, 3.2 in 4.2 Training for the parties implementing the construction work | Training of construction participants The contractor is also obliged to inform all construction participants in detail about relevant concepts, studies, elaborations defining sustainable construction methods for the following areas: - noise protection (Environmental Impact Assessment Report No 100123-11523, dated 11.5.2023, supplemented on 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.)) - dust protection - protection of soil and groundwater (Environmental Impact Assessment Report No. 100123-11523, dated 11.5.2023, supplemented 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.), Risk analysis for contamination of the groundwater No. 0346-023/2023, May 2023 (Geološko projektiranje d.o.o.)) - construction waste management (Construction Waste Management Plan) The training shall be carried out in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.1 1.2, 2.2, 3.2 and 4.2 Training for the parties implementing the construction work
0.2.14 | Navodila za obratovanje in vzdrževanje objekta Izvajalec pripravi Navodila za obratovanje in vzdrževanje objekta skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilih: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual | Instructions for the operation and maintenance of the facility The Contractor shall prepare the Operation and Maintenance Instructions for the Facility in accordance with the applicable Slovenian legislation and the DGNB System Instructions specified in the Criteria: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual
0.2.15 | Meritve kontrole kakovosti gradnje Izvajalec mora upoštevati, da se bodo po koncu gradnje izvedle naslednje meritve: - meritve zrakotesnosti - meritve s termokamero (termografija) - meritve akustike - meritve zvočne zaščite ovoja stavbe - meritve zvočne zaščite ločilnih elementov med posameznimi prostori različnih namembnosti - meritve udarnega zvoka - meritve vlažnosti vgrajenih elementov, pred vgradnjo finalnih tlakov - test odvoda dima in toplote Meritve morajo opraviti ustrezno usposobljeni preskusni organi ali strokovnjaki ter rezultate oceniti in primerjati z zahtevami. Obseg opravljenih meritev mora biti sorazmeren z velikostjo zgradbe in mora ustrezno odražati cilj preverjanja kakovosti zgradbe. Smiselno je, da izvajalec del tekom gradnje za sprotno kontrolo kakovosti vgrajenih materialov, elementov in opreme, sam izvaja meritve. Končne meritve (ob primopredaji) izvede tretja oseba kot neodvisna potrditev doseganja zahtev. Meritve se izvajajo skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 2. Quality control measurements | Construction quality control measurements The contractor must take into account that the following measurements will be carried out after completion of the construction: - airtightness measurements - thermal camera measurements (thermography) - acoustics measurements - measurements of the sound insulation of the building envelope - measurements of the sound insulation of the separating elements between different rooms of different uses - impact sound measurements - moisture measurements of the installed elements, prior to the installation of the final flooring - smoke and heat extraction test The measurements shall be carried out by suitably qualified test bodies or experts and the results evaluated and compared with the requirements. The extent of the measurements carried out shall be proportionate to the size of the building and shall adequately reflect the objective of the building quality verification. It is reasonable for the contractor to carry out his own measurements during construction to check the quality of the materials, elements and equipment installed. Final measurements (at handover) are carried out by a third party as an independent confirmation of compliance with the requirements. The measurements shall be carried out in accordance with the applicable Slovenian legislation and the DGNB system instructions specified in the benchmark: PRO 2.2 2. Quality control measurements
0.2.16 | Zagotavljanje kakovosti za uporabljene gradbene proizvode Izvajalec mora zagotavljati izvajanje primerjav med definiranim in dejansko uporabljenim materialom, elementom ali opremo skladno seznamom: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), vključno z dokazno dokumentacijo ugotovitev primerjav ter skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 3.1 Quality assurance for the used construction products | Quality assurance for the construction products used The Contractor shall ensure that comparisons are made between the defined and the actual material, element or equipment used in accordance with the list: DGNB Quality Grades of Installed Materials, Elements and Equipment (JULFS--7X9001), including supporting documentation of the findings of the comparisons, and in accordance with the DGNB system instructions defined in the Criterion: PRO 2.2 3.1 Quality assurance for the used construction products
0.2.17 | Zaščita pred vlago Izvajalec predloži dokumentacijo, ki dokazuje, da je bil izveden program prezračevanja, prilagojen stavbi, s čimer se zagotovi pogoje, da so vgrajeni gradbeni elementi ustrezno suhi, skladno z navodili DGNB opredeljenimi v merilu: PRO 2.2 4.1 Mould prevention | Protection against moisture The Contractor shall provide documentation demonstrating that a building-specific ventilation programme has been implemented to ensure that the building elements installed are adequately dry, in accordance with the DGNB guidelines specified in the criteria: PRO 2.2 4.1 Mould prevention
0.2.18 | Preizkusi delovanja sistemov Izvajalec sodeluje pri izvedbi predhodnega in končnega preizkusa delovanja vseh bistvenih tehničnih komponent stavbe in pripravi ustrezne dokazne dokumentacije ter pri usposabljanju vzdrževalcev/upravljalcev stavbe, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators | System performance tests The Contractor shall be involved in the performance of the preliminary and final performance tests of all essential technical components of the building and the preparation of the relevant supporting documentation, as well as in the training of the maintenance/management staff of the building, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators
0.2.19 | Poročilo o zagonu objekta Izvajalec sodeluje pri pripravi končnega poročila o zagonu objekta, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 5.1 Creation of a detailed final report | Commissioning report The Contractor shall be involved in the preparation of the final commissioning report, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 5.1 Creation of a detailed final report
0.2.20 | Koncept celovitega delovanja sistemov v stavbi Izvajalec sodeluje pri procesu implementiranja stalnega nadzora in nastavitev delovanja stavbe ter usposabljanju vzdrževalcev/upravljalcev stavbe. Navedeno se izvede v skladu z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 6.1 Creation and handover of an integral operating concept | The concept of integrated building systems The contractor is involved in the process of implementing the building's continuous monitoring and settings and training the building's maintenance/management staff. This shall be done in accordance with the DGNB system instructions defined in the benchmark: PRO 2.3 6.1 Creation and handover of an integral operating concept
0.2.21 | Prilagoditev nastavitev sistemov po začetni fazi uporabe objekta Izvajalec sodeluje pri ponovnem pregledu delovanja vseh bistvenih tehničnih sistemov ter eventualni ponovni prilagoditvi teh sistemov s strani strokovnjaka oz. (neodvisne) tretje osebe. Postopek se izvede po približno 10–14 mesecih po zaključku gradnje, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 7.1 Readjustment of the system following initial operating phase | Adjusting system settings after the initial phase of use of the building The Contractor shall be involved in the re-examination of the functioning of all essential technical systems and the possible re-adjustment of these systems by an expert or (independent) third party. The procedure shall be carried out approximately 10-14 months after completion of construction, in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.3 7.1 Readjustment of the system following initial operating phase

## 3.13.0_Rekapitulacija
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
| REKAPITULACIJA STROŠKOV ELEKTRO DEL | COST SUMMARY OF ELECTRICAL WORKS
| 3 NAČRT S PODROČJA ELEKTROTEHNIKE | 3 DOCUMENTATION IN THE FIELD OF ELECTRICAL ENGINEERING
| 3/13 Avtomatizacija zgradbe - BMS in CNS | 3/13 Building Automation - BMS and CMS
3.13 | ELEKTRO DELA | ELECTRICAL WORKS
3.13.1 | Klimatizacija in prezračevanje (inštalacije) | Air conditioning and ventilation (installations) | 0
3.13.2 | Klimatizacija in prezračevanje (HW & SW) | Air conditioning and ventilation (HW & SW) | 0
3.13.3 | Energetika (inštalacije) | Energy (installations) | 0
3.13.4 | Energetika (HW & SW) | Energy (HW & SW) | 0
3.13.5 | Sistem upravljanja stavb (inštalacije) | Building management system (installations) | 0
3.13.6 | Sistem upravljanja stavb (HW & SW) | Building Management System (HW & SW) | 0
3.13.7 | OSTALO | OTHER | 0
0
0 | NEPREDVIDENA DELA | UNFORSEEN WORKS | 0
| SKUPAJ ELEKTRO DELA | TOTAL ELECTRICAL WORKS | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT

## 3.13.1_HVAC_INŠ
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.13 | ELEKTRO DELA | ELECTRICAL WORKS
3.13.1 | Klimatizacija in prezračevanje (inštalacije) | Air conditioning and ventilation (installations) | [5 empty] | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description |  |  | EM | Količina | Cena/EM | Cena
1 | Klimatizacija in prezračevanje (inštalacije) | Air conditioning and ventilation (installations)
1.1 | Dobava in montaža kovinske omare +HVAC_K1-R1 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +HVAC_K1-R1 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1000 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1000 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2010402DP. | such as Schneider, type: NSYSFN2010402DP. | kos | 1
| - Podstavek 200 mm, širine 1000 mm, | - Base 200 mm, width 1000 mm,
| kot naprimer Schneider, tip: NSYSPF10200. | such as Schneider, type: NSYSPF10200. | kos | 2
| - stranica podstavka 200 mm, globine 400 mm, | - base side 200 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4200. | such as Schneider, type: NSYSPS4200. | kos | 2
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1000 mm, | - Lower crossbar with PanelSeT cable entry - 1000 mm,
| kot naprimer Rittal, tip: 2388.050. | such as Rittal, type: 2388.050. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Rittal, tip: 2388.100. | such as Rittal, type: 2388.100. | kos | 15
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Rittal, tip: 7077.000. | such as Rittal, type: 7077.000. | kos | 12
| V močnostno omaro +HVAC_K1-R1 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +HVAC_K1-R1 power cabinet:
| - glavno stikalo In=100 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=100 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C113100LS. | such as Schneider, type: C113100LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, | - Led cabinet light, 11W, 230V, without socket, on/off, 4000K,
| kot naprimer Rittal, tip: 2500.200. | such as Rittal, type: 2500.200. | kos | 1
| - Priključni kabel za LED svetilko OR 3000mm, | - Connecting cable for LED luminaire OR 3000mm,
| kot naprimer Rittal, tip: 2500.400. | such as Rittal, type: 2500.400. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Motorski odklopnik 3P, 4 - 6,3 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 4 - 6.3 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P10 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P10 + GVAN11. | kos | 1
| - Motorski odklopnik 3P, 2,5 - 4 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 2,5 - 4 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P08 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P08 + GVAN11. | kos | 3
| - Motorski odklopnik 3P, 0,4 - 0,63 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 0,4 - 0,63 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P04 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P04 + GVAN11. | kos | 4
| - Štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 20 kA, | - 40 A, four-pole circuit breaker with C characteristic, 20 kA,
| kot naprimer Schneider, Acti 9 iC60L, tip: A9F84440. | such as Schneider, Acti 9 iC60L, type: A9F84440. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Pomožni kontakt 1 C/O za enopolni inštalacijski odklopnik, | - Auxiliary contact 1 C/O for single-pole circuit breaker,
| kot naprimer Schneider, Acti9 A9A iOF, tip: A9A26904. | such as Schneider, Acti9 A9A iOF, type: A9A26904. | kos | 1
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 1
| - Kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 6 A s C karakteristiko, 30mA, tip A in pomožni kontakt 2 C/O, | - Combination protection switch with overcurrent protection (KZS), 1P+N, 6 A with C characteristic, 30mA, type A and auxiliary contact 2 C/O,
| kot naprimer Schneider, Acti 9 iDPN H, tip: A9D37606, pomožni kontakt tip: A9A26919. | such as Schneider, Acti 9 iDPN H, type: A9D37606, auxiliary contact type: A9A26919. | kos | 2
| - Kontaktor, 3P (3NO), 6 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, | - Contactor, 3P (3NO), 6 A, coil 230 V AC, 50 Hz and auxiliary contact block 1 NO + 1 NC,
| kot naprimer Schneider tip: TeSys LC-1, LC1K06013P7 + LA1KN113. | such as for example Schneider tip: TeSys LC-1, LC1K06013P7 + LA1KN113. | kos | 4
| Na tuljavah kontaktorjev bodo priključeni supresorji za dušenje prenapetostnih špic, ki nastanejo pri izklopu kontaktorja. V kolikor niso ti supresorji že v samem kontaktorju, bodo kontaktorji opremljeni z RC členi oz. varistorji pri izmeničnih krmilnih napetostih, oz. z diodami pri enosmernih krmilnih napetostih. | Suppressors will be connected to the contactor coils to suppress overvoltage spikes that occur when the contactor is switched off. If these suppressors are not already in the contactor itself, the contactors will be equipped with RC links or varistors for AC control voltages, or diodes for DC control voltages.
| - Kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 3P+N, 6 A s C karakteristiko, 30 mA, tip A in pomožni kontakt 2 C/O, | - Combination protection switch with overcurrent protection (KZS), 3P+N, 6 A with C characteristic, 30 mA, type A and auxiliary contact 2 C/O,
| kot naprimer ETI tip: 002174421 + in 002159500. | such as the ETI type: 002174421 + and 002159500. | kos | 2
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 1
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 4
| - Sponke 35 mm2 za montažo na DIN letev, | - 35 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 35 | such as Phoenix Contact type: UT 35 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 97
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 8
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 15
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
1.2 | Dobava in montaža kovinske omare +HVAC_K1-PLC1 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of metal cabinet +HVAC_K1-PLC1 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1000 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1000 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2010402DP. | such as Schneider, type: NSYSFN2010402DP. | kos | 1
| - Podstavek 200 mm, širine 1000 mm, | - Base 200 mm, width 1000 mm,
| kot naprimer Schneider, tip: NSYSPF10200. | such as Schneider, type: NSYSPF10200. | kos | 2
| - stranica podstavka 200 mm, globine 400 mm, | - base side 200 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4200. | such as Schneider, type: NSYSPS4200. | kos | 2
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1000 mm, | - Lower crossbar with PanelSeT cable entry - 1000 mm,
| kot naprimer Rittal, tip: 2388.050. | such as Rittal, type: 2388.050. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Rittal, tip: 2388.100. | such as Rittal, type: 2388.100. | kos | 17
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Rittal, tip: 7077.000. | such as Rittal, type: 7077.000. | kos | 14
| V krmilno omaro +HVAC_K1-PLC1 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +HVAC_K1-PLC1 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, | - Led cabinet light, 11W, 230V, without socket, on/off, 4000K,
| kot naprimer Rittal, tip: 2500.200. | such as Rittal, type: 2500.200. |  | 1
| - Priključni kabel za LED svetilko OR 3000mm, | - Connecting cable for LED luminaire OR 3000mm,
| kot naprimer Rittal, tip: 2500.400. | such as Rittal, type: 2500.400. | kos | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Rittal, tip: SK 3240.200. | such as Rittal, type: SK 3240.200. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Rittal, tip: SK 3240.100 + SK 3240.200. | such as Rittal, type: SK 3240.100 + SK 3240.200. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omaro. | - 2x RJ45 socket (communication socket) and associated enclosure for installation in a cabinet. | kos | 1
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 2
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Vgradna zelena kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed green LED signal light, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB3 + ZBZ32. | like for example Schneider tip: XB4BVB3 + ZBZ32. | kos | 1
| - Vgradna rdeča kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed red LED signal light, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB4 + ZBZ32. | like for example Schneider tip: XB4BVB4 + ZBZ32. | kos | 2
| - Vgradna modre tipke z delovnim kontaktom in nosilcem tipkala, | - Built-in blue keys with working contact and key holder,
| kot naprimer Schneider tip: XB4BA61 + ZBZ32. | like for example Schneider tip: XB4BA61 + ZBZ32. | kos | 3
| - Enotni blok za funkcijo testne luči 24 V AC DC, | - Single block for 24 V AC DC test light function,
| kot naprimer Schneider tip: ZBZG156. | such as Schneider type: ZBZG156. | kos | 3
| - Vgradna tipka za izklop v sili z gobo, 2x NC, za vgradnjo na vrata omare, komplet s ploščico, | - Emergency stop push-button with sponge, 2x NC, for mounting on cabinet doors, complete with plate,
| kot naprimer Schneider tip: XB5AT842 + ZBE102+ZBY9360. | like for example Schneider tip: XB5AT842+ZBE102+ZBY9360. | kos | 1
| - Varnostni rele za izklop v sili, izhodi 3 NO in 1 NC, napajanje 24 VDC, povezovalni modul | - Emergency stop safety relay, 3 NO and 1 NC outputs, 24 VDC power supply, connection module
| kot naprimer Siemens tip: 3SK1121-1AB40 + 3ZY1212-2DA00. | as for example Siemens type: 3SK1121-1AB40 + 3ZY1212-2DA00. | kos | 1
| - Razšeritveni varnostni rele za izklop v sili, izhodi 4 NO in 1 NC, napajanje 24 VDC, povezovalni modul (podnožje) | - Emergency trip safety relay, 4 NO and 1 NC outputs, 24 VDC power supply, connection module (base)
| kot naprimer Siemens tip: 3SK1211-1BB40 + 3ZY1212-2BA00. | such as for example Siemens type: 3SK1211-1BB40 + 3ZY1212-2BA00. | kos | 1
| - Varnostni rele z, izhodi 3 NO in 3 NC, napajanje 24 VDC, | - Safety relay with, 3 NO and 3 NC outputs, 24 VDC power supply,
| kot naprimer Phoenix Contact tip: 24UC/URM/3X1/3X2, 2981842. | as for example Phoenix Contact type: 24UC/URM/3X1/3X2, 2981842. | kos | 2
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 26
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 1
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Varnostni ločilni transformator 315 VAC/24 VAC, | - Safety isolating transformer 315 VAC/24 VAC,
| kot na primer Siemens tip: 4AM4342-4TN00-0EA0 | such as Siemens type: 4AM4342-4TN00-0EA0 | kos | 1
| - Sponke 4 mm2 za montažo na DIN letev, | - 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 4 | such as Phoenix Contact type: UT 4 | kos | 1
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 267
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 33
| - Sponke varovalčna (5x20), | - Buckle guard (5x20),
| kot na primer Phoenix Contact tip: PTC 4 - HESILED 24 | such as Phoenix Contact type: PTC 4 - HESILED 24 | kos | 51
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
1.3 | Dobava in montaža kovinske omare +HVAC_K1-R2 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +HVAC_K1-R2 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1000 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1000 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2010402DP. | such as Schneider, type: NSYSFN2010402DP. | kos | 1
| - Podstavek 200 mm, širine 1000 mm, | - Base 200 mm, width 1000 mm,
| kot naprimer Schneider, tip: NSYSPF10200. | such as Schneider, type: NSYSPF10200. | kos | 2
| - stranica podstavka 200 mm, globine 400 mm, | - base side 200 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4200. | such as Schneider, type: NSYSPS4200. | kos | 2
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1000 mm, | - Lower crossbar with PanelSeT cable entry - 1000 mm,
| kot naprimer Rittal, tip: 2388.050. | such as Rittal, type: 2388.050. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Rittal, tip: 2388.100. | such as Rittal, type: 2388.100. | kos | 15
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Rittal, tip: 7077.000. | such as Rittal, type: 7077.000. | kos | 12
| V močnostno omaro +HVAC_K1-R2 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +HVAC_K1-R2 power cabinet:
| - glavno stikalo In=50 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=50 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C113050LS. | such as Schneider, type: C113050LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, | - Led cabinet light, 11W, 230V, without socket, on/off, 4000K,
| kot naprimer Rittal, tip: 2500.200. | such as Rittal, type: 2500.200. | kos | 1
| - Priključni kabel za LED svetilko OR 3000mm, | - Connecting cable for LED luminaire OR 3000mm,
| kot naprimer Rittal, tip: 2500.400. | such as Rittal, type: 2500.400. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Motorski odklopnik 3P, 6 - 10 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 6 - 10 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P14 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P14 + GVAN11. | kos | 2
| - Motorski odklopnik 3P, 4 - 6,3 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 4 - 6.3 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P10 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P10 + GVAN11. | kos | 6
| - Motorski odklopnik 3P, 2,5 - 4 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 2,5 - 4 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P08 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P08 + GVAN11. | kos | 4
| - Motorski odklopnik 3P, 0,4 - 0,63 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 0,4 - 0,63 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P04 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P04 + GVAN11. | kos | 4
| - Štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 20 kA, | - 40 A, four-pole circuit breaker with C characteristic, 20 kA,
| kot naprimer Schneider, Acti 9 iC60L, tip: A9F84440. | such as Schneider, Acti 9 iC60L, type: A9F84440. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Pomožni kontakt 1 C/O za enopolni inštalacijski odklopnik, | - Auxiliary contact 1 C/O for single-pole circuit breaker,
| kot naprimer Schneider, Acti9 A9A iOF, tip: A9A26904. | such as Schneider, Acti9 A9A iOF, type: A9A26904. | kos | 1
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 1
| - Kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 6 A s C karakteristiko, 30mA, tip A in pomožni kontakt 2 C/O, | - Combination protection switch with overcurrent protection (KZS), 1P+N, 6 A with C characteristic, 30mA, type A and auxiliary contact 2 C/O,
| kot naprimer Schneider, Acti 9 iDPN H, tip: A9D37606, pomožni kontakt tip: A9A26919. | such as Schneider, Acti 9 iDPN H, type: A9D37606, auxiliary contact type: A9A26919. | kos | 2
| - Kontaktor, 3P (3NO), 6 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, | - Contactor, 3P (3NO), 6 A, coil 230 V AC, 50 Hz and auxiliary contact block 1 NO + 1 NC,
| kot naprimer Schneider tip: TeSys LC-1, LC1K06013P7 + LA1KN113. | such as for example Schneider tip: TeSys LC-1, LC1K06013P7 + LA1KN113. | kos | 4
| - Kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 3P+N, 6 A s C karakteristiko, 30 mA, tip A in pomožni kontakt 2 C/O, | - Combination protection switch with overcurrent protection (KZS), 3P+N, 6 A with C characteristic, 30 mA, type A and auxiliary contact 2 C/O,
| kot naprimer ETI tip: 002174421 + in 002159500. | such as the ETI type: 002174421 + and 002159500. | kos | 2
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 1
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 4
| - Sponke 16 mm2 za montažo na DIN letev, | - 16 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 16 | such as Phoenix Contact type: UT 16 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 110
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 8
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 15
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
1.4 | Dobava in montaža kovinske omare +HVAC_K1-PLC2 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of metal cabinet +HVAC_K1-PLC2 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1000 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1000 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2010402DP. | such as Schneider, type: NSYSFN2010402DP. | kos | 1
| - Podstavek 200 mm, širine 1000 mm, | - Base 200 mm, width 1000 mm,
| kot naprimer Schneider, tip: NSYSPF10200. | such as Schneider, type: NSYSPF10200. | kos | 2
| - stranica podstavka 200 mm, globine 400 mm, | - base side 200 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4200. | such as Schneider, type: NSYSPS4200. | kos | 2
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1000 mm, | - Lower crossbar with PanelSeT cable entry - 1000 mm,
| kot naprimer Rittal, tip: 2388.050. | such as Rittal, type: 2388.050. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Rittal, tip: 2388.100. | such as Rittal, type: 2388.100. | kos | 12
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Rittal, tip: 7077.000. | such as Rittal, type: 7077.000. | kos | 13
| V krmilno omaro +HVAC_K1-PLC2 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +HVAC_K1-PLC2 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, | - Led cabinet light, 11W, 230V, without socket, on/off, 4000K,
| kot naprimer Rittal, tip: 2500.200. | such as Rittal, type: 2500.200. |  | 1
| - Priključni kabel za LED svetilko OR 3000mm, | - Connecting cable for LED luminaire OR 3000mm,
| kot naprimer Rittal, tip: 2500.400. | such as Rittal, type: 2500.400. | kos | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Rittal, tip: SK 3240.200. | such as Rittal, type: SK 3240.200. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Rittal, tip: SK 3240.100 + SK 3240.200. | as for example Rittal, type: SK 3240.100 + SK 3240.200. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omaro. | - 2x RJ45 socket (communication socket) and associated enclosure for installation in a cabinet. | kos | 1
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 2
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Vgradna zelena kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed green LED signal light, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB3 + ZBZ32. | like for example Schneider tip: XB4BVB3 + ZBZ32. | kos | 1
| - Vgradna rdeča kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed red LED signal light, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB4 + ZBZ32. | like for example Schneider tip: XB4BVB4 + ZBZ32. | kos | 2
| - Vgradna modre tipke z delovnim kontaktom in nosilcem tipkala, | - Built-in blue keys with working contact and key holder,
| kot naprimer Schneider tip: XB4BA61 + ZBZ32. | like for example Schneider tip: XB4BA61 + ZBZ32. | kos | 3
| - Enotni blok za funkcijo testne luči 24 V AC DC, | - Single block for 24 V AC DC test light function,
| kot naprimer Schneider tip: ZBZG156. | such as Schneider type: ZBZG156. | kos | 3
| - Vgradna tipka za izklop v sili z gobo, 2x NC, za vgradnjo na vrata omare, komplet s ploščico, | - Emergency stop push-button with sponge, 2x NC, for mounting on cabinet doors, complete with plate,
| kot naprimer Schneider tip: XB5AT842 + ZBE102+ZBY9360. | like for example Schneider tip: XB5AT842+ZBE102+ZBY9360. | kos | 1
| - Varnostni rele za izklop v sili, izhodi 3 NO in 1 NC, napajanje 24 VDC, povezovalni modul | - Emergency stop safety relay, 3 NO and 1 NC outputs, 24 VDC power supply, connection module
| kot naprimer Siemens tip: 3SK1121-1AB40 + 3ZY1212-2DA00. | as for example Siemens type: 3SK1121-1AB40 + 3ZY1212-2DA00. | kos | 1
| - Razšeritveni varnostni rele za izklop v sili, izhodi 4 NO in 1 NC, napajanje 24 VDC, povezovalni modul (podnožje) | - Emergency trip safety relay, 4 NO and 1 NC outputs, 24 VDC power supply, connection module (base)
| kot naprimer Siemens tip: 3SK1211-1BB40 + 3ZY1212-2BA00. | such as for example Siemens type: 3SK1211-1BB40 + 3ZY1212-2BA00. | kos | 1
| - Varnostni rele z, izhodi 3 NO in 3 NC, napajanje 24 VDC, | - Safety relay with, 3 NO and 3 NC outputs, 24 VDC power supply,
| kot naprimer Phoenix Contact tip: 24UC/URM/3X1/3X2, 2981842. | as for example Phoenix Contact type: 24UC/URM/3X1/3X2, 2981842. | kos | 2
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 22
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 1
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Varnostni ločilni transformator 315 VAC/24 VAC, | - Safety isolating transformer 315 VAC/24 VAC,
| kot na primer Siemens tip: 4AM4342-4TN00-0EA0 | such as Siemens type: 4AM4342-4TN00-0EA0 | kos | 1
| - Sponke 4 mm2 za montažo na DIN letev, | - 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 4 | such as Phoenix Contact type: UT 4 | kos | 1
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 302
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 39
| - Sponke varovalčna (5x20), | - Buckle guard (5x20),
| kot na primer Phoenix Contact tip: PTC 4 - HESILED 24 | such as Phoenix Contact type: PTC 4 - HESILED 24 | kos | 54
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
1.5 | Dobava in montaža kovinske omare +HVAC_K1-R3 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +HVAC_K1-R3 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1000 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1000 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2010402DP. | such as Schneider, type: NSYSFN2010402DP. | kos | 1
| - Podstavek 200 mm, širine 1000 mm, | - Base 200 mm, width 1000 mm,
| kot naprimer Schneider, tip: NSYSPF10200. | such as Schneider, type: NSYSPF10200. | kos | 2
| - stranica podstavka 200 mm, globine 400 mm, | - base side 200 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4200. | such as Schneider, type: NSYSPS4200. | kos | 2
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1000 mm, | - Lower crossbar with PanelSeT cable entry - 1000 mm,
| kot naprimer Rittal, tip: 2388.050. | such as Rittal, type: 2388.050. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Rittal, tip: 2388.100. | such as Rittal, type: 2388.100. | kos | 15
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Rittal, tip: 7077.000. | such as Rittal, type: 7077.000. | kos | 13
| V močnostno omaro +HVAC_K1-R3 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +HVAC_K1-R3 power cabinet:
| - glavno stikalo In=100 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=100 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C113100LS. | such as Schneider, type: C113100LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, | - Led cabinet light, 11W, 230V, without socket, on/off, 4000K,
| kot naprimer Rittal, tip: 2500.200. | such as Rittal, type: 2500.200. | kos | 1
| - Priključni kabel za LED svetilko OR 3000mm, | - Connecting cable for LED luminaire OR 3000mm,
| kot naprimer Rittal, tip: 2500.400. | such as Rittal, type: 2500.400. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Motorski odklopnik 3P, 9 - 14 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 9 - 14 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P16 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P16 + GVAN11. | kos | 2
| - Motorski odklopnik 3P, 6 - 10 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 6 - 10 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P14 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P14 + GVAN11. | kos | 2
| - Motorski odklopnik 3P, 4 - 6,3 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 4 - 6.3 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P10 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P10 + GVAN11. | kos | 1
| - Motorski odklopnik 3P, 2,5 - 4 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 2.5 - 4 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P08 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P08 + GVAN11. | kos | 1
| - Motorski odklopnik 3P, 0,4 - 0,63 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 0,4 - 0,63 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P04 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P04 + GVAN11. | kos | 4
| - Štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 20 kA, | - 40 A, four-pole circuit breaker with C characteristic, 20 kA,
| kot naprimer Schneider, Acti 9 iC60L, tip: A9F84440. | such as Schneider, Acti 9 iC60L, type: A9F84440. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Pomožni kontakt 1 C/O za enopolni inštalacijski odklopnik, | - Auxiliary contact 1 C/O for single-pole circuit breaker,
| kot naprimer Schneider, Acti9 A9A iOF, tip: A9A26904. | such as Schneider, Acti9 A9A iOF, type: A9A26904. | kos | 1
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 1
| - Kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 6 A s C karakteristiko, 30mA, tip A in pomožni kontakt 2 C/O, | - Combination protection switch with overcurrent protection (KZS), 1P+N, 6 A with C characteristic, 30mA, type A and auxiliary contact 2 C/O,
| kot naprimer Schneider, Acti 9 iDPN H, tip: A9D37606, pomožni kontakt tip: A9A26919. | such as Schneider, Acti 9 iDPN H, type: A9D37606, auxiliary contact type: A9A26919. | kos | 2
| - Kontaktor, 3P (3NO), 6 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, | - Contactor, 3P (3NO), 6 A, coil 230 V AC, 50 Hz and auxiliary contact block 1 NO + 1 NC,
| kot naprimer Schneider tip: TeSys LC-1, LC1K06013P7 + LA1KN113. | such as for example Schneider tip: TeSys LC-1, LC1K06013P7 + LA1KN113. | kos | 4
| - Kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 3P+N, 6 A s C karakteristiko, 30 mA, tip A in pomožni kontakt 2 C/O, | - Combination protection switch with overcurrent protection (KZS), 3P+N, 6 A with C characteristic, 30 mA, type A and auxiliary contact 2 C/O,
| kot naprimer ETI tip: 002174421 + in 002159500. | such as the ETI type: 002174421 + and 002159500. | kos | 3
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 1
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 4
| - Sponke 35 mm2 za montažo na DIN letev, | - 35 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 35 | such as Phoenix Contact type: UT 35 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 115
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 9
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 16
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
1.6 | Dobava in montaža kovinske omare +HVAC_K1-PLC3 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of metal cabinet +HVAC_K1-PLC3 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1000 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1000 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2010402DP. | such as Schneider, type: NSYSFN2010402DP. | kos | 1
| - Podstavek 200 mm, širine 1000 mm, | - Base 200 mm, width 1000 mm,
| kot naprimer Schneider, tip: NSYSPF10200. | such as Schneider, type: NSYSPF10200. | kos | 2
| - stranica podstavka 200 mm, globine 400 mm, | - base side 200 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4200. | such as Schneider, type: NSYSPS4200. | kos | 2
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1000 mm, | - Lower crossbar with PanelSeT cable entry - 1000 mm,
| kot naprimer Rittal, tip: 2388.050. | such as Rittal, type: 2388.050. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Rittal, tip: 2388.100. | such as Rittal, type: 2388.100. | kos | 17
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Rittal, tip: 7077.000. | such as Rittal, type: 7077.000. | kos | 14
| V krmilno omaro +HVAC_K1-PLC3 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +HVAC_K1-PLC3 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, | - Led cabinet light, 11W, 230V, without socket, on/off, 4000K,
| kot naprimer Rittal, tip: 2500.200. | such as Rittal, type: 2500.200. |  | 1
| - Priključni kabel za LED svetilko OR 3000mm, | - Connecting cable for LED luminaire OR 3000mm,
| kot naprimer Rittal, tip: 2500.400. | such as Rittal, type: 2500.400. | kos | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Rittal, tip: SK 3240.200. | such as Rittal, type: SK 3240.200. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Rittal, tip: SK 3240.100 + SK 3240.200. | such as Rittal, type: SK 3240.100 + SK 3240.200. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omaro. | - 2x RJ45 socket (communication socket) and associated enclosure for installation in a cabinet. | kos | 1
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 2
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Vgradna zelena kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed green LED signal lamp, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB3 + ZBZ32. | like for example Schneider tip: XB4BVB3 + ZBZ32. | kos | 1
| - Vgradna rdeča kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed red LED signal light, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB4 + ZBZ32. | like for example Schneider tip: XB4BVB4 + ZBZ32. | kos | 2
| - Vgradna modre tipke z delovnim kontaktom in nosilcem tipkala, | - Built-in blue keys with working contact and key holder,
| kot naprimer Schneider tip: XB4BA61 + ZBZ32. | like for example Schneider tip: XB4BA61 + ZBZ32. | kos | 3
| - Enotni blok za funkcijo testne luči 24 V AC DC, | - Single block for 24 V AC DC test light function,
| kot naprimer Schneider tip: ZBZG156. | such as Schneider type: ZBZG156. | kos | 3
| - Vgradna tipka za izklop v sili z gobo, 2x NC, za vgradnjo na vrata omare, komplet s ploščico, | - Emergency stop push-button with sponge, 2x NC, for mounting on cabinet doors, complete with plate,
| kot naprimer Schneider tip: XB5AT842 + ZBE102+ZBY9360. | like for example Schneider tip: XB5AT842+ZBE102+ZBY9360. | kos | 1
| - Varnostni rele za izklop v sili, izhodi 3 NO in 1 NC, napajanje 24 VDC, povezovalni modul | - Emergency stop safety relay, 3 NO and 1 NC outputs, 24 VDC power supply, connection module
| kot naprimer Siemens tip: 3SK1121-1AB40 + 3ZY1212-2DA00. | as for example Siemens type: 3SK1121-1AB40 + 3ZY1212-2DA00. | kos | 1
| - Razšeritveni varnostni rele za izklop v sili, izhodi 4 NO in 1 NC, napajanje 24 VDC, povezovalni modul (podnožje) | - Emergency trip safety relay, 4 NO and 1 NC outputs, 24 VDC power supply, connection module (base)
| kot naprimer Siemens tip: 3SK1211-1BB40 + 3ZY1212-2BA00. | such as for example Siemens type: 3SK1211-1BB40 + 3ZY1212-2BA00. | kos | 1
| - Varnostni rele z, izhodi 3 NO in 3 NC, napajanje 24 VDC, | - Safety relay with, 3 NO and 3 NC outputs, 24 VDC power supply,
| kot naprimer Phoenix Contact tip: 24UC/URM/3X1/3X2, 2981842. | as for example Phoenix Contact type: 24UC/URM/3X1/3X2, 2981842. | kos | 2
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 22
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 1
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Varnostni ločilni transformator 315 VAC/24 VAC, | - Safety isolating transformer 315 VAC/24 VAC,
| kot na primer Siemens tip: 4AM4342-4TN00-0EA0 | such as Siemens type: 4AM4342-4TN00-0EA0 | kos | 1
| - Sponke 4 mm2 za montažo na DIN letev, | - 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 4 | such as Phoenix Contact type: UT 4 | kos | 1
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 294
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 35
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| - Sponke varovalčna (5x20), | - Buckle guard (5x20),
| kot na primer Phoenix Contact tip: PTC 4 - HESILED 24 | such as Phoenix Contact type: PTC 4 - HESILED 24 | kos | 50
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
1.7 | Dobava in montaža kovinske omare +HVAC_K1-R4 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +HVAC_K1-R4 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1000 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1000 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2010402DP. | such as Schneider, type: NSYSFN2010402DP. | kos | 1
| - Podstavek 200 mm, širine 1000 mm, | - Base 200 mm, width 1000 mm,
| kot naprimer Schneider, tip: NSYSPF10200. | such as Schneider, type: NSYSPF10200. | kos | 2
| - stranica podstavka 200 mm, globine 400 mm, | - base side 200 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4200. | such as Schneider, type: NSYSPS4200. | kos | 2
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1000 mm, | - Lower crossbar with PanelSeT cable entry - 1000 mm,
| kot naprimer Rittal, tip: 2388.050. | such as Rittal, type: 2388.050. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Rittal, tip: 2388.100. | such as Rittal, type: 2388.100. | kos | 15
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Rittal, tip: 7077.000. | such as Rittal, type: 7077.000. | kos | 12
| V močnostno omaro +HVAC_K1-R4 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +HVAC_K1-R4 power cabinet:
| - glavno stikalo In=50 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=50 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C113050LS. | such as Schneider, type: C113050LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, | - Led cabinet light, 11W, 230V, without socket, on/off, 4000K,
| kot naprimer Rittal, tip: 2500.200. | such as Rittal, type: 2500.200. | kos | 1
| - Priključni kabel za LED svetilko OR 3000mm, | - Connecting cable for LED luminaire OR 3000mm,
| kot naprimer Rittal, tip: 2500.400. | such as Rittal, type: 2500.400. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Motorski odklopnik 3P, 4 - 6,3 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 4 - 6.3 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P10 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P10 + GVAN11. | kos | 4
| - Motorski odklopnik 3P, 0,4 - 0,63 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 0,4 - 0,63 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P04 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P04 + GVAN11. | kos | 4
| - Štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 20 kA, | - 40 A, four-pole circuit breaker with C characteristic, 20 kA,
| kot naprimer Schneider, Acti 9 iC60L, tip: A9F84440. | such as Schneider, Acti 9 iC60L, type: A9F84440. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Pomožni kontakt 1 C/O za enopolni inštalacijski odklopnik, | - Auxiliary contact 1 C/O for single-pole circuit breaker,
| kot naprimer Schneider, Acti9 A9A iOF, tip: A9A26904. | such as Schneider, Acti9 A9A iOF, type: A9A26904. | kos | 1
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 1
| - Kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 6 A s C karakteristiko, 30mA, tip A in pomožni kontakt 2 C/O, | - Combination protection switch with overcurrent protection (KZS), 1P+N, 6 A with C characteristic, 30mA, type A and auxiliary contact 2 C/O,
| kot naprimer Schneider, Acti 9 iDPN H, tip: A9D37606, pomožni kontakt tip: A9A26919. | such as Schneider, Acti 9 iDPN H, type: A9D37606, auxiliary contact type: A9A26919. | kos | 2
| - Kontaktor, 3P (3NO), 6 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, | - Contactor, 3P (3NO), 6 A, coil 230 V AC, 50 Hz and auxiliary contact block 1 NO + 1 NC,
| kot naprimer Schneider tip: TeSys LC-1, LC1K06013P7 + LA1KN113. | such as for example Schneider tip: TeSys LC-1, LC1K06013P7 + LA1KN113. | kos | 4
| - Kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 3P+N, 6 A s C karakteristiko, 30 mA, tip A in pomožni kontakt 2 C/O, | - Combination protection switch with overcurrent protection (KZS), 3P+N, 6 A with C characteristic, 30 mA, type A and auxiliary contact 2 C/O,
| kot naprimer ETI tip: 002174421 + in 002159500. | such as the ETI type: 002174421 + and 002159500. | kos | 1
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 1
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 4
| - Sponke 35 mm2 za montažo na DIN letev, | - 35 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 16 | such as Phoenix Contact type: UT 16 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 87
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 8
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 12
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
1.8 | Dobava in montaža kovinske omare +HVAC_K1-PLC4 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of metal cabinet +HVAC_K1-PLC4 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1000 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1000 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2010402DP. | such as Schneider, type: NSYSFN2010402DP. | kos | 1
| - Podstavek 200 mm, širine 1000 mm, | - Base 200 mm, width 1000 mm,
| kot naprimer Schneider, tip: NSYSPF10200. | such as Schneider, type: NSYSPF10200. | kos | 2
| - stranica podstavka 200 mm, globine 400 mm, | - base side 200 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4200. | such as Schneider, type: NSYSPS4200. | kos | 2
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1000 mm, | - Lower crossbar with PanelSeT cable entry - 1000 mm,
| kot naprimer Rittal, tip: 2388.050. | such as Rittal, type: 2388.050. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Rittal, tip: 2388.100. | such as Rittal, type: 2388.100. | kos | 17
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Rittal, tip: 7077.000. | such as Rittal, type: 7077.000. | kos | 14
| V krmilno omaro +HVAC_K1-PLC4 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +HVAC_K1-PLC4 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, | - Led cabinet light, 11W, 230V, without socket, on/off, 4000K,
| kot naprimer Rittal, tip: 2500.200. | such as Rittal, type: 2500.200. |  | 1
| - Priključni kabel za LED svetilko OR 3000mm, | - Connecting cable for LED luminaire OR 3000mm,
| kot naprimer Rittal, tip: 2500.400. | such as Rittal, type: 2500.400. | kos | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Rittal, tip: SK 3240.200. | such as Rittal, type: SK 3240.200. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Rittal, tip: SK 3240.100 + SK 3240.200. | as for example Rittal, type: SK 3240.100 + SK 3240.200. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omaro. | - 2x RJ45 socket (communication socket) and associated enclosure for installation in a cabinet. | kos | 1
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 2
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Vgradna zelena kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed green LED signal light, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB3 + ZBZ32. | like for example Schneider tip: XB4BVB3 + ZBZ32. | kos | 1
| - Vgradna rdeča kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed red LED signal light, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB4 + ZBZ32. | like for example Schneider tip: XB4BVB4 + ZBZ32. | kos | 2
| - Vgradna modre tipke z delovnim kontaktom in nosilcem tipkala, | - Built-in blue keys with working contact and key holder,
| kot naprimer Schneider tip: XB4BA61 + ZBZ32. | like for example Schneider tip: XB4BA61 + ZBZ32. | kos | 3
| - Enotni blok za funkcijo testne luči 24 V AC DC, | - Single block for 24 V AC DC test light function,
| kot naprimer Schneider tip: ZBZG156. | such as Schneider type: ZBZG156. | kos | 3
| - Vgradna tipka za izklop v sili z gobo, 2x NC, za vgradnjo na vrata omare, komplet s ploščico, | - Emergency stop push-button with sponge, 2x NC, for mounting on cabinet doors, complete with plate,
| kot naprimer Schneider tip: XB5AT842 + ZBE102+ZBY9360. | like for example Schneider tip: XB5AT842+ZBE102+ZBY9360. | kos | 1
| - Varnostni rele za izklop v sili, izhodi 3 NO in 1 NC, napajanje 24 VDC, povezovalni modul | - Emergency stop safety relay, 3 NO and 1 NC outputs, 24 VDC power supply, connection module
| kot naprimer Siemens tip: 3SK1121-1AB40 + 3ZY1212-2DA00. | as for example Siemens type: 3SK1121-1AB40 + 3ZY1212-2DA00. | kos | 1
| - Razšeritveni varnostni rele za izklop v sili, izhodi 4 NO in 1 NC, napajanje 24 VDC, povezovalni modul (podnožje) | - Emergency trip safety relay, 4 NO and 1 NC outputs, 24 VDC power supply, connection module (base)
| kot naprimer Siemens tip: 3SK1211-1BB40 + 3ZY1212-2BA00. | such as for example Siemens type: 3SK1211-1BB40 + 3ZY1212-2BA00. | kos | 1
| - Varnostni rele z, izhodi 3 NO in 3 NC, napajanje 24 VDC, | - Safety relay with, 3 NO and 3 NC outputs, 24 VDC power supply,
| kot naprimer Phoenix Contact tip: 24UC/URM/3X1/3X2, 2981842. | as for example Phoenix Contact type: 24UC/URM/3X1/3X2, 2981842. | kos | 2
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 22
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 1
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Varnostni ločilni transformator 315 VAC/24 VAC, | - Safety isolating transformer 315 VAC/24 VAC,
| kot na primer Siemens tip: 4AM4342-4TN00-0EA0 | such as Siemens type: 4AM4342-4TN00-0EA0 | kos | 1
| - Sponke 4 mm2 za montažo na DIN letev, | - 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 4 | such as Phoenix Contact type: UT 4 | kos | 1
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 294
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 35
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| - Sponke varovalčna (5x20), | - Buckle guard (5x20),
| kot na primer Phoenix Contact tip: PTC 4 - HESILED 24 | such as Phoenix Contact type: PTC 4 - HESILED 24 | kos | 50
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
1.9 | Dobava in montaža kovinske omare +HVAC_K1-R5 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +HVAC_K1-R5 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1000 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1000 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2010402DP. | such as Schneider, type: NSYSFN2010402DP. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1000 mm, | - Lower crossbar with PanelSeT cable entry - 1000 mm,
| kot naprimer Rittal, tip: 2388.050. | such as Rittal, type: 2388.050. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Rittal, tip: 2388.100. | such as Rittal, type: 2388.100. | kos | 15
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Rittal, tip: 7077.000. | such as Rittal, type: 7077.000. | kos | 12
| V močnostno omaro +HVAC_K1-R5 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +HVAC_K1-R5 power cabinet:
| - glavno stikalo In=160 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=160 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of installing a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C123160LS. | such as Schneider, type: C123160LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, | - Led cabinet light, 11W, 230V, without socket, on/off, 4000K,
| kot naprimer Rittal, tip: 2500.200. | such as Rittal, type: 2500.200. | kos | 1
| - Priključni kabel za LED svetilko OR 3000mm, | - Connecting cable for LED luminaire OR 3000mm,
| kot naprimer Rittal, tip: 2500.400. | such as Rittal, type: 2500.400. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Motorski odklopnik 3P, 0,25 - 0,4 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 0,25 - 0,4 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P03 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P03 + GVAN11. | kos | 2
| - Motorski odklopnik 3P, 1 - 1,6 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 1 - 1.6 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P06 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P06 + GVAN11. | kos | 1
| - Motorski odklopnik 3P, 1,6 - 2,5 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 1,6 - 2,5 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P07 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P07 + GVAN11. | kos | 1
| - Motorski odklopnik 3P, 2,5 - 4 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 2,5 - 4 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P08 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P08 + GVAN11. | kos | 1
| - Motorski odklopnik 3P, 4 - 6,3 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 4 - 6.3 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P10 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P10 + GVAN11. | kos | 1
| - Motorski odklopnik 3P, 6 - 10 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 6 - 10 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P14 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P14 + GVAN11. | kos | 11
| - Štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 20 kA, | - 40 A, four-pole circuit breaker with C characteristic, 20 kA,
| kot naprimer Schneider, Acti 9 iC60L, tip: A9F84440. | such as Schneider, Acti 9 iC60L, type: A9F84440. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 5
| - Tripolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84306. | such as Schneider, Acti 9 iC60H, type: A9F84306. | kos | 2
| - Tripolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84310. | such as Schneider, Acti 9 iC60H, type: A9F84310. | kos | 1
| - Tripolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Tripolar 16 A, C-rated, 15 kA installation circuit breaker,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84316. | such as Schneider, Acti 9 iC60H, type: A9F84316. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 4
| - Pomožni kontakt 1 C/O za enopolni inštalacijski odklopnik, | - Auxiliary contact 1 C/O for single-pole circuit breaker,
| kot naprimer Schneider, Acti9 A9A iOF, tip: A9A26904. | such as Schneider, Acti9 A9A iOF, type: A9A26904. | kos | 14
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 1
| - Kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 3P+N, 10 A s C karakteristiko, 30 mA, tip A in pomožni kontakt 2 C/O, | - Combination protection switch with overcurrent protection (KZS), 3P+N, 10 A with C characteristic, 30 mA, type A and auxiliary contact 2 C/O,
| kot naprimer ETI tip: 002174922 + in 002159500. | such as the ETI type: 002174922 + and 002159500. | kos | 1
| - Kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 10 A s C karakteristiko, 30mA, tip A in pomožni kontakt 2 C/O, | - Combination protection switch with overcurrent protection (KZS), 1P+N, 10 A with C characteristic, 30mA, type A and auxiliary contact 2 C/O,
| kot naprimer Schneider, Acti 9 iDPN H, tip: A9D37606, pomožni kontakt tip: A9A26919. | such as Schneider, Acti 9 iDPN H, type: A9D37606, auxiliary contact type: A9A26919. | kos | 1
| - Kontaktor, 3P (3NO), 6 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, | - Contactor, 3P (3NO), 6 A, coil 230 V AC, 50 Hz and auxiliary contact block 1 NO + 1 NC,
| kot naprimer Schneider tip: TeSys LC-1, LC1K06013P7 + LA1KN113. | such as for example Schneider tip: TeSys LC-1, LC1K06013P7 + LA1KN113. | kos | 1
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 1
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 2
| - Sponke 95 mm2 za montažo na DIN letev, | - 95 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UKH 70 | such as Phoenix Contact type: UKH 70 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 80
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 10
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 30
| - priključne sponke - ostale, | - connecting clips - other,
| kot na primer Phoenix Contact | such as Phoenix Contact | kos | 30
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
1.10 | Dobava in montaža kovinske omare +HVAC_K1-PLC5 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of metal cabinet +HVAC_K1-PLC5 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1600 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1600 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2016402DP. | such as Schneider, type: NSYSFN2016402DP. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1600 mm, | - Lower crossbar with PanelSeT cable entry - 1600 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider. | such as Schneider. | kos | 17
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider. | such as Schneider. | kos | 14
| V krmilno omaro +HVAC_K1-PLC5 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +HVAC_K1-PLC5 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, | - Led cabinet light, 11W, 230V, without socket, on/off, 4000K,
| kot naprimer Rittal, tip: 2500.200. | such as Rittal, type: 2500.200. |  | 1
| - Priključni kabel za LED svetilko OR 3000mm, | - Connecting cable for LED luminaire OR 3000mm,
| kot naprimer Rittal, tip: 2500.400. | such as Rittal, type: 2500.400. | kos | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Rittal, tip: SK 3240.200. | such as Rittal, type: SK 3240.200. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Rittal, tip: SK 3240.100 + SK 3240.200. | as for example Rittal, type: SK 3240.100 + SK 3240.200. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omaro. | - 2x RJ45 socket (communication socket) and associated enclosure for installation in a cabinet. | kos | 1
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 1
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Vgradna zelena kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed green LED signal light, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB3 + ZBZ32. | like for example Schneider tip: XB4BVB3 + ZBZ32. | kos | 1
| - Vgradna rdeča kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed red LED signal light, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB4 + ZBZ32. | like for example Schneider tip: XB4BVB4 + ZBZ32. | kos | 2
| - Vgradna modre tipke z delovnim kontaktom in nosilcem tipkala, | - Built-in blue keys with working contact and key holder,
| kot naprimer Schneider tip: XB4BA61 + ZBZ32. | like for example Schneider tip: XB4BA61 + ZBZ32. | kos | 2
| - Enotni blok za funkcijo testne luči 24 V AC DC, | - Single block for 24 V AC DC test light function,
| kot naprimer Schneider tip: ZBZG156. | such as Schneider type: ZBZG156. | kos | 3
| - Vgradna tipka za izklop v sili z gobo, 2x NC, za vgradnjo na vrata omare, komplet s ploščico, | - Emergency stop push-button with sponge, 2x NC, for mounting on cabinet doors, complete with plate,
| kot naprimer Schneider tip: XB5AT842 + ZBE102+ZBY9360. | like for example Schneider tip: XB5AT842+ZBE102+ZBY9360. | kos | 1
| - Varnostni rele za izklop v sili, izhodi 3 NO in 1 NC, napajanje 24 VDC, povezovalni modul | - Emergency stop safety relay, 3 NO and 1 NC outputs, 24 VDC power supply, connection module
| kot naprimer Siemens tip: 3SK1121-1AB40 + 3ZY1212-2DA00. | as for example Siemens type: 3SK1121-1AB40 + 3ZY1212-2DA00. | kos | 1
| - Razšeritveni varnostni rele za izklop v sili, izhodi 4 NO in 1 NC, napajanje 24 VDC, povezovalni modul (podnožje) | - Emergency trip safety relay, 4 NO and 1 NC outputs, 24 VDC power supply, connection module (base)
| kot naprimer Siemens tip: 3SK1211-1BB40 + 3ZY1212-2BA00. | such as for example Siemens type: 3SK1211-1BB40 + 3ZY1212-2BA00. | kos | 1
| - Varnostni rele z, izhodi 3 NO in 3 NC, napajanje 24 VDC, | - Safety relay with, 3 NO and 3 NC outputs, 24 VDC power supply,
| kot naprimer Phoenix Contact tip: 24UC/URM/3X1/3X2, 2981842. | as for example Phoenix Contact type: 24UC/URM/3X1/3X2, 2981842. | kos | 2
| - Rele-sponka, 24 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21. | such as Phoenix Contact type: PLC-RSC-24UC/21. | kos | 58
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 7
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 1
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Varnostni ločilni transformator 315 VAC/24 VAC, | - Safety isolating transformer 315 VAC/24 VAC,
| kot na primer Siemens tip: 4AM4342-4TN00-0EA0 | such as Siemens type: 4AM4342-4TN00-0EA0 | kos | 1
| - Sponke 4 mm2 za montažo na DIN letev, | - 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 4 | such as Phoenix Contact type: UT 4 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 180
| - Sponke 2,5 mm2, modre za montažo na DIN letev, | - DIN rail mounting clips 2,5 mm2, blue,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 40
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 - PE | such as Phoenix Contact type: PT 2,5 - PE | kos | 40
| - Sponke 2,5 mm2, dvojne, za montažo na DIN letev, | - Clips 2,5 mm2, double, for DIN rail mounting,
| kot na primer Phoenix Contact tip: UTTB 2,5-MT-P/P | such as Phoenix Contact type: UTTB 2,5-MT-P/P | kos | 185
| - Sponke varovalčna (5x20), 0,5 A vložek | - Fuse clips (5x20), 0.5 A insert
| kot na primer Phoenix Contact tip: PTC 4 - HESILED 24 | such as Phoenix Contact type: PTC 4 - HESILED 24 | kos | 105
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
1.11 | Dobava in montaža kovinske omare +HVAC_S1-R1 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +HVAC_S1-R1 consisting of one bay in IP 55 protection RAL 7035.
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN". |  |  | kpl | 1 |  | 0
| Dimenzije omare so: višina 2000 mm, širina 800 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima enokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 800 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height single-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20840P. | such as Schneider, type: NSYSFN20840P. | kos | 1
| - Podstavek 200 mm, širine 800 mm, | - Base 200 mm, width 800 mm,
| kot naprimer Schneider, tip: NSYSPF8200. | such as Schneider, type: NSYSPF8200. | kos | 2
| - stranica podstavka 200 mm, globine 400 mm, | - base side 200 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4200. | such as Schneider, type: NSYSPS4200. | kos | 2
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1000 mm, | - Lower crossbar with PanelSeT cable entry - 1000 mm,
| kot naprimer Rittal, tip: 2388.050. | such as Rittal, type: 2388.050. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Rittal, tip: 2388.100. | such as Rittal, type: 2388.100. | kos | 15
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Rittal, tip: 7077.000. | such as Rittal, type: 7077.000. | kos | 12
| V močnostno omaro +HVAC_S1-R1 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +HVAC_S1-R1 power cabinet:
| - glavno stikalo In=100 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=100 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C113100LS. | such as Schneider, type: C113100LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, | - Led cabinet light, 11W, 230V, without socket, on/off, 4000K,
| kot naprimer Rittal, tip: 2500.200. | such as Rittal, type: 2500.200. | kos | 1
| - Priključni kabel za LED svetilko OR 3000mm, | - Connecting cable for LED luminaire OR 3000mm,
| kot naprimer Rittal, tip: 2500.400. | such as Rittal, type: 2500.400. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - Prezračevalni filter, | - Ventilation filter,
| kot naprimer Rittal, tip: SK 3237.300. | such as Rittal, type: SK 3237.300. | kos | 2
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Motorski odklopnik 3P, 0,25 - 0,4 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 0,25 - 0,4 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P03 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P03 + GVAN11. | kos | 1
| - Motorski odklopnik 3P, 1 - 1,6 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 1 - 1.6 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P06 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P06 + GVAN11. | kos | 1
| - Motorski odklopnik 3P, 2,5 - 4 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 2,5 - 4 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P08 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P08 + GVAN11. | kos | 1
| - Motorski odklopnik 3P, 4 - 6,3 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 4 - 6.3 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P10 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P10 + GVAN11. | kos | 1
| - Motorski odklopnik 3P, 6 - 10 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 6 - 10 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P14 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P14 + GVAN11. | kos | 2
| - Motorski odklopnik 3P, 9 - 14 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 9 - 14 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P16 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P16 + GVAN11. | kos | 2
| - Štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 20 kA, | - 40 A, four-pole circuit breaker with C characteristic, 20 kA,
| kot naprimer Schneider, Acti 9 iC60L, tip: A9F84440. | such as Schneider, Acti 9 iC60L, type: A9F84440. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Pomožni kontakt 1 C/O za enopolni inštalacijski odklopnik, | - Auxiliary contact 1 C/O for single-pole circuit breaker,
| kot naprimer Schneider, Acti9 A9A iOF, tip: A9A26904. | such as Schneider, Acti9 A9A iOF, type: A9A26904. | kos | 1
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 2
| - Pomožni kontakt 1 C/O za enopolni inštalacijski odklopnik, | - Auxiliary contact 1 C/O for single-pole circuit breaker,
| kot naprimer Schneider, Acti9 A9A iOF, tip: A9A26909. | such as Schneider, Acti9 A9A iOF, type: A9A26909. | kos | 1
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 1
| - Kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 6 A s C karakteristiko, 30mA, tip A in pomožni kontakt 2 C/O, | - Combination protection switch with overcurrent protection (KZS), 1P+N, 6 A with C characteristic, 30mA, type A and auxiliary contact 2 C/O,
| kot naprimer Schneider, Acti 9 iDPN H, tip: A9D37606, pomožni kontakt tip: A9A26919. | such as Schneider, Acti 9 iDPN H, type: A9D37606, auxiliary contact type: A9A26919. | kos | 2
| - Kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip A in pomožni kontakt 2 C/O, | - Combination protection switch with overcurrent protection (KZS), 1P+N, 16 A with C characteristic, 30mA, type A and auxiliary contact 2 C/O,
| kot naprimer Schneider, Acti 9 iDPN H, tip: A9D37616, pomožni kontakt tip: A9A26919. | such as Schneider, Acti 9 iDPN H, type: A9D37616, auxiliary contact type: A9A26919. | kos | 3
| - Kontaktor, 3P (3NO), 6 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, | - Contactor, 3P (3NO), 6 A, coil 230 V AC, 50 Hz and auxiliary contact block 1 NO + 1 NC,
| kot naprimer Schneider tip: TeSys LC-1, LC1K06013P7 + LA1KN113. | such as for example Schneider tip: TeSys LC-1, LC1K06013P7 + LA1KN113. | kos | 5
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21. | such as Phoenix Contact type: PLC-RSC-230UC/21. | kos | 1
| - Rele-sponka, 24 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC- 24UC/21. | such as Phoenix Contact type: PLC-RSC- 24UC/21. | kos | 5
| - Sponke 50 mm2 za montažo na DIN letev, | - 50 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 35 | such as Phoenix Contact type: UT 35 | kos | 3
| - Sponke 2,5 mm2 vzmetne priklop motorjev za montažo na DIN letev, | - 2.5 mm2 spring clips for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5-PE/3L | such as Phoenix Contact type: PT 2,5-PE/3L | kos | 7
| - Sponke 2,5 mm2 vmznetna za montažo na DIN letev, | - 2.5 mm2 clips for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 | such as Phoenix Contact type: PT 2,5 | kos | 8
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 BU | such as Phoenix Contact type: PT 2,5 BU | kos | 8
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 8
| - Sponke 1,5 mm2 vmznetna večnivojska za montažo na DIN letev, | - 1,5 mm2 clips in multilevel for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 1,5/S-3L | such as Phoenix Contact type: PT 1,5/S-3L | kos | 24
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
1.12 | Dobava in montaža kovinske omare +HVAC_S1-PLC1 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of metal cabinet +HVAC_S1-PLC1 consisting of one bay in IP 55 protection RAL 7035.
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN". |  |  | kpl | 1 |  | 0
| Dimenzije omare so: višina 2000 mm, širina 1000 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1000 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2010402DP. | such as Schneider, type: NSYSFN2010402DP. | kos | 1
| - Podstavek 200 mm, širine 1000 mm, | - Base 200 mm, width 1000 mm,
| kot naprimer Schneider, tip: NSYSPF10200. | such as Schneider, type: NSYSPF10200. | kos | 2
| - stranica podstavka 200 mm, globine 400 mm, | - base side 200 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4200. | such as Schneider, type: NSYSPS4200. | kos | 2
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1000 mm, | - Lower crossbar with PanelSeT cable entry - 1000 mm,
| kot naprimer Rittal, tip: 2388.050. | such as Rittal, type: 2388.050. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Rittal, tip: 2388.100. | such as Rittal, type: 2388.100. | kos | 90
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Rittal, tip: 7077.000. | such as Rittal, type: 7077.000. | kos | 20
| V krmilno omaro +HVAC_S1-PLC1 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +HVAC_S1-PLC1 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, | - Led cabinet light, 11W, 230V, without socket, on/off, 4000K,
| kot naprimer Rittal, tip: 2500.200. | such as Rittal, type: 2500.200. |  | 1
| - Priključni kabel za LED svetilko OR 3000mm, | - Connecting cable for LED luminaire OR 3000mm,
| kot naprimer Rittal, tip: 2500.400. | such as Rittal, type: 2500.400. | kos | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Rittal, tip: SK 3110.000. | such as Rittal, type: SK 3110.000. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Rittal, tip: SK 3240.100 + SK 3240.200. | as for example Rittal, type: SK 3240.100 + SK 3240.200. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica), | - Socket 2x RJ45 (communication socket),
| kot na primer Weidmuller tip: IE-XM-RJ45/RJ45 | such as Weidmuller type: IE-XM-RJ45/RJ45 | kos | 2
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 4
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Vgradna zelena kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed green LED signal light, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB3 + ZBZ32. | like for example Schneider tip: XB4BVB3 + ZBZ32. | kos | 1
| - Vgradna rdeča kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed red LED signal light, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB4 + ZBZ32. | like for example Schneider tip: XB4BVB4 + ZBZ32. | kos | 2
| - Vgradna modre tipke z delovnim kontaktom in nosilcem tipkala, | - Built-in blue keys with working contact and key holder,
| kot naprimer Schneider tip: XB4BA61 + ZBZ32. | like for example Schneider tip: XB4BA61 + ZBZ32. | kos | 3
| - Enotni blok za funkcijo testne luči 24 V AC DC, | - Single block for 24 V AC DC test light function,
| kot naprimer Schneider tip: ZBZG156. | such as Schneider type: ZBZG156. | kos | 3
| - Vgradna tipka za izklop v sili z gobo, 2x NC, za vgradnjo na vrata omare, komplet s ploščico, | - Emergency stop push-button with sponge, 2x NC, for mounting on cabinet doors, complete with plate,
| kot naprimer Schneider tip: XB5AT842 + ZBE102+ZBY9360. | like for example Schneider tip: XB5AT842+ZBE102+ZBY9360. | kos | 1
| - Varnostni rele za izklop v sili, izhodi 3 NO in 1 NC, napajanje 24 VDC, povezovalni modul | - Emergency stop safety relay, 3 NO and 1 NC outputs, 24 VDC power supply, connection module
| kot naprimer Siemens tip: 3SK1121-1AB40 + 3ZY1212-2DA00. | as for example Siemens type: 3SK1121-1AB40 + 3ZY1212-2DA00. | kos | 1
| - Razšeritveni varnostni rele za izklop v sili, izhodi 4 NO in 1 NC, napajanje 24 VDC, povezovalni modul (podnožje) | - Emergency trip safety relay, 4 NO and 1 NC outputs, 24 VDC power supply, connection module (base)
| kot naprimer Siemens tip: 3SK1211-1BB40 + 3ZY1212-2BA00. | such as for example Siemens type: 3SK1211-1BB40 + 3ZY1212-2BA00. | kos | 1
| - Konktaktor z dodatnim inštalacijskim priborom | - Connector with additional installation accessories
| kot naprimer Eaton, tip DILER-40-G-C(24VDC)+40DILE-C. | such as Eaton, type DILER-40-G-C(24VDC)+40DILE-C. | kos | 8
| - Rele-sponka, 24 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC- 24UC/21. | such as Phoenix Contact type: PLC-RSC- 24UC/21. | kos | 61
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC- 24UC/21-21. | such as Phoenix Contact type: PLC-RSC- 24UC/21-21. | kos | 17
| - Rele-sponka, 230 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21. | such as Phoenix Contact type: PLC-RSC-230UC/21. | kos | 1
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Varnostni ločilni transformator 315 VAC/24 VAC, | - Safety isolating transformer 315 VAC/24 VAC,
| kot na primer Siemens tip: 4AM4342-4TN00-0EA0 | such as Siemens type: 4AM4342-4TN00-0EA0 | kos | 1
| - Sponke 6 mm2 za montažo na DIN letev, | - 6 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 6 | such as Phoenix Contact type: UT 6 | kos | 1
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - PE | such as Phoenix Contact type: PT 2,5 - PE | kos | 1
| - Sponke 1,5 mm2 za montažo na DIN letev, | - 1.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PTTB 1,5/S | such as Phoenix Contact type: PTTB 1,5/S | kos | 6
| - Sponke 1,5 mm2 več nivojske za montažo na DIN letev, | - 1.5 mm2 multi-level clips for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 1,5/S-3L | such as Phoenix Contact type: PT 1,5/S-3L | kos | 55
| - Sponke 1,5 mm2, dvojne odklopne, za montažo na DIN letev, | - Clips 1,5 mm2, double hinged, for DIN rail mounting,
| kot na primer Phoenix Contact tip: PTT 1,5/S-2MT | such as Phoenix Contact type: PTT 1,5/S-2MT | kos | 88
| - Sponke varovalčna (5x20), 0,5 A vložek | - Fuse clips (5x20), 0.5 A insert
| kot na primer Phoenix Contact tip: PTC 4 - HESILED 24 | such as Phoenix Contact type: PTC 4 - HESILED 24 | kos | 82
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
1.13 | Dobava in montaža kovinske omare +HVAC_S1-R2 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +HVAC_S1-R2 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 800 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima enokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 800 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height single-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20840P. | such as Schneider, type: NSYSFN20840P. | kos | 1
| - Podstavek 200 mm, širine 800 mm, | - Base 200 mm, width 800 mm,
| kot naprimer Schneider, tip: NSYSPF8200. | such as Schneider, type: NSYSPF8200. | kos | 2
| - stranica podstavka 200 mm, globine 400 mm, | - base side 200 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4200. | such as Schneider, type: NSYSPS4200. | kos | 2
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1000 mm, | - Lower crossbar with PanelSeT cable entry - 1000 mm,
| kot naprimer Rittal, tip: 2388.050. | such as Rittal, type: 2388.050. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Rittal, tip: 2388.100. | such as Rittal, type: 2388.100. | kos | 5
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Rittal, tip: 7077.000. | such as Rittal, type: 7077.000. | kos | 12
| V močnostno omaro +HVAC_S1-R2 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +HVAC_S1-R2 power cabinet:
| - glavno stikalo In=100 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=100 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C123100LS. | such as Schneider, type: C123100LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, | - Led cabinet light, 11W, 230V, without socket, on/off, 4000K,
| kot naprimer Rittal, tip: 2500.200. | such as Rittal, type: 2500.200. | kos | 1
| - Priključni kabel za LED svetilko OR 3000mm, | - Connecting cable for LED luminaire OR 3000mm,
| kot naprimer Rittal, tip: 2500.400. | such as Rittal, type: 2500.400. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - Prezračevalni filter, | - Ventilation filter,
| kot naprimer Rittal, tip: SK 3237.300. | such as Rittal, type: SK 3237.300. | kos | 2
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Motorski odklopnik 3P, 0,25-0,4 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 0,25-0,4 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P03 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P03 + GVAN11. | kos | 1
| - Motorski odklopnik 3P, 4-6,3 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 4-6.3 A, thermomagnetic protection, complete with additional installation accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P10 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P10 + GVAN11. | kos | 3
| - Motorski odklopnik 3P, 6-10 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit-breaker 3P, 6-10 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P14 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P14 + GVAN11. | kos | 4
| - Štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 20 kA, | - 40 A, four-pole circuit breaker with C characteristic, 20 kA,
| kot naprimer Schneider, Acti 9 iC60L, tip: A9F84440. | such as Schneider, Acti 9 iC60L, type: A9F84440. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Pomožni kontakt 1 C/O za enopolni inštalacijski odklopnik, | - Auxiliary contact 1 C/O for single-pole circuit breaker,
| kot naprimer Schneider, Acti9 A9A iOF, tip: A9A26904. | such as Schneider, Acti9 A9A iOF, type: A9A26904. | kos | 1
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 1
| - Kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 6 A s C karakteristiko, 30mA, tip A in pomožni kontakt 2 C/O, | - Combination protection switch with overcurrent protection (KZS), 1P+N, 6 A with C characteristic, 30mA, type A and auxiliary contact 2 C/O,
| kot naprimer Schneider, Acti 9 iDPN H, tip: A9D37606, pomožni kontakt tip: A9A26919. | such as Schneider, Acti 9 iDPN H, type: A9D37606, auxiliary contact type: A9A26919. | kos | 1
| - Kontaktor, 3P (3NO), 6 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, | - Contactor, 3P (3NO), 6 A, coil 230 V AC, 50 Hz and auxiliary contact block 1 NO + 1 NC,
| kot naprimer Schneider tip: TeSys LC-1, LC1K06013P7 + LA1KN113. | such as for example Schneider tip: TeSys LC-1, LC1K06013P7 + LA1KN113. | kos | 1
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21. | such as Phoenix Contact type: PLC-RSC-230UC/21. | kos | 1
| - Rele-sponka, 24 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip:PLC-RSC- 24UC/21. | such as Phoenix Contact type:PLC-RSC- 24UC/21. | kos | 1
| - Sponke 50 mm2 za montažo na DIN letev, | - 50 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UKH 50 | such as Phoenix Contact type: UKH 50 | kos | 3
| - Sponke 2,5 mm2 vzmetne priklop motorjev za montažo na DIN letev, | - 2.5 mm2 spring clips for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5-PE/3L | such as Phoenix Contact type: PT 2,5-PE/3L | kos | 8
| - Sponke 2,5 mm2 vmznetna za montažo na DIN letev, | - 2.5 mm2 clips for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 | such as Phoenix Contact type: PT 2,5 | kos | 2
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 BU | such as Phoenix Contact type: PT 2,5 BU | kos | 2
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 2
| - Sponke 1,5 mm2 vmznetna večnivojska za montažo na DIN letev, | - 1,5 mm2 clips in multilevel for DIN rail mounting,
| kot na primer Phoenix Contact tip: PTTB 1,5/S | such as Phoenix Contact type: PTTB 1,5/S | kos | 21
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
1.14 | Dobava in montaža kovinske omare +HVAC_S1-PLC2 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of metal cabinet +HVAC_S1-PLC2 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1000 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1000 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2010402DP. | such as Schneider, type: NSYSFN2010402DP. | kos | 1
| - Podstavek 200 mm, širine 1000 mm, | - Base 200 mm, width 1000 mm,
| kot naprimer Schneider, tip: NSYSPF10200. | such as Schneider, type: NSYSPF10200. | kos | 2
| - stranica podstavka 200 mm, globine 400 mm, | - base side 200 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4200. | such as Schneider, type: NSYSPS4200. | kos | 2
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1000 mm, | - Lower crossbar with PanelSeT cable entry - 1000 mm,
| kot naprimer Rittal, tip: 2388.050. | such as Rittal, type: 2388.050. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Rittal, tip: 2388.100. | such as Rittal, type: 2388.100. | kos | 40
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Rittal, tip: 7077.000. | such as Rittal, type: 7077.000. | kos | 10
| V krmilno omaro +HVAC_S1-PLC2 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +HVAC_S1-PLC2 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, | - Led cabinet light, 11W, 230V, without socket, on/off, 4000K,
| kot naprimer Rittal, tip: 2500.200. | such as Rittal, type: 2500.200. |  | 1
| - Priključni kabel za LED svetilko OR 3000mm, | - Connecting cable for LED luminaire OR 3000mm,
| kot naprimer Rittal, tip: 2500.400. | such as Rittal, type: 2500.400. | kos | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Rittal, tip: SK 3110.000. | such as Rittal, type: SK 3110.000. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Rittal, tip: SK 3240.100 + SK 3240.200. | such as Rittal, type: SK 3240.100 + SK 3240.200. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica), | - Socket 2x RJ45 (communication socket),
| kot na primer Weidmuller tip: IE-XM-RJ45/RJ45 | such as Weidmuller type: IE-XM-RJ45/RJ45 | kos | 2
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 3
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Vgradna zelena kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed green LED signal light, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB3 + ZBZ32. | like for example Schneider tip: XB4BVB3 + ZBZ32. | kos | 1
| - Vgradna rdeča kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed red LED signal light, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB4 + ZBZ32. | like for example Schneider tip: XB4BVB4 + ZBZ32. | kos | 2
| - Vgradna modre tipke z delovnim kontaktom in nosilcem tipkala, | - Built-in blue keys with working contact and key holder,
| kot naprimer Schneider tip: XB4BA61 + ZBZ32. | like for example Schneider tip: XB4BA61 + ZBZ32. | kos | 3
| - Enotni blok za funkcijo testne luči 24 V AC DC, | - Single block for 24 V AC DC test light function,
| kot naprimer Schneider tip: ZBZG156. | such as Schneider type: ZBZG156. | kos | 3
| - Vgradna tipka za izklop v sili z gobo, 2x NC, za vgradnjo na vrata omare, komplet s ploščico, | - Emergency stop push-button with sponge, 2x NC, for mounting on cabinet doors, complete with plate,
| kot naprimer Schneider tip: XB5AT842 + ZBE102+ZBY9360. | like for example Schneider tip: XB5AT842+ZBE102+ZBY9360. | kos | 1
| - Varnostni rele za izklop v sili, izhodi 3 NO in 1 NC, napajanje 24 VDC, povezovalni modul | - Emergency stop safety relay, 3 NO and 1 NC outputs, 24 VDC power supply, connection module
| kot naprimer Siemens tip: 3SK1121-1AB40 + 3ZY1212-2DA00. | as for example Siemens type: 3SK1121-1AB40 + 3ZY1212-2DA00. | kos | 1
| - Razšeritveni varnostni rele za izklop v sili, izhodi 4 NO in 1 NC, napajanje 24 VDC, povezovalni modul (podnožje) | - Emergency trip safety relay, 4 NO and 1 NC outputs, 24 VDC power supply, connection module (base)
| kot naprimer Siemens tip: 3SK1211-1BB40 + 3ZY1212-2BA00. | such as for example Siemens type: 3SK1211-1BB40 + 3ZY1212-2BA00. | kos | 1
| - Konktaktor z dodatnim inštalacijskim priborom | - Connector with additional installation accessories
| kot naprimer Eaton, tip DILER-40-G-C(24VDC)+40DILE-C. | such as Eaton, type DILER-40-G-C(24VDC)+40DILE-C. | kos | 3
| - Rele-sponka, 24 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC- 24UC/21. | such as Phoenix Contact type: PLC-RSC- 24UC/21. | kos | 14
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC- 24UC/21-21. | such as Phoenix Contact type: PLC-RSC- 24UC/21-21. | kos | 3
| - Rele-sponka, 230 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21. | such as Phoenix Contact type: PLC-RSC-230UC/21. | kos | 1
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Varnostni ločilni transformator 315 VAC/24 VAC, | - Safety isolating transformer 315 VAC/24 VAC,
| kot na primer Siemens tip: 4AM4342-4TN00-0EA0 | such as Siemens type: 4AM4342-4TN00-0EA0 | kos | 1
| - Sponke 6 mm2 za montažo na DIN letev, | - 6 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 6 | such as Phoenix Contact type: UT 6 | kos | 1
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - PE | such as Phoenix Contact type: PT 2,5 - PE | kos | 1
| - Sponke 1,5 mm2 za montažo na DIN letev, | - 1.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PTTB 1,5/S | such as Phoenix Contact type: PTTB 1,5/S | kos | 6
| - Sponke 1,5 mm2 več nivojske za montažo na DIN letev, | - 1.5 mm2 multi-level clips for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 1,5/S-3L | such as Phoenix Contact type: PT 1,5/S-3L | kos | 37
| - Sponke 1,5 mm2, dvojne odklopne, za montažo na DIN letev, | - Clips 1,5 mm2, double hinged, for DIN rail mounting,
| kot na primer Phoenix Contact tip: PTT 1,5/S-2MT | such as Phoenix Contact type: PTT 1,5/S-2MT | kos | 46
| - Sponke varovalčna (5x20), 0,5 A vložek | - Fuse clips (5x20), 0.5 A insert
| kot na primer Phoenix Contact tip: PTC 4 - HESILED 24 | such as Phoenix Contact type: PTC 4 - HESILED 24 | kos | 36
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
1.15 | Dobava in montaža kovinske omare +HVAC_S1-R3 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +HVAC_S1-R3 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 800 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 800 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20840P. | such as Schneider, type: NSYSFN20840P. | kos | 1
| - Podstavek 200 mm, širine 800 mm, | - Base 200 mm, width 800 mm,
| kot naprimer Schneider, tip: NSYSPF8200. | such as Schneider, type: NSYSPF8200. | kos | 2
| - stranica podstavka 200 mm, globine 400 mm, | - base side 200 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4200. | such as Schneider, type: NSYSPS4200. | kos | 2
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Prezračevalni filter, | - Ventilation filter,
| kot naprimer Rittal, tip: SK 3237.300. | such as Rittal, type: SK 3237.300. | kos | 2
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1000 mm, | - Lower crossbar with PanelSeT cable entry - 1000 mm,
| kot naprimer Rittal, tip: 2388.050. | such as Rittal, type: 2388.050. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Rittal, tip: 2388.100. | such as Rittal, type: 2388.100. | kos | 18
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Rittal, tip: 7077.000. | such as Rittal, type: 7077.000. | kos | 10
| V močnostno omaro +HVAC_S1-R3 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +HVAC_S1-R3 power cabinet:
| - glavno stikalo In=160 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=160 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of installing a lock (padlock) on the switch, terminals. The switch shall comply and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C123160LS. | such as Schneider, type: C123160LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, | - Led cabinet light, 11W, 230V, without socket, on/off, 4000K,
| kot naprimer Rittal, tip: 2500.200. | such as Rittal, type: 2500.200. | kos | 1
| - Priključni kabel za LED svetilko OR 3000mm, | - Connecting cable for LED luminaire OR 3000mm,
| kot naprimer Rittal, tip: 2500.400. | such as Rittal, type: 2500.400. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Motorski odklopnik 3P,0,25 - 0,4 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P,0,25 - 0,4 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P03 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P03 + GVAN11. | kos | 2
| - Motorski odklopnik 3P,2,5 - 4 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P,2,5 - 4 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P08 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P08 + GVAN11. | kos | 1
| - Motorski odklopnik 3P, 4 - 6,3 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 4 - 6.3 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P10 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P10 + GVAN11. | kos | 1
| - Motorski odklopnik 3P, 6 - 10 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 6 - 10 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P14 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P14 + GVAN11. | kos | 7
| - Motorski odklopnik 3P, 9 - 14 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 9 - 14 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P16 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P16 + GVAN11. | kos | 6
| - Motorski odklopnik 3P, 17 - 23 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 17 - 23 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P21 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P21 + GVAN11. | kos | 1
| - Kontaktor, 3P (3NO), 6 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, | - Contactor, 3P (3NO), 6 A, coil 230 V AC, 50 Hz and auxiliary contact block 1 NO + 1 NC,
| kot naprimer Schneider tip: TeSys LC-1, LC1K06013P7 + LA1KN113. | such as for example Schneider tip: TeSys LC-1, LC1K06013P7 + LA1KN113. | kos | 2
| - Štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 20 kA, | - 40 A, four-pole circuit breaker with C characteristic, 20 kA,
| kot naprimer Schneider, Acti 9 iC60L, tip: A9F84440. | such as Schneider, Acti 9 iC60L, type: A9F84440. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Pomožni kontakt 1 C/O za enopolni inštalacijski odklopnik, | - Auxiliary contact 1 C/O for single-pole circuit breaker,
| kot naprimer Schneider, Acti9 A9A iOF, tip: A9A26904. | such as Schneider, Acti9 A9A iOF, type: A9A26904. | kos | 1
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 1
| - Kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 6 A s C karakteristiko, 30mA, tip A in pomožni kontakt 2 C/O, | - Combination protection switch with overcurrent protection (KZS), 1P+N, 6 A with C characteristic, 30mA, type A and auxiliary contact 2 C/O,
| kot naprimer Schneider, Acti 9 iDPN H, tip: A9D37606, pomožni kontakt tip: A9A26919. | such as Schneider, Acti 9 iDPN H, type: A9D37606, auxiliary contact type: A9A26919. | kos | 1
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21. | such as Phoenix Contact type: PLC-RSC-230UC/21. | kos | 1
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip:PLC-RSC- 24UC/21. | such as Phoenix Contact type:PLC-RSC- 24UC/21. | kos | 2
| - Sponke 50 mm2 za montažo na DIN letev, | - 50 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UKH 50 | such as Phoenix Contact type: UKH 50 | kos | 3
| - Sponke 2,5 mm2 vzmetne priklop motorjev za montažo na DIN letev, | - 2.5 mm2 spring clips for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5-PE/3L | such as Phoenix Contact type: PT 2,5-PE/3L | kos | 18
| - Sponke 2,5 mm2 vmznetna za montažo na DIN letev, | - 2.5 mm2 clips for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 | such as Phoenix Contact type: PT 2,5 | kos | 1
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 BU | such as Phoenix Contact type: PT 2,5 BU | kos | 1
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 1
| - Sponke 1,5 mm2 vmznetna večnivojska za montažo na DIN letev, | - 1,5 mm2 clips in multilevel for DIN rail mounting,
| kot na primer Phoenix Contact tip: PTTB 1,5/S | such as Phoenix Contact type: PTTB 1,5/S | kos | 41
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
1.16 | Dobava in montaža kovinske omare +HVAC_S1-PLC3 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of metal cabinet +HVAC_S1-PLC3 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1600 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1600 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2016402DP. | such as Schneider, type: NSYSFN2016402DP. | kos | 1
| - Podstavek 200 mm, širine 1600 mm, | - Base 200 mm, width 1600 mm,
| kot naprimer Schneider, tip: NSYSPF16200. | such as Schneider, type: NSYSPF16200. | kos | 2
| - stranica podstavka 200 mm, globine 400 mm, | - base side 200 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4200. | such as Schneider, type: NSYSPS4200. | kos | 2
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1600 mm, | - Lower crossbar with PanelSeT cable entry - 1600 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider. | such as Schneider. | kos | 350
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider. | such as Schneider. | kos | 50
| V krmilno omaro +HVAC_S1-PLC3 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +HVAC_S1-PLC3 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, | - Led cabinet light, 11W, 230V, without socket, on/off, 4000K,
| kot naprimer Rittal, tip: 2500.200. | such as Rittal, type: 2500.200. |  | 1
| - Priključni kabel za LED svetilko OR 3000mm, | - Connecting cable for LED luminaire OR 3000mm,
| kot naprimer Rittal, tip: 2500.400. | such as Rittal, type: 2500.400. | kos | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Rittal, tip: SK 3240.200. | such as Rittal, type: SK 3240.200. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Rittal, tip: SK 3240.100 + SK 3240.200. | as for example Rittal, type: SK 3240.100 + SK 3240.200. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica), | - Socket 2x RJ45 (communication socket),
| kot na primer Weidmuller tip: IE-XM-RJ45/RJ45 | such as Weidmuller type: IE-XM-RJ45/RJ45 | kos | 2
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 4
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Vgradna zelena kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed green LED signal lamp, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB3 + ZBZ32. | like for example Schneider tip: XB4BVB3 + ZBZ32. | kos | 1
| - Vgradna rdeča kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed red LED signal light, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB4 + ZBZ32. | like for example Schneider tip: XB4BVB4 + ZBZ32. | kos | 2
| - Vgradna modre tipke z delovnim kontaktom in nosilcem tipkala, | - Built-in blue keys with working contact and key holder,
| kot naprimer Schneider tip: XB4BA61 + ZBZ32. | like for example Schneider tip: XB4BA61 + ZBZ32. | kos | 2
| - Enotni blok za funkcijo testne luči 24 V AC DC, | - Single block for 24 V AC DC test light function,
| kot naprimer Schneider tip: ZBZG156. | such as Schneider type: ZBZG156. | kos | 3
| - Vgradna tipka za izklop v sili z gobo, 2x NC, za vgradnjo na vrata omare, komplet s ploščico, | - Emergency stop push-button with sponge, 2x NC, for mounting on cabinet doors, complete with plate,
| kot naprimer Schneider tip: XB5AT842 + ZBE102+ZBY9360. | like for example Schneider tip: XB5AT842+ZBE102+ZBY9360. | kos | 1
| - Varnostni rele za izklop v sili, izhodi 3 NO in 1 NC, napajanje 24 VDC, povezovalni modul | - Emergency stop safety relay, 3 NO and 1 NC outputs, 24 VDC power supply, connection module
| kot naprimer Siemens tip: 3SK1121-1AB40 + 3ZY1212-2DA00. | as for example Siemens type: 3SK1121-1AB40 + 3ZY1212-2DA00. | kos | 1
| - Razšeritveni varnostni rele za izklop v sili, izhodi 4 NO in 1 NC, napajanje 24 VDC, povezovalni modul (podnožje) | - Emergency trip safety relay, 4 NO and 1 NC outputs, 24 VDC power supply, connection module (base)
| kot naprimer Siemens tip: 3SK1211-1BB40 + 3ZY1212-2BA00. | such as Siemens type: 3SK1211-1BB40 + 3ZY1212-2BA00. | kos | 1
| - Konktaktor z dodatnim inštalacijskim priborom | - Connector with additional installation accessories
| kot naprimer Eaton, tip DILER-40-G-C(24VDC)+40DILE-C. | such as Eaton, type DILER-40-G-C(24VDC)+40DILE-C. | kos | 5
| - Rele-sponka, 230 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21. | such as Phoenix Contact type: PLC-RSC-230UC/21. | kos | 1
| - Rele-sponka, 24 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC- 24UC/21. | such as Phoenix Contact type: PLC-RSC- 24UC/21. | kos | 40
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC- 24UC/21-21. | such as Phoenix Contact type: PLC-RSC- 24UC/21-21. | kos | 6
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Varnostni ločilni transformator 315 VAC/24 VAC, | - Safety isolating transformer 315 VAC/24 VAC,
| kot na primer Siemens tip: 4AM4342-4TN00-0EA0 | such as Siemens type: 4AM4342-4TN00-0EA0 | kos | 1
| - Sponke 6 mm2 za montažo na DIN letev, | - 6 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 6 | such as Phoenix Contact type: UT 6 | kos | 1
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - PE | such as Phoenix Contact type: PT 2,5 - PE | kos | 1
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 1,5 - PE | such as Phoenix Contact type: PT 1,5 - PE | kos | 6
| - Sponke 1,5 mm2 za montažo na DIN letev, | - 1.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PTTB 1,5/S | such as Phoenix Contact type: PTTB 1,5/S | kos | 6
| - Sponke 1,5 mm2 več nivojske za montažo na DIN letev, | - 1.5 mm2 multi-level clips for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 1,5/S-3L | such as Phoenix Contact type: PT 1,5/S-3L | kos | 94
| - Sponke 1,5 mm2, dvojne odklopne, za montažo na DIN letev, | - Clips 1,5 mm2, double hinged, for DIN rail mounting,
| kot na primer Phoenix Contact tip: PTT 1,5/S-2MT | such as Phoenix Contact type: PTT 1,5/S-2MT | kos | 252
| - Sponke varovalčna (5x20), 0,5 A vložek | - Fuse clips (5x20), 0.5 A insert
| kot na primer Phoenix Contact tip: PTC 4 - HESILED 24 | such as Phoenix Contact type: PTC 4 - HESILED 24 | kos | 241
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
1.17 | Dobava in montaža kovinske omare +HVAC_S1-R4 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +HVAC_S1-R4 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 800 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 800 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20840P. | such as Schneider, type: NSYSFN20840P. | kos | 1
| - Podstavek 200 mm, širine 800 mm, | - Base 200 mm, width 800 mm,
| kot naprimer Schneider, tip: NSYSPF8200. | such as Schneider, type: NSYSPF8200. | kos | 2
| - stranica podstavka 200 mm, globine 400 mm, | - base side 200 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4200. | such as Schneider, type: NSYSPS4200. | kos | 2
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Prezračevalni filter, | - Ventilation filter,
| kot naprimer Rittal, tip: SK 3237.300. | such as Rittal, type: SK 3237.300. | kos | 2
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1000 mm, | - Lower crossbar with PanelSeT cable entry - 1000 mm,
| kot naprimer Rittal, tip: 2388.050. | such as Rittal, type: 2388.050. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Rittal, tip: 2388.100. | such as Rittal, type: 2388.100. | kos | 10
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Rittal, tip: 7077.000. | such as Rittal, type: 7077.000. | kos | 8
| V močnostno omaro +HVAC_S1-R4 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +HVAC_S1-R4 power cabinet:
| - glavno stikalo In=50 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=50 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of installing a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C113050LS. | such as Schneider, type: C113050LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, | - Led cabinet light, 11W, 230V, without socket, on/off, 4000K,
| kot naprimer Rittal, tip: 2500.200. | such as Rittal, type: 2500.200. | kos | 1
| - Priključni kabel za LED svetilko OR 3000mm, | - Connecting cable for LED luminaire OR 3000mm,
| kot naprimer Rittal, tip: 2500.400. | such as Rittal, type: 2500.400. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Motorski odklopnik 3P,0,4 - 0,63 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P,0,4 - 0,63 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P04 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P04 + GVAN11. | kos | 4
| - Motorski odklopnik 3P, 4 - 6,3 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 4 - 6.3 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P10 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P10 + GVAN11. | kos | 4
| - Kontaktor, 3P (3NO), 6 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, | - Contactor, 3P (3NO), 6 A, coil 230 V AC, 50 Hz and auxiliary contact block 1 NO + 1 NC,
| kot naprimer Schneider tip: TeSys LC-1, LC1K06013P7 + LA1KN113. | such as for example Schneider tip: TeSys LC-1, LC1K06013P7 + LA1KN113. | kos | 4
| - Štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 20 kA, | - 40 A, four-pole circuit breaker with C characteristic, 20 kA,
| kot naprimer Schneider, Acti 9 iC60L, tip: A9F84440. | such as Schneider, Acti 9 iC60L, type: A9F84440. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Pomožni kontakt 1 C/O za enopolni inštalacijski odklopnik, | - Auxiliary contact 1 C/O for single-pole circuit breaker,
| kot naprimer Schneider, Acti9 A9A iOF, tip: A9A26904. | such as Schneider, Acti9 A9A iOF, type: A9A26904. | kos | 1
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 1
| - Kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 6 A s C karakteristiko, 30mA, tip A in pomožni kontakt 2 C/O, | - Combination protection switch with overcurrent protection (KZS), 1P+N, 6 A with C characteristic, 30mA, type A and auxiliary contact 2 C/O,
| kot naprimer Schneider, Acti 9 iDPN H, tip: A9D37606, pomožni kontakt tip: A9A26919. | such as Schneider, Acti 9 iDPN H, type: A9D37606, auxiliary contact type: A9A26919. | kos | 3
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21. | such as Phoenix Contact type: PLC-RSC-230UC/21. | kos | 1
| - Rele-sponka, 24 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip:PLC-RSC- 24UC/21. | such as Phoenix Contact type:PLC-RSC- 24UC/21. | kos | 4
| - Sponke 25 mm2 za montažo na DIN letev, | - 25 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 16 | such as Phoenix Contact type: UT 16 | kos | 3
| - Sponke 2,5 mm2 vmznetna za montažo na DIN letev, | - 2.5 mm2 clips for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 | such as Phoenix Contact type: PT 2,5 | kos | 22
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 BU | such as Phoenix Contact type: PT 2,5 BU | kos | 7
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 12
| - Sponke 1,5 mm2 vmznetna večnivojska za montažo na DIN letev, | - 1,5 mm2 clips in multilevel for DIN rail mounting,
| kot na primer Phoenix Contact tip: PTTB 1,5/S | such as Phoenix Contact type: PTTB 1,5/S | kos | 28
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
1.18 | Dobava in montaža kovinske omare +HVAC_S1-PLC4 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of metal cabinet +HVAC_S1-PLC4 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1000 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1000 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2010402DP. | such as Schneider, type: NSYSFN2010402DP. | kos | 1
| - Podstavek 200 mm, širine 1000 mm, | - Base 200 mm, width 1000 mm,
| kot naprimer Schneider, tip: NSYSPF10200. | such as Schneider, type: NSYSPF10200. | kos | 2
| - stranica podstavka 200 mm, globine 400 mm, | - base side 200 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4200. | such as Schneider, type: NSYSPS4200. | kos | 2
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1000 mm, | - Lower crossbar with PanelSeT cable entry - 1000 mm,
| kot naprimer Rittal, tip: 2388.050. | such as Rittal, type: 2388.050. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Rittal, tip: 2388.100. | such as Rittal, type: 2388.100. | kos | 55
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Rittal, tip: 7077.000. | such as Rittal, type: 7077.000. | kos | 13
| V krmilno omaro +HVAC_S1-PLC4 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +HVAC_S1-PLC4 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, | - Led cabinet light, 11W, 230V, without socket, on/off, 4000K,
| kot naprimer Rittal, tip: 2500.200. | such as Rittal, type: 2500.200. |  | 1
| - Priključni kabel za LED svetilko OR 3000mm, | - Connecting cable for LED luminaire OR 3000mm,
| kot naprimer Rittal, tip: 2500.400. | such as Rittal, type: 2500.400. | kos | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Rittal, tip: SK 3240.200. | such as Rittal, type: SK 3240.200. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Rittal, tip: SK 3240.100 + SK 3240.200. | as for example Rittal, type: SK 3240.100 + SK 3240.200. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica), | - Socket 2x RJ45 (communication socket),
| kot na primer Weidmuller tip: IE-XM-RJ45/RJ45 | such as Weidmuller type: IE-XM-RJ45/RJ45 | kos | 2
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 4
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Vgradna zelena kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed green LED signal light, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB3 + ZBZ32. | like for example Schneider tip: XB4BVB3 + ZBZ32. | kos | 1
| - Vgradna rdeča kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed red LED signal light, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB4 + ZBZ32. | like for example Schneider tip: XB4BVB4 + ZBZ32. | kos | 2
| - Vgradna modre tipke z delovnim kontaktom in nosilcem tipkala, | - Built-in blue keys with working contact and key holder,
| kot naprimer Schneider tip: XB4BA61 + ZBZ32. | like for example Schneider tip: XB4BA61 + ZBZ32. | kos | 2
| - Enotni blok za funkcijo testne luči 24 V AC DC, | - Single block for 24 V AC DC test light function,
| kot naprimer Schneider tip: ZBZG156. | such as Schneider type: ZBZG156. | kos | 3
| - Vgradna tipka za izklop v sili z gobo, 2x NC, za vgradnjo na vrata omare, komplet s ploščico, | - Emergency stop push-button with sponge, 2x NC, for mounting on cabinet doors, complete with plate,
| kot naprimer Schneider tip: XB5AT842 + ZBE102+ZBY9360. | like for example Schneider tip: XB5AT842+ZBE102+ZBY9360. | kos | 1
| - Varnostni rele za izklop v sili, izhodi 3 NO in 1 NC, napajanje 24 VDC, povezovalni modul | - Emergency stop safety relay, 3 NO and 1 NC outputs, 24 VDC power supply, connection module
| kot naprimer Siemens tip: 3SK1121-1AB40 + 3ZY1212-2DA00. | as for example Siemens type: 3SK1121-1AB40 + 3ZY1212-2DA00. | kos | 1
| - Razšeritveni varnostni rele za izklop v sili, izhodi 4 NO in 1 NC, napajanje 24 VDC, povezovalni modul (podnožje) | - Emergency trip safety relay, 4 NO and 1 NC outputs, 24 VDC power supply, connection module (base)
| kot naprimer Siemens tip: 3SK1211-1BB40 + 3ZY1212-2BA00. | such as for example Siemens type: 3SK1211-1BB40 + 3ZY1212-2BA00. | kos | 1
| - Konktaktor z dodatnim inštalacijskim priborom | - Connector with additional installation accessories
| kot naprimer Eaton, tip DILER-40-G-C(24VDC)+40DILE-C. | such as Eaton, type DILER-40-G-C(24VDC)+40DILE-C. | kos | 3
| - Rele-sponka, 230 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21. | such as Phoenix Contact type: PLC-RSC-230UC/21. | kos | 1
| - Rele-sponka, 24 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC- 24UC/21. | such as Phoenix Contact type: PLC-RSC- 24UC/21. | kos | 20
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Varnostni ločilni transformator 315 VAC/24 VAC, | - Safety isolating transformer 315 VAC/24 VAC,
| kot na primer Siemens tip: 4AM4342-4TN00-0EA0 | such as Siemens type: 4AM4342-4TN00-0EA0 | kos | 1
| - Sponke 6 mm2 za montažo na DIN letev, | - 6 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 6 | such as Phoenix Contact type: UT 6 | kos | 1
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - PE | such as Phoenix Contact type: PT 2,5 - PE | kos | 1
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 1,5 - PE | such as Phoenix Contact type: PT 1,5 - PE | kos | 6
| - Sponke 1,5 mm2 za montažo na DIN letev, | - 1.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PTTB 1,5/S | such as Phoenix Contact type: PTTB 1,5/S | kos | 77
| - Sponke 1,5 mm2, dvojne odklopne, za montažo na DIN letev, | - Clips 1,5 mm2, double hinged, for DIN rail mounting,
| kot na primer Phoenix Contact tip: PTT 1,5/S-2MT | such as Phoenix Contact type: PTT 1,5/S-2MT | kos | 80
| - Sponke varovalčna (5x20), 0,5 A vložek | - Fuse clips (5x20), 0.5 A insert
| kot na primer Phoenix Contact tip: PTC 4 - HESILED 24 | such as Phoenix Contact type: PTC 4 - HESILED 24 | kos | 53
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
1.19 | Dobava in montaža kovinske omare +HVAC_S1-R5 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +HVAC_S1-R5 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 800 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima enokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 800 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height single-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20840P. | such as Schneider, type: NSYSFN20840P. | kos | 1
| - Podstavek 200 mm, širine 800 mm, | - Base 200 mm, width 800 mm,
| kot naprimer Schneider, tip: NSYSPF8200. | such as Schneider, type: NSYSPF8200. | kos | 2
| - stranica podstavka 200 mm, globine 400 mm, | - base side 200 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4200. | such as Schneider, type: NSYSPS4200. | kos | 2
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1000 mm, | - Lower crossbar with PanelSeT cable entry - 1000 mm,
| kot naprimer Rittal, tip: 2388.050. | such as Rittal, type: 2388.050. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Rittal, tip: 2388.100. | such as Rittal, type: 2388.100. | kos | 5
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Rittal, tip: 7077.000. | such as Rittal, type: 7077.000. | kos | 12
| V močnostno omaro +HVAC_S1-R5 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +HVAC_S1-R5 power cabinet:
| - glavno stikalo In=100 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=100 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C123100LS. | such as Schneider, type: C123100LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, | - Led cabinet light, 11W, 230V, without socket, on/off, 4000K,
| kot naprimer Rittal, tip: 2500.200. | such as Rittal, type: 2500.200. | kos | 1
| - Priključni kabel za LED svetilko OR 3000mm, | - Connecting cable for LED luminaire OR 3000mm,
| kot naprimer Rittal, tip: 2500.400. | such as Rittal, type: 2500.400. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - Prezračevalni filter, | - Ventilation filter,
| kot naprimer Rittal, tip: SK 3237.300. | such as Rittal, type: SK 3237.300. | kos | 2
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Motorski odklopnik 3P, 0,4-0,63 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 0,4-0,63 A, thermomagnetic protection, complete with additional installation accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P04 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P04 + GVAN11. | kos | 2
| - Motorski odklopnik 3P, 6-10 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit-breaker 3P, 6-10 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P14 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P14 + GVAN11. | kos | 4
| - Štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 20 kA, | - 40 A, four-pole circuit breaker with C characteristic, 20 kA,
| kot naprimer Schneider, Acti 9 iC60L, tip: A9F84440. | such as Schneider, Acti 9 iC60L, type: A9F84440. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Pomožni kontakt 1 C/O za enopolni inštalacijski odklopnik, | - Auxiliary contact 1 C/O for single-pole circuit breaker,
| kot naprimer Schneider, Acti9 A9A iOF, tip: A9A26904. | such as Schneider, Acti9 A9A iOF, type: A9A26904. | kos | 1
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 1
| - Kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 6 A s C karakteristiko, 30mA, tip A in pomožni kontakt 2 C/O, | - Combination protection switch with overcurrent protection (KZS), 1P+N, 6 A with C characteristic, 30mA, type A and auxiliary contact 2 C/O,
| kot naprimer Schneider, Acti 9 iDPN H, tip: A9D37606, pomožni kontakt tip: A9A26919. | such as Schneider, Acti 9 iDPN H, type: A9D37606, auxiliary contact type: A9A26919. | kos | 1
| - Kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip A in pomožni kontakt 2 C/O, | - Combination protection switch with overcurrent protection (KZS), 1P+N, 16 A with C characteristic, 30mA, type A and auxiliary contact 2 C/O,
| kot naprimer Schneider, Acti 9 iDPN H, tip: A9D37616, pomožni kontakt tip: A9A26919. | such as Schneider, Acti 9 iDPN H, type: A9D37616, auxiliary contact type: A9A26919. | kos | 3
| - Kontaktor, 3P (3NO), 6 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, | - Contactor, 3P (3NO), 6 A, coil 230 V AC, 50 Hz and auxiliary contact block 1 NO + 1 NC,
| kot naprimer Schneider tip: TeSys LC-1, LC1K06013P7 + LA1KN113. | such as for example Schneider tip: TeSys LC-1, LC1K06013P7 + LA1KN113. | kos | 5
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21. | such as Phoenix Contact type: PLC-RSC-230UC/21. | kos | 1
| - Rele-sponka, 24 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip:PLC-RSC- 24UC/21. | such as Phoenix Contact type:PLC-RSC- 24UC/21. | kos | 5
| - Sponke 16 mm2 za montažo na DIN letev, | - 16 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 16 | such as Phoenix Contact type: UT 16 | kos | 3
| - Sponke 2,5 mm2 vzmetne priklop motorjev za montažo na DIN letev, | - 2.5 mm2 spring clips for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5-PE/3L | such as Phoenix Contact type: PT 2,5-PE/3L | kos | 7
| - Sponke 2,5 mm2 vmznetna za montažo na DIN letev, | - 2.5 mm2 clips for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 | such as Phoenix Contact type: PT 2,5 | kos | 4
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 BU | such as Phoenix Contact type: PT 2,5 BU | kos | 4
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 11
| - Sponke 1,5 mm2 vmznetna večnivojska za montažo na DIN letev, | - 1,5 mm2 clips in multilevel for DIN rail mounting,
| kot na primer Phoenix Contact tip: PTTB 1,5/S | such as Phoenix Contact type: PTTB 1,5/S | kos | 10
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
1.20 | Dobava in montaža kovinske omare +HVAC_S1-PLC5 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of metal cabinet +HVAC_S1-PLC5 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1000 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1000 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2010402DP. | such as Schneider, type: NSYSFN2010402DP. | kos | 1
| - Podstavek 200 mm, širine 1000 mm, | - Base 200 mm, width 1000 mm,
| kot naprimer Schneider, tip: NSYSPF10200. | such as Schneider, type: NSYSPF10200. | kos | 2
| - stranica podstavka 200 mm, globine 400 mm, | - base side 200 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4200. | such as Schneider, type: NSYSPS4200. | kos | 2
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1000 mm, | - Lower crossbar with PanelSeT cable entry - 1000 mm,
| kot naprimer Rittal, tip: 2388.050. | such as Rittal, type: 2388.050. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Rittal, tip: 2388.100. | such as Rittal, type: 2388.100. | kos | 22
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Rittal, tip: 7077.000. | such as Rittal, type: 7077.000. | kos | 10
| V krmilno omaro +HVAC_S1-PLC5 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +HVAC_S1-PLC5 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, | - Led cabinet light, 11W, 230V, without socket, on/off, 4000K,
| kot naprimer Rittal, tip: 2500.200. | such as Rittal, type: 2500.200. |  | 1
| - Priključni kabel za LED svetilko OR 3000mm, | - Connecting cable for LED luminaire OR 3000mm,
| kot naprimer Rittal, tip: 2500.400. | such as Rittal, type: 2500.400. | kos | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Rittal, tip: SK 3110.000. | such as Rittal, type: SK 3110.000. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Rittal, tip: SK 3240.100 + SK 3240.200. | such as Rittal, type: SK 3240.100 + SK 3240.200. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica), | - Socket 2x RJ45 (communication socket),
| kot na primer Weidmuller tip: IE-XM-RJ45/RJ45 | such as Weidmuller type: IE-XM-RJ45/RJ45 | kos | 2
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 3
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Vgradna zelena kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed green LED signal light, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB3 + ZBZ32. | like for example Schneider tip: XB4BVB3 + ZBZ32. | kos | 1
| - Vgradna rdeča kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed red LED signal light, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB4 + ZBZ32. | like for example Schneider tip: XB4BVB4 + ZBZ32. | kos | 2
| - Vgradna modre tipke z delovnim kontaktom in nosilcem tipkala, | - Built-in blue keys with working contact and key holder,
| kot naprimer Schneider tip: XB4BA61 + ZBZ32. | like for example Schneider tip: XB4BA61 + ZBZ32. | kos | 3
| - Enotni blok za funkcijo testne luči 24 V AC DC, | - Single block for 24 V AC DC test light function,
| kot naprimer Schneider tip: ZBZG156. | such as Schneider type: ZBZG156. | kos | 3
| - Vgradna tipka za izklop v sili z gobo, 2x NC, za vgradnjo na vrata omare, komplet s ploščico, | - Emergency stop push-button with sponge, 2x NC, for mounting on cabinet doors, complete with plate,
| kot naprimer Schneider tip: XB5AT842 + ZBE102+ZBY9360. | like for example Schneider tip: XB5AT842+ZBE102+ZBY9360. | kos | 1
| - Varnostni rele za izklop v sili, izhodi 3 NO in 1 NC, napajanje 24 VDC, povezovalni modul | - Emergency stop safety relay, 3 NO and 1 NC outputs, 24 VDC power supply, connection module
| kot naprimer Siemens tip: 3SK1121-1AB40 + 3ZY1212-2DA00. | as for example Siemens type: 3SK1121-1AB40 + 3ZY1212-2DA00. | kos | 1
| - Razšeritveni varnostni rele za izklop v sili, izhodi 4 NO in 1 NC, napajanje 24 VDC, povezovalni modul (podnožje) | - Emergency trip safety relay, 4 NO and 1 NC outputs, 24 VDC power supply, connection module (base)
| kot naprimer Siemens tip: 3SK1211-1BB40 + 3ZY1212-2BA00. | such as for example Siemens type: 3SK1211-1BB40 + 3ZY1212-2BA00. | kos | 1
| - Konktaktor z dodatnim inštalacijskim priborom | - Connector with additional installation accessories
| kot naprimer Eaton, tip DILER-40-G-C(24VDC)+40DILE-C. | such as Eaton, type DILER-40-G-C(24VDC)+40DILE-C. | kos | 3
| - Rele-sponka, 24 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC- 24UC/21. | such as Phoenix Contact type: PLC-RSC- 24UC/21. | kos | 13
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC- 24UC/21-21. | such as Phoenix Contact type: PLC-RSC- 24UC/21-21. | kos | 2
| - Rele-sponka, 230 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21. | such as Phoenix Contact type: PLC-RSC-230UC/21. | kos | 1
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Varnostni ločilni transformator 315 VAC/24 VAC, | - Safety isolating transformer 315 VAC/24 VAC,
| kot na primer Siemens tip: 4AM4342-4TN00-0EA0 | such as Siemens type: 4AM4342-4TN00-0EA0 | kos | 1
| - Sponke 6 mm2 za montažo na DIN letev, | - 6 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 6 | such as Phoenix Contact type: UT 6 | kos | 1
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - PE | such as Phoenix Contact type: PT 2,5 - PE | kos | 1
| - Sponke 1,5 mm2 za montažo na DIN letev, | - 1.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PTTB 1,5/S | such as Phoenix Contact type: PTTB 1,5/S | kos | 6
| - Sponke 1,5 mm2 več nivojske za montažo na DIN letev, | - 1.5 mm2 multi-level clips for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 1,5/S-3L | such as Phoenix Contact type: PT 1,5/S-3L | kos | 28
| - Sponke 1,5 mm2, dvojne odklopne, za montažo na DIN letev, | - 1,5 mm2, double hinged, for DIN rail mounting,
| kot na primer Phoenix Contact tip: PTT 1,5/S-2MT | such as Phoenix Contact type: PTT 1,5/S-2MT | kos | 40
| - Sponke varovalčna (5x20), 0,5 A vložek | - Fuse clips (5x20), 0.5 A insert
| kot na primer Phoenix Contact tip: PTC 4 - HESILED 24 | such as Phoenix Contact type: PTC 4 - HESILED 24 | kos | 35
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
1.21 | Dobava in montaža kovinske omare +HVAC_S1-R6 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +HVAC_S1-R6 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 800 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima enokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 800 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height single-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20840P. | such as Schneider, type: NSYSFN20840P. | kos | 1
| - Podstavek 200 mm, širine 800 mm, | - Base 200 mm, width 800 mm,
| kot naprimer Schneider, tip: NSYSPF8200. | such as Schneider, type: NSYSPF8200. | kos | 2
| - stranica podstavka 200 mm, globine 400 mm, | - base side 200 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4200. | such as Schneider, type: NSYSPS4200. | kos | 2
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1000 mm, | - Lower crossbar with PanelSeT cable entry - 1000 mm,
| kot naprimer Rittal, tip: 2388.050. | such as Rittal, type: 2388.050. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Rittal, tip: 2388.100. | such as Rittal, type: 2388.100. | kos | 10
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Rittal, tip: 7077.000. | such as Rittal, type: 7077.000. | kos | 25
| V močnostno omaro +HVAC_S1-R6 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +HVAC_S1-R6 power cabinet:
| - glavno stikalo In=250 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=250 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of installing a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C253250S. | such as Schneider, type: C253250S. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, | - Led cabinet light, 11W, 230V, without socket, on/off, 4000K,
| kot naprimer Rittal, tip: 2500.200. | such as Rittal, type: 2500.200. | kos | 1
| - Priključni kabel za LED svetilko OR 3000mm, | - Connecting cable for LED luminaire OR 3000mm,
| kot naprimer Rittal, tip: 2500.400. | such as Rittal, type: 2500.400. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - Prezračevalni filter, | - Ventilation filter,
| kot naprimer Rittal, tip: SK 3237.300. | such as Rittal, type: SK 3237.300. | kos | 2
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Motorski odklopnik 3P, 0,25-0,4 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 0,25-0,4 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P03 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P03 + GVAN11. | kos | 1
| - Motorski odklopnik 3P, 0,4-0,63 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 0,4-0,63 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P04 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P04 + GVAN11. | kos | 2
| - Motorski odklopnik 3P, 6-10 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 6-10 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P14 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P14 + GVAN11. | kos | 1
| - Motorski odklopnik 3P, 9-14 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 9-14 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P16 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P16 + GVAN11. | kos | 12
| - Motorski odklopnik 3P, 17-23 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 17-23 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P21 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P21 + GVAN11. | kos | 1
| - Štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 20 kA, | - 40 A, four-pole circuit breaker with C characteristic, 20 kA,
| kot naprimer Schneider, Acti 9 iC60L, tip: A9F84440. | such as Schneider, Acti 9 iC60L, type: A9F84440. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Pomožni kontakt 1 C/O za enopolni inštalacijski odklopnik, | - Auxiliary contact 1 C/O for single-pole circuit breaker,
| kot naprimer Schneider, Acti9 A9A iOF, tip: A9A26904. | such as Schneider, Acti9 A9A iOF, type: A9A26904. | kos | 1
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 1
| - Kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 6 A s C karakteristiko, 30mA, tip A in pomožni kontakt 2 C/O, | - Combination protection switch with overcurrent protection (KZS), 1P+N, 6 A with C characteristic, 30mA, type A and auxiliary contact 2 C/O,
| kot naprimer Schneider, Acti 9 iDPN H, tip: A9D37606, pomožni kontakt tip: A9A26919. | such as Schneider, Acti 9 iDPN H, type: A9D37606, auxiliary contact type: A9A26919. | kos | 1
| - Kontaktor, 3P (3NO), 6 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, | - Contactor, 3P (3NO), 6 A, coil 230 V AC, 50 Hz and auxiliary contact block 1 NO + 1 NC,
| kot naprimer Schneider tip: TeSys LC-1, LC1K06013P7 + LA1KN113. | such as for example Schneider tip: TeSys LC-1, LC1K06013P7 + LA1KN113. | kos | 1
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21. | such as Phoenix Contact type: PLC-RSC-230UC/21. | kos | 1
| - Rele-sponka, 24 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip:PLC-RSC- 24UC/21. | such as Phoenix Contact type:PLC-RSC- 24UC/21. | kos | 1
| - Sponke 95 mm2 za montažo na DIN letev, | - 95 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UKH 70 | such as Phoenix Contact type: UKH 70 | kos | 3
| - Sponke 2,5 mm2 vzmetne priklop motorjev za montažo na DIN letev, | - 2.5 mm2 spring clips for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5-PE/3L | such as Phoenix Contact type: PT 2,5-PE/3L | kos | 16
| - Sponke 4 mm2 vzmetne priklop motorjev za montažo na DIN letev, | - 4 mm2 spring clips for DIN rail mounting of motors,
| kot na primer Phoenix Contact tip: PT 4-PE/3L | such as Phoenix Contact type: PT 4-PE/3L | kos | 1
| - Sponke 2,5 mm2 vmznetna za montažo na DIN letev, | - 2.5 mm2 clips for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 | such as Phoenix Contact type: PT 2,5 | kos | 2
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 BU | such as Phoenix Contact type: PT 2,5 BU | kos | 2
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 2
| - Sponke 1,5 mm2 vmznetna večnivojska za montažo na DIN letev, | - 1,5 mm2 clips in multilevel for DIN rail mounting,
| kot na primer Phoenix Contact tip: PTTB 1,5/S | such as Phoenix Contact type: PTTB 1,5/S | kos | 39
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
1.22 | Dobava in montaža kovinske omare +HVAC_S1-PLC6 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of metal cabinet +HVAC_S1-PLC6 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije dveh omar so: Polje 1: višina 2000 mm, širina 1000 mm in globina 400 mm. Polje 2: višina 2000 mm, širina 800 mm in globina 400 mm. Obe omari stojita na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omari imata dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the two cupboards are: Bay 1: height 2000 mm, width 1000 mm and depth 400 mm. Bay 2: height 2000 mm, width 800 mm and depth 400 mm. Both cupboards stand on a 200 mm high plinth. A roundel for the plinth of the electrical cupboard is to be made. The cupboards have a full-height double-leaf door at the front, a comfort handle and a two-perforated key-operated closure.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Polje 1:Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Box 1:Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2010402DP. | such as Schneider, type: NSYSFN2010402DP. | kos | 1
| - Podstavek 200 mm, širine 1000 mm, | - Base 200 mm, width 1000 mm,
| kot naprimer Schneider, tip: NSYSPF10200. | such as Schneider, type: NSYSPF10200. | kos | 2
| - stranica podstavka 200 mm, globine 400 mm, | - base side 200 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4200. | such as Schneider, type: NSYSPS4200. | kos | 2
| - Polje 2:Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Box 2:Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20840P. | such as Schneider, type: NSYSFN20840P. | kos | 1
| - Podstavek 200 mm, širine 800 mm, | - Base 200 mm, width 800 mm,
| kot naprimer Schneider, tip: NSYSPF8200. | such as Schneider, type: NSYSPF8200. | kos | 2
| - stranica podstavka 200 mm, globine 400 mm, | - base side 200 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4200. | such as Schneider, type: NSYSPS4200. | kos | 2
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1600 mm, | - Lower crossbar with PanelSeT cable entry - 1600 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider. | such as Schneider. | kos | 300
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider. | such as Schneider. | kos | 90
| V krmilno omaro +HVAC_S1-PLC5 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +HVAC_S1-PLC5 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, | - Led cabinet light, 11W, 230V, without socket, on/off, 4000K,
| kot naprimer Rittal, tip: 2500.200. | such as Rittal, type: 2500.200. |  | 1
| - Priključni kabel za LED svetilko OR 3000mm, | - Connecting cable for LED luminaire OR 3000mm,
| kot naprimer Rittal, tip: 2500.400. | such as Rittal, type: 2500.400. | kos | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Rittal, tip: SK 3240.200. | such as Rittal, type: SK 3240.200. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Rittal, tip: SK 3240.100 + SK 3240.200. | as for example Rittal, type: SK 3240.100 + SK 3240.200. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica), | - Socket 2x RJ45 (communication socket),
| kot na primer Weidmuller tip: IE-XM-RJ45/RJ45 | such as Weidmuller type: IE-XM-RJ45/RJ45 | kos | 2
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 4
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Vgradna zelena kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed green LED signal light, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB3 + ZBZ32. | like for example Schneider tip: XB4BVB3 + ZBZ32. | kos | 1
| - Vgradna rdeča kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed red LED signal light, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB4 + ZBZ32. | like for example Schneider tip: XB4BVB4 + ZBZ32. | kos | 2
| - Vgradna modre tipke z delovnim kontaktom in nosilcem tipkala, | - Built-in blue keys with working contact and key holder,
| kot naprimer Schneider tip: XB4BA61 + ZBZ32. | like for example Schneider tip: XB4BA61 + ZBZ32. | kos | 2
| - Enotni blok za funkcijo testne luči 24 V AC DC, | - Single block for 24 V AC DC test light function,
| kot naprimer Schneider tip: ZBZG156. | such as Schneider type: ZBZG156. | kos | 3
| - Vgradna tipka za izklop v sili z gobo, 2x NC, za vgradnjo na vrata omare, komplet s ploščico, | - Emergency stop push-button with sponge, 2x NC, for mounting on cabinet doors, complete with plate,
| kot naprimer Schneider tip: XB5AT842 + ZBE102+ZBY9360. | like for example Schneider tip: XB5AT842+ZBE102+ZBY9360. | kos | 1
| - Varnostni rele za izklop v sili, izhodi 3 NO in 1 NC, napajanje 24 VDC, povezovalni modul | - Emergency stop safety relay, 3 NO and 1 NC outputs, 24 VDC power supply, connection module
| kot naprimer Siemens tip: 3SK1121-1AB40 + 3ZY1212-2DA00. | as for example Siemens type: 3SK1121-1AB40 + 3ZY1212-2DA00. | kos | 1
| - Razšeritveni varnostni rele za izklop v sili, izhodi 4 NO in 1 NC, napajanje 24 VDC, povezovalni modul (podnožje) | - Emergency trip safety relay, 4 NO and 1 NC outputs, 24 VDC power supply, connection module (base)
| kot naprimer Siemens tip: 3SK1211-1BB40 + 3ZY1212-2BA00. | such as for example Siemens type: 3SK1211-1BB40 + 3ZY1212-2BA00. | kos | 1
| - Konktaktor z dodatnim inštalacijskim priborom | - Connector with additional installation accessories
| kot naprimer Eaton, tip DILER-40-G-C(24VDC)+40DILE-C. | such as Eaton, type DILER-40-G-C(24VDC)+40DILE-C. | kos | 7
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 1
| - Rele-sponka, 24 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21. | such as Phoenix Contact type: PLC-RSC-24UC/21. | kos | 36
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 3
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Varnostni ločilni transformator 315 VAC/24 VAC, | - Safety isolating transformer 315 VAC/24 VAC,
| kot na primer Siemens tip: 4AM4342-4TN00-0EA0 | such as Siemens type: 4AM4342-4TN00-0EA0 | kos | 1
| - Sponke 6 mm2 za montažo na DIN letev, | - 6 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 6 | such as Phoenix Contact type: UT 6 | kos | 1
| - Sponke ozemljitvene 1,5 mm2 za montažo na DIN letev, | - Earthing clips 1,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 1,5 - PE | such as Phoenix Contact type: PT 1,5 - PE | kos | 6
| - Sponke 1,5 mm2 več nivojske za montažo na DIN letev, | - 1.5 mm2 multi-level clips for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 1,5/S-3L | such as Phoenix Contact type: PT 1,5/S-3L | kos | 85
| - Sponke 1,5 mm2, dvojne odklopne, za montažo na DIN letev, | - Clips 1,5 mm2, double hinged, for DIN rail mounting,
| kot na primer Phoenix Contact tip: PTT 1,5/S-2MT | such as Phoenix Contact type: PTT 1,5/S-2MT | kos | 213
| - Sponke varovalčna (5x20), 0,5 A vložek | - Fuse clips (5x20), 0.5 A insert
| kot na primer Phoenix Contact tip: PTC 4 - HESILED 24 | such as Phoenix Contact type: PTC 4 - HESILED 24 | kos | 188
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
1.23 | Dobava in montaža kovinske omare +HVAC_N1-PLC6 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of metal cabinet +HVAC_N1-PLC6 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1200 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ.Omara je sestavljena iz dveh polj močnostno in krmilno. | The dimensions of the cabinet are: height 2000 mm, width 1200 mm and depth 400 mm. The whole cabinet stands on a base of height 200 mm. The rounded base for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforated lock.The cabinet is composed of two fields power and control.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2016402DP. | such as Schneider, type: NSYSFN2016402DP. | kos | 1
| - Podstavek 200 mm, širine 1200 mm, | - Base 200 mm, width 1200 mm,
| kot naprimer Schneider, tip: NSYSPF12200. | such as Schneider, type: NSYSPF12200. | kos | 2
| - stranica podstavka 200 mm, globine 400 mm, | - base side 200 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4200. | such as Schneider, type: NSYSPS4200. | kos | 2
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1200 mm, | - Lower crossbar with PanelSeT cable entry - 1200 mm,
| kot naprimer Rittal, tip: 2388.125. | such as Rittal, type: 2388.125. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Rittal, tip: 2388.100. | such as Rittal, type: 2388.100. | kos | 70
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Rittal, tip: 7077.000. | such as Rittal, type: 7077.000. | kos | 30
| POLJE 1:V močnostno omaro +HVAC_N1-R6 se dobavi in vgradi naslednja elektro oprema: | BOX 1:The following electrical equipment shall be supplied and installed in the +HVAC_N1-R6 power cabinet:
| - glavno stikalo In=50 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=50 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C113050LS. | such as Schneider, type: C113050LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Motorski odklopnik 3P, 1,6 - 2,5 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 1,6 - 2,5 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P07 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P07 + GVAN11. | kos | 1
| - Motorski odklopnik 3P, 4 - 6,3 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 4 - 6.3 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P10 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P10 + GVAN11. | kos | 4
| - Motorski odklopnik 3P, 6 - 10 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 6 - 10 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P14 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P14 + GVAN11. | kos | 1
| - Štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 20 kA, | - 40 A, four-pole circuit breaker with C characteristic, 20 kA,
| kot naprimer Schneider, Acti 9 iC60L, tip: A9F84440. | such as Schneider, Acti 9 iC60L, type: A9F84440. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 2
| - Tripolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84306. | such as Schneider, Acti 9 iC60H, type: A9F84306. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 1
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 1
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21. | such as Phoenix Contact type: PLC-RSC-230UC/21. | kos | 1
| - Rele-sponka, 24 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21. | such as Phoenix Contact type: PLC-RSC-24UC/21. | kos | 1
| - Sponke 35 mm2 za montažo na DIN letev, | - 35 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 35 | such as Phoenix Contact type: UT 35 | kos | 3
| - Sponke 2,5 mm2 vzmetne priklop motorjev za montažo na DIN letev, | - 2.5 mm2 spring clips for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5-PE/3L | such as Phoenix Contact type: PT 2,5-PE/3L | kos | 6
| - Sponke 4 mm2 vzmetne priklop motorjev za montažo na DIN letev, | - 4 mm2 spring clips for DIN rail mounting,
| - Sponke 1,5 mm2 vmznetna dvonivojska za montažo na DIN letev, | - 1,5 mm2 clips in two-level DIN rail mounting,
| kot na primer Phoenix Contact tip: PTTB 1,5/S | such as Phoenix Contact type: PTTB 1,5/S | kos | 13
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
| POLJE 2: V krmilno omaro +HVAC_N1-PLC6 se dobavi in vgradi naslednja elektro oprema: | BOX 2: The following electrical equipment shall be supplied and installed in the +HVAC_N1-PLC6 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, | - Led cabinet light, 11W, 230V, without socket, on/off, 4000K,
| kot naprimer Rittal, tip: 2500.200. | such as Rittal, type: 2500.200. |  | 1
| - Priključni kabel za LED svetilko OR 3000mm, | - Connecting cable for LED luminaire OR 3000mm,
| kot naprimer Rittal, tip: 2500.400. | such as Rittal, type: 2500.400. | kos | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Rittal, tip: SK 3240.200. | such as Rittal, type: SK 3240.200. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Rittal, tip: SK 3240.100 + SK 3240.200. | as for example Rittal, type: SK 3240.100 + SK 3240.200. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica), | - Socket 2x RJ45 (communication socket),
| kot na primer Weidmuller tip: IE-XM-RJ45/RJ45 | such as Weidmuller type: IE-XM-RJ45/RJ45 | kos | 2
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 1
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Vgradna zelena kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed green LED signal lamp, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB3 + ZBZ32. | like for example Schneider tip: XB4BVB3 + ZBZ32. | kos | 1
| - Vgradna rdeča kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed red LED signal light, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB4 + ZBZ32. | like for example Schneider tip: XB4BVB4 + ZBZ32. | kos | 2
| - Vgradna modre tipke z delovnim kontaktom in nosilcem tipkala, | - Built-in blue keys with working contact and key holder,
| kot naprimer Schneider tip: XB4BA61 + ZBZ32. | like for example Schneider tip: XB4BA61 + ZBZ32. | kos | 2
| - Enotni blok za funkcijo testne luči 24 V AC DC, | - Single block for 24 V AC DC test light function,
| kot naprimer Schneider tip: ZBZG156. | such as Schneider type: ZBZG156. | kos | 3
| - Vgradna tipka za izklop v sili z gobo, 2x NC, za vgradnjo na vrata omare, komplet s ploščico, | - Emergency stop push-button with sponge, 2x NC, for mounting on cabinet doors, complete with plate,
| kot naprimer Schneider tip: XB5AT842 + ZBE102+ZBY9360. | like for example Schneider tip: XB5AT842+ZBE102+ZBY9360. | kos | 1
| - Varnostni rele za izklop v sili, izhodi 3 NO in 1 NC, napajanje 24 VDC, povezovalni modul | - Emergency stop safety relay, 3 NO and 1 NC outputs, 24 VDC power supply, connection module
| kot naprimer Siemens tip: 3SK1121-1AB40 + 3ZY1212-2DA00. | as for example Siemens type: 3SK1121-1AB40 + 3ZY1212-2DA00. | kos | 1
| - Razšeritveni varnostni rele za izklop v sili, izhodi 4 NO in 1 NC, napajanje 24 VDC, povezovalni modul (podnožje) | - Emergency trip safety relay, 4 NO and 1 NC outputs, 24 VDC power supply, connection module (base)
| kot naprimer Siemens tip: 3SK1211-1BB40 + 3ZY1212-2BA00. | such as for example Siemens type: 3SK1211-1BB40 + 3ZY1212-2BA00. | kos | 1
| - Konktaktor z dodatnim inštalacijskim priborom | - Connector with additional installation accessories
| kot naprimer Eaton, tip DILER-40-G-C(24VDC)+40DILE-C. | such as Eaton, type DILER-40-G-C(24VDC)+40DILE-C. | kos | 2
| - Rele-sponka, 230 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21. | such as Phoenix Contact type: PLC-RSC-230UC/21. | kos | 1
| - Rele-sponka, 24 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21. | such as Phoenix Contact type: PLC-RSC-24UC/21. | kos | 21
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Varnostni ločilni transformator 315 VAC/24 VAC, | - Safety isolating transformer 315 VAC/24 VAC,
| kot na primer Siemens tip: 4AM4342-4TN00-0EA0 | such as Siemens type: 4AM4342-4TN00-0EA0 | kos | 1
| - Sponke 6 mm2 za montažo na DIN letev, | - 6 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 6 | such as Phoenix Contact type: UT 6 | kos | 1
| - Sponke 1,5 mm2 več nivojske za montažo na DIN letev, | - 1.5 mm2 multi-level clips for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 1,5/S-3L | such as Phoenix Contact type: PT 1,5/S-3L | kos | 45
| - Sponke 1,5 mm2 dvo nivojska za montažo na DIN letev, | - 1.5 mm2 two-level DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PTTB 1,5/S | such as Phoenix Contact type: PTTB 1,5/S | kos | 20
| - Sponke 1,5 mm2, dvojne odklopne, za montažo na DIN letev, | - Clips 1,5 mm2, double hinged, for DIN rail mounting,
| kot na primer Phoenix Contact tip: PTT 1,5/S-2MT | such as Phoenix Contact type: PTT 1,5/S-2MT | kos | 98
| - Sponke varovalčna (5x20), 0,5 A vložek | - Fuse clips (5x20), 0.5 A insert
| kot na primer Phoenix Contact tip: PTC 4 - HESILED 24 | such as Phoenix Contact type: PTC 4 - HESILED 24 | kos | 175
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
1.24 | Dobava in montaža kovinske omare +HVAC_K1-PLC7 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of metal cabinet +HVAC_K1-PLC7 consisting of one box with IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1200 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ.Omara je sestavljena iz dveh polj močnostno in krmilno. | The dimensions of the cabinet are: height 2000 mm, width 1200 mm and depth 400 mm. The whole cabinet stands on a base of height 200 mm. The rounded base for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforated lock.The cabinet is composed of two fields power and control.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2016402DP. | such as Schneider, type: NSYSFN2016402DP. | kos | 1
| - Podstavek 200 mm, širine 1200 mm, | - Base 200 mm, width 1200 mm,
| kot naprimer Schneider, tip: NSYSPF12200. | such as Schneider, type: NSYSPF12200. | kos | 2
| - stranica podstavka 200 mm, globine 400 mm, | - base side 200 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4200. | such as Schneider, type: NSYSPS4200. | kos | 2
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1200 mm, | - Lower crossbar with PanelSeT cable entry - 1200 mm,
| kot naprimer Rittal, tip: 2388.125. | such as Rittal, type: 2388.125. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Rittal, tip: 2388.100. | such as Rittal, type: 2388.100. | kos | 70
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Rittal, tip: 7077.000. | such as Rittal, type: 7077.000. | kos | 30
| POLJE 1:V močnostno omaro +HVAC_K1-R7 se dobavi in vgradi naslednja elektro oprema: | BOX 1:The following electrical equipment shall be supplied and installed in the +HVAC_K1-R7 power cabinet:
| - glavno stikalo In=50 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=50 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C113050LS. | such as Schneider, type: C113050LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Motorski odklopnik 3P, 1,6 - 2,5 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 1,6 - 2,5 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P07 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P07 + GVAN11. | kos | 1
| - Motorski odklopnik 3P, 4 - 6,3 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 4 - 6.3 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P10 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P10 + GVAN11. | kos | 4
| - Motorski odklopnik 3P, 6 - 10 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 6 - 10 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P14 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P14 + GVAN11. | kos | 1
| - Štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 20 kA, | - 40 A, four-pole circuit breaker with C characteristic, 20 kA,
| kot naprimer Schneider, Acti 9 iC60L, tip: A9F84440. | such as Schneider, Acti 9 iC60L, type: A9F84440. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 2
| - Tripolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84306. | such as Schneider, Acti 9 iC60H, type: A9F84306. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 1
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 1
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21. | such as Phoenix Contact type: PLC-RSC-230UC/21. | kos | 1
| - Rele-sponka, 24 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21. | such as Phoenix Contact type: PLC-RSC-24UC/21. | kos | 1
| - Sponke 35 mm2 za montažo na DIN letev, | - 35 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 35 | such as Phoenix Contact type: UT 35 | kos | 3
| - Sponke 2,5 mm2 vzmetne priklop motorjev za montažo na DIN letev, | - 2.5 mm2 spring clips for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5-PE/3L | such as Phoenix Contact type: PT 2,5-PE/3L | kos | 6
| - Sponke 4 mm2 vzmetne priklop motorjev za montažo na DIN letev, | - 4 mm2 spring clips for DIN rail mounting,
| - Sponke 1,5 mm2 vmznetna dvonivojska za montažo na DIN letev, | - 1,5 mm2 clips in two-level DIN rail mounting,
| kot na primer Phoenix Contact tip: PTTB 1,5/S | such as Phoenix Contact type: PTTB 1,5/S | kos | 13
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
| POLJE 2: V krmilno omaro +HVAC_K1-PLC7 se dobavi in vgradi naslednja elektro oprema: | BOX 2: The following electrical equipment shall be supplied and installed in the control cabinet +HVAC_K1-PLC7:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, | - Led cabinet light, 11W, 230V, without socket, on/off, 4000K,
| kot naprimer Rittal, tip: 2500.200. | such as Rittal, type: 2500.200. |  | 1
| - Priključni kabel za LED svetilko OR 3000mm, | - Connecting cable for LED luminaire OR 3000mm,
| kot naprimer Rittal, tip: 2500.400. | such as Rittal, type: 2500.400. | kos | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Rittal, tip: SK 3240.200. | such as Rittal, type: SK 3240.200. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Rittal, tip: SK 3240.100 + SK 3240.200. | as for example Rittal, type: SK 3240.100 + SK 3240.200. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica), | - Socket 2x RJ45 (communication socket),
| kot na primer Weidmuller tip: IE-XM-RJ45/RJ45 | such as Weidmuller type: IE-XM-RJ45/RJ45 | kos | 2
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 1
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Vgradna zelena kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed green LED signal light, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB3 + ZBZ32. | like for example Schneider tip: XB4BVB3 + ZBZ32. | kos | 1
| - Vgradna rdeča kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed red LED signal light, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB4 + ZBZ32. | like for example Schneider tip: XB4BVB4 + ZBZ32. | kos | 2
| - Vgradna modre tipke z delovnim kontaktom in nosilcem tipkala, | - Built-in blue keys with working contact and key holder,
| kot naprimer Schneider tip: XB4BA61 + ZBZ32. | like for example Schneider tip: XB4BA61 + ZBZ32. | kos | 2
| - Enotni blok za funkcijo testne luči 24 V AC DC, | - Single block for 24 V AC DC test light function,
| kot naprimer Schneider tip: ZBZG156. | such as Schneider type: ZBZG156. | kos | 3
| - Vgradna tipka za izklop v sili z gobo, 2x NC, za vgradnjo na vrata omare, komplet s ploščico, | - Emergency stop push-button with sponge, 2x NC, for mounting on cabinet doors, complete with plate,
| kot naprimer Schneider tip: XB5AT842 + ZBE102+ZBY9360. | like for example Schneider tip: XB5AT842+ZBE102+ZBY9360. | kos | 1
| - Varnostni rele za izklop v sili, izhodi 3 NO in 1 NC, napajanje 24 VDC, povezovalni modul | - Emergency stop safety relay, 3 NO and 1 NC outputs, 24 VDC power supply, connection module
| kot naprimer Siemens tip: 3SK1121-1AB40 + 3ZY1212-2DA00. | as for example Siemens type: 3SK1121-1AB40 + 3ZY1212-2DA00. | kos | 1
| - Razšeritveni varnostni rele za izklop v sili, izhodi 4 NO in 1 NC, napajanje 24 VDC, povezovalni modul (podnožje) | - Emergency trip safety relay, 4 NO and 1 NC outputs, 24 VDC power supply, connection module (base)
| kot naprimer Siemens tip: 3SK1211-1BB40 + 3ZY1212-2BA00. | such as for example Siemens type: 3SK1211-1BB40 + 3ZY1212-2BA00. | kos | 1
| - Konktaktor z dodatnim inštalacijskim priborom | - Connector with additional installation accessories
| kot naprimer Eaton, tip DILER-40-G-C(24VDC)+40DILE-C. | such as Eaton, type DILER-40-G-C(24VDC)+40DILE-C. | kos | 2
| - Rele-sponka, 230 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21. | such as Phoenix Contact type: PLC-RSC-230UC/21. | kos | 1
| - Rele-sponka, 24 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21. | such as Phoenix Contact type: PLC-RSC-24UC/21. | kos | 10
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Varnostni ločilni transformator 315 VAC/24 VAC, | - Safety isolating transformer 315 VAC/24 VAC,
| kot na primer Siemens tip: 4AM4342-4TN00-0EA0 | such as Siemens type: 4AM4342-4TN00-0EA0 | kos | 1
| - Sponke 6 mm2 za montažo na DIN letev, | - 6 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 6 | such as Phoenix Contact type: UT 6 | kos | 1
| - Sponke 1,5 mm2 več nivojske za montažo na DIN letev, | - 1.5 mm2 multi-level clips for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 1,5/S-3L | such as Phoenix Contact type: PT 1,5/S-3L | kos | 30
| - Sponke 1,5 mm2 dvo nivojska za montažo na DIN letev, | - 1.5 mm2 two-level DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PTTB 1,5/S | such as Phoenix Contact type: PTTB 1,5/S | kos | 20
| - Sponke 1,5 mm2, dvojne odklopne, za montažo na DIN letev, | - Clips 1,5 mm2, double hinged, for DIN rail mounting,
| kot na primer Phoenix Contact tip: PTT 1,5/S-2MT | such as Phoenix Contact type: PTT 1,5/S-2MT | kos | 65
| - Sponke varovalčna (5x20), 0,5 A vložek | - Fuse clips (5x20), 0.5 A insert
| kot na primer Phoenix Contact tip: PTC 4 - HESILED 24 | such as Phoenix Contact type: PTC 4 - HESILED 24 | kos | 100
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
1.25 | Dobava in montaža kovinske omare +HVAC_PREZ-ST-1; -2; -3 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of metal enclosures +HVAC_PREZ-ST-1; -2; -3 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 3 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 600 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima enokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ.Omara je sestavljena iz dveh polj močnostno in krmilno. Razdelilniki morajo ustrezati standardu SIST EN 61439-1,2 | The dimensions of the cabinet are: height 2000 mm, width 600 mm and depth 400 mm. The whole cabinet stands on a base of height 200 mm. The rounding for the base of the electrical cabinet. The cabinet has a full height single leaf door at the front, a comfort handle and a two-point keyed closure.The cabinet consists of two fields power and control. The distributors shall comply with the standard SIST EN 61439-1,2
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider. | such as Schneider. | kos | 1
| V omaro se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the cabinet:
| - glavno stikalo In=32 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=32 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Motorski odklopnik 3P, 6 - 10 A, termomagnetna zaščita, komplet z dodatnim inštalacijskim priborom, | - Motor circuit breaker 3P, 6 - 10 A, thermomagnetic protection, complete with accessories,
| kot naprimer Schneider, tip: TeSys GV2 tip: GV2P14 + GVAN11. | such as Schneider, type: TeSys GV2 type: GV2P14 + GVAN11. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Tripolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84306. | such as Schneider, Acti 9 iC60H, type: A9F84306. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 1
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 1
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21. | such as Phoenix Contact type: PLC-RSC-230UC/21. | kos | 1
| - Rele-sponka, 24 VAC/DC (1x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (1x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21. | such as Phoenix Contact type: PLC-RSC-24UC/21. | kos | 1
| - Sponke 16 mm2 za montažo na DIN letev, | - 16 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 16 | such as Phoenix Contact type: UT 16 | kos | 3
| - Sponke 2,5 mm2 vzmetne priklop motorjev za montažo na DIN letev, | - 2.5 mm2 spring clips for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5-PE/3L | such as Phoenix Contact type: PT 2,5-PE/3L | kos | 6
| - Sponke 4 mm2 vzmetne priklop motorjev za montažo na DIN letev, | - 4 mm2 spring clips for DIN rail mounting,
| - Sponke 1,5 mm2 vmznetna dvonivojska za montažo na DIN letev, | - 1.5 mm2 clips in two-level DIN rail mounting,
| kot na primer Phoenix Contact tip: PTTB 1,5/S | such as Phoenix Contact type: PTTB 1,5/S | kos | 13
| Dobava in montaža comfort enote za upravljanje napajanja, 10 A, za eno alarmno skupino in eno prezračevalno enoto.Barva: oranžna RAL 2011 Samodejno preklapljanje iz omrežja v baterijo. V nujnih primerih, z baterijo 24 V, je sistemska avtonomija zagotovljena vsaj 72 ur.Spredaj je nadzorna plošča za alarm:- gumb za ročno aktiviranje alarma, tipko za ponastavitev in LED indikacijo "alarm", "pri delu" in "napaka"- dva okrogla gumba za osvetljevanje motorja za "odprto" prezračevanje; "Close", oprema po EN54 kot naprimer GEZE ali Norica. | Supply and installation of comfort power management unit, 10 A, for one alarm group and one ventilation unit.Colour: orange RAL 2011 Automatic switchover from mains to battery. In case of emergency, with a 24 V battery, system autonomy is guaranteed for at least 72 hours.Alarm control panel on the front:- manual alarm activation button, reset button and LED indication "alarm", "in operation" and "fault"- two round buttons to illuminate the motor for "open" ventilation; "Close", equipment according to EN54, such as for example GEZE or Norica. | kos | 1
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo sistema. Pridobitev potrditve projektanta in nadzora. | Drawing up of the current diagrams of the distribution system according to the system equipment supplied. Obtaining the approval of the designer and supervision. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … Celotni sestav mora biti izveden po EN54 | Complete with electrical installation material, lead-in plates, copper bus bars, system cables, wiring, potential equalisation, cable marking, nameplates, gaskets, ... The complete assembly must be made according to EN54 | kpl | 1
1.26 | Dobava in montaža požarne tipke / tipkalo, kot naprimer GEZE ali NORICA | Supply and installation of a fire key/keypad, such as GEZE or NORICA |  |  | kpl | 17 |  | 0
1.27 | Dobava in montaža stikala za dnevno prezračevanje/ventilacijo, kot naprimer: GEZE ali NORICA | Supply and installation of a day ventilation/ventilation switch such as GEZE or NORICA |  |  | kpl | 3 |  | 0
1.28 | Montaža in ožičenje frekvenčnega pretvornika Danfoss iz serije VLT FC102 v zaščiti IP55. | Installation and wiring of the Danfoss VLT FC102 series frequency converter in IP55 protection. |  |  | kpl | 18 |  | 0
1.29 | Dobava in montaža 3 polnega servisnega stikala z možnostjo zaklepanja z obešanko, z rumeno podlogo in rdečim gumbom ter pomožnim delovnim kontaktom, nadometna montaža v zaščiti IP65, za elektromotor moči do 13kW, fa.: Eaton, tip: P1-25-I2/SVB/HI11. | Supply and installation of a 3-pole service switch with lockable padlock, with yellow lining and red button and auxiliary operating contact, overhead mounting in IP65 protection, for electric motor up to 13kW, fa.: Eaton, type: P1-25-I2/SVB/HI11. |  |  | kpl | 13 |  | 0
1.30 | Dobava in montaža 1 polnega stikala za v "Ex" območje, Eaton, tip: GHG2610005L0002. | Supply and installation of 1 pole switch for "Ex" zone, Eaton, type: GHG2610005L0002. |  |  | kpl | 5 |  | 0
1.31 | - Dobava in montaža razdelilne doze za nadometno montažo 104 x 104 mm, komplet z ranžirnimi sponkami, | - Supply and installation of a 104 x 104 mm overhead distribution box, complete with shunting clips, |  |  | kpl | 33 |  | 0
| kot na primer Phoenix Contact distribucijski blok tip: PTFIX 6x2,5 BN + distribucijski blok tip: PTFIX 6x2,5 BU + distribucijski ozemljitveni blok tip: PTFIX 6x2,5 GNYE, 2 x zaključni blok PTFIX-F | such as Phoenix Contact distribution block type: PTFIX 6x2,5 BN + distribution block type: PTFIX 6x2,5 BU + distribution earthing block type: PTFIX 6x2,5 GNYE, 2 x termination block PTFIX-F
1.32 | - Dobava in polaganje na kabelske police oz. uvlečenje v inštalacijske cevi kabla F/FTP-Category 6A, 4x2, 23 AWG, za PROFINET oz. ETHERNET komunikacijo. | - Supply and installation of F/FTP-Category 6A, 4x2, 23 AWG cable for PROFINET or ETHERNET communication on cable racks or in installation pipes. |  |  | m | 1540 |  | 0
1.33 | - Dobava in polaganje na kabelske police oz. uvlečenje v inštalacijske cevi kabla UNITRONIC BUS FD P LD 1X2X0,25, za MODBUS komunikacijo. | - Supply and installation of UNITRONIC BUS FD P LD 1X2X0,25 cable for MODBUS communication on cable racks or in installation pipes. |  |  | m | 7200 |  | 0
1.34 | - Dobava in polaganje protipožarnega kabla (klasifikacije Cca-S2-d2-a1) na kabelske police in v zaščitne cevi, | - Supply and installation of fire-fighting cable (classification Cca-S2-d2-a1) on cable racks and in protection tubes,
| kot primer LAPP: | as an example of LAPP:
| - LiHCH 2x1 mm2 | - LiHCH 2x1 mm2 |  |  | m | 33200 |  | 0
| - LiHCH 4x1 mm2 | - LiHCH 4x1 mm2 |  |  | m | 34900 |  | 0
1.35 | - Dobava in polaganje protipožarnega kabla (klasifikacije Cca-S2-d2-a1) na kabelske police in v zaščitne cevi, | - Supply and installation of fire-fighting cable (classification Cca-S2-d2-a1) on cable racks and in protection tubes,
| kot primer LAPP: | as an example of LAPP:
| - OL-100H 3G1,5 mm2 | - OL-100H 3G1,5 mm2 |  |  | m | 4100 |  | 0
| - OL-100H 4G1,5 mm2 | - OL-100H 4G1,5 mm2 |  |  | m | 4300 |  | 0
| - OL-100H 5G1,5 mm2 | - OL-100H 5G1,5 mm2 |  |  | m | 640 |  | 0
| - OL-100H 4G2,5 mm2 | - OL-100H 4G2,5 mm2 |  |  | m | 2100 |  | 0
| - OL-100H 4G4 mm2 | - OL-100H 4G4 mm2 |  |  | m | 250 |  | 0
| - OL-100H 3G4 mm2 | - OL-100H 3G4 mm2 |  |  | m | 250 |  | 0
1.36 | - Dobava in polaganje protipožarnega kabla (klasifikacije Cca-S2-d2-a1) na kabelske police in v zaščitne cevi, | - Supply and installation of fire-fighting cable (classification Cca-S2-d2-a1) on cable racks and in protection tubes,
| kot primer LAPP: | as an example of LAPP:
| - OL-110H 2x1 mm2 | - OL-110H 2x1 mm2 |  |  | m | 19200 |  | 0
| - OL-110H 3G1,5 mm2 | - OL-110H 3G1,5 mm2 |  |  | m | 720 |  | 0
| - OL-110H 4x0,75 mm2 | - OL-110H 4x0,75 mm2 |  |  | m | 3240 |  | 0
| - OL-110H 4x1 mm2 | - OL-110H 4x1 mm2 |  |  | m | 29300 |  | 0
| - OL-110H 5G1 mm2 | - OL-110H 5G1 mm2 |  |  | m | 7200 |  | 0
| - OL-110H 25G0,75 mm2 | - OL-110H 25G0,75 mm2 |  |  | m | 230 |  | 0
1.37 | - Dobava in polaganje ognje-odpornih kablov tipa JE-H(St)H Bd FE180/E30, rdeče barve, halogen free, na kabelske police in v zaščitne cevi. Pri polaganju mora biti uporabljen poseben pribor, ki je predviden za ognje-odporene kable (police, cevi, obešala, ...) in način polaganja na kabelske police in v zaščitne cevi, certifikat o ustreznostie (kabel mora biti posebej namenjen za javljanje požara). | - Supply and installation of fire-resistant cables type JE-H(St)H Bd FE180/E30, red, halogen free, on cable racks and in protective tubes. The installation must be carried out using the special accessories provided for fire-resistant cables (racks, hoses, hangers, etc.) and the method of installation on the cable racks and in the protective tubes must be certified (the cable must be specially designed for fire detection).
| kot primer LAPP: | as an example of LAPP:
| - JE-H(St)H 4x2x0,8 mm FE180/E30 - rdeče barve | - JE-H(St)H 4x2x0,8 mm FE180/E30 - red |  |  | m | 250 |  | 0
1.38 | - Dobava in polaganje ognje-odpornih kablov tipa JE-H(St)H Bd FE180/E30, rdeče barve, halogen free, na kabelske police in v zaščitne cevi. Pri polaganju mora biti uporabljen poseben pribor, ki je predviden za ognje-odporene kable (police, cevi, obešala, ...) in način polaganja na kabelske police in v zaščitne cevi, certifikat o ustreznostie (kabel mora biti posebej namenjen za javljanje požara). | - Supply and installation of fire-resistant cables type JE-H(St)H Bd FE180/E30, red, halogen free, on cable racks and in protective tubes. The installation must be carried out using the special accessories provided for fire-resistant cables (racks, hoses, hangers, etc.) and the method of installation on the cable racks and in the protective tubes must be certified (the cable must be specially designed for fire detection).
| kot primer LAPP: | as an example of LAPP:
| - NHXH-J 3x1,5 mm2 FE180/E30 | - NHXH-J 3x1,5 mm2 FE180/E30 |  |  | m | 150 |  | 0
| - NHXH-J 3x2,5 mm2 FE180/E30 | - NHXH-J 3x2,5 mm2 FE180/E30 |  |  | m | 160 |  | 0
1.39 | - Dobava in polaganje kabla za EX na kabelske police in v zaščitne cevi EX, | - Supply and installation of EX cable on cable racks and in EX protection tubes,
| kot primer LAPP: | as an example of LAPP:
| - ÖLFLEX EB CY 3X1 mm2 | - ÖLFLEX EB CY 3X1 mm2 |  |  | m | 620 |  | 0
1.40 | - Sistem SB-ES, BETAfixss, E30/E90, razmik med objemkami < 800mm. Ob montaži upoštevati navodila proizvajalca: | - System SB-ES, BETAfixss, E30/E90, clamp spacing < 800mm. Follow manufacturer's instructions for installation:
| - ESM 6-8 M6 enostavna objemka | - ESM 6-8 M6 single clamp |  |  | m | 620 |  | 0
| - zidni vložek FNA M6x45 | - fNA wall insert M6x45 |  |  | m | 620 |  | 0
1.41 | Dobava in montaža vodnikov za izenačevanje potencialov: | Supply and installation of equipotential bonding conductors:
| - HO7V-K 6 mm2 | - HO7V-K 6 mm2 |  |  | m | 710 |  | 0
| - HO7V-K 10 mm2 | - HO7V-K 10 mm2 |  |  | m | 320 |  | 0
| - HO7V-K 16 mm2 | - HO7V-K 16 mm2 |  |  | m | 300 |  | 0
| - HO7V-K 25 mm2 | - HO7V-K 25 mm2 |  |  | m | 210 |  | 0
| - HO7V-K 50 mm2 | - HO7V-K 50 mm2 |  |  | m | 130 |  | 0
1.42 | Premostitve prirobnic in stikov na prezračevalnih kanalih in cevovodih ( Cu pletenica 35 mm2) | Bridging of flanges and joints on ventilation ducts and pipelines (Cu braid 35 mm2) |  |  | kos | 1650 |  | 0
1.43 | Dobava in polaganje pocinkanih kabelskih polic s pokrovom ter spojnim in pritrdilnim materialom. - PK50 svetlo modre barve (EEx i) | Supply and installation of galvanised cable racks with cover and joining and fixing material. - PK50 light blue (EEx i) |  |  | kos | 210 |  | 0
1.44 | Dobava in montaža kabelskih polic STAGO (alternativa ELBA, BAKS, OPTIMA-SF z enakovrednimi tehničnimi lastnismi), komplet s pritrdilnim priborom, obešalnim priborom, koleni, s pokrovi, spojnim materialom in višinskimi prehodi, hladno cinkane. | Supply and installation of STAGO cable racks (alternative to ELBA, BAKS, OPTIMA-SF with equivalent technical characteristics), complete with fixing fittings, hanging fittings, elbows, with covers, fasteners and height transitions, cold galvanised.
| - polica širine 50 mm/60 mm | - shelf width 50 mm/60 mm |  |  | m | 310 |  | 0
| - polica širine 100 mm/60 mm | - shelf width 100 mm/60 mm |  |  | m | 210 |  | 0
| - polica širine 200 mm/60 mm | - shelf width 200 mm/60 mm |  |  | m | 190 |  | 0
| - polica širine 400 mm/60 mm | - shelf width 400 mm/60 mm |  |  | m | 110 |  | 0
1.45 | Dobava in montaža PN cevi fi16 do fi32, komplet s koleni | Supply and installation of PN pipes fi16 to fi32, complete with elbows |  |  | m | 2100 |  | 0
1.46 | Dobava in motaža nerjavičih jekljenih cevi, od fi=16 do fi=50mm za montažo v čiste prostore, za zaščito kablov komplet s pritrdilnim materialom. | Supply and installation of stainless steel tubes, from fi=16 to fi=50mm for installation in clean rooms, for cable protection, complete with fixing material. |  |  | m | 290 |  | 0
1.47 | Certifikati za posamezno vgrajeno opremo in sisteme za "Ex" območje certificirana s strani akreditiranega laboratorija v skladu z evropsko direktivo 2014/34/EU (ATEX 114). | Certificates for individual installed equipment and systems for the "Ex" zone certified by an accredited laboratory in accordance with European Directive 2014/34/EU (ATEX 114). |  |  | kpl | 1 |  | 0
1.48 | Dobava in montaža različnih jeklenih profilov za pomožne konstrukcije. | Supply and installation of various steel profiles for ancillary structures. |  |  | kg | 340 |  | 0
1.49 | Izdelava priključkov na novih krmilnih, regulacijskih in ostalih elementih, sondah itd. | Making connections to new controls, regulators, probes, etc. |  |  | kos | 3280 |  | 0
1.50 | Izdelava močnostnih priključkov na motornih pogonih in na ostalih močnostnih porabnikov do električne moči: | Making power connections on motor drives and other power consumers up to electrical power:
| - do moči 2,2 kW | - up to 2,2 kW |  |  | kos | 59 |  | 0
| - do moči 2,3 kW do 15,0 kW | - up to 2,3 kW up to 15,0 kW |  |  | kos | 81 |  | 0
1.51 | Pregled sistema odvoda dima in toplote s strani pooblaščene inštitucije in sodelovanje serviserja pri pregledu in pridobitev pozitivnega potrdila pooblaščene inštitucije: | Inspection of the smoke and heat extraction system by an approved institution and participation of the technician in the inspection and obtaining a positive certificate from an approved institution: |  |  | kpl | 1 |  | 0
| Klimatizacija in prezračevanje (inštalacije) | Air conditioning and ventilation (installations) | [5 empty] | 0

## 3.13.2_HVAC_HW&SW
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.13 | ELEKTRO DELA | ELECTRICAL WORKS
3.13.2 | Klimatizacija in prezračevanje (HW & SW) | Air conditioning and ventilation (HW & SW) | [5 empty] | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description |  |  | EM | Količina | Cena/EM | Cena
2 | Klimatizacija in prezračevanje (HW & SW) | Air conditioning and ventilation (HW & SW)
2.1 | Dobava PLC postaje HVAC_K1-PLC1 (locirana v +HVAC_K1-PLC1), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the PLC station HVAC_K1-PLC1 (located in +HVAC_K1-PLC1), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - digitalni vhodi (DI) | - digital Inputs (DI) | točk | 54
| - digitalni izhodi (DO) | - digital outputs (DO) | točk | 26
| - analogni vhodi (AI) | - analogue inputs (AI) | točk | 42
| - analogni izhodi (AO) | - analogue outputs (AO) | točk | 29
| - komunikacijske povezave (Ethernet, Profinet, Modbus, Profibus, ...) | - communication links (Ethernet, Profinet, Modbus, Profibus, ...) | kpl | 1
| Predvidena konfiguracija PLC postaje HVAC_K1-PLC1 (locirana v omari +HVAC_K1-PLC1), ki bo namenjena računalniškemu nadzoru in vodenju klimatizacije in prezračevanju je: | The planned configuration of the PLC station HVAC_K1-PLC1 (located in cabinet +HVAC_K1-PLC1), which will be used for computer control and management of air conditioning and ventilation is:
| - Napajalnik 24 VAC, 10 W, | - Power supply 24 VAC, 10 W,
| kot naprimer Schneider tip: SXWPS24VX10001 + | such as Schneider tip: SXWPS24VX10001 +
| podnožje SXWTBPSW110001. | base SXWTBPSW110001. | kos | 1
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port),
| kot naprimer Schneider tip: SXWASPXXX10001 + | such as Schneider tip: SXWASPXXX10001 +
| podnožje SXWTBASW110002. | base SXWTBASW110002. | kos | 1
| - Povezovalni komunikacijski kabel med moduli, 1.5 m , | - Communication cable between modules, 1.5 m ,
| kot naprimer Schneider tip: SXWSCABLE10002 | such as for example Schneider type: SXWSCABLE10002 | kos | 2
| - Digitalni vhodni (DI) modul za 16 vhodov, 24 VDC, | - Digital input (DI) module for 16 inputs, 24 VDC,
| kot naprimer Schneider tip: SXWDI16XX10001 + | such as Schneider tip: SXWDI16XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 4
| - Digitalni izhodni (DO) modul za 12 izhodov, 24 VDC, | - Digital output (DO) module for 12 outputs, 24 VDC,
| kot naprimer Schneider tip: SXWDOA12X10001 + | such as Schneider tip: SXWDOA12X10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 3
| - Analogni vhodni modul za 16 analognih vhodov UI, | - Analogue input module for 16 analogue AI inputs,
| kot naprimer Schneider tip: SXWUI16XX10001 + | such as Schneider tip: SXWUI16XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 4
| - Analogni izhodni modul za 8 analognih izhodov U, | - Analog output module for 8 analogue U outputs,
| kot naprimer Schneider tip: SXWAOV8XX10001 + | such as Schneider tip: SXWAOV8XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 4
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
2.2 | Dobava PLC postaje HVAC_K1-PLC2 (locirana v +HVAC_K1-PLC2), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the PLC station HVAC_K1-PLC2 (located in +HVAC_K1-PLC2), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - digitalni vhodi (DI) | - digital Inputs (DI) | točk | 58
| - digitalni izhodi (DO) | - digital outputs (DO) | točk | 26
| - analogni vhodi (AI) | - analogue inputs (AI) | točk | 49
| - analogni izhodi (AO) | - analogue outputs (AO) | točk | 32
| - komunikacijske povezave (Ethernet, Profinet, Modbus, Profibus, ...) | - communication links (Ethernet, Profinet, Modbus, Profibus, ...) | kpl | 1
| Predvidena konfiguracija PLC postaje HVAC_K1-PLC2 (locirana v omari +HVAC_K1-PLC2), ki bo namenjena računalniškemu nadzoru in vodenju klimatizacije in prezračevanju je: | The planned configuration of the PLC station HVAC_K1-PLC2 (located in cabinet +HVAC_K1-PLC2), which will be used for computer control and management of air conditioning and ventilation is:
| - Napajalnik 24 VAC, 10 W, | - Power supply 24 VAC, 10 W,
| kot naprimer Schneider tip: SXWPS24VX10001 + | such as Schneider tip: SXWPS24VX10001 +
| podnožje SXWTBPSW110001. | base SXWTBPSW110001. | kos | 1
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port),
| kot naprimer Schneider tip: SXWASPXXX10001 + | such as Schneider tip: SXWASPXXX10001 +
| podnožje SXWTBASW110002. | base SXWTBASW110002. | kos | 1
| - Povezovalni komunikacijski kabel med moduli, 1.5 m , | - Communication cable between modules, 1.5 m ,
| kot naprimer Schneider tip: SXWSCABLE10002 | such as for example Schneider type: SXWSCABLE10002 | kos | 2
| - Digitalni vhodni (DI) modul za 16 vhodov, 24 VDC, | - Digital input (DI) module for 16 inputs, 24 VDC,
| kot naprimer Schneider tip: SXWDI16XX10001 + | such as Schneider tip: SXWDI16XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 4
| - Digitalni izhodni (DO) modul za 12 izhodov, 24 VDC, | - Digital output (DO) module for 12 outputs, 24 VDC,
| kot naprimer Schneider tip: SXWDOA12X10001 + | such as Schneider tip: SXWDOA12X10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 3
| - Analogni vhodni modul za 16 analognih vhodov UI, | - Analogue input module for 16 analogue AI inputs,
| kot naprimer Schneider tip: SXWUI16XX10001 + | such as Schneider tip: SXWUI16XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 4
| - Analogni izhodni modul za 8 analognih izhodov U, | - Analog output module for 8 analogue U outputs,
| kot naprimer Schneider tip: SXWAOV8XX10001 + | such as Schneider tip: SXWAOV8XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 4
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
2.3 | Dobava PLC postaje HVAC_K1-PLC3 (locirana v +HVAC_K1-PLC3), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the PLC station HVAC_K1-PLC3 (located in +HVAC_K1-PLC3), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - digitalni vhodi (DI) | - digital Inputs (DI) | točk | 62
| - digitalni izhodi (DO) | - digital outputs (DO) | točk | 26
| - analogni vhodi (AI) | - analogue inputs (AI) | točk | 46
| - analogni izhodi (AO) | - analogue outputs (AO) | točk | 31
| - komunikacijske povezave (Ethernet, Profinet, Modbus, Profibus, ...) | - communication links (Ethernet, Profinet, Modbus, Profibus, ...) | kpl | 1
| Predvidena konfiguracija PLC postaje HVAC_K1-PLC3 (locirana v omari +HVAC_K1-PLC3), ki bo namenjena računalniškemu nadzoru in vodenju klimatizacije in prezračevanju je: | The planned configuration of the PLC station HVAC_K1-PLC3 (located in cabinet +HVAC_K1-PLC3), which will be used for computer control and management of air conditioning and ventilation is:
| - Napajalnik 24 VAC, 10 W, | - Power supply 24 VAC, 10 W,
| kot naprimer Schneider tip: SXWPS24VX10001 + | such as Schneider tip: SXWPS24VX10001 +
| podnožje SXWTBPSW110001. | base SXWTBPSW110001. | kos | 1
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port),
| kot naprimer Schneider tip: SXWASPXXX10001 + | such as Schneider tip: SXWASPXXX10001 +
| podnožje SXWTBASW110002. | base SXWTBASW110002. | kos | 1
| - Povezovalni komunikacijski kabel med moduli, 1.5 m , | - Communication cable between modules, 1.5 m ,
| kot naprimer Schneider tip: SXWSCABLE10002 | such as for example Schneider type: SXWSCABLE10002 | kos | 1
| - Digitalni vhodni (DI) modul za 16 vhodov, 24 VDC, | - Digital input (DI) module for 16 inputs, 24 VDC,
| kot naprimer Schneider tip: SXWDI16XX10001 + | such as Schneider tip: SXWDI16XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 4
| - Digitalni izhodni (DO) modul za 12 izhodov, 24 VDC, | - Digital output (DO) module for 12 outputs, 24 VDC,
| kot naprimer Schneider tip: SXWDOA12X10001 + | such as Schneider tip: SXWDOA12X10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 3
| - Analogni vhodni modul za 16 analognih vhodov UI, | - Analogue input module for 16 analogue AI inputs,
| kot naprimer Schneider tip: SXWUI16XX10001 + | such as Schneider tip: SXWUI16XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 3
| - Analogni izhodni modul za 8 analognih izhodov U, | - Analog output module for 8 analogue U outputs,
| kot naprimer Schneider tip: SXWAOV8XX10001 + | such as Schneider tip: SXWAOV8XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 4
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
2.4 | Dobava PLC postaje HVAC_K1-PLC4 (locirana v +HVAV_K1-PLC4), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the PLC station HVAC_K1-PLC4 (located in +HVAV_K1-PLC4), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - digitalni vhodi (DI) | - digital Inputs (DI) | točk | 54
| - digitalni izhodi (DO) | - digital outputs (DO) | točk | 26
| - analogni vhodi (AI) | - analogue inputs (AI) | točk | 42
| - analogni izhodi (AO) | - analogue outputs (AO) | točk | 29
| - komunikacijske povezave (Ethernet, Profinet, Modbus, Profibus, ...) | - communication links (Ethernet, Profinet, Modbus, Profibus, ...) | kpl | 1
| Predvidena konfiguracija PLC postaje HVAC_K1-PLC4 (locirana v omari +HVAC_K1-PLC4), ki bo namenjena računalniškemu nadzoru in vodenju klimatizacije in prezračevanju je: | The planned configuration of the PLC station HVAC_K1-PLC4 (located in cabinet +HVAC_K1-PLC4), which will be used for computer control and management of air conditioning and ventilation is:
| - Napajalnik 24 VAC, 10 W, | - Power supply 24 VAC, 10 W,
| kot naprimer Schneider tip: SXWPS24VX10001 + | such as Schneider tip: SXWPS24VX10001 +
| podnožje SXWTBPSW110001. | base SXWTBPSW110001. | kos | 1
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port),
| kot naprimer Schneider tip: SXWASPXXX10001 + | such as Schneider tip: SXWASPXXX10001 +
| podnožje SXWTBASW110002. | base SXWTBASW110002. | kos | 1
| - Povezovalni komunikacijski kabel med moduli, 1.5 m , | - Communication cable between modules, 1.5 m ,
| kot naprimer Schneider tip: SXWSCABLE10002 | such as for example Schneider type: SXWSCABLE10002 | kos | 1
| - Digitalni vhodni (DI) modul za 16 vhodov, 24 VDC, | - Digital input (DI) module for 16 inputs, 24 VDC,
| kot naprimer Schneider tip: SXWDI16XX10001 + | such as Schneider tip: SXWDI16XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 4
| - Digitalni izhodni (DO) modul za 12 izhodov, 24 VDC, | - Digital output (DO) module for 12 outputs, 24 VDC,
| kot naprimer Schneider tip: SXWDOA12X10001 + | such as Schneider tip: SXWDOA12X10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 3
| - Analogni vhodni modul za 16 analognih vhodov UI, | - Analogue input module for 16 analogue AI inputs,
| kot naprimer Schneider tip: SXWUI16XX10001 + | such as Schneider tip: SXWUI16XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 3
| - Analogni izhodni modul za 8 analognih izhodov U, | - Analog output module for 8 analogue U outputs,
| kot naprimer Schneider tip: SXWAOV8XX10001 + | such as Schneider tip: SXWAOV8XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 4
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
2.5 | Dobava PLC postaje HVAC_K1-PLC5 (locirana v +HVAC_K1-PLC5), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the PLC station HVAC_K1-PLC5 (located in +HVAC_K1-PLC5), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - digitalni vhodi (DI) | - digital Inputs (DI) | točk | 131
| - digitalni izhodi (DO) | - digital outputs (DO) | točk | 72
| - analogni vhodi (AI) | - analogue inputs (AI) | točk | 60
| - analogni izhodi (AO) | - analogue outputs (AO) | točk | 75
| - komunikacijske povezave (Ethernet, Profinet, Modbus, Profibus, ...) | - communication links (Ethernet, Profinet, Modbus, Profibus, ...) | kpl | 5
| Predvidena konfiguracija PLC postaje HVAC_K1-PLC5 (locirana v omari +HVACK11-PLC5), ki bo namenjena računalniškemu nadzoru in vodenju klimatizacije in prezračevanju je: | The planned configuration of the PLC station HVAC_K1-PLC5 (located in cabinet +HVACK11-PLC5), which will be used for computer control and management of air conditioning and ventilation is:
| - Napajalnik 24 VAC, 10 W, | - Power supply 24 VAC, 10 W,
| kot naprimer Schneider tip: SXWPS24VX10001 + | such as Schneider tip: SXWPS24VX10001 +
| podnožje SXWTBPSW110001. | base SXWTBPSW110001. | kos | 3
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port),
| kot naprimer Schneider tip: SXWASPXXX10001 + | such as Schneider tip: SXWASPXXX10001 +
| podnožje SXWTBASW110002. | base SXWTBASW110002. | kos | 2
| - Povezovalni komunikacijski kabel med moduli, 1.5 m , | - Communication cable between modules, 1.5 m ,
| kot naprimer Schneider tip: SXWSCABLE10002 | such as for example Schneider type: SXWSCABLE10002 | kos | 2
| - Digitalni vhodni (DI) modul za 16 vhodov, 24 VDC, | - Digital input (DI) module for 16 inputs, 24 VDC,
| kot naprimer Schneider tip: SXWDI16XX10001 + | such as Schneider tip: SXWDI16XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 9
| - Digitalni izhodni (DO) modul za 12 izhodov, 24 VDC, | - Digital output (DO) module for 12 outputs, 24 VDC,
| kot naprimer Schneider tip: SXWDOA12X10001 + | such as Schneider tip: SXWDOA12X10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 6
| - Analogni vhodni (AI) modul za 16 analognih vhodov UI, | - Analogue input (AI) module for 16 analogue AI inputs,
| kot naprimer Schneider tip: SXWUI16XX10001 + | such as Schneider tip: SXWUI16XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 4
| - Analogni izhodni (AO) modul za 8 analognih izhodov U, | - Analog output (AO) module for 8 analogue U outputs,
| kot naprimer Schneider tip: SXWAOV8XX10001 + | such as Schneider tip: SXWAOV8XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 10
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
2.6 | Dobava PLC postaje HVAC_S1-PLC1 (locirana v +HVAC_S1-PLC1), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the HVAC_S1-PLC1 PLC station (located in +HVAC_S1-PLC1), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - digitalni vhodi (DI) | - digital Inputs (DI) | točk | 60
| - digitalni izhodi (DO) | - digital outputs (DO) | točk | 21
| - analogni vhodi (AI) | - analogue inputs (AI) | točk | 52
| - analogni izhodi (AO) | - analogue outputs (AO) | točk | 51
| - komunikacijske povezave (Ethernet, Profinet, Modbus, Profibus, ...) | - communication links (Ethernet, Profinet, Modbus, Profibus, ...) | kpl | 15
| Predvidena konfiguracija PLC postaje HVAC_S1-PLC1 (locirana v omari +HVAC_S1-PLC1), ki bo namenjena računalniškemu nadzoru in vodenju klimatizacije in prezračevanju je: | The planned configuration of the PLC station HVAC_S1-PLC1 (located in cabinet +HVAC_S1-PLC1), which will be used for computer control and management of air conditioning and ventilation is:
| - Napajalnik 24 VAC, 10 W, | - Power supply 24 VAC, 10 W,
| kot naprimer Schneider tip: SXWPS24VX10001 + | such as Schneider tip: SXWPS24VX10001 +
| podnožje SXWTBPSW110001. | base SXWTBPSW110001. | kos | 4
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port),
| kot naprimer Schneider tip: SXWASPXXX10001 + | such as Schneider tip: SXWASPXXX10001 +
| podnožje SXWTBASW110002. | base SXWTBASW110002. | kos | 1
| - Povezovalni komunikacijski kabel med moduli, 1.5 m , | - Communication cable between modules, 1.5 m ,
| kot naprimer Schneider tip: SXWSCABLE10002 | such as for example Schneider type: SXWSCABLE10002 | kos | 2
| - Digitalni vhodni (DI) modul za 16 vhodov, 24 VDC, | - Digital input (DI) module for 16 inputs, 24 VDC,
| kot naprimer Schneider tip: SXWDI16XX10001 + | such as Schneider tip: SXWDI16XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 4
| - Digitalni izhodni (DO) modul za 12 izhodov, 24 VDC, | - Digital output (DO) module for 12 outputs, 24 VDC,
| kot naprimer Schneider tip: SXWDOA12X10001 + | such as Schneider tip: SXWDOA12X10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 2
| - Analogni vhodni (AI) modul za 16 analognih vhodov UI, | - Analogue input (AI) module for 16 analogue AI inputs,
| kot naprimer Schneider tip: SXWUI16XX10001 + | such as Schneider tip: SXWUI16XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 4
| - Analogni izhodni (AO) modul za 8 analognih izhodov U, | - Analog output (AO) module for 8 analogue U outputs,
| kot naprimer Schneider tip: SXWAOV8XX10001 + | such as Schneider tip: SXWAOV8XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 7
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
2.7 | Dobava PLC postaje HVAC_S1-PLC2 (locirana v +HVAC_S1-PLC2), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the HVAC_S1-PLC2 PLC station (located in +HVAC_S1-PLC2), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - digitalni vhodi (DI) | - digital Inputs (DI) | točk | 36
| - digitalni izhodi (DO) | - digital outputs (DO) | točk | 14
| - analogni vhodi (AI) | - analogue inputs (AI) | točk | 27
| - analogni izhodi (AO) | - analogue outputs (AO) | točk | 25
| - komunikacijske povezave (Ethernet, Profinet, Modbus, Profibus, ...) | - communication links (Ethernet, Profinet, Modbus, Profibus, ...) | kpl | 3
| Predvidena konfiguracija PLC postaje HVAC_S1-PLC2 (locirana v omari +HVAC_S1-PLC2), ki bo namenjena računalniškemu nadzoru in vodenju klimatizacije in prezračevanju je: | The planned configuration of the PLC station HVAC_S1-PLC2 (located in cabinet +HVAC_S1-PLC2), which will be used for computer control and management of air conditioning and ventilation is:
| - Napajalnik 24 VAC, 10 W, | - Power supply 24 VAC, 10 W,
| kot naprimer Schneider tip: SXWPS24VX10001 + | such as Schneider tip: SXWPS24VX10001 +
| podnožje SXWTBPSW110001. | base SXWTBPSW110001. | kos | 2
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port),
| kot naprimer Schneider tip: SXWASPXXX10001 + | such as Schneider tip: SXWASPXXX10001 +
| podnožje SXWTBASW110002. | base SXWTBASW110002. | kos | 1
| - Povezovalni komunikacijski kabel med moduli, 1.5 m , | - Communication cable between modules, 1.5 m ,
| kot naprimer Schneider tip: SXWSCABLE10002 | such as for example Schneider type: SXWSCABLE10002 | kos | 2
| - Digitalni vhodni (DI) modul za 16 vhodov, 24 VDC, | - Digital input (DI) module for 16 inputs, 24 VDC,
| kot naprimer Schneider tip: SXWDI16XX10001 + | such as Schneider tip: SXWDI16XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 3
| - Digitalni izhodni (DO) modul za 12 izhodov, 24 VDC, | - Digital output (DO) module for 12 outputs, 24 VDC,
| kot naprimer Schneider tip: SXWDOA12X10001 + | such as Schneider tip: SXWDOA12X10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 2
| - Analogni vhodni (AI) modul za 16 analognih vhodov UI, | - Analogue input (AI) module for 16 analogue AI inputs,
| kot naprimer Schneider tip: SXWUI16XX10001 + | such as Schneider tip: SXWUI16XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 2
| - Analogni izhodni (AO) modul za 8 analognih izhodov U, | - Analog output (AO) module for 8 analogue U outputs,
| kot naprimer Schneider tip: SXWAOV8XX10001 + | such as Schneider tip: SXWAOV8XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 4
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
2.8 | Dobava PLC postaje HVAC_S1-PLC3 (locirana v +HVAC_S1-PLC3), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the HVAC_S1-PLC3 PLC station (located in +HVAC_S1-PLC3), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - digitalni vhodi (DI) | - digital Inputs (DI) | točk | 93
| - digitalni izhodi (DO) | - digital outputs (DO) | točk | 41
| - analogni vhodi (AI) | - analogue inputs (AI) | točk | 129
| - analogni izhodi (AO) | - analogue outputs (AO) | točk | 159
| - komunikacijske povezave (Ethernet, Profinet, Modbus, Profibus, ...) | - communication links (Ethernet, Profinet, Modbus, Profibus, ...) | kpl | 51
| Predvidena konfiguracija PLC postaje HVAC_S1-PLC3 (locirana v omari +HVAC_S1-PLC3), ki bo namenjena računalniškemu nadzoru in vodenju klimatizacije in prezračevanju je: | The planned configuration of the PLC station HVAC_S1-PLC3 (located in cabinet +HVAC_S1-PLC3), which will be used for computer control and management of air conditioning and ventilation is:
| - Napajalnik 24 VAC, 10 W, | - Power supply 24 VAC, 10 W,
| kot naprimer Schneider tip: SXWPS24VX10001 + | such as Schneider tip: SXWPS24VX10001 +
| podnožje SXWTBPSW110001. | base SXWTBPSW110001. | kos | 5
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port),
| kot naprimer Schneider tip: SXWASPXXX10001 + | such as Schneider tip: SXWASPXXX10001 +
| podnožje SXWTBASW110002. | base SXWTBASW110002. | kos | 2
| - Povezovalni komunikacijski kabel med moduli, 1.5 m , | - Communication cable between modules, 1.5 m ,
| kot naprimer Schneider tip: SXWSCABLE10002 | such as for example Schneider type: SXWSCABLE10002 | kos | 5
| - Digitalni vhodni (DI) modul za 16 vhodov, 24 VDC, | - Digital input (DI) module for 16 inputs, 24 VDC,
| kot naprimer Schneider tip: SXWCOM48510001 + | such as Schneider tip: SXWCOM48510001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 6
| - Digitalni izhodni (DO) modul za 12 izhodov, 24 VDC, | - Digital output (DO) module for 12 outputs, 24 VDC,
| kot naprimer Schneider tip: SXWDOA12X10001 + | such as Schneider tip: SXWDOA12X10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 4
| - Analogni vhodni (AI) modul za 16 analognih vhodov UI, | - Analogue input (AI) module for 16 analogue AI inputs,
| kot naprimer Schneider tip: SXWUI16XX10001 + | such as Schneider tip: SXWUI16XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 9
| - Analogni izhodni (AO) modul za 8 analognih izhodov U, | - Analog output (AO) module for 8 analogue U outputs,
| kot naprimer Schneider tip: SXWAOV8XX10001 + | such as Schneider tip: SXWAOV8XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 20
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
2.9 | Dobava PLC postaje HVAC_S1-PLC4 (locirana v +HVAC_S1-PLC4), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the HVAC_S1-PLC4 PLC station (located in +HVAC_S1-PLC4), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - digitalni vhodi (DI) | - digital Inputs (DI) | točk | 48
| - digitalni izhodi (DO) | - digital outputs (DO) | točk | 22
| - analogni vhodi (AI) | - analogue inputs (AI) | točk | 51
| - analogni izhodi (AO) | - analogue outputs (AO) | točk | 36
| - komunikacijske povezave (Ethernet, Profinet, Modbus, Profibus, ...) | - communication links (Ethernet, Profinet, Modbus, Profibus, ...) | kpl | 1
| Predvidena konfiguracija PLC postaje HVAC_S1-PLC4 (locirana v omari +HVAC_S1-PLC4), ki bo namenjena računalniškemu nadzoru in vodenju klimatizacije in prezračevanju je: | The planned configuration of the PLC station HVAC_S1-PLC4 (located in cabinet +HVAC_S1-PLC4), which will be used for computer control and management of air conditioning and ventilation is:
| - Napajalnik 24 VAC, 10 W, | - Power supply 24 VAC, 10 W,
| kot naprimer Schneider tip: SXWPS24VX10001 + | such as Schneider tip: SXWPS24VX10001 +
| podnožje SXWTBPSW110001. | base SXWTBPSW110001. | kos | 2
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port),
| kot naprimer Schneider tip: SXWASPXXX10001 + | such as Schneider tip: SXWASPXXX10001 +
| podnožje SXWTBASW110002. | base SXWTBASW110002. | kos | 1
| - Povezovalni komunikacijski kabel med moduli, 1.5 m , | - Communication cable between modules, 1.5 m ,
| kot naprimer Schneider tip: SXWSCABLE10002 | such as for example Schneider type: SXWSCABLE10002 | kos | 2
| - Digitalni vhodni (DI) modul za 16 vhodov, 24 VDC, | - Digital input (DI) module for 16 inputs, 24 VDC,
| kot naprimer Schneider tip: SXWDI16XX10001 + | such as for example Schneider tip: SXWDI16XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 4
| - Digitalni izhodni (DO) modul za 12 izhodov, 24 VDC, | - Digital output (DO) module for 12 outputs, 24 VDC,
| kot naprimer Schneider tip: SXWDOA12X10001 + | such as Schneider tip: SXWDOA12X10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 2
| - Analogni vhodni modul za 16 analognih vhodov UI, | - Analogue input module for 16 analogue AI inputs,
| kot naprimer Schneider tip: SXWUI16XX10001 + | such as Schneider tip: SXWUI16XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 4
| - Analogni izhodni modul za 8 analognih izhodov U, | - Analog output module for 8 analogue U outputs,
| kot naprimer Schneider tip: SXWAOV8XX10001 + | such as Schneider tip: SXWAOV8XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 5
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
2.10 | Dobava PLC postaje HVAC_S1-PLC5 (locirana v +HVAC_S1-PLC5), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the HVAC_S1-PLC5 PLC station (located in +HVAC_S1-PLC5), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - digitalni vhodi (DI) | - digital Inputs (DI) | točk | 36
| - digitalni izhodi (DO) | - digital outputs (DO) | točk | 14
| - analogni vhodi (AI) | - analogue inputs (AI) | točk | 26
| - analogni izhodi (AO) | - analogue outputs (AO) | točk | 19
| - komunikacijske povezave (Ethernet, Profinet, Modbus, Profibus, ...) | - communication links (Ethernet, Profinet, Modbus, Profibus, ...) | kpl | 2
| Predvidena konfiguracija PLC postaje HVAC_S1-PLC5 (locirana v omari +HVAC_S1-PLC5), ki bo namenjena računalniškemu nadzoru in vodenju klimatizacije in prezračevanju je: | The planned configuration of the PLC station HVAC_S1-PLC5 (located in cabinet +HVAC_S1-PLC5), which will be used for computer control and management of air conditioning and ventilation is:
| - Napajalnik 24 VAC, 10 W, | - Power supply 24 VAC, 10 W,
| kot naprimer Schneider tip: SXWPS24VX10001 + | such as Schneider tip: SXWPS24VX10001 +
| podnožje SXWTBPSW110001. | base SXWTBPSW110001. | kos | 2
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port),
| kot naprimer Schneider tip: SXWASPXXX10001 + | such as Schneider tip: SXWASPXXX10001 +
| podnožje SXWTBASW110002. | base SXWTBASW110002. | kos | 1
| - Povezovalni komunikacijski kabel med moduli, 1.5 m , | - Communication cable between modules, 1.5 m ,
| kot naprimer Schneider tip: SXWSCABLE10002 | such as for example Schneider type: SXWSCABLE10002 | kos | 2
| - Digitalni vhodni (DI) modul za 16 vhodov, 24 VDC, | - Digital input (DI) module for 16 inputs, 24 VDC,
| kot naprimer Schneider tip: SXWDI16XX10001 + | such as Schneider tip: SXWDI16XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 3
| - Digitalni izhodni (DO) modul za 12 izhodov, 24 VDC, | - Digital output (DO) module for 12 outputs, 24 VDC,
| kot naprimer Schneider tip: SXWDOA12X10001 + | such as Schneider tip: SXWDOA12X10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 2
| - Analogni vhodni modul za 16 analognih vhodov UI, | - Analogue input module for 16 analogue AI inputs,
| kot naprimer Schneider tip: SXWUI16XX10001 + | such as Schneider tip: SXWUI16XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 2
| - Analogni izhodni modul za 8 analognih izhodov U, | - Analog output module for 8 analogue U outputs,
| kot naprimer Schneider tip: SXWAOV8XX10001 + | such as Schneider tip: SXWAOV8XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 3
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
2.11 | Dobava PLC postaje HVAC_S1-PLC6 (locirana v +HVAC_S1-PLC5), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the PLC station HVAC_S1-PLC6 (located in +HVAC_S1-PLC5), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - digitalni vhodi (DI) | - digital Inputs (DI) | točk | 79
| - digitalni izhodi (DO) | - digital outputs (DO) | točk | 33
| - analogni vhodi (AI) | - analogue inputs (AI) | točk | 134
| - analogni izhodi (AO) | - analogue outputs (AO) | točk | 114
| - komunikacijske povezave (Ethernet, Profinet, Modbus, Profibus, ...) | - communication links (Ethernet, Profinet, Modbus, Profibus, ...) | kpl | 42
| Predvidena konfiguracija PLC postaje HVAC_S1-PLC6 (locirana v omari +HVAC_S1-PLC6), ki bo namenjena računalniškemu nadzoru in vodenju klimatizacije in prezračevanju je: | The planned configuration of the PLC station HVAC_S1-PLC6 (located in cabinet +HVAC_S1-PLC6), which will be used for computer control and management of air conditioning and ventilation is:
| - Napajalnik 24 VAC, 10 W, | - Power supply 24 VAC, 10 W,
| kot naprimer Schneider tip: SXWPS24VX10001 + | such as Schneider tip: SXWPS24VX10001 +
| podnožje SXWTBPSW110001. | base SXWTBPSW110001. | kos | 5
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port),
| kot naprimer Schneider tip: SXWASPXXX10001 + | such as Schneider tip: SXWASPXXX10001 +
| podnožje SXWTBASW110002. | base SXWTBASW110002. | kos | 2
| - Povezovalni komunikacijski kabel med moduli, 1.5 m , | - Communication cable between modules, 1.5 m ,
| kot naprimer Schneider tip: SXWSCABLE10002 | such as for example Schneider type: SXWSCABLE10002 | kos | 3
| - Digitalni vhodni (DI) modul za 16 vhodov, 24 VDC, | - Digital input (DI) module for 16 inputs, 24 VDC,
| kot naprimer Schneider tip: SXWDI16XX10001 + | such as Schneider tip: SXWDI16XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 6
| - Digitalni izhodni (DO) modul za 12 izhodov, 24 VDC, | - Digital output (DO) module for 12 outputs, 24 VDC,
| kot naprimer Schneider tip: SXWDOA12X10001 + | such as Schneider tip: SXWDOA12X10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 4
| - Analogni vhodni modul za 16 analognih vhodov UI, | - Analogue input module for 16 analogue AI inputs,
| kot naprimer Schneider tip: SXWUI16XX10001 + | such as Schneider tip: SXWUI16XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 9
| - Analogni izhodni modul za 8 analognih izhodov U, | - Analog output module for 8 analogue U outputs,
| kot naprimer Schneider tip: SXWAOV8XX10001 + | such as Schneider tip: SXWAOV8XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 15
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
2.12 | Dobava PLC postaje HVAC_N1-PLC6 (locirana v +HVAC_S1-PLC6), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the PLC station HVAC_N1-PLC6 (located in +HVAC_S1-PLC6), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - digitalni vhodi (DI) | - digital Inputs (DI) | točk | 55
| - digitalni izhodi (DO) | - digital outputs (DO) | točk | 24
| - analogni vhodi (AI) | - analogue inputs (AI) | točk | 40
| - analogni izhodi (AO) | - analogue outputs (AO) | točk | 65
| - komunikacijske povezave (Ethernet, Profinet, Modbus, Profibus, ...) | - communication links (Ethernet, Profinet, Modbus, Profibus, ...) | kpl | 15
| Predvidena konfiguracija PLC postaje HVAC_N1-PLC6 (locirana v omari +HVAC_N1-PLC6), ki bo namenjena računalniškemu nadzoru in vodenju klimatizacije in prezračevanju je: | The planned configuration of the PLC station HVAC_N1-PLC6 (located in cabinet +HVAC_N1-PLC6), which will be used for computer control and management of air conditioning and ventilation is:
| - Napajalnik 24 VAC, 10 W, | - Power supply 24 VAC, 10 W,
| kot naprimer Schneider tip: SXWPS24VX10001 + | such as Schneider tip: SXWPS24VX10001 +
| podnožje SXWTBPSW110001. | base SXWTBPSW110001. | kos | 3
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port),
| kot naprimer Schneider tip: SXWASPXXX10001 + | such as Schneider tip: SXWASPXXX10001 +
| podnožje SXWTBASW110002. | base SXWTBASW110002. | kos | 1
| - Povezovalni komunikacijski kabel med moduli, 1.5 m , | - Communication cable between modules, 1.5 m ,
| kot naprimer Schneider tip: SXWSCABLE10002 | such as for example Schneider type: SXWSCABLE10002 | kos | 3
| - Digitalni vhodni (DI) modul za 16 vhodov, 24 VDC, | - Digital input (DI) module for 16 inputs, 24 VDC,
| kot naprimer Schneider tip: SXWDI16XX10001 + | such as for example Schneider tip: SXWDI16XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 4
| - Digitalni izhodni (DO) modul za 12 izhodov, 24 VDC, | - Digital output (DO) module for 12 outputs, 24 VDC,
| kot naprimer Schneider tip: SXWDOA12X10001 + | such as Schneider tip: SXWDOA12X10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 3
| - Analogni vhodni modul za 16 analognih vhodov UI, | - Analogue input module for 16 analogue AI inputs,
| kot naprimer Schneider tip: SXWUI16XX10001 + | such as Schneider tip: SXWUI16XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 3
| - Analogni izhodni modul za 8 analognih izhodov U, | - Analog output module for 8 analogue U outputs,
| kot naprimer Schneider tip: SXWAOV8XX10001 + | such as Schneider tip: SXWAOV8XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 9
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
2.13 | Dobava PLC postaje HVAC_K1-PLC7 (locirana v +HVAC_K1-PLC7), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the PLC station HVAC_K1-PLC7 (located in +HVAC_K1-PLC7), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - digitalni vhodi (DI) | - digital Inputs (DI) | točk | 19
| - digitalni izhodi (DO) | - digital outputs (DO) | točk | 12
| - analogni vhodi (AI) | - analogue inputs (AI) | točk | 4
| - analogni izhodi (AO) | - analogue outputs (AO) | točk | 4
| - komunikacijske povezave (Ethernet, Profinet, Modbus, Profibus, ...) | - communication links (Ethernet, Profinet, Modbus, Profibus, ...) | kpl | 3
| Predvidena konfiguracija PLC postaje HVAC_K1-PLC7 (locirana v omari +HVAC_K1-PLC7), ki bo namenjena računalniškemu nadzoru in vodenju klimatizacije in prezračevanju je: | The planned configuration of the PLC station HVAC_K1-PLC7 (located in cabinet +HVAC_K1-PLC7), which will be used for computer control and management of air conditioning and ventilation is:
| - Napajalnik 24 VAC, 10 W, | - Power supply 24 VAC, 10 W,
| kot naprimer Schneider tip: SXWPS24VX10001 + | such as Schneider tip: SXWPS24VX10001 +
| podnožje SXWTBPSW110001. | base SXWTBPSW110001. | kos | 1
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port),
| kot naprimer Schneider tip: SXWASPXXX10001 + | such as Schneider tip: SXWASPXXX10001 +
| podnožje SXWTBASW110002. | base SXWTBASW110002. | kos | 1
| - Povezovalni komunikacijski kabel med moduli, 1.5 m , | - Communication cable between modules, 1.5 m ,
| kot naprimer Schneider tip: SXWSCABLE10002 | such as for example Schneider type: SXWSCABLE10002 | kos | 3
| - Digitalni vhodni (DI) modul za 16 vhodov, 24 VDC, | - Digital input (DI) module for 16 inputs, 24 VDC,
| kot naprimer Schneider tip: SXWDI16XX10001 + | such as Schneider tip: SXWDI16XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 2
| - Digitalni izhodni (DO) modul za 12 izhodov, 24 VDC, | - Digital output (DO) module for 12 outputs, 24 VDC,
| kot naprimer Schneider tip: SXWDOA12X10001 + | such as Schneider tip: SXWDOA12X10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 2
| - Analogni vhodni modul za 16 analognih vhodov UI, | - Analogue input module for 16 analogue AI inputs,
| kot naprimer Schneider tip: SXWUI16XX10001 + | such as Schneider tip: SXWUI16XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 1
| - Analogni izhodni modul za 8 analognih izhodov U, | - Analog output module for 8 analogue U outputs,
| kot naprimer Schneider tip: SXWAOV8XX10001 + | such as Schneider tip: SXWAOV8XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 1
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
2.14 | Dobava, parametriranje in zagon frekvenčnega pretvornika Danfoss iz serije VLT FC102 v zaščiti IP55, komplet s filtrom, mrežno dušilko, LCD grafičnim krmilnim panelom, Profinet komunikacijsko kartico, kartico za priključitev PTC zaščite ter Safe-stop funkcijo in montažno ploščo. | Supply, parameterisation and commissioning of a Danfoss VLT FC102 series frequency converter in IP55 protection, complete with filter, mains choke, LCD graphic control panel, Profinet communication card, PTC protection connection card, safe-stop function and mounting plate.
| - frekvenčni pretvornik za elektromotor nazivne moči 0,37 kW. | - frequency converter for an electric motor rated at 0.37 kW. |  |  | kpl | 1 |  | 0
| - frekvenčni pretvornik za elektromotor nazivne moči 0,75 kW. | - frequency converter for an electric motor rated at 0.75 kW. |  |  | kpl | 1 |  | 0
| - frekvenčni pretvornik za elektromotor nazivne moči 1,1 kW. | - frequency inverter for an electric motor rated at 1.1 kW. |  |  | kpl | 4 |  | 0
| - frekvenčni pretvornik za elektromotor nazivne moči 1,4 kW. | - frequency inverter for 1.4 kW electric motor. |  |  | kpl | 1 |  | 0
| - frekvenčni pretvornik za elektromotor nazivne moči 4 kW. | - frequency converter for a 4 kW electric motor. |  |  | kpl | 3 |  | 0
| - frekvenčni pretvornik za elektromotor nazivne moči 2,2 kW. | - frequency converter for electric motor rated at 2.2 kW. |  |  | kpl | 3 |  | 0
2.15 | Frekvenčni pretvornik z mrežno dušilko in filtrom (razred C2 po EN 61800-3), zaščita IP54, komunikacijska kartica(Profinet) MCA120, PTC kartica (Safe Stop - STO) MCB112 za pogone v Ex izvedbi. Danfoss, serija FC102. | Frequency converter with mains choke and filter (class C2 according to EN 61800-3), protection IP54, communication card (Profinet) MCA120, PTC card (Safe Stop - STO) MCB112 for actuators in Ex version. Danfoss, FC102 series.
| - frekvenčni pretvornik za elektromotor nazivne moči 0,18 kW. | - frequency converter for an electric motor rated at 0.18 kW. |  |  | kpl | 2 |  | 0
| - frekvenčni pretvornik za elektromotor nazivne moči 0,37 kW. | - frequency converter for an electric motor rated at 0.37 kW. |  |  | kpl | 1 |  | 0
| - frekvenčni pretvornik za elektromotor nazivne moči 7,5 kW. | - frequency converter for an electric motor rated at 7.5 kW. |  |  | kpl | 1 |  | 0
| - frekvenčni pretvornik za elektromotor nazivne moči 11,0 kW. | - frequency converter for an electric motor rated at 11.0 kW. |  |  | kpl | 1 |  | 0
2.16 | Dobava, Izdelava, inštalacija, testiranje in spuščanje v pogon sistemske programske opreme PLC in SCADA za sisteme nadzora HVAC v skladu s P&ID shemami, funkcijskih zahtev in zahtev naročnika oziroma uporabnika. OPOMBA: SCADA nadzorni sistem je potrebno izdelati skupen za cel objekt in možnost ločenega prikaza in vodenja za posamezni oddelek. | Supply, Manufacture, installation, testing and commissioning of PLC and SCADA system software for HVAC control systems in accordance with P&ID diagrams, functional requirements and customer or user requirements. NOTE: The SCADA control system should be common for the whole building and the possibility of separate display and management for each department. |  |  | kpl | 1 |  | 0
| - izdelava vizualizacijskih prikazov na SCADA sistemu-skupen; | - creating visualisation displays on a SCADA system - common; | kos | 5
| - izdelava vizualizacijskih prikazov na SCADA sistemu-posamezni laboratoriski oddelek; ocenjeno | - creation of visualisation displays on SCADA system - individual laboratory department; evaluated | kos | 35
| - parametriranje signalov, alarmov in zgodovine; | - parameterisation of signals, alarms and history; | kpl | 1
| - izdelava in vzpostavitev delovanja celotnega sistema preko preglednih grafičnih prikazov in sinoptičnih slik, izdelanih v skladu z zahtevami s strani naročnika; | - the production and set-up of the entire system through clear graphical displays and synoptic images, produced in accordance with the customer's requirements; | kpl | 1
| - izdelava podatkovne baze, | - creation of a database, | kpl | 1
| - izdelava gonilnikov za povezavo sistemov na SCADA sistem. Dodati vizualizacijske prikaze, dodati bazo podatkov, alarmov in zgodovino za sistem; | - creation of drivers to connect the systems to the SCADA system. Add visualisation displays, add database, alarms and history for the system; | kpl | 1
| - izdelava in dokumentiranje xDS - Design Specification (FS - Functional Specification, HDS - Hardware Design Specification in SDS - Software Design Specification); | - creation and documentation of xDS - Design Specification (FS - Functional Specification, HDS - Hardware Design Specification and SDS - Software Design Specification); | kpl | 1
| - izvedba in dokumentiranje IQ/OQ/QTZ/ZP; | - iQ/OQ/QTZ/ZP implementation and documentation; | kpl | 1
| - dobava vseh potrebnih SW licenc za SCADA sistem; | - supply of all necessary software licences for the SCADA system; | kpl | 1
| - izvedba komunikacijskega vmesnika s samostojnimi napravami za potrebe delovanja in nadzora in prikaz osnovnih statusov delovanja na SCADA sistemu; | - implementation of a communication interface with stand-alone devices for operation and control purposes and display of basic operational statuses on the SCADA system; | kpl | 1
| - izvedba komunikacijskega vmesnika in integracije v centralni Historian za naslednje podatke -Procesne vrednosti | - implementation of a communication interface and integration into the central Historian for the following data -Process values | kpl | 1
| OPOMBA: pred izdelavo sistemske programske opreme je potrebno v sodelovanju z investitorjem izdelati detajlno funkcionalno specifikacijo. | NOTE: Before the system software can be developed, a detailed functional specification must be drawn up in cooperation with the investor.
| OPOMBA: izdelana programska oprema mora zadovoljevati zahteve strojno-tehnološkega projekta, elektro projekta, investitorja ter mora biti ustrezno dokumentirana na zapisljivem mediju! | NOTE: The software developed must satisfy the requirements of the mechanical engineering project, the electrical project, the investor and must be properly documented on a recordable medium!
| OPOMBA: računalnik za SCADA nadzorni sistem s OS win10 dobavi naročnik. | NOTE: The computer for the SCADA control system with win10 OS shall be supplied by the customer.
| Klimatizacija in prezračevanje (HW & SW) | Air conditioning and ventilation (HW & SW) | [5 empty] | 0

## 3.13.3_ENS_INŠ
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.13 | ELEKTRO DELA | ELECTRICAL WORKS
3.13.3 | Energetika (inštalacije) | Energy (installations) | [5 empty] | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description |  |  | EM | Količina | Cena/EM | Cena
3 | Energetika (inštalacije) | Energy (installations)
3.1 | Dobava in montaža kovinske omare +ENS_K1-R1 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of metal cabinet +ENS_K1-R1 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1000 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1000 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2010402DP. | such as Schneider, type: NSYSFN2010402DP. | kos | 1
| - Podstavek 200 mm, širine 1000 mm, | - Base 200 mm, width 1000 mm,
| kot naprimer Schneider, tip: NSYSPF10200. | such as Schneider, type: NSYSPF10200. | kos | 2
| - stranica podstavka 200 mm, globine 400 mm, | - base side 200 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4200. | such as Schneider, type: NSYSPS4200. | kos | 2
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1000 mm, | - Lower crossbar with PanelSeT cable entry - 1000 mm,
| kot naprimer Rittal, tip: 2388.050. | such as Rittal, type: 2388.050. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Rittal, tip: 2388.100. | such as Rittal, type: 2388.100. | kos | 25
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Rittal, tip: 7077.000. | such as Rittal, type: 7077.000. | kos | 20
| V močnostno omaro +ENS_K1-R1 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +ENS_K1-R1 power cabinet:
| - glavno stikalo In=630 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=630 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of installing a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C633630S. | such as Schneider, type: C633630S. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV432598T. | such as Schneider, type: LV432598T. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, | - Led cabinet light, 11W, 230V, without socket, on/off, 4000K,
| kot naprimer Rittal, tip: 2500.200. | such as Rittal, type: 2500.200. | kos | 1
| - Priključni kabel za LED svetilko OR 3000mm, | - Connecting cable for LED luminaire OR 3000mm,
| kot naprimer Rittal, tip: 2500.400. | such as Rittal, type: 2500.400. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10, 3x38 mm - varovalka gG 1A, | - Fuse disconnector 2P, 25 A, for fuse 10, 3x38 mm - fuse gG 1A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 20 kA, | - 40 A, four-pole circuit breaker with C characteristic, 20 kA,
| kot naprimer Schneider, Acti 9 iC60L, tip: A9F84440. | such as Schneider, Acti 9 iC60L, type: A9F84440. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 1
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 3
| - Pomožni kontakt 2 C/O za inštalacijski odklopnik, | - Auxiliary contact 2 C/O for the installation circuit breaker,
| kot naprimer Schneider, Acti9 A9A iOF, tip: A9A26909. | such as Schneider, Acti9 A9A iOF, type: A9A26909. | kos | 2
| - Tripolni inštalacijski odklopnik 32 A, s C karakteristiko, 15 kA, | - Tripolar 32 A installation circuit breaker, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84332. | such as Schneider, Acti 9 iC60H, type: A9F84332. | kos | 3
| - Pomožni kontakt 2 C/O za inštalacijski odklopnik, | - Auxiliary contact 2 C/O for the installation circuit breaker,
| kot naprimer Schneider, Acti9 A9A iOF, tip: A9A26909. | such as Schneider, Acti9 A9A iOF, type: A9A26909. | kos | 3
| - Tripolni inštalacijski odklopnik 25 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 25 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84325. | such as Schneider, Acti 9 iC60H, type: A9F84325. | kos | 9
| - Pomožni kontakt 2 C/O za inštalacijski odklopnik, | - Auxiliary contact 2 C/O for the installation circuit breaker,
| kot naprimer Schneider, Acti9 A9A iOF, tip: A9A26909. | such as Schneider, Acti9 A9A iOF, type: A9A26909. | kos | 9
| - Tripolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Tripolar 16 A, C-characteristic, 15 kA installation circuit breaker,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84316. | such as Schneider, Acti 9 iC60H, type: A9F84316. | kos | 3
| - Pomožni kontakt 2 C/O za inštalacijski odklopnik, | - Auxiliary contact 2 C/O for the installation circuit breaker,
| kot naprimer Schneider, Acti9 A9A iOF, tip: A9A26909. | such as Schneider, Acti9 A9A iOF, type: A9A26909. | kos | 3
| - Tripolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84310. | such as Schneider, Acti 9 iC60H, type: A9F84310. | kos | 6
| - Pomožni kontakt 2 C/O za inštalacijski odklopnik, | - Auxiliary contact 2 C/O for the installation circuit breaker,
| kot naprimer Schneider, Acti9 A9A iOF, tip: A9A26909. | such as Schneider, Acti9 A9A iOF, type: A9A26909. | kos | 6
| - Kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 6 A s C karakteristiko, 30mA, tip A in pomožni kontakt 2 C/O, | - Combination protection switch with overcurrent protection (KZS), 1P+N, 6 A with C characteristic, 30mA, type A and auxiliary contact 2 C/O,
| kot naprimer Schneider, Acti 9 iDPN H, tip: A9D37606, pomožni kontakt tip: A9A26919. | such as Schneider, Acti 9 iDPN H, type: A9D37606, auxiliary contact type: A9A26919. | kos | 9
| - Kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip A in pomožni kontakt 2 C/O, | - Combination protection switch with overcurrent protection (KZS), 1P+N, 16 A with C characteristic, 30mA, type A and auxiliary contact 2 C/O,
| kot naprimer Schneider, Acti 9 iDPN H, tip: A9D37616, pomožni kontakt tip: A9A26919. | such as Schneider, Acti 9 iDPN H, type: A9D37616, auxiliary contact type: A9A26919. | kos | 6
| - Kontaktor, 3P (3NO), 32 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, | - Contactor, 3P (3NO), 32 A, coil 230 V AC, 50 Hz and auxiliary contact block 1 NO + 1 NC,
| kot naprimer Schneider tip: TeSys LC-1, LC1E3210P7 + LA1KN113. | such as for example Schneider tip: TeSys LC-1, LC1E3210P7 + LA1KN113. | kos | 1
| Na tuljavah kontaktorjev bodo priključeni supresorji za dušenje prenapetostnih špic, ki nastanejo pri izklopu kontaktorja. V kolikor niso ti supresorji že v samem kontaktorju, bodo kontaktorji opremljeni z RC členi oz. varistorji pri izmeničnih krmilnih napetostih, oz. z diodami pri enosmernih krmilnih napetostih. | Suppressors will be connected to the contactor coils to suppress overvoltage spikes that occur when the contactor is switched off. If these suppressors are not already in the contactor itself, the contactors will be equipped with RC links or varistors for AC control voltages, or diodes for DC control voltages.
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 1
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 1
| - Sponke 240 mm2 za montažo na DIN letev, | - Clips 240 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: UKH 250 | such as Phoenix Contact type: UKH 250 | kos | 3
| - Sponke 10 mm2 za montažo na DIN letev, | - 10 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 10 - MT | such as Phoenix Contact type: PT 10 - MT | kos | 3
| - Sponke ozemljitvene 10 mm2 za montažo na DIN letev, | - Earthing clips 10 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 10 PE | such as Phoenix Contact type: PT 10 PE | kos | 1
| - Sponke 4 mm2 za montažo na DIN letev, | - 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 4 - MT | such as Phoenix Contact type: PT 4 - MT | kos | 6
| - Sponke ozemljitvene 4 mm2 za montažo na DIN letev, | - 4 mm2 earthing clips for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 4 PE | such as Phoenix Contact type: PT 4 PE | kos | 2
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 71
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 21
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 40
| - Sponke 1,5 mm2 modre za montažo na DIN letev, | - 1,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 1,5 - MT | such as Phoenix Contact type: PT 1,5 - MT | kos | 126
| - Sponke varovalčna (5x20), | - Buckle guard (5x20),
| kot na primer Phoenix Contact tip: PTC 4 - HESILED 24 | such as Phoenix Contact type: PTC 4 - HESILED 24 | kos | 6
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
3.2 | Dobava in montaža dveh kovinskih omar +ENS-K1-PLC1 sestavljene iz dveh polj v zaščiti IP 55 barve RAL 7035. | Supply and installation of two metal cabinets +ENS-K1-PLC1 consisting of two bays in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare POLJE 1 so: višina 2000 mm, širina 800 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet BOX 1 are: height 2000 mm, width 800 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20840P. | such as Schneider, type: NSYSFN20840P. | kos | 1
| - Hrbtna plošča, širine 800x2000 mm, | - Back panel, width 800x2000 mm,
| kot naprimer Schneider, tip: NSYBPN208. | such as Schneider, type: NSYBPN208. | kos | 1
| - Podstavek 200 mm, širine 800 mm, | - Base 200 mm, width 800 mm,
| kot naprimer Schneider, tip: NSYSPF8200. | such as Schneider, type: NSYSPF8200. | kos | 2
| - stranica podstavka 200 mm, globine 400 mm, | - base side 200 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4200. | such as Schneider, type: NSYSPS4200. | kos | 2
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1000 mm, | - Lower crossbar with PanelSeT cable entry - 1000 mm,
| kot naprimer Rittal, tip: 2388.050. | such as Rittal, type: 2388.050. | kos | 1
| Dimenzije omare POLJE 2 so: višina 2000 mm, širina 600 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 600 mm and depth 400 mm. The whole cabinet stands on a 200 mm high base. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20640P. | such as Schneider, type: NSYSFN20640P. | kos | 1
| - Hrbtna plošča, širine 600x2000 mm, | - Back panel, width 600x2000 mm,
| kot naprimer Schneider, tip: NSYBPN206. | such as Schneider, type: NSYBPN206. | kos | 1
| - Podstavek 200 mm, širine 600 mm, | - Base 200 mm, width 600 mm,
| kot naprimer Schneider, tip: NSYSPF6200. | such as Schneider, type: NSYSPF6200. | kos | 2
| - stranica podstavka 200 mm, globine 400 mm, | - base side 200 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4200. | such as Schneider, type: NSYSPS4200. | kos | 2
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1000 mm, | - Lower crossbar with PanelSeT cable entry - 1000 mm,
| kot naprimer Rittal, tip: 2388.050. | such as Rittal, type: 2388.050. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Rittal, tip: 2388.100. | such as Rittal, type: 2388.100. | kos | 28
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Rittal, tip: 7077.000. | such as Rittal, type: 7077.000. | kos | 21
| V krmilno omaro +ENS-K1-PLC1 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +ENS-K1-PLC1 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, | - Led cabinet light, 11W, 230V, without socket, on/off, 4000K,
| kot naprimer Rittal, tip: 2500.200. | such as Rittal, type: 2500.200. |  | 1
| - Priključni kabel za LED svetilko OR 3000mm, | - Connecting cable for LED luminaire OR 3000mm,
| kot naprimer Rittal, tip: 2500.400. | such as Rittal, type: 2500.400. | kos | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Rittal, tip: SK 3240.200. | such as Rittal, type: SK 3240.200. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Rittal, tip: SK 3240.100 + SK 3240.200. | such as Rittal, type: SK 3240.100 + SK 3240.200. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omaro. | - 2x RJ45 socket (communication socket) and associated enclosure for installation in a cabinet. | kos | 1
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 2
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Vgradna zelena kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed green LED signal light, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB3 + ZBZ32. | like for example Schneider tip: XB4BVB3 + ZBZ32. | kos | 21
| - Vgradna rdeča kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed red LED signal light, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB4 + ZBZ32. | like for example Schneider tip: XB4BVB4 + ZBZ32. | kos | 21
| - Vgradna modre tipke z delovnim kontaktom in nosilcem tipkala, | - Built-in blue keys with working contact and key holder,
| kot naprimer Schneider tip: XB4BA61 + ZBZ32. | like for example Schneider tip: XB4BA61 + ZBZ32. | kos | 3
| - Enotni blok za funkcijo testne luči 24 V AC DC, | - Single block for 24 V AC DC test light function,
| kot naprimer Schneider tip: ZBZG156. | such as Schneider type: ZBZG156. | kos | 42
| - Vgradno stikalo Ø 22, 3 položajni 2NO, | - Recessed switch Ø 22, 3-position 2NO,
| kot naprimer Schneider tip: XB7ND33 + ZBZ32. | like for example Schneider tip: XB7ND33 + ZBZ32. | kos | 22
| - Vgradna tipka za izklop v sili z gobo, 2x NC, za vgradnjo na vrata omare, komplet s ploščico, | - Emergency stop push-button with sponge, 2x NC, for mounting on cabinet doors, complete with plate,
| kot naprimer Schneider tip: XB5AT842 + ZBE102+ZBY9360. | like for example Schneider tip: XB5AT842+ZBE102+ZBY9360. | kos | 1
| - Varnostni rele za izklop v sili, izhodi 3 NO in 1 NC, napajanje 24 VDC, povezovalni modul | - Emergency stop safety relay, 3 NO and 1 NC outputs, 24 VDC power supply, connection module
| kot naprimer Siemens tip: 3SK1121-1AB40 + 3ZY1212-2DA00. | as for example Siemens type: 3SK1121-1AB40 + 3ZY1212-2DA00. | kos | 1
| - Mrežno stikalo 5 port, | - 5 port network switch,
| kot naprimer Siemens tip: 6GK5005-0BA00-1AB2. | such as Siemens type: 6GK5005-0BA00-1AB2. | kos | 1
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 124
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 1
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Varnostni ločilni transformator 315 VAC/24 VAC, | - Safety isolating transformer 315 VAC/24 VAC,
| kot na primer Siemens tip: 4AM4342-4TN00-0EA0 | such as Siemens type: 4AM4342-4TN00-0EA0 | kos | 1
| - Sponke 4 mm2 za montažo na DIN letev, | - 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 4 | such as Phoenix Contact type: UT 4 | kos | 1
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 6
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 2
| - Sponke 1,5 mm2 za montažo na DIN letev, | - 1.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 1,5 - MT | such as Phoenix Contact type: PT 1,5 - MT | kos | 541
| - Sponke 1,5 mm2 modre za montažo na DIN letev, | - 1,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 1,5 - MT BU | such as Phoenix Contact type: PT 1,5 - MT BU | kos | 39
| - Sponke varovalčna (5x20), | - Buckle guard (5x20),
| kot na primer Phoenix Contact tip: PTC 4 - HESILED 24 | such as Phoenix Contact type: PTC 4 - HESILED 24 | kos | 38
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
3.3 | Dobava in montaža kovinske omare +ENS_K1-R2 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +ENS_K1-R2 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1200 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1200 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2012402DP. | such as Schneider, type: NSYSFN2012402DP. | kos | 1
| - Podstavek 200 mm, širine 1200 mm, | - Base 200 mm, width 1200 mm,
| kot naprimer Schneider, tip: NSYSPF12200. | such as Schneider, type: NSYSPF12200. | kos | 2
| - stranica podstavka 200 mm, globine 400 mm, | - base side 200 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4200. | such as Schneider, type: NSYSPS4200. | kos | 2
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1000 mm, | - Lower crossbar with PanelSeT cable entry - 1000 mm,
| kot naprimer Rittal, tip: 2388.050. | such as Rittal, type: 2388.050. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Rittal, tip: 2388.100. | such as Rittal, type: 2388.100. | kos | 23
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Rittal, tip: 7077.000. | such as Rittal, type: 7077.000. | kos | 16
| V močnostno omaro +ENS_K1-R2 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +ENS_K1-R2 power cabinet:
| - glavno stikalo In=400 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=400 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: NSX400NA. | such as Schneider, type: NSX400NA. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV432598T. | such as Schneider, type: LV432598T. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, | - Led cabinet light, 11W, 230V, without socket, on/off, 4000K,
| kot naprimer Rittal, tip: 2500.200. | such as Rittal, type: 2500.200. | kos | 1
| - Priključni kabel za LED svetilko OR 3000mm, | - Connecting cable for LED luminaire OR 3000mm,
| kot naprimer Rittal, tip: 2500.400. | such as Rittal, type: 2500.400. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10, 3x38 mm - varovalka gG 1A, | - Fuse disconnector 2P, 25 A, for fuse 10, 3x38 mm - fuse gG 1A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Štiripolni inštalacijski odklopnik 40 A, s C karakteristiko, 20 kA, | - 40 A, four-pole circuit breaker with C characteristic, 20 kA,
| kot naprimer Schneider, Acti 9 iC60L, tip: A9F84440. | such as Schneider, Acti 9 iC60L, type: A9F84440. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 1
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 1
| - Tripolni inštalacijski odklopnik 32 A, s C karakteristiko, 15 kA, | - Tripolar 32 A installation circuit breaker, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84332. | such as Schneider, Acti 9 iC60H, type: A9F84332. | kos | 2
| - Pomožni kontakt 2 C/O za inštalacijski odklopnik, | - Auxiliary contact 2 C/O for the installation circuit breaker,
| kot naprimer Schneider, Acti9 A9A iOF, tip: A9A26909. | such as Schneider, Acti9 A9A iOF, type: A9A26909. | kos | 3
| - Tripolni inštalacijski odklopnik 25 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 25 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84325. | such as Schneider, Acti 9 iC60H, type: A9F84325. | kos | 6
| - Pomožni kontakt 2 C/O za inštalacijski odklopnik, | - Auxiliary contact 2 C/O for the installation circuit breaker,
| kot naprimer Schneider, Acti9 A9A iOF, tip: A9A26909. | such as Schneider, Acti9 A9A iOF, type: A9A26909. | kos | 6
| - Tripolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Tripolar 16 A, C-characteristic, 15 kA installation circuit breaker,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84316. | such as Schneider, Acti 9 iC60H, type: A9F84316. | kos | 8
| - Pomožni kontakt 2 C/O za inštalacijski odklopnik, | - Auxiliary contact 2 C/O for the installation circuit breaker,
| kot naprimer Schneider, Acti9 A9A iOF, tip: A9A26909. | such as Schneider, Acti9 A9A iOF, type: A9A26909. | kos | 8
| - Tripolni inštalacijski odklopnik 20 A, s C karakteristiko, 15 kA, | - Tripolar 20 A installation circuit breaker, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84320. | such as Schneider, Acti 9 iC60H, type: A9F84320. | kos | 1
| - Pomožni kontakt 2 C/O za inštalacijski odklopnik, | - Auxiliary contact 2 C/O for the installation circuit breaker,
| kot naprimer Schneider, Acti9 A9A iOF, tip: A9A26909. | such as Schneider, Acti9 A9A iOF, type: A9A26909. | kos | 1
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 3
| - Pomožni kontakt 2 C/O za inštalacijski odklopnik, | - Auxiliary contact 2 C/O for the installation circuit breaker,
| kot naprimer Schneider, Acti9 A9A iOF, tip: A9A26904. | such as Schneider, Acti9 A9A iOF, type: A9A26904. | kos | 3
| - Kombinirani zaščitno stikalo z nadtokovno zaščito (KZS), 1P+N, 16 A s C karakteristiko, 30mA, tip A in pomožni kontakt 2 C/O, | - Combination protection switch with overcurrent protection (KZS), 1P+N, 16 A with C characteristic, 30mA, type A and auxiliary contact 2 C/O,
| kot naprimer Schneider, Acti 9 iDPN H, tip: A9D37616, pomožni kontakt tip: A9A26919. | such as Schneider, Acti 9 iDPN H, type: A9D37616, auxiliary contact type: A9A26919. | kos | 6
| - Kontaktor, 3P (3NO), 32 A, tuljava 230 V AC, 50Hz in pomožni kontaktni blok 1 NO + 1 NC, | - Contactor, 3P (3NO), 32 A, coil 230 V AC, 50 Hz and auxiliary contact block 1 NO + 1 NC,
| kot naprimer Schneider tip: TeSys LC-1, LC1E3210P7 + LA1KN113. | such as for example Schneider tip: TeSys LC-1, LC1E3210P7 + LA1KN113. | kos | 1
| Na tuljavah kontaktorjev bodo priključeni supresorji za dušenje prenapetostnih špic, ki nastanejo pri izklopu kontaktorja. V kolikor niso ti supresorji že v samem kontaktorju, bodo kontaktorji opremljeni z RC členi oz. varistorji pri izmeničnih krmilnih napetostih, oz. z diodami pri enosmernih krmilnih napetostih. | Suppressors will be connected to the contactor coils to suppress overvoltage spikes that occur when the contactor is switched off. If these suppressors are not already in the contactor itself, the contactors will be equipped with RC links or varistors for AC control voltages, or diodes for DC control voltages.
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 1
| - Sponke 240 mm2 za montažo na DIN letev, | - Clips 240 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: UKH 240 | such as Phoenix Contact type: UKH 240 | kos | 3
| - Sponke 35 mm2 za montažo na DIN letev, | - 35 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 35 | such as Phoenix Contact type: UT 35 | kos | 6
| - Sponke ozemljitvene 35 mm2 za montažo na DIN letev, | - Earthing clips 35 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: UT 35 PE | such as Phoenix Contact type: UT 35 PE | kos | 2
| - Sponke 4 mm2 za montažo na DIN letev, | - 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 4 - MT | such as Phoenix Contact type: PT 4 - MT | kos | 3
| - Sponke modra 4 mm2 za montažo na DIN letev, | - Blue 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 4 BU | such as Phoenix Contact type: PT 4 BU | kos | 1
| - Sponke ozemljitvene 4 mm2 za montažo na DIN letev, | - 4 mm2 earthing clips for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 4 PE | such as Phoenix Contact type: PT 4 PE | kos | 1
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 76
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 42
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 42
| - Sponke 1,5 mm2 modre za montažo na DIN letev, | - 1,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 1,5 - MT | such as Phoenix Contact type: PT 1,5 - MT | kos | 130
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
3.4 | Dobava in montaža dveh kovinskih omar +ENS-K1-PLC2 sestavljene iz dveh polj v zaščiti IP 55 barve RAL 7035. | Supply and installation of two metal cabinets +ENS-K1-PLC2 consisting of two bays in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare POLJE 1 so: višina 2000 mm, širina 800 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet BOX 1 are: height 2000 mm, width 800 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20840P. | such as Schneider, type: NSYSFN20840P. | kos | 1
| - Hrbtna plošča, širine 800x2000 mm, | - Back panel, width 800x2000 mm,
| kot naprimer Schneider, tip: NSYBPN208. | such as Schneider, type: NSYBPN208. | kos | 1
| - Podstavek 200 mm, širine 800 mm, | - Base 200 mm, width 800 mm,
| kot naprimer Schneider, tip: NSYSPF8200. | such as Schneider, type: NSYSPF8200. | kos | 2
| - stranica podstavka 200 mm, globine 400 mm, | - base side 200 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4200. | such as Schneider, type: NSYSPS4200. | kos | 2
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1000 mm, | - Lower crossbar with PanelSeT cable entry - 1000 mm,
| kot naprimer Rittal, tip: 2388.050. | such as Rittal, type: 2388.050. | kos | 1
| Dimenzije omare POLJE 2 so: višina 2000 mm, širina 600 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 600 mm and depth 400 mm. The whole cabinet stands on a 200 mm high base. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20640P. | such as Schneider, type: NSYSFN20640P. | kos | 1
| - Hrbtna plošča, širine 600x2000 mm, | - Back panel, width 600x2000 mm,
| kot naprimer Schneider, tip: NSYBPN206. | such as Schneider, type: NSYBPN206. | kos | 1
| - Podstavek 200 mm, širine 600 mm, | - Base 200 mm, width 600 mm,
| kot naprimer Schneider, tip: NSYSPF6200. | such as Schneider, type: NSYSPF6200. | kos | 2
| - stranica podstavka 200 mm, globine 400 mm, | - base side 200 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4200. | such as Schneider, type: NSYSPS4200. | kos | 2
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1000 mm, | - Lower crossbar with PanelSeT cable entry - 1000 mm,
| kot naprimer Rittal, tip: 2388.050. | such as Rittal, type: 2388.050. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Rittal, tip: 2388.100. | such as Rittal, type: 2388.100. | kos | 17
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Rittal, tip: 7077.000. | such as Rittal, type: 7077.000. | kos | 14
| V krmilno omaro +ENS-K1-PLC2 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +ENS-K1-PLC2 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Rittal, tip: 2506.120. | such as Rittal, type: 2506.120. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, | - Led cabinet light, 11W, 230V, without socket, on/off, 4000K,
| kot naprimer Rittal, tip: 2500.200. | such as Rittal, type: 2500.200. |  | 1
| - Priključni kabel za LED svetilko OR 3000mm, | - Connecting cable for LED luminaire OR 3000mm,
| kot naprimer Rittal, tip: 2500.400. | such as Rittal, type: 2500.400. | kos | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Rittal, tip: SK 3240.200. | such as Rittal, type: SK 3240.200. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Rittal, tip: SK 3240.100 + SK 3240.200. | as for example Rittal, type: SK 3240.100 + SK 3240.200. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omaro. | - 2x RJ45 socket (communication socket) and associated enclosure for installation in a cabinet. | kos | 1
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 2
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Vgradna zelena kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed green LED signal light, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB3 + ZBZ32. | like for example Schneider tip: XB4BVB3 + ZBZ32. | kos | 2
| - Vgradna rdeča kompletna signalna svetilka LED, Ø 22, 24 VDC, | - Recessed red LED signal light, Ø 22, 24 VDC,
| kot naprimer Schneider tip: XB4BVB4 + ZBZ32. | like for example Schneider tip: XB4BVB4 + ZBZ32. | kos | 2
| - Vgradna modre tipke z delovnim kontaktom in nosilcem tipkala, | - Built-in blue keys with working contact and key holder,
| kot naprimer Schneider tip: XB4BA61 + ZBZ32. | like for example Schneider tip: XB4BA61 + ZBZ32. | kos | 3
| - Enotni blok za funkcijo testne luči 24 V AC DC, | - Single block for 24 V AC DC test light function,
| kot naprimer Schneider tip: ZBZG156. | such as Schneider type: ZBZG156. | kos | 4
| - Vgradna tipka za izklop v sili z gobo, 2x NC, za vgradnjo na vrata omare, komplet s ploščico, | - Emergency stop push-button with sponge, 2x NC, for mounting on cabinet doors, complete with plate,
| kot naprimer Schneider tip: XB5AT842 + ZBE102+ZBY9360. | like for example Schneider tip: XB5AT842+ZBE102+ZBY9360. | kos | 1
| - Varnostni rele za izklop v sili, izhodi 3 NO in 1 NC, napajanje 24 VDC, povezovalni modul | - Emergency stop safety relay, 3 NO and 1 NC outputs, 24 VDC power supply, connection module
| kot naprimer Siemens tip: 3SK1121-1AB40 + 3ZY1212-2DA00. | as for example Siemens type: 3SK1121-1AB40 + 3ZY1212-2DA00. | kos | 1
| - Mrežno stikalo 5 port, | - Network switch 5 port,
| kot naprimer Siemens tip: 6GK5005-0BA00-1AB2. | such as Siemens type: 6GK5005-0BA00-1AB2. | kos | 1
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 26
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 1
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Varnostni ločilni transformator 315 VAC/24 VAC, | - Safety isolating transformer 315 VAC/24 VAC,
| kot na primer Siemens tip: 4AM4342-4TN00-0EA0 | such as Siemens type: 4AM4342-4TN00-0EA0 | kos | 1
| - Sponke 4 mm2 za montažo na DIN letev, | - 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 4 | such as Phoenix Contact type: UT 4 | kos | 1
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 10
| - Sponke 1,5 mm2 za montažo na DIN letev, | - 1.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 1,5 - MT | such as Phoenix Contact type: PT 1,5 - MT | kos | 509
| - Sponke 1,5 mm2 modre za montažo na DIN letev, | - 1,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 1,5 - MT BU | such as Phoenix Contact type: PT 1,5 - MT BU | kos | 20
| - Sponke 1,5 mm2 ozemljitveni za montažo na DIN letev, | - 1.5 mm2 earthing clips for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 1,5 - MT PE | such as Phoenix Contact type: PT 1,5 - MT PE | kos | 9
| - Sponke varovalčna (5x20), | - Buckle guard (5x20),
| kot na primer Phoenix Contact tip: PTC 4 - HESILED 24 | such as Phoenix Contact type: PTC 4 - HESILED 24 | kos | 42
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
3.5 | - Dobava in polaganje na kabelske police oz. uvlečenje v inštalacijske cevi kabla F/FTP-Category 6A, 4x2, 23 AWG, za PROFINET oz. ETHERNET komunikacijo. | - Supply and installation of F/FTP-Category 6A, 4x2, 23 AWG cable for PROFINET or ETHERNET communication on cable racks or in installation pipes. |  |  | m | 250 |  | 0
3.6 | - Dobava in polaganje na kabelske police oz. uvlečenje v inštalacijske cevi kabla MODBUS komunikacija, 2x2 mm2, | - Supply and installation of MODBUS communication cable, 2x2 mm2, on cable racks or in installation pipes,
| kot primer LAPP: | as an example of LAPP:
| BUS LD 1X2X0,22 | BUS LD 1X2X0,22 |  |  | m | 420 |  | 0
3.7 | - Dobava in polaganje protipožarnega kabla (klasifikacije Cca-S2-d2-a1) na kabelske police in v zaščitne cevi, | - Supply and installation of fire-fighting cable (classification Cca-S2-d2-a1) on cable racks and in protection tubes,
| kot primer LAPP: | as an example of LAPP:
| - LiHCH 2x1 mm2 | - LiHCH 2x1 mm2 |  |  | m | 1750 |  | 0
| - LiHCH 4x1 mm2 | - LiHCH 4x1 mm2 |  |  | m | 12880 |  | 0
3.8 | - Dobava in polaganje protipožarnega kabla (klasifikacije Cca-S2-d2-a1) na kabelske police in v zaščitne cevi, | - Supply and installation of fire-fighting cable (classification Cca-S2-d2-a1) on cable racks and in protection tubes,
| kot primer LAPP: | as an example of LAPP:
| - OL-100H 3G1,5 mm2 | - OL-100H 3G1,5 mm2 |  |  | m | 3080 |  | 0
| - OL-100H 3G2,5 mm2 | - OL-100H 3G2,5 mm2 |  |  | m | 140 |  | 0
| - OL-100H 4G1,5 mm2 | - OL-100H 4G1,5 mm2 |  |  | m | 560 |  | 0
| - OL-100H 5G1,5 mm2 | - OL-100H 5G1,5 mm2 |  |  | m | 540 |  | 0
| - OL-100H 4G2,5 mm2 | - OL-100H 4G2,5 mm2 |  |  | m | 140 |  | 0
| - OL-100H 5G2,5 mm2 | - OL-100H 5G2,5 mm2 |  |  | m | 700 |  | 0
| - OL-100H 4G4 mm2 | - OL-100H 4G4 mm2 |  |  | m | 840 |  | 0
| - OL-100H 4G10 mm2 | - OL-100H 4G10 mm2 |  |  | m | 70 |  | 0
| - OL-100H 4G50 mm2 | - OL-100H 4G50 mm2 |  |  | m | 140 |  | 0
| - OL-100H 5G4 mm2 | - OL-100H 5G4 mm2 |  |  | m | 420 |  | 0
3.9 | - Dobava in polaganje protipožarnega kabla (klasifikacije Cca-S2-d2-a1) na kabelske police in v zaščitne cevi, | - Supply and installation of fire-fighting cable (classification Cca-S2-d2-a1) on cable racks and in protection tubes,
| kot primer LAPP: | as an example of LAPP:
| - OL-110H 2x1 mm2 | - OL-110H 2x1 mm2 |  |  | m | 1540 |  | 0
| - OL-110H 3G1,5 mm2 | - OL-110H 3G1,5 mm2 |  |  | m | 1050 |  | 0
| - OL-110H 5x0,75 mm2 | - OL-110H 5x0,75 mm2 |  |  | m | 210 |  | 0
| - OL-110H 4x1 mm2 | - OL-110H 4x1 mm2 |  |  | m | 1680 |  | 0
| - OL-110H 5G1 mm2 | - OL-110H 5G1 mm2 |  |  | m | 2380 |  | 0
| - OL-110H 7G1 mm2 | - OL-110H 7G1 mm2 |  |  | m | 1330 |  | 0
| - OL-110H 12G0,75 mm2 | - OL-110H 12G0,75 mm2 |  |  | m | 1260 |  | 0
| - OL-110H 18G0,75 mm2 | - OL-110H 18G0,75 mm2 |  |  | m | 140 |  | 0
| - OL-110H 25G0,75 mm2 | - OL-110H 25G0,75 mm2 |  |  | m | 910 |  | 0
3.10 | Dobava in montaža vodnikov za izenačevanje potencialov: | Supply and installation of equipotential bonding conductors:
| - HO7V-K 6 mm2 | - HO7V-K 6 mm2 |  |  | m | 210 |  | 0
| - HO7V-K 10 mm2 | - HO7V-K 10 mm2 |  |  | m | 100 |  | 0
| - HO7V-K 16 mm2 | - HO7V-K 16 mm2 |  |  | m | 150 |  | 0
| - HO7V-K 25 mm2 | - HO7V-K 25 mm2 |  |  | m | 120 |  | 0
| - HO7V-K 50 mm2 | - HO7V-K 50 mm2 |  |  | m | 100 |  | 0
3.11 | Premostitve prirobnic in stikov na prezračevalnih kanalih in cevovodih ( Cu pletenica 35 mm2) | Bridging of flanges and joints on ventilation ducts and pipelines (Cu braid 35 mm2) |  |  | kos | 180 |  | 0
3.12 | Dobava in montaža kabelskih polic STAGO (alternativa ELBA, BAKS, OPTIMA-SF z enakovrednimi tehničnimi lastnismi), komplet s pritrdilnim priborom, obešalnim priborom, koleni, s pokrovi, spojnim materialom in višinskimi prehodi, hladno cinkane. | Supply and installation of STAGO cable racks (alternative to ELBA, BAKS, OPTIMA-SF with equivalent technical characteristics), complete with fixing fittings, hanging fittings, elbows, with covers, fasteners and height transitions, cold galvanised.
| - polica širine 50 mm/60 mm | - shelf width 50 mm/60 mm |  |  | m | 90 |  | 0
| - polica širine 100 mm/60 mm | - shelf width 100 mm/60 mm |  |  | m | 100 |  | 0
| - polica širine 200 mm/60 mm | - shelf width 200 mm/60 mm |  |  | m | 120 |  | 0
| - polica širine 400 mm/60 mm | - shelf width 400 mm/60 mm |  |  | m | 50 |  | 0
3.13 | 'Dobava in montaža PN cevi fi16 do fi32, komplet s koleni | Supply and installation of PN pipes fi16 to fi32, complete with elbows |  |  | m | 1250 |  | 0
3.14 | Dobava in motaža nerjavičih jekljenih cevi, od fi=16 do fi=50mm za montažo v čiste prostore, za zaščito kablov komplet s pritrdilnim materialom. | Supply and installation of stainless steel tubes, from fi=16 to fi=50mm for installation in clean rooms, for cable protection, complete with fixing material. |  |  | m | 200 |  | 0
3.15 | Dobava in montaža različnih jeklenih profilov za pomožne konstrukcije. | Supply and installation of various steel profiles for ancillary structures. |  |  | kg | 350 |  | 0
3.16 | Izdelava priključkov na novih krmilnih, regulacijskih in ostalih elementih, sondah itd. | Making connections to new controls, regulators, probes, etc. |  |  | kos | 490 |  | 0
3.17 | Izdelava močnostnih priključkov na motornih pogonih in na ostalih močnostnih porabnikov do električne moči: | Making power connections on motor drives and other power consumers up to electrical power:
| - do moči 2,2 kW | - up to 2,2 kW |  |  | kos | 55 |  | 0
| - do moči 2,3 kW do 15,0 kW | - up to 2,3 kW up to 15,0 kW |  |  | kos | 30 |  | 0
| - do moči 31,0 kW do 55,0 kW | - up to 31,0 kW up to 55,0 kW |  |  | kos | 2 |  | 0
| Energetika (inštalacije) | Energy (installations) | [5 empty] | 0

## 3.13.4_ENS_HW&SW
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.13 | ELEKTRO DELA | ELECTRICAL WORKS
3.13.4 | Energetika (HW & SW) | Energy (HW & SW) | [5 empty] | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description |  |  | EM | Količina | Cena/EM | Cena
4 | Energetika (HW & SW) | Energy (HW & SW)
4.1 | Dobava PLC postaje ENS_K1-PLC1 (locirana v +ENS_K1-PLC1), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the PLC station ENS_K1-PLC1 (located in +ENS_K1-PLC1), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - digitalni vhodi (DI) | - digital Inputs (DI) | točk | 104
| - digitalni izhodi (DO) | - digital outputs (DO) | točk | 68
| - analogni vhodi (AI) | - analogue inputs (AI) | točk | 43
| - analogni izhodi (AO) | - analogue outputs (AO) | točk | 9
| - komunikacijske povezave (Ethernet, Profinet, Modbus, Profibus, ...) | - communication links (Ethernet, Profinet, Modbus, Profibus, ...) | kpl | 1
| Predvidena konfiguracija PLC postaje ENS_K1-PLC1 (locirana v omari +ENS_K1-PLC1), ki bo namenjena računalniškemu nadzoru in vodenju klimatizacije in prezračevanju je: | The planned configuration of the PLC station ENS_K1-PLC1 (located in cabinet +ENS_K1-PLC1), which will be used for computer control and management of air conditioning and ventilation is:
| - Napajalnik 24 VAC, 10 W, | - Power supply 24 VAC, 10 W,
| kot naprimer Schneider tip: SXWPS24VX10001 + | such as Schneider tip: SXWPS24VX10001 +
| podnožje SXWTBPSW110001. | base SXWTBPSW110001. | kos | 2
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port),
| kot naprimer Schneider tip: SXWASPXXX10001 + | such as Schneider tip: SXWASPXXX10001 +
| podnožje SXWTBASW110002. | base SXWTBASW110002. | kos | 1
| - Povezovalni komunikacijski kabel med moduli, 1.5 m , | - Communication cable between modules, 1.5 m ,
| kot naprimer Schneider tip: SXWSCABLE10002 + | such as Schneider tip: SXWSCABLE10002 + | kos | 2
| - Digitalni vhodni (DI) modul za 16 vhodov, 24 VDC, | - Digital input (DI) module for 16 inputs, 24 VDC,
| kot naprimer Schneider tip: SXWDI16XX10001 + | such as Schneider tip: SXWDI16XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 6
| - Digitalni izhodni (DO) modul za 12 izhodov, 24 VDC, | - Digital output (DO) module for 12 outputs, 24 VDC,
| kot naprimer Schneider tip: SXWDOA12X10001 + | such as Schneider tip: SXWDOA12X10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 6
| - Analogni vhodni modul za 16 analognih vhodov UI, | - Analogue input module for 16 analogue AI inputs,
| kot naprimer Schneider tip: SXWUI16XX10001 + | such as Schneider tip: SXWUI16XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 3
| - Analogni izhodni modul za 8 analognih izhodov U, | - Analog output module for 8 analogue U outputs,
| kot naprimer Schneider tip: SXWAOV8XX10001 + | such as Schneider tip: SXWAOV8XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 2
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
4.2 | Dobava PLC postaje ENS_K1-PLC2 (locirana v +ENS_K1-PLC2), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the PLC station ENS_K1-PLC2 (located in +ENS_K1-PLC2), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope:
| - digitalni vhodi (DI) | - digital Inputs (DI) | točk | 150
| - digitalni izhodi (DO) | - digital outputs (DO) | točk | 25
| - analogni vhodi (AI) | - analogue inputs (AI) | točk | 39
| - analogni izhodi (AO) | - analogue outputs (AO) | točk | 37
| - komunikacijske povezave (Ethernet, Profinet, Modbus, Profibus, ...) | - communication links (Ethernet, Profinet, Modbus, Profibus, ...) | kpl | 1
| Predvidena konfiguracija PLC postaje ENS_K1-PLC2 (locirana v omari +ENS_K1-PLC2), ki bo namenjena računalniškemu nadzoru in vodenju klimatizacije in prezračevanju je: | The planned configuration of the PLC station ENS_K1-PLC2 (located in cabinet +ENS_K1-PLC2), which will be used for computer control and management of air conditioning and ventilation, is:
| - Napajalnik 24 VAC, 10 W, | - Power supply 24 VAC, 10 W,
| kot naprimer Schneider tip: SXWPS24VX10001 + | such as Schneider tip: SXWPS24VX10001 +
| podnožje SXWTBPSW110001. | base SXWTBPSW110001. | kos | 2
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port),
| kot naprimer Schneider tip: SXWASPXXX10001 + | such as Schneider tip: SXWASPXXX10001 +
| podnožje SXWTBASW110002. | base SXWTBASW110002. | kos | 1
| - Povezovalni komunikacijski kabel med moduli, 1.5 m , | - Communication cable between modules, 1.5 m ,
| kot naprimer Schneider tip: SXWSCABLE10002 + | such as Schneider tip: SXWSCABLE10002 + | kos | 3
| - Digitalni vhodni (DI) modul za 16 vhodov, 24 VDC, | - Digital input (DI) module for 16 inputs, 24 VDC,
| kot naprimer Schneider tip: SXWDI16XX10001 + | such as Schneider tip: SXWDI16XX10001 +
| podnožje SXWTBIOW110001. | base SXWTBIOW110001. | kos | 10
| Energetika (HW & SW) | Energy (HW & SW) | [5 empty] | 0

## 3.13.5_BMS_INŠ
Investitor: | UNIVERZA V LJUBLJANI | UNIVERZA V LJUBLJANI
Gradnja: | Fakulteta za strojništvo | Fakulteta za strojništvo
Objekt: | STAVBA FAKULTETE | STAVBA FAKULTETE
3.13 | ELEKTRO DELA | ELECTRICAL WORKS
3.13.5 | Sistem upravljanja stavb (inštalacije) | Building management system (installations) | [5 empty] | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description |  |  | EM | Količina | Cena/EM | Cena
5 | Sistem upravljanja stavb (inštalacije) | Building management system (installations)
5.1 | Dobava in montaža kovinske omare +BMS.N3-1-R.1 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS.N3-1-R.1 consisting of one bay, IP 55 RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 600 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 600 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20640P. | such as Schneider, type: NSYSFN20640P. | kos | 1
| - Podstavek 100 mm, širine 600 mm, | - Base 100 mm, width 600 mm,
| kot naprimer Schneider, tip: NSYSPF6100. | such as Schneider, type: NSYSPF6100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1600 mm, | - Lower crossbar with PanelSeT cable entry - 1600 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider | such as Schneider | kos | 15
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider | such as Schneider | kos | 12
| V močnostno omaro +BMS-N3-1-R.1 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-N3-1-R.1 power cabinet:
| - glavno stikalo In=50 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=50 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C113050LS. | such as Schneider, type: C113050LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider | such as Schneider | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 15
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 12
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 3
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 5
| - Sponke 16 mm2 za montažo na DIN letev, | - 16 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 16 | such as Phoenix Contact type: UT 16 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 90
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 50
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 50
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.2 | Dobava in montaža kovinske omare +BMS-N3-1-R.2 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS-N3-1-R.2 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1200 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1200 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2012402DP. | such as Schneider, type: NSYSFN2012402DP. | kos | 1
| - Podstavek 100 mm, širine 1200 mm, | - Base 100 mm, width 1200 mm,
| kot naprimer Schneider, tip: NSYSPF12100. | such as Schneider, type: NSYSPF12100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1200 mm, | - Lower crossbar with PanelSeT cable entry - 1200 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider. | such as Schneider. | kos | 17
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider. | such as Schneider. | kos | 14
| V krmilno omaro +BMS-N3-1-R.2 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-N3-1-R.2 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. |  | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omaro. | - 2x RJ45 socket (communication socket) and associated enclosure for installation in a cabinet. | kos | 1
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 2
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 10
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 5
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Sponke 4 mm2 za montažo na DIN letev, | - 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 4 | such as Phoenix Contact type: UT 4 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 50
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 20
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 20
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.3 | Dobava in montaža kovinske omare +BMS.N3-2-R.1 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS.N3-2-R.1 consisting of one bay, IP 55 RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 600 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 600 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20640P. | such as Schneider, type: NSYSFN20640P. | kos | 1
| - Podstavek 100 mm, širine 600 mm, | - Base 100 mm, width 600 mm,
| kot naprimer Schneider, tip: NSYSPF6100. | such as Schneider, type: NSYSPF6100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1600 mm, | - Lower crossbar with PanelSeT cable entry - 1600 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider | such as Schneider | kos | 15
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider | such as Schneider | kos | 12
| V močnostno omaro +BMS-N3-2-R.1 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-N3-2-R.1 power cabinet:
| - glavno stikalo In=50 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=50 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C113050LS. | such as Schneider, type: C113050LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider | such as Schneider | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 12
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 10
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 3
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 5
| - Sponke 16 mm2 za montažo na DIN letev, | - 16 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 16 | such as Phoenix Contact type: UT 16 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 90
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 50
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 50
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.4 | Dobava in montaža kovinske omare +BMS-N3-2-R.2 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS-N3-2-R.2 consisting of one bay, IP 55 RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1200 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1200 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2012402DP. | such as Schneider, type: NSYSFN2012402DP. | kos | 1
| - Podstavek 100 mm, širine 1200 mm, | - Base 100 mm, width 1200 mm,
| kot naprimer Schneider, tip: NSYSPF12100. | such as Schneider, type: NSYSPF12100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1200 mm, | - Lower crossbar with PanelSeT cable entry - 1200 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider. | such as Schneider. | kos | 17
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider. | such as Schneider. | kos | 14
| V krmilno omaro +BMS-N3-2-R.2 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-N3-2-R.2 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. |  | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omaro. | - 2x RJ45 socket (communication socket) and associated enclosure for installation in a cabinet. | kos | 1
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 2
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 10
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 5
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Sponke 4 mm2 za montažo na DIN letev, | - 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 4 | such as Phoenix Contact type: UT 4 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 50
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 20
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 20
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.5 | Dobava in montaža kovinske omare +BMS.N3-3-R.1 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS.N3-3-R.1 consisting of one bay, IP 55 RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 600 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 600 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20640P. | such as Schneider, type: NSYSFN20640P. | kos | 1
| - Podstavek 100 mm, širine 600 mm, | - Base 100 mm, width 600 mm,
| kot naprimer Schneider, tip: NSYSPF6100. | such as Schneider, type: NSYSPF6100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1600 mm, | - Lower crossbar with PanelSeT cable entry - 1600 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider | such as Schneider | kos | 15
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider | such as Schneider | kos | 12
| V močnostno omaro +BMS-N3-3-R.1 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-N3-3-R.1 power cabinet:
| - glavno stikalo In=50 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=50 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C113050LS. | such as Schneider, type: C113050LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider | such as Schneider | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 10
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 8
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 3
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 5
| - Sponke 16 mm2 za montažo na DIN letev, | - 16 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 16 | such as Phoenix Contact type: UT 16 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 80
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 40
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 40
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.6 | Dobava in montaža kovinske omare +BMS-N3-3-R.2 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS-N3-3-R.2 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1200 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1200 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2012402DP. | such as Schneider, type: NSYSFN2012402DP. | kos | 1
| - Podstavek 100 mm, širine 1200 mm, | - Base 100 mm, width 1200 mm,
| kot naprimer Schneider, tip: NSYSPF12100. | such as Schneider, type: NSYSPF12100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1200 mm, | - Lower crossbar with PanelSeT cable entry - 1200 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider. | such as Schneider. | kos | 17
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider. | such as Schneider. | kos | 14
| V krmilno omaro +BMS-N3-3-R.2 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-N3-3-R.2 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. |  | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omaro. | - 2x RJ45 socket (communication socket) and associated enclosure for installation in a cabinet. | kos | 1
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 2
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 8
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 4
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Sponke 4 mm2 za montažo na DIN letev, | - 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 4 | such as Phoenix Contact type: UT 4 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 50
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 20
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 20
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.7 | Dobava in montaža kovinske omare +BMS.N3-4-R.1 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS.N3-4-R.1 consisting of one bay, IP 55 RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 600 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 600 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20640P. | such as Schneider, type: NSYSFN20640P. | kos | 1
| - Podstavek 100 mm, širine 600 mm, | - Base 100 mm, width 600 mm,
| kot naprimer Schneider, tip: NSYSPF6100. | such as Schneider, type: NSYSPF6100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1600 mm, | - Lower crossbar with PanelSeT cable entry - 1600 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider | such as Schneider | kos | 15
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider | such as Schneider | kos | 12
| V močnostno omaro +BMS-N3-4-R.1 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-N3-4-R.1 power cabinet:
| - glavno stikalo In=50 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=50 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C113050LS. | such as Schneider, type: C113050LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider | such as Schneider | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 15
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 12
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 3
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 5
| - Sponke 16 mm2 za montažo na DIN letev, | - 16 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 16 | such as Phoenix Contact type: UT 16 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 90
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 50
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 50
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.8 | Dobava in montaža kovinske omare +BMS-N3-4-R.2 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS-N3-4-R.2 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1200 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1200 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2012402DP. | such as Schneider, type: NSYSFN2012402DP. | kos | 1
| - Podstavek 100 mm, širine 1200 mm, | - Base 100 mm, width 1200 mm,
| kot naprimer Schneider, tip: NSYSPF12100. | such as Schneider, type: NSYSPF12100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1200 mm, | - Lower crossbar with PanelSeT cable entry - 1200 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider. | such as Schneider. | kos | 17
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider. | such as Schneider. | kos | 14
| V krmilno omaro +BMS-N3-4-R.2 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-N3-4-R.2 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. |  | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omaro. | - 2x RJ45 socket (communication socket) and associated enclosure for installation in a cabinet. | kos | 1
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 2
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 10
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 5
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Sponke 4 mm2 za montažo na DIN letev, | - 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 4 | such as Phoenix Contact type: UT 4 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 50
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 20
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 20
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.9 | Dobava in montaža kovinske omare +BMS.N2-1-R.1 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS.N2-1-R.1 consisting of one bay, IP 55 RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 600 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 600 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20640P. | such as Schneider, type: NSYSFN20640P. | kos | 1
| - Podstavek 100 mm, širine 600 mm, | - Base 100 mm, width 600 mm,
| kot naprimer Schneider, tip: NSYSPF6100. | such as Schneider, type: NSYSPF6100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1600 mm, | - Lower crossbar with PanelSeT cable entry - 1600 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider | such as Schneider | kos | 15
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider | such as Schneider | kos | 12
| V močnostno omaro +BMS-N2-1-R.1 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-N2-1-R.1 power cabinet:
| - glavno stikalo In=50 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=50 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C113050LS. | such as Schneider, type: C113050LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider | such as Schneider | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 14
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 12
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 3
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 5
| - Sponke 16 mm2 za montažo na DIN letev, | - 16 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 16 | such as Phoenix Contact type: UT 16 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 90
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 50
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 50
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.10 | Dobava in montaža kovinske omare +BMS-N2-1-R.2 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS-N2-1-R.2 consisting of one bay, IP 55 RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1200 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1200 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2012402DP. | such as Schneider, type: NSYSFN2012402DP. | kos | 1
| - Podstavek 100 mm, širine 1200 mm, | - Base 100 mm, width 1200 mm,
| kot naprimer Schneider, tip: NSYSPF12100. | such as Schneider, type: NSYSPF12100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1200 mm, | - Lower crossbar with PanelSeT cable entry - 1200 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider. | such as Schneider. | kos | 17
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider. | such as Schneider. | kos | 14
| V krmilno omaro +BMS-N2-1-R.2 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-N2-1-R.2 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. |  | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omaro. | - 2x RJ45 socket (communication socket) and associated enclosure for installation in a cabinet. | kos | 1
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 2
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 10
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 5
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Sponke 4 mm2 za montažo na DIN letev, | - 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 4 | such as Phoenix Contact type: UT 4 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 50
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 20
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 20
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.11 | Dobava in montaža kovinske omare +BMS.N2-2-R.1 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS.N2-2-R.1 consisting of one bay, IP 55 RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 600 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 600 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20640P. | such as Schneider, type: NSYSFN20640P. | kos | 1
| - Podstavek 100 mm, širine 600 mm, | - Base 100 mm, width 600 mm,
| kot naprimer Schneider, tip: NSYSPF6100. | such as Schneider, type: NSYSPF6100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1600 mm, | - Lower crossbar with PanelSeT cable entry - 1600 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider | such as Schneider | kos | 15
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider | such as Schneider | kos | 12
| V močnostno omaro +BMS-N2-2-R.1 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-N2-2-R.1 power cabinet:
| - glavno stikalo In=50 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=50 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C113050LS. | such as Schneider, type: C113050LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider | such as Schneider | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 16
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 14
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 3
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 5
| - Sponke 16 mm2 za montažo na DIN letev, | - 16 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 16 | such as Phoenix Contact type: UT 16 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 100
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 60
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 60
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.12 | Dobava in montaža kovinske omare +BMS-N2-2-R.2 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS-N2-2-R.2 consisting of one bay, IP 55 RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1600 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1600 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2016402DP. | such as Schneider, type: NSYSFN2016402DP. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1600 mm, | - Lower crossbar with PanelSeT cable entry - 1600 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider. | such as Schneider. | kos | 17
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider. | such as Schneider. | kos | 14
| V krmilno omaro +BMS-N2-2-R.2 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-N2-2-R.2 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. |  | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omaro. | - 2x RJ45 socket (communication socket) and associated enclosure for installation in a cabinet. | kos | 1
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 2
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 15
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 10
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Sponke 4 mm2 za montažo na DIN letev, | - 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 4 | such as Phoenix Contact type: UT 4 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 100
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 30
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 30
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.13 | Dobava in montaža kovinske omare +BMS.N2-3-R.1 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS.N2-3-R.1 consisting of one bay, IP 55 RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 600 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 600 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20640P. | such as Schneider, type: NSYSFN20640P. | kos | 1
| - Podstavek 100 mm, širine 600 mm, | - Base 100 mm, width 600 mm,
| kot naprimer Schneider, tip: NSYSPF6100. | such as Schneider, type: NSYSPF6100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1600 mm, | - Lower crossbar with PanelSeT cable entry - 1600 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider | such as Schneider | kos | 15
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider | such as Schneider | kos | 12
| V močnostno omaro +BMS-N2-3-R.1 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-N2-3-R.1 power cabinet:
| - glavno stikalo In=50 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=50 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C113050LS. | such as Schneider, type: C113050LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider | such as Schneider | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 14
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 12
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 3
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 5
| - Sponke 16 mm2 za montažo na DIN letev, | - 16 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 16 | such as Phoenix Contact type: UT 16 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 90
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 50
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 50
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.14 | Dobava in montaža kovinske omare +BMS-N2-3-R.2 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS-N2-3-R.2 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1200 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1200 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2012402DP. | such as Schneider, type: NSYSFN2012402DP. | kos | 1
| - Podstavek 100 mm, širine 1200 mm, | - Base 100 mm, width 1200 mm,
| kot naprimer Schneider, tip: NSYSPF12100. | such as Schneider, type: NSYSPF12100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1200 mm, | - Lower crossbar with PanelSeT cable entry - 1200 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider. | such as Schneider. | kos | 17
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider. | such as Schneider. | kos | 14
| V krmilno omaro +BMS-N2-3-R.2 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-N2-3-R.2 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. |  | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omaro. | - 2x RJ45 socket (communication socket) and associated enclosure for installation in a cabinet. | kos | 1
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 2
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 10
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 5
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Sponke 4 mm2 za montažo na DIN letev, | - 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 4 | such as Phoenix Contact type: UT 4 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 50
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 20
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 20
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.15 | Dobava in montaža kovinske omare +BMS.N2-4-R.1 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS.N2-4-R.1 consisting of one bay, IP 55 RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 800 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 800 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20840P | such as Schneider, type: NSYSFN20840P | kos | 1
| - Podstavek 100 mm, širine 800 mm, | - Base 100 mm, width 800 mm,
| kot naprimer Schneider, tip: NSYSPF8100. | such as Schneider, type: NSYSPF8100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1600 mm, | - Lower crossbar with PanelSeT cable entry - 1600 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider | such as Schneider | kos | 15
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider | such as Schneider | kos | 12
| V močnostno omaro +BMS-N2-4-R.1 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-N2-4-R.1 power cabinet:
| - glavno stikalo In=50 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=50 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C113050LS. | such as Schneider, type: C113050LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider | such as Schneider | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 23
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 16
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 3
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 5
| - Sponke 16 mm2 za montažo na DIN letev, | - 16 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 16 | such as Phoenix Contact type: UT 16 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 120
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 70
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 70
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.16 | Dobava in montaža kovinske omare +BMS-N2-4-R.2 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS-N2-4-R.2 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1200 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1200 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2012402DP. | such as Schneider, type: NSYSFN2012402DP. | kos | 2
| - Podstavek 100 mm, širine 1200 mm, | - Base 100 mm, width 1200 mm,
| kot naprimer Schneider, tip: NSYSPF12100. | such as Schneider, type: NSYSPF12100. | kos | 2
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 2
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 2
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 2
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 2
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 2
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1200 mm, | - Lower crossbar with PanelSeT cable entry - 1200 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 2
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider. | such as Schneider. | kos | 28
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider. | such as Schneider. | kos | 22
| V krmilno omaro +BMS-N2-4-R.2 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-N2-4-R.2 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. |  | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omaro. | - 2x RJ45 socket (communication socket) and associated enclosure for installation in a cabinet. | kos | 1
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 2
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 4
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 17
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 10
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 2
| - Sponke 4 mm2 za montažo na DIN letev, | - 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 4 | such as Phoenix Contact type: UT 4 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 120
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 70
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 70
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.17 | Dobava in montaža kovinske omare +BMS.N1-1-R.1 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS.N1-1-R.1 consisting of one bay, IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 600 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 600 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20640P. | such as Schneider, type: NSYSFN20640P. | kos | 1
| - Podstavek 100 mm, širine 600 mm, | - Base 100 mm, width 600 mm,
| kot naprimer Schneider, tip: NSYSPF6100. | such as Schneider, type: NSYSPF6100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1600 mm, | - Lower crossbar with PanelSeT cable entry - 1600 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider | such as Schneider | kos | 15
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider | such as Schneider | kos | 12
| V močnostno omaro +BMS-N1-1-R.1 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-N1-1-R.1 power cabinet:
| - glavno stikalo In=50 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=50 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C113050LS. | such as Schneider, type: C113050LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider | such as Schneider | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 14
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 12
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 3
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 5
| - Sponke 16 mm2 za montažo na DIN letev, | - 16 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 16 | such as Phoenix Contact type: UT 16 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 90
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 50
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 50
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.18 | Dobava in montaža kovinske omare +BMS-N1-1-R.2 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS-N1-1-R.2 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1200 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1200 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2012402DP. | such as Schneider, type: NSYSFN2012402DP. | kos | 1
| - Podstavek 100 mm, širine 1200 mm, | - Base 100 mm, width 1200 mm,
| kot naprimer Schneider, tip: NSYSPF12100. | such as Schneider, type: NSYSPF12100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1200 mm, | - Lower crossbar with PanelSeT cable entry - 1200 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider. | such as Schneider. | kos | 17
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider. | such as Schneider. | kos | 14
| V krmilno omaro +BMS-N1-1-R.2 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-N1-1-R.2 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. |  | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omaro. | - 2x RJ45 socket (communication socket) and associated enclosure for installation in a cabinet. | kos | 1
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 2
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 10
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 5
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Sponke 4 mm2 za montažo na DIN letev, | - 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 4 | such as Phoenix Contact type: UT 4 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 50
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 20
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 20
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.19 | Dobava in montaža kovinske omare +BMS.N1-2-R.1 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS.N1-2-R.1 consisting of one bay, IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 600 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 600 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20640P. | such as Schneider, type: NSYSFN20640P. | kos | 1
| - Podstavek 100 mm, širine 600 mm, | - Base 100 mm, width 600 mm,
| kot naprimer Schneider, tip: NSYSPF6100. | such as Schneider, type: NSYSPF6100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1600 mm, | - Lower crossbar with PanelSeT cable entry - 1600 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider | such as Schneider | kos | 15
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider | such as Schneider | kos | 12
| V močnostno omaro +BMS-N1-2-R.1 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-N1-2-R.1 power cabinet:
| - glavno stikalo In=50 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=50 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C113050LS. | such as Schneider, type: C113050LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider | such as Schneider | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 16
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 14
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 3
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 5
| - Sponke 16 mm2 za montažo na DIN letev, | - 16 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 16 | such as Phoenix Contact type: UT 16 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 100
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 60
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 60
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.20 | Dobava in montaža kovinske omare +BMS-N1-2-R.2 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS-N1-2-R.2 consisting of one bay, IP 55 RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1600 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1600 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2016402DP. | such as Schneider, type: NSYSFN2016402DP. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1600 mm, | - Lower crossbar with PanelSeT cable entry - 1600 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider. | such as Schneider. | kos | 17
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider. | such as Schneider. | kos | 14
| V krmilno omaro +BMS-N1-2-R.2 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-N1-2-R.2 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. |  | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omaro. | - 2x RJ45 socket (communication socket) and associated enclosure for installation in a cabinet. | kos | 1
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 2
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 15
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 10
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Sponke 4 mm2 za montažo na DIN letev, | - 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 4 | such as Phoenix Contact type: UT 4 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 100
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 30
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 30
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.21 | Dobava in montaža kovinske omare +BMS.N1-3-R.1 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS.N1-3-R.1 consisting of one bay, IP 55 RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 600 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 600 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20640P. | such as Schneider, type: NSYSFN20640P. | kos | 1
| - Podstavek 100 mm, širine 600 mm, | - Base 100 mm, width 600 mm,
| kot naprimer Schneider, tip: NSYSPF6100. | such as Schneider, type: NSYSPF6100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1600 mm, | - Lower crossbar with PanelSeT cable entry - 1600 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider | such as Schneider | kos | 15
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider | such as Schneider | kos | 12
| V močnostno omaro +BMS-N1-3-R.1 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-N1-3-R.1 power cabinet:
| - glavno stikalo In=50 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=50 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C113050LS. | such as Schneider, type: C113050LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider | such as Schneider | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 20
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 18
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 3
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 5
| - Sponke 16 mm2 za montažo na DIN letev, | - 16 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 16 | such as Phoenix Contact type: UT 16 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 100
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 70
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 70
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.22 | Dobava in montaža kovinske omare +BMS-N1-3-R.2 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS-N1-3-R.2 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1600 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1600 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2016402DP. | such as Schneider, type: NSYSFN2016402DP. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1600 mm, | - Lower crossbar with PanelSeT cable entry - 1600 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider. | such as Schneider. | kos | 20
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider. | such as Schneider. | kos | 16
| V krmilno omaro +BMS-N1-3-R.2 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-N1-3-R.2 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. |  | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omaro. | - 2x RJ45 socket (communication socket) and associated enclosure for installation in a cabinet. | kos | 1
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 2
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 15
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 10
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Sponke 4 mm2 za montažo na DIN letev, | - 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 4 | such as Phoenix Contact type: UT 4 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 120
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 40
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 40
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.23 | Dobava in montaža kovinske omare +BMS.N1-4-R.1 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS.N1-4-R.1 consisting of one bay, IP 55 RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 600 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 600 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20640P. | such as Schneider, type: NSYSFN20640P. | kos | 1
| - Podstavek 100 mm, širine 600 mm, | - Base 100 mm, width 600 mm,
| kot naprimer Schneider, tip: NSYSPF6100. | such as Schneider, type: NSYSPF6100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1600 mm, | - Lower crossbar with PanelSeT cable entry - 1600 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider | such as Schneider | kos | 15
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider | such as Schneider | kos | 12
| V močnostno omaro +BMS-N1-4-R.1 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-N1-4-R.1 power cabinet:
| - glavno stikalo In=50 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=50 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C113050LS. | such as Schneider, type: C113050LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider | such as Schneider | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 16
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 14
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 3
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 5
| - Sponke 16 mm2 za montažo na DIN letev, | - 16 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 16 | such as Phoenix Contact type: UT 16 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 100
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 60
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 60
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.24 | Dobava in montaža kovinske omare +BMS-N1-4-R.2 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS-N1-4-R.2 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1600 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1600 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2016402DP. | such as Schneider, type: NSYSFN2016402DP. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1600 mm, | - Lower crossbar with PanelSeT cable entry - 1600 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider. | such as Schneider. | kos | 17
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider. | such as Schneider. | kos | 14
| V krmilno omaro +BMS-N1-4-R.2 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-N1-4-R.2 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. |  | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omaro. | - 2x RJ45 socket (communication socket) and associated enclosure for installation in a cabinet. | kos | 1
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 2
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 15
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 10
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Sponke 4 mm2 za montažo na DIN letev, | - 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 4 | such as Phoenix Contact type: UT 4 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 100
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 30
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 30
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.25 | Dobava in montaža kovinske omare +BMS.N1-5-R.1 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS.N1-5-R.1 consisting of one bay, IP 55 RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 600 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 600 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20640P. | such as Schneider, type: NSYSFN20640P. | kos | 1
| - Podstavek 100 mm, širine 600 mm, | - Base 100 mm, width 600 mm,
| kot naprimer Schneider, tip: NSYSPF6100. | such as Schneider, type: NSYSPF6100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1600 mm, | - Lower crossbar with PanelSeT cable entry - 1600 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider | such as Schneider | kos | 15
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider | such as Schneider | kos | 12
| V močnostno omaro +BMS-N1-5-R.1 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-N1-5-R.1 power cabinet:
| - glavno stikalo In=50 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=50 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C113050LS. | such as Schneider, type: C113050LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider | such as Schneider | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 10
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 8
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 3
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 5
| - Sponke 16 mm2 za montažo na DIN letev, | - 16 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 16 | such as Phoenix Contact type: UT 16 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 80
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 40
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 40
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.26 | Dobava in montaža kovinske omare +BMS-N1-5-R.2 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS-N1-5-R.2 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1200 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1200 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2012402DP. | such as Schneider, type: NSYSFN2012402DP. | kos | 1
| - Podstavek 100 mm, širine 1200 mm, | - Base 100 mm, width 1200 mm,
| kot naprimer Schneider, tip: NSYSPF12100. | such as Schneider, type: NSYSPF12100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1200 mm, | - Lower crossbar with PanelSeT cable entry - 1200 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider. | such as Schneider. | kos | 17
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider. | such as Schneider. | kos | 14
| V krmilno omaro +BMS-N1-5-R.2 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-N1-5-R.2 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. |  | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omaro. | - 2x RJ45 socket (communication socket) and associated enclosure for installation in a cabinet. | kos | 1
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 2
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 8
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 4
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Sponke 4 mm2 za montažo na DIN letev, | - 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 4 | such as Phoenix Contact type: UT 4 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 50
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 20
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 20
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.27 | Dobava in montaža kovinske omare +BMS.N1-6-R.1 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS.N1-6-R.1 consisting of one bay, IP 55 RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 600 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 600 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20640P. | such as Schneider, type: NSYSFN20640P. | kos | 1
| - Podstavek 100 mm, širine 600 mm, | - Base 100 mm, width 600 mm,
| kot naprimer Schneider, tip: NSYSPF6100. | such as Schneider, type: NSYSPF6100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1600 mm, | - Lower crossbar with PanelSeT cable entry - 1600 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider | such as Schneider | kos | 15
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider | such as Schneider | kos | 12
| V močnostno omaro +BMS-N1-6-R.1 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-N1-6-R.1 power cabinet:
| - glavno stikalo In=50 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=50 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C113050LS. | such as Schneider, type: C113050LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider | such as Schneider | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 15
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 12
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 3
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 5
| - Sponke 16 mm2 za montažo na DIN letev, | - 16 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 16 | such as Phoenix Contact type: UT 16 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 90
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 50
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 50
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.28 | Dobava in montaža kovinske omare +BMS-N1-6-R.2 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS-N1-6-R.2 consisting of one bay, IP 55 RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1200 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1200 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2012402DP. | such as Schneider, type: NSYSFN2012402DP. | kos | 1
| - Podstavek 100 mm, širine 1200 mm, | - Base 100 mm, width 1200 mm,
| kot naprimer Schneider, tip: NSYSPF12100. | such as Schneider, type: NSYSPF12100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1200 mm, | - Lower crossbar with PanelSeT cable entry - 1200 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider. | such as Schneider. | kos | 17
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider. | such as Schneider. | kos | 14
| V krmilno omaro +BMS-N1-6-R.2 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-N1-6-R.2 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. |  | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omaro. | - 2x RJ45 socket (communication socket) and associated enclosure for installation in a cabinet. | kos | 1
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 2
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 10
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 5
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Sponke 4 mm2 za montažo na DIN letev, | - 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 4 | such as Phoenix Contact type: UT 4 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 50
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 20
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 20
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.29 | Dobava in montaža kovinske omare +BMS.P1-1-R.1 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS.P1-1-R.1 consisting of one bay, IP 55 RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 600 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 600 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20640P. | such as Schneider, type: NSYSFN20640P. | kos | 1
| - Podstavek 100 mm, širine 600 mm, | - Base 100 mm, width 600 mm,
| kot naprimer Schneider, tip: NSYSPF6100. | such as Schneider, type: NSYSPF6100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1600 mm, | - Lower crossbar with PanelSeT cable entry - 1600 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider | such as Schneider | kos | 15
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider | such as Schneider | kos | 12
| V močnostno omaro +BMS-P1-1-R.1 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-P1-1-R.1 power cabinet:
| - glavno stikalo In=50 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=50 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C113050LS. | such as Schneider, type: C113050LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider | such as Schneider | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 10
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 8
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 3
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 5
| - Sponke 16 mm2 za montažo na DIN letev, | - 16 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 16 | such as Phoenix Contact type: UT 16 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 80
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 40
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 40
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.30 | Dobava in montaža kovinske omare +BMS-P1-1-R.2 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS-P1-1-R.2 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1200 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1200 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2012402DP. | such as Schneider, type: NSYSFN2012402DP. | kos | 1
| - Podstavek 100 mm, širine 1200 mm, | - Base 100 mm, width 1200 mm,
| kot naprimer Schneider, tip: NSYSPF12100. | such as Schneider, type: NSYSPF12100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1200 mm, | - Lower crossbar with PanelSeT cable entry - 1200 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider. | such as Schneider. | kos | 17
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider. | such as Schneider. | kos | 14
| V krmilno omaro +BMS-P1-1-R.2 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-P1-1-R.2 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. |  | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omaro. | - 2x RJ45 socket (communication socket) and associated enclosure for installation in a cabinet. | kos | 1
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 2
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 8
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 4
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Sponke 4 mm2 za montažo na DIN letev, | - 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 4 | such as Phoenix Contact type: UT 4 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 50
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 20
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 20
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.31 | Dobava in montaža kovinske omare +BMS.P1-2-R.1 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS.P1-2-R.1 consisting of one bay, IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 600 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 600 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20640P. | such as Schneider, type: NSYSFN20640P. | kos | 1
| - Podstavek 100 mm, širine 600 mm, | - Base 100 mm, width 600 mm,
| kot naprimer Schneider, tip: NSYSPF6100. | such as Schneider, type: NSYSPF6100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1600 mm, | - Lower crossbar with PanelSeT cable entry - 1600 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider | such as Schneider | kos | 15
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider | such as Schneider | kos | 12
| V močnostno omaro +BMS-P1-2-R.1 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-P1-2-R.1 power cabinet:
| - glavno stikalo In=50 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=50 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C113050LS. | such as Schneider, type: C113050LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider | such as Schneider | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 10
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 8
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 3
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 5
| - Sponke 16 mm2 za montažo na DIN letev, | - 16 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 16 | such as Phoenix Contact type: UT 16 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 80
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 40
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 40
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.32 | Dobava in montaža kovinske omare +BMS-P1-2-R.2 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS-P1-2-R.2 consisting of one bay, IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1200 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1200 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2012402DP. | such as Schneider, type: NSYSFN2012402DP. | kos | 1
| - Podstavek 100 mm, širine 1200 mm, | - Base 100 mm, width 1200 mm,
| kot naprimer Schneider, tip: NSYSPF12100. | such as Schneider, type: NSYSPF12100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1200 mm, | - Lower crossbar with PanelSeT cable entry - 1200 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider. | such as Schneider. | kos | 17
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider. | such as Schneider. | kos | 14
| V krmilno omaro +BMS-P1-2-R.2 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-P1-2-R.2 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. |  | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omaro. | - 2x RJ45 socket (communication socket) and associated enclosure for installation in a cabinet. | kos | 1
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 2
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 8
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 4
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Sponke 4 mm2 za montažo na DIN letev, | - 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 4 | such as Phoenix Contact type: UT 4 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 50
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 20
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 20
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.33 | Dobava in montaža kovinske omare +BMS.P1-3-R.1 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS.P1-3-R.1 consisting of one bay, IP 55 RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 800 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 800 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20840P | such as Schneider, type: NSYSFN20840P | kos | 1
| - Podstavek 100 mm, širine 800 mm, | - Base 100 mm, width 800 mm,
| kot naprimer Schneider, tip: NSYSPF8100. | such as Schneider, type: NSYSPF8100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1600 mm, | - Lower crossbar with PanelSeT cable entry - 1600 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider | such as Schneider | kos | 15
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider | such as Schneider | kos | 12
| V močnostno omaro +BMS-P1-3-R.1 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-P1-3-R.1 power cabinet:
| - glavno stikalo In=50 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=50 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C113050LS. | such as Schneider, type: C113050LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider | such as Schneider | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 26
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 19
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 3
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 5
| - Sponke 16 mm2 za montažo na DIN letev, | - 16 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 16 | such as Phoenix Contact type: UT 16 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 150
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 80
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 80
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.34 | Dobava in montaža kovinske omare +BMS-P1-3-R.2 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS-P1-3-R.2 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1200 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1200 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2012402DP. | such as Schneider, type: NSYSFN2012402DP. | kos | 2
| - Podstavek 100 mm, širine 1200 mm, | - Base 100 mm, width 1200 mm,
| kot naprimer Schneider, tip: NSYSPF12100. | such as Schneider, type: NSYSPF12100. | kos | 2
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 2
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 2
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 2
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 2
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 2
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1200 mm, | - Lower crossbar with PanelSeT cable entry - 1200 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 2
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider. | such as Schneider. | kos | 28
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider. | such as Schneider. | kos | 22
| V krmilno omaro +BMS-P1-3-R.2 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the control cabinet +BMS-P1-3-R.2:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. |  | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omaro. | - 2x RJ45 socket (communication socket) and associated enclosure for installation in a cabinet. | kos | 1
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 2
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 4
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 20
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 15
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 2
| - Sponke 4 mm2 za montažo na DIN letev, | - 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 4 | such as Phoenix Contact type: UT 4 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 150
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 70
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 70
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.35 | Dobava in montaža kovinske omare +BMS.P1-4-R.1 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS.P1-4-R.1 consisting of one bay, IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 600 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 600 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20640P. | such as Schneider, type: NSYSFN20640P. | kos | 1
| - Podstavek 100 mm, širine 600 mm, | - Base 100 mm, width 600 mm,
| kot naprimer Schneider, tip: NSYSPF6100. | such as Schneider, type: NSYSPF6100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1600 mm, | - Lower crossbar with PanelSeT cable entry - 1600 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider | such as Schneider | kos | 15
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider | such as Schneider | kos | 12
| V močnostno omaro +BMS-P1-4-R.1 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-P1-4-R.1 power cabinet:
| - glavno stikalo In=50 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=50 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C113050LS. | such as Schneider, type: C113050LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider | such as Schneider | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 16
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 14
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 3
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 5
| - Sponke 16 mm2 za montažo na DIN letev, | - 16 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 16 | such as Phoenix Contact type: UT 16 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 100
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 60
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 60
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.36 | Dobava in montaža kovinske omare +BMS-P1-4-R.2 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS-P1-4-R.2 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1600 mm in globina 400 mm. Celotna omara stoji na podstavku višine 200 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1600 mm and depth 400 mm. The whole cabinet stands on a base of 200 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2016402DP. | such as Schneider, type: NSYSFN2016402DP. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1600 mm, | - Lower crossbar with PanelSeT cable entry - 1600 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta SZ (za kable z opletom premera fi=3-10mm), | - EMC braid connector SZ (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider. | such as Schneider. | kos | 17
| - Objemka za pritrjevanje kabla DK (za kable premera fi=6-14mm), | - DK cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider. | such as Schneider. | kos | 14
| V krmilno omaro +BMS-P1-4-R.2 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-P1-4-R.2 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. |  | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omaro. | - 2x RJ45 socket (communication socket) and associated enclosure for installation in a cabinet. | kos | 1
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 2
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 15
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 10
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Sponke 4 mm2 za montažo na DIN letev, | - 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 4 | such as Phoenix Contact type: UT 4 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 100
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 30
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 30
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.37 | Dobava in montaža kovinske omare +BMS.P1-5-R.1 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS.P1-5-R.1 consisting of one bay, IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 600 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 600 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20640P. | such as Schneider, type: NSYSFN20640P. | kos | 1
| - Podstavek 100 mm, širine 600 mm, | - Base 100 mm, width 600 mm,
| kot naprimer Schneider, tip: NSYSPF6100. | such as Schneider, type: NSYSPF6100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1600 mm, | - Lower crossbar with PanelSeT cable entry - 1600 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider | such as Schneider | kos | 15
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider | such as Schneider | kos | 12
| V močnostno omaro +BMS-P1-5-R.1 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-P1-5-R.1 power cabinet:
| - glavno stikalo In=50 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=50 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C113050LS. | such as Schneider, type: C113050LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider | such as Schneider | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 13
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 11
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 3
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 5
| - Sponke 16 mm2 za montažo na DIN letev, | - 16 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 16 | such as Phoenix Contact type: UT 16 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 80
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 30
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 30
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.38 | Dobava in montaža kovinske omare +BMS-P1-5-R.2 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS-P1-5-R.2 consisting of one bay in IP 55 protection RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1200 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1200 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2012402DP. | such as Schneider, type: NSYSFN2012402DP. | kos | 1
| - Podstavek 100 mm, širine 1200 mm, | - Base 100 mm, width 1200 mm,
| kot naprimer Schneider, tip: NSYSPF12100. | such as Schneider, type: NSYSPF12100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1200 mm, | - Lower crossbar with PanelSeT cable entry - 1200 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider. | such as Schneider. | kos | 17
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider. | such as Schneider. | kos | 14
| V krmilno omaro +BMS-P1-5-R.2 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-P1-5-R.2 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. |  | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omaro. | - 2x RJ45 socket (communication socket) and associated enclosure for installation in a cabinet. | kos | 1
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 2
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 10
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 5
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Sponke 4 mm2 za montažo na DIN letev, | - 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 4 | such as Phoenix Contact type: UT 4 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 50
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 20
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 20
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.39 | Dobava in montaža kovinske omare +BMS.P1-6-R.1 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS.P1-6-R.1 consisting of one bay, IP 55 RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 600 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 600 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN20640P. | such as Schneider, type: NSYSFN20640P. | kos | 1
| - Podstavek 100 mm, širine 600 mm, | - Base 100 mm, width 600 mm,
| kot naprimer Schneider, tip: NSYSPF6100. | such as Schneider, type: NSYSPF6100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1600 mm, | - Lower crossbar with PanelSeT cable entry - 1600 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider | such as Schneider | kos | 15
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider | such as Schneider | kos | 12
| V močnostno omaro +BMS-P1-6-R.1 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-P1-6-R.1 power cabinet:
| - glavno stikalo In=50 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=50 A with accessories: concealment of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: C113050LS. | such as Schneider, type: C113050LS. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: LV426934T. | such as Schneider, type: LV426934T. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 4-polni, Imax=40 kA, In=15 kA Class II, | - 4-pole surge arrester, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40601. | such as Schneider, type: A9L40601. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Rittal, tip: 2500.460. | such as Rittal, type: 2500.460. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider | such as Schneider | kos | 1
| - Napetostni krmilni rele, obseg 183 do 528 V AC, 1 C/O, | - Voltage control relay, range 183 to 528 V AC, 1 C/O,
| kot naprimer Schneider, tip: RM17UB310. | such as Schneider, type: RM17UB310. | kos | 1
| - Varovalčni ločilnik 2P, 25 A, za varovalko 10,3x38 mm - varovalka gG 1 A, | - Fuse disconnector 2P, 25 A, for fuse 10,3x38 mm - fuse gG 1 A,
| kot naprimer Schneider, tip: kot naprimer: A9N15651. | such as Schneider, type: such as A9N15651. | kos | 1
| - Tripolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Tripolar installation circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84304. | such as Schneider, Acti 9 iC60H, type: A9F84304. | kos | 1
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 12
| - Enopolni inštalacijski odklopnik 16 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 16 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84116. | such as Schneider, Acti 9 iC60H, type: A9F84116. | kos | 10
| - Bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - White complete LED signal lamp, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 3
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 3
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 5
| - Sponke 16 mm2 za montažo na DIN letev, | - 16 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 16 | such as Phoenix Contact type: UT 16 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 80
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 30
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 30
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.40 | Dobava in montaža kovinske omare +BMS-P1-6-R.2 sestavljene iz enega polja v zaščiti IP 55 barve RAL 7035. | Supply and installation of a metal cabinet +BMS-P1-6-R.2 consisting of one bay, IP 55 RAL 7035. |  |  | kpl | 1 |  | 0
| kot naprimer tip: “Schneider”, tip: SFN. | such as type: "Schneider", type: "SFN".
| Dimenzije omare so: višina 2000 mm, širina 1200 mm in globina 400 mm. Celotna omara stoji na podstavku višine 100 mm. Izdelava zaokrožnice za podstavek elektro omare. Omara ima dvokrilna vrata po celi višini spredaj, konfortno ročko in dvo-peresnim zapiralom na ključ. | The dimensions of the cabinet are: height 2000 mm, width 1200 mm and depth 400 mm. The whole cabinet stands on a base of 100 mm height. The rounding for the base of the electrical cabinet is made. The cabinet has a full-height double-leaf door at the front, a comfort handle and a key-operated two-perforation lock.
| OPOMBA: na vratih so izvedene odprtine za prezračevanje in vgrajeni filtri za zrak. V notranjosti omare se montira predal za dokumentacijo. | NOTE: Ventilation openings and air filters shall be provided on the doors. A documentation drawer shall be fitted inside the cabinet.
| - Osnovna omara (vrata z dvo-peresnim zapiranjem, montažna plošča, zadnja stena, zgornaj plošča, spodnja plošča in ostali pribor), | - Base cabinet (bi-folding door, mounting plate, rear panel, top panel, bottom panel and other accessories),
| kot naprimer Schneider, tip: NSYSFN2012402DP. | such as Schneider, type: NSYSFN2012402DP. | kos | 1
| - Podstavek 100 mm, širine 1200 mm, | - Base 100 mm, width 1200 mm,
| kot naprimer Schneider, tip: NSYSPF12100. | such as Schneider, type: NSYSPF12100. | kos | 1
| - stranica podstavka 100 mm, globine 400 mm, | - base side 100 mm, depth 400 mm,
| kot naprimer Schneider, tip: NSYSPS4100. | such as Schneider, type: NSYSPS4100. | kos | 1
| - Stranska desna stena, | - Right side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Stranska leva stena, | - Left side wall,
| kot naprimer Schneider, tip: NSY2SPN204. | such as Schneider, type: NSY2SPN204. | kos | 1
| - Ročka za odpiranje, | - Opening handle,
| kot naprimer Schneider, tip: NSYBLKHN123. | such as Schneider, type: NSYBLKHN123. | kos | 1
| - Cilinder vložek, | - Cylinder insert,
| kot naprimer Schneider, tip: NSYINE11. | such as Schneider, type: NSYINE11. | kos | 1
| - Torba za načrte A4, | - A4 plan bag,
| kot naprimer Schneider, tip: NSYDPA4. | such as Schneider, type: NSYDPA4. | kos | 1
| - Spodnja prečna letev s kabelsko uvodnico PanelSeT - 1200 mm, | - Lower crossbar with PanelSeT cable entry - 1200 mm,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - EMC spojka opleta (za kable z opletom premera fi=3-10mm), | - EMC braid connector (for cables with braid diameter fi=3-10mm),
| kot naprimer Schneider. | such as Schneider. | kos | 17
| - Objemka za pritrjevanje kabla (za kable premera fi=6-14mm), | - Cable clamp (for cables with diameter fi=6-14mm),
| kot naprimer Schneider. | such as Schneider. | kos | 14
| V krmilno omaro +BMS-P1-6-R.2 se dobavi in vgradi naslednja elektro oprema: | The following electrical equipment shall be supplied and installed in the +BMS-P1-6-R.2 control cabinet:
| - glavno stikalo In=40 A s priborom: prikritje priključnih sponk, ročica za montažo v omaro možnost namestitve ključavnice (obešanke) na stikalo, sponke. Stikalo mora biti skladno in označeno z zahtevami sistema LOTO, | - main switch In=40 A with accessories: concealing of terminals, handle for mounting in the cabinet possibility of fitting a lock (padlock) on the switch, terminals. The switch shall comply with and be marked according to the requirements of the LOTO system,
| kot naprimer Schneider, tip: A9S70640. | such as Schneider, type: A9S70640. | kos | 1
| - Vrtljiva podaljšana ročica za krmiljenje glavnega ločilnega stikala, | - Rotatable extended lever for controlling the main isolating switch,
| kot naprimer Schneider, tip: A9A27006. | such as Schneider, type: A9A27006. | kos | 1
| - Adapterski mehanizem za podaljšano ročico, | - Adapter mechanism for extended handle,
| kot naprimer Schneider, tip: A9A27008. | such as Schneider, type: A9A27008. | kos | 1
| - Prenapetostni odvodnik 1P+N, Imax=40 kA, In=15 kA Class II, | - Surge arrester 1P+N, Imax=40 kA, In=15 kA Class II,
| kot naprimer Schneider, tip: A9L40500. | such as Schneider, type: A9L40500. | kos | 1
| - Vgradna vtičnica 250V, 16A, za montažo na DIN letev, | - 250V, 16A, DIN rail mounting socket,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - končno stikalo za LED luč 230V 1A, | - limit switch for LED light 230V 1A,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Luč za v omaro Led, 11W, 230V, brez vtičnice, z vklop/izklop, 4000K, priključni kabel za LED svetilko. | - Led cabinet light, 11W, 230V, without socket, with on/off switch, 4000K, connecting cable for LED lamp.
| kot naprimer Schneider. | such as Schneider. |  | 1
| - Prostorski termostat, 5-60 °C, 230 VAC, | - Room thermostat, 5-60 °C, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Ventilator za prezr. omare s filtrom, 230 VAC, | - Cabinet fan with filter, 230 VAC,
| kot naprimer Schneider. | such as Schneider. | kos | 1
| - Vtičnica 2x RJ45 (komunikacijska vtičnica) ter pripadajoče ohišje za namestitev v omaro. | - 2x RJ45 socket (communication socket) and associated enclosure for installation in a cabinet. | kos | 1
| - Enopolni inštalacijski odklopnik 4 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 4 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84104. | such as Schneider, Acti 9 iC60H, type: A9F84104. | kos | 2
| - Enopolni inštalacijski odklopnik 6 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 6 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84106. | such as Schneider, Acti 9 iC60H, type: A9F84106. | kos | 2
| - Enopolni inštalacijski odklopnik 10 A, s C karakteristiko, 15 kA, | - Single-pole circuit breaker 10 A, with C characteristic, 15 kA,
| kot naprimer Schneider, Acti 9 iC60H, tip: A9F84110. | such as Schneider, Acti 9 iC60H, type: A9F84110. | kos | 2
| - Vgradna bela kompletna signalna svetilka LED, Ø 22, 230 do 240 V, | - Recessed white LED signal light, Ø 22, 230 to 240 V,
| kot naprimer Schneider tip: XB4BVM1 + ZBZ32. | like for example Schneider tip: XB4BVM1 + ZBZ32. | kos | 1
| - Rele-sponka, 24 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 24 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-24UC/21-21. | such as Phoenix Contact type: PLC-RSC-24UC/21-21. | kos | 10
| - Rele-sponka, 230 VAC/DC (2x CO preklopni kontakt), | - Relay-coupler, 230 VAC/DC (2x CO switching contact),
| kot na primer Phoenix Contact tip: PLC-RSC-230UC/21-21. | such as Phoenix Contact type: PLC-RSC-230UC/21-21. | kos | 5
| - Napajalnik 230 VAC/24 VDC-10 A z kratkostično zaščito 1-10 A, | - Power supply 230 VAC/24 VDC-10 A with short-circuit protection 1-10 A,
| kot na primer Phoenix Contact tip: TRIO 3, 1252696 | such as Phoenix Contact type: TRIO 3, 1252696 | kos | 1
| - Sponke 4 mm2 za montažo na DIN letev, | - 4 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: UT 4 | such as Phoenix Contact type: UT 4 | kos | 3
| - Sponke 2,5 mm2 za montažo na DIN letev, | - 2.5 mm2 DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT | such as Phoenix Contact type: PT 2,5 - MT | kos | 50
| - Sponke 2,5 mm2 modre za montažo na DIN letev, | - 2,5 mm2 blue DIN rail mounting clips,
| kot na primer Phoenix Contact tip: PT 2,5 - MT BU | such as Phoenix Contact type: PT 2,5 - MT BU | kos | 20
| - Sponke ozemljitvene 2,5 mm2 za montažo na DIN letev, | - Earthing clips 2,5 mm2 for DIN rail mounting,
| kot na primer Phoenix Contact tip: PT 2,5 PE | such as Phoenix Contact type: PT 2,5 PE | kos | 20
| Izdelava tokovnih delavniških shem razdelilnega sestava glede na dobavljeno opremo BMS sistema. | Creation of current flow diagrams of the distribution assembly according to the BMS system equipment supplied. | kpl | 1
| Komplet z elektro inštalacijskim materialom, uvodnicami, bakerenimi zbiralkami, sistemskimi kabli, ožičenjem, izenačevanjem potencialov, označevanjem kablov, napisnimi ploščicami, tesnili, … | Complete with electrical installation materials, prefixes, copper busbars, system cables, wiring, equipotential bonding, cable marking, nameplates, gaskets, .. | kpl | 1
5.41 | - Dobava in montaža razdelilne doze za nadometno montažo 104 x 104 mm, komplet z ranžirnimi sponkami, | - Supply and installation of a 104 x 104 mm overhead distribution box, complete with shunting clips, |  |  | kpl | 120 |  | 0
| kot na primer Phoenix Contact distribucijski blok tip: PTFIX 6x2,5 BN + distribucijski blok tip: PTFIX 6x2,5 BU + distribucijski ozemljitveni blok tip: PTFIX 6x2,5 GNYE, 2 x zaključni blok PTFIX-F | such as Phoenix Contact distribution block type: PTFIX 6x2,5 BN + distribution block type: PTFIX 6x2,5 BU + distribution earthing block type: PTFIX 6x2,5 GNYE, 2 x termination block PTFIX-F
5.42 | - Dobava in polaganje na kabelske police oz. uvlečenje v inštalacijske cevi kabla F/FTP-Category 6A, 4x2, 23 AWG,halogen free, za PROFINET oz. ETHERNET komunikacijo. | - Supply and installation of F/FTP-Category 6A, 4x2, 23 AWG, halogen free, for PROFINET or ETHERNET communication on cable racks or in installation pipes. |  |  | m | 5500 |  | 0
5.43 | - Dobava in polaganje protipožarnega kabla (klasifikacije Cca-S2-d2-a1) na kabelske police in v zaščitne cevi, | - Supply and installation of fire-fighting cable (classification Cca-S2-d2-a1) on cable racks and in protection tubes,
| kot primer LAPP: | as an example of LAPP:
| - LiHCH 2x1 mm2 | - LiHCH 2x1 mm2 |  |  | m | 20730 |  | 0
| - LiHCH 4x1 mm2 | - LiHCH 4x1 mm2 |  |  | m | 6500 |  | 0
5.44 | - Dobava in polaganje protipožarnega kabla (klasifikacije Cca-S2-d2-a1) na kabelske police in v zaščitne cevi, | - Supply and installation of fire-fighting cable (classification Cca-S2-d2-a1) on cable racks and in protection tubes,
| kot primer LAPP: | as an example of LAPP:
| - OL-100H 3G1,5 mm2 | - OL-100H 3G1,5 mm2 |  |  | m | 43700 |  | 0
| - OL-100H 3G2,5 mm2 | - OL-100H 3G2,5 mm2 |  |  | m | 20130 |  | 0
| - OL-100H 5G1,5 mm2 | - OL-100H 5G1,5 mm2 |  |  | m | 37840 |  | 0
5.45 | Dobava in montaža vodnikov za izenačevanje potencialov: | Supply and installation of equipotential bonding conductors:
| - HO7V-K 6 mm2 | - HO7V-K 6 mm2 |  |  | m | 250 |  | 0
| - HO7V-K 10 mm2 | - HO7V-K 10 mm2 |  |  | m | 110 |  | 0
| - HO7V-K 16 mm2 | - HO7V-K 16 mm2 |  |  | m | 100 |  | 0
| - HO7V-K 25 mm2 | - HO7V-K 25 mm2 |  |  | m | 90 |  | 0
| - HO7V-K 50 mm2 | - HO7V-K 50 mm2 |  |  | m | 60 |  | 0
5.46 | Premostitve prirobnic in stikov na prezračevalnih kanalih in cevovodih ( Cu pletenica 35 mm2) | Bridging of flanges and joints on ventilation ducts and pipelines (Cu braid 35 mm2) |  |  | kos | 150 |  | 0
5.47 | 'Dobava in montaža PN cevi fi16 do fi32, komplet s koleni | Supply and installation of PN pipes fi16 to fi32, complete with elbows |  |  | m | 8400 |  | 0
5.48 | Dobava in motaža nerjavičih jekljenih cevi, od fi=16 do fi=50mm za montažo v čiste prostore, za zaščito kablov komplet s pritrdilnim materialom. | Supply and installation of stainless steel tubes, from fi=16 to fi=50mm for installation in clean rooms, for cable protection, complete with fixing material. |  |  | m | 150 |  | 0
5.49 | Dobava in montaža različnih jeklenih profilov za pomožne konstrukcije. | Supply and installation of various steel profiles for ancillary structures. |  |  | kg | 240 |  | 0
5.50 | Izdelava priključkov na novih krmilnih, regulacijskih in ostalih elementih, sondah itd. | Making connections to new controls, regulators, probes, etc. |  |  | kos | 2355 |  | 0
5.51 | Izdelava močnostnih priključkov na motornih pogonih in na ostalih močnostnih porabnikov do električne moči: | Power connections on motor drives and other power consumers up to electrical power:
| - do moči 2,2 kW (FC in senčila) | - up to 2.2 kW (FC and shades) |  |  | kos | 1617 |  | 0
| Sistem upravljanja stavb (inštalacije) | Building management system (installations) | [5 empty] | 0

## 3.13.6_BMS_HW&SW
Investitor: | UNIVERZA V LJUBLJANI | UNIVERZA V LJUBLJANI
Gradnja: | Fakulteta za strojništvo | Fakulteta za strojništvo
Objekt: | STAVBA FAKULTETE | STAVBA FAKULTETE
3.13 | ELEKTRO DELA | ELECTRICAL WORKS
3.13.6 | Sistem upravljanja stavb (HW & SW) | Building Management System (HW & SW) | [5 empty] | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description |  |  | EM | Količina | Cena/EM | Cena
6 | Sistem upravljanja stavb (HW & SW) | Building Management System (HW & SW)
6.1 | Dobava BMS postaje BMS-N3-1-R.2 (locirana v +BMS-N3-1-R.2), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the BMS station BMS-N3-1-R.2 (located in +BMS-N3-1-R.2), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - krmiljenje ventilatorskih konvektorjev (EC motor, 4-cevni sistem) | - fan coil control (EC motor, 4-pipe system) | kos | 25
| - krmiljenje zunanjih žaluzij s SMI pogoni | - control of external blinds with SMI actuators | kos | 61
| - detekcija odprtosti oken | - window open detection | kos | 15
| - komunikacijske povezave (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | - communication connections (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | kos | 35
| Predvidena konfiguracija BMS postaje BMS-N3-1-R.2 (locirana v omari +BMS-N3-1-R.2), ki bo namenjena računalniškemu nadzoru in vodenju sistema upravljanja zgradb je: | The intended configuration of the BMS station BMS-N3-1-R.2 (located in cabinet +BMS-N3-1-R.2), which will be used for computer control and management of the building management system, is:
| - Napajalnik 24 VAC, 10 W, komplet s pritrditvenim materialom na DIN. | - Power supply 24 VAC, 10 W, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWPS24VX10001 + podnožje SXWTBPSW110001. | such as Schneider type: SXWPS24VX10001 + base SXWTBPSW110001. | kos | 1
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), komplet s pritrditvenim materialom na DIN. | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port), complete with DIN mounting material.
| kot naprimer Schneider tip: SXWASPXXX10001 + podnožje SXWTBASW110002. | such as Schneider type: SXWASPXXX10001 + base SXWTBASW110002. | kos | 1
| - Sobni BACnet krmilnik RPC16A krmilnik, 230 VAC napajanje, 8x I/O, 4x rele, 4x triac, BACnet, komplet s pritrditvenim materialom na DIN. | - Room BACnet controller RPC16A controller, 230 VAC power supply, 8x I/O, 4x relay, 4x triac, BACnet, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRCF16A10003 | such as for example Schneider type: SXWRCF16A10003 | kos | 3
| - I/O modul za RPC krmilnik, 10x relejski izhod, 12x DI, komunikacija Room bus, napajanje 24V DC preko komunikacije, priključek 2xRJ45, tip CRS-HH-REL-10, komplet s pritrditvenim materialom na DIN. | - I/O module for RPC controller, 10x relay output, 12x DI, Room bus communication, 24V DC power supply via communication, 2xRJ45 connector, type CRS-HH-REL-10, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWHHREL10001+SXWDINEND10001 | as for example Schneider tip: SXWHHREL10001+SXWDINEND10001 | kos | 6
| - Razširitveni SMI modul RP-C-EXT-BL-SMI-4-HV-PD za 4 žaluzije, komplet s pritrditvenim materialom na DIN. | - SMI expansion module RP-C-EXT-BL-SMI-4-HV-PD for 4 blinds, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | as for example Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | kos | 15
| - Razširitveni DALI modul RP-C-EXT-DALI-M-PD, komplet s pritrditvenim materialom na DIN. | - DALI Expansion Module RP-C-EXT-DALI-M-PD, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 3
| - Modbus/ KNX modul RP-C-EXT-KNX, komplet s pritrditvenim materialom na DIN. | - Modbus/KNX module RP-C-EXT-KNX, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 2
| - Napajalnik KNX linije MTN684064, komplet s pritrditvenim materialom na DIN. | - Power supply for KNX line MTN684064, complete with DIN mounting material.
| kot naprimer Schneider tip: MTN684064 | such as Schneider type: MTN684064 | kos | 2
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
6.2 | Dobava BMS postaje BMS-N3-2-R.2 (locirana v +BMS-N3-2-R.2), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the BMS station BMS-N3-2-R.2 (located in +BMS-N3-2-R.2), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - krmiljenje ventilatorskih konvektorjev (EC motor, 4-cevni sistem) | - fan coil control (EC motor, 4-pipe system) | kos | 35
| - krmiljenje zunanjih žaluzij s SMI pogoni | - control of external blinds with SMI actuators | kos | 54
| - detekcija odprtosti oken | - window open detection | kos | 22
| - komunikacijske povezave (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | - communication connections (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | kos | 36
| Predvidena konfiguracija BMS postaje BMS-N3-2-R.2 (locirana v omari +BMS-N3-2-R.2), ki bo namenjena računalniškemu nadzoru in vodenju sistema upravljanja zgradb je: | The planned configuration of the BMS station BMS-N3-2-R.2 (located in cabinet +BMS-N3-2-R.2), which will be used for computer control and management of the building management system, is:
| - Sobni BACnet krmilnik RPC16A krmilnik, 230 VAC napajanje, 8x I/O, 4x rele, 4x triac, BACnet, komplet s pritrditvenim materialom na DIN. | - Room BACnet controller RPC16A controller, 230 VAC power supply, 8x I/O, 4x relay, 4x triac, BACnet, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRCF16A10003 | such as for example Schneider type: SXWRCF16A10003 | kos | 3
| - I/O modul za RPC krmilnik, 10x relejski izhod, 12x DI, komunikacija Room bus, napajanje 24V DC preko komunikacije, priključek 2xRJ45, tip CRS-HH-REL-10, komplet s pritrditvenim materialom na DIN. | - I/O module for RPC controller, 10x relay output, 12x DI, Room bus communication, 24V DC power supply via communication, 2xRJ45 connector, type CRS-HH-REL-10, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWHHREL10001+SXWDINEND10001 | as for example Schneider tip: SXWHHREL10001+SXWDINEND10001 | kos | 8
| - Razširitveni SMI modul RP-C-EXT-BL-SMI-4-HV-PD za 4 žaluzije, komplet s pritrditvenim materialom na DIN. | - SMI expansion module RP-C-EXT-BL-SMI-4-HV-PD for 4 blinds, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | as for example Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | kos | 13
| - Razširitveni DALI modul RP-C-EXT-DALI-M-PD, komplet s pritrditvenim materialom na DIN. | - DALI Expansion Module RP-C-EXT-DALI-M-PD, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 3
| - Modbus/ KNX modul RP-C-EXT-KNX, komplet s pritrditvenim materialom na DIN. | - Modbus/KNX module RP-C-EXT-KNX, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 2
| - Napajalnik KNX linije MTN684064, komplet s pritrditvenim materialom na DIN. | - Power supply for KNX line MTN684064, complete with DIN mounting material.
| kot naprimer Schneider tip: MTN684064 | such as Schneider type: MTN684064 | kos | 2
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
6.3 | Dobava BMS postaje BMS-N3-3-R.2 (locirana v +BMS-N3-3-R.2), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the BMS station BMS-N3-3-R.2 (located in +BMS-N3-3-R.2), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - krmiljenje ventilatorskih konvektorjev (EC motor, 4-cevni sistem) | - fan coil control (EC motor, 4-pipe system) | kos | 20
| - krmiljenje zunanjih žaluzij s SMI pogoni | - control of external blinds with SMI actuators | kos | 32
| - detekcija odprtosti oken | - window open detection | kos | 10
| - glavne komunikacijske povezave (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | - main communication connections (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | kos | 25
| Predvidena konfiguracija BMS postaje BMS-N3-3-R.2 (locirana v omari +BMS-N3-3-R.2), ki bo namenjena računalniškemu nadzoru in vodenju sistema upravljanja zgradb je: | The planned configuration of the BMS station BMS-N3-3-R.2 (located in cabinet +BMS-N3-3-R.2), which will be used for computer control and management of the building management system, is:
| - Napajalnik 24 VAC, 10 W, komplet s pritrditvenim materialom na DIN. | - Power supply 24 VAC, 10 W, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWPS24VX10001 + podnožje SXWTBPSW110001. | such as Schneider type: SXWPS24VX10001 + base SXWTBPSW110001. | kos | 1
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), komplet s pritrditvenim materialom na DIN. | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port), complete with DIN mounting material.
| kot naprimer Schneider tip: SXWASPXXX10001 + podnožje SXWTBASW110002. | such as Schneider type: SXWASPXXX10001 + base SXWTBASW110002. | kos | 1
| - Sobni BACnet krmilnik RPC16A krmilnik, 230 VAC napajanje, 8x I/O, 4x rele, 4x triac, BACnet, komplet s pritrditvenim materialom na DIN. | - Room BACnet controller RPC16A controller, 230 VAC power supply, 8x I/O, 4x relay, 4x triac, BACnet, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRCF16A10003 | such as for example Schneider type: SXWRCF16A10003 | kos | 3
| - I/O modul za RPC krmilnik, 10x relejski izhod, 12x DI, komunikacija Room bus, napajanje 24V DC preko komunikacije, priključek 2xRJ45, tip CRS-HH-REL-10, komplet s pritrditvenim materialom na DIN. | - I/O module for RPC controller, 10x relay output, 12x DI, Room bus communication, 24V DC power supply via communication, 2xRJ45 connector, type CRS-HH-REL-10, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWHHREL10001+SXWDINEND10001 | as for example Schneider tip: SXWHHREL10001+SXWDINEND10001 | kos | 10
| - Razširitveni SMI modul RP-C-EXT-BL-SMI-4-HV-PD za 4 žaluzije, komplet s pritrditvenim materialom na DIN. | - SMI expansion module RP-C-EXT-BL-SMI-4-HV-PD for 4 blinds, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | as for example Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | kos | 9
| - Razširitveni DALI modul RP-C-EXT-DALI-M-PD, komplet s pritrditvenim materialom na DIN. | - DALI Expansion Module RP-C-EXT-DALI-M-PD, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 3
| - Modbus/ KNX modul RP-C-EXT-KNX, komplet s pritrditvenim materialom na DIN. | - Modbus/KNX module RP-C-EXT-KNX, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 2
| - Napajalnik KNX linije MTN684064, komplet s pritrditvenim materialom na DIN. | - Power supply for KNX line MTN684064, complete with DIN mounting material.
| kot naprimer Schneider tip: MTN684064 | such as Schneider type: MTN684064 | kos | 2
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
6.4 | Dobava BMS postaje BMS-N3-4-R.2 (locirana v +BMS-N3-4-R.2), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the BMS station BMS-N3-4-R.2 (located in +BMS-N3-4-R.2), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - krmiljenje ventilatorskih konvektorjev (EC motor, 4-cevni sistem) | - fan coil control (EC motor, 4-pipe system) | kos | 25
| - krmiljenje zunanjih žaluzij s SMI pogoni | - control of external blinds with SMI actuators | kos | 50
| - detekcija odprtosti oken | - window open detection | kos | 18
| - glavne komunikacijske povezave (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | - main communication connections (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | kos | 36
| Predvidena konfiguracija BMS postaje BMS-N3-4-R.2 (locirana v omari +BMS-N3-4-R.2), ki bo namenjena računalniškemu nadzoru in vodenju sistema upravljanja zgradb je: | The planned configuration of the BMS station BMS-N3-4-R.2 (located in cabinet +BMS-N3-4-R.2), which will be used for computer control and management of the building management system, is:
| - Sobni BACnet krmilnik RPC16A krmilnik, 230 VAC napajanje, 8x I/O, 4x rele, 4x triac, BACnet, komplet s pritrditvenim materialom na DIN. | - Room BACnet controller RPC16A controller, 230 VAC power supply, 8x I/O, 4x relay, 4x triac, BACnet, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRCF16A10003 | such as for example Schneider type: SXWRCF16A10003 | kos | 3
| - I/O modul za RPC krmilnik, 10x relejski izhod, 12x DI, komunikacija Room bus, napajanje 24V DC preko komunikacije, priključek 2xRJ45, tip CRS-HH-REL-10, komplet s pritrditvenim materialom na DIN. | - I/O module for RPC controller, 10x relay output, 12x DI, Room bus communication, 24V DC power supply via communication, 2xRJ45 connector, type CRS-HH-REL-10, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWHHREL10001+SXWDINEND10001 | as for example Schneider tip: SXWHHREL10001+SXWDINEND10001 | kos | 6
| - Razširitveni SMI modul RP-C-EXT-BL-SMI-4-HV-PD za 4 žaluzije, komplet s pritrditvenim materialom na DIN. | - SMI expansion module RP-C-EXT-BL-SMI-4-HV-PD for 4 blinds, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | as for example Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | kos | 12
| - Razširitveni DALI modul RP-C-EXT-DALI-M-PD, komplet s pritrditvenim materialom na DIN. | - DALI Expansion Module RP-C-EXT-DALI-M-PD, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 3
| - Modbus/ KNX modul RP-C-EXT-KNX, komplet s pritrditvenim materialom na DIN. | - Modbus/KNX module RP-C-EXT-KNX, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 3
| - Napajalnik KNX linije MTN684064, komplet s pritrditvenim materialom na DIN. | - Power supply for KNX line MTN684064, complete with DIN mounting material.
| kot naprimer Schneider tip: MTN684064 | such as Schneider type: MTN684064 | kos | 3
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
6.5 | Dobava BMS postaje BMS-N2-1-R.2 (locirana v +BMS-N2-1-R.2), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the BMS station BMS-N2-1-R.2 (located in +BMS-N2-1-R.2), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - krmiljenje ventilatorskih konvektorjev (EC motor, 4-cevni sistem) | - fan coil control (EC motor, 4-pipe system) | kos | 37
| - krmiljenje zunanjih žaluzij s SMI pogoni | - control of external blinds with SMI actuators | kos | 62
| - detekcija odprtosti oken | - window open detection | kos | 22
| - komunikacijske povezave (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | - communication connections (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | kos | 41
| Predvidena konfiguracija BMS postaje BMS-N2-1-R.2 (locirana v omari +BMS-N2-1-R.2), ki bo namenjena računalniškemu nadzoru in vodenju sistema upravljanja zgradb je: | The planned configuration of the BMS station BMS-N2-1-R.2 (located in cabinet +BMS-N2-1-R.2), which will be used for computer control and management of the building management system, is:
| - Napajalnik 24 VAC, 10 W, komplet s pritrditvenim materialom na DIN. | - Power supply 24 VAC, 10 W, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWPS24VX10001 + podnožje SXWTBPSW110001. | such as Schneider type: SXWPS24VX10001 + base SXWTBPSW110001. | kos | 1
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), komplet s pritrditvenim materialom na DIN. | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port), complete with DIN mounting material.
| kot naprimer Schneider tip: SXWASPXXX10001 + podnožje SXWTBASW110002. | such as Schneider type: SXWASPXXX10001 + base SXWTBASW110002. | kos | 1
| - Sobni BACnet krmilnik RPC16A krmilnik, 230 VAC napajanje, 8x I/O, 4x rele, 4x triac, BACnet, komplet s pritrditvenim materialom na DIN. | - Room BACnet controller RPC16A controller, 230 VAC power supply, 8x I/O, 4x relay, 4x triac, BACnet, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRCF16A10003 | such as for example Schneider type: SXWRCF16A10003 | kos | 3
| - I/O modul za RPC krmilnik, 10x relejski izhod, 12x DI, komunikacija Room bus, napajanje 24V DC preko komunikacije, priključek 2xRJ45, tip CRS-HH-REL-10, komplet s pritrditvenim materialom na DIN. | - I/O module for RPC controller, 10x relay output, 12x DI, Room bus communication, 24V DC power supply via communication, 2xRJ45 connector, type CRS-HH-REL-10, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWHHREL10001+SXWDINEND10001 | as for example Schneider tip: SXWHHREL10001+SXWDINEND10001 | kos | 10
| - Razširitveni SMI modul RP-C-EXT-BL-SMI-4-HV-PD za 4 žaluzije, komplet s pritrditvenim materialom na DIN. | - SMI expansion module RP-C-EXT-BL-SMI-4-HV-PD for 4 blinds, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | as for example Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | kos | 16
| - Razširitveni DALI modul RP-C-EXT-DALI-M-PD, komplet s pritrditvenim materialom na DIN. | - DALI Expansion Module RP-C-EXT-DALI-M-PD, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 4
| - Modbus/ KNX modul RP-C-EXT-KNX, komplet s pritrditvenim materialom na DIN. | - Modbus/KNX module RP-C-EXT-KNX, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 4
| - Napajalnik KNX linije MTN684064, komplet s pritrditvenim materialom na DIN. | - Power supply for KNX line MTN684064, complete with DIN mounting material.
| kot naprimer Schneider tip: MTN684064 | such as Schneider type: MTN684064 | kos | 4
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
6.6 | Dobava BMS postaje BMS-N2-2-R.2 (locirana v +BMS-N2-2-R.2), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the BMS station BMS-N2-2-R.2 (located in +BMS-N2-2-R.2), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - krmiljenje ventilatorskih konvektorjev (EC motor, 4-cevni sistem) | - fan coil control (EC motor, 4-pipe system) | kos | 42
| - krmiljenje zunanjih žaluzij s SMI pogoni | - control of external blinds with SMI actuators | kos | 16
| - detekcija odprtosti oken | - window open detection | kos | 24
| - komunikacijske povezave (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | - communication connections (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | kos | 44
| Predvidena konfiguracija BMS postaje BMS-N2-2-R.2 (locirana v omari +BMS-N2-2-R.2), ki bo namenjena računalniškemu nadzoru in vodenju sistema upravljanja zgradb je: | The intended configuration of the BMS station BMS-N2-2-R.2 (located in cabinet +BMS-N2-2-R.2), which will be used for computer control and management of the building management system, is:
| - Sobni BACnet krmilnik RPC16A krmilnik, 230 VAC napajanje, 8x I/O, 4x rele, 4x triac, BACnet, komplet s pritrditvenim materialom na DIN. | - Room BACnet controller RPC16A controller, 230 VAC power supply, 8x I/O, 4x relay, 4x triac, BACnet, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRCF16A10003 | such as for example Schneider type: SXWRCF16A10003 | kos | 4
| - I/O modul za RPC krmilnik, 10x relejski izhod, 12x DI, komunikacija Room bus, napajanje 24V DC preko komunikacije, priključek 2xRJ45, tip CRS-HH-REL-10, komplet s pritrditvenim materialom na DIN. | - I/O module for RPC controller, 10x relay output, 12x DI, Room bus communication, 24V DC power supply via communication, 2xRJ45 connector, type CRS-HH-REL-10, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWHHREL10001+SXWDINEND10001 | as for example Schneider tip: SXWHHREL10001+SXWDINEND10001 | kos | 12
| - Razširitveni SMI modul RP-C-EXT-BL-SMI-4-HV-PD za 4 žaluzije, komplet s pritrditvenim materialom na DIN. | - SMI expansion module RP-C-EXT-BL-SMI-4-HV-PD for 4 blinds, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | as for example Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | kos | 16
| - Razširitveni DALI modul RP-C-EXT-DALI-M-PD, komplet s pritrditvenim materialom na DIN. | - DALI Expansion Module RP-C-EXT-DALI-M-PD, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 4
| - Modbus/ KNX modul RP-C-EXT-KNX, komplet s pritrditvenim materialom na DIN. | - Modbus/KNX module RP-C-EXT-KNX, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 4
| - Napajalnik KNX linije MTN684064, komplet s pritrditvenim materialom na DIN. | - Power supply for KNX line MTN684064, complete with DIN mounting material.
| kot naprimer Schneider tip: MTN684064 | such as Schneider type: MTN684064 | kos | 4
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
6.7 | Dobava BMS postaje BMS-N2-3-R.2 (locirana v +BMS-N2-3-R.2), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the BMS station BMS-N2-3-R.2 (located in +BMS-N2-3-R.2), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - krmiljenje ventilatorskih konvektorjev (EC motor, 4-cevni sistem) | - fan coil control (EC motor, 4-pipe system) | kos | 37
| - krmiljenje zunanjih žaluzij s SMI pogoni | - control of external blinds with SMI actuators | kos | 54
| - detekcija odprtosti oken | - window open detection | kos | 29
| - komunikacijske povezave (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | - communication connections (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | kos | 39
| Predvidena konfiguracija BMS postaje BMS-N2-3-R.2 (locirana v omari +BMS-N2-3-R.2), ki bo namenjena računalniškemu nadzoru in vodenju sistema upravljanja zgradb je: | The planned configuration of the BMS station BMS-N2-3-R.2 (located in cabinet +BMS-N2-3-R.2), which will be used for computer control and management of the building management system, is:
| - Napajalnik 24 VAC, 10 W, komplet s pritrditvenim materialom na DIN. | - Power supply 24 VAC, 10 W, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWPS24VX10001 + podnožje SXWTBPSW110001. | such as Schneider type: SXWPS24VX10001 + base SXWTBPSW110001. | kos | 1
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), komplet s pritrditvenim materialom na DIN. | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port), complete with DIN mounting material.
| kot naprimer Schneider tip: SXWASPXXX10001 + podnožje SXWTBASW110002. | such as Schneider type: SXWASPXXX10001 + base SXWTBASW110002. | kos | 1
| - Sobni BACnet krmilnik RPC16A krmilnik, 230 VAC napajanje, 8x I/O, 4x rele, 4x triac, BACnet, komplet s pritrditvenim materialom na DIN. | - Room BACnet controller RPC16A controller, 230 VAC power supply, 8x I/O, 4x relay, 4x triac, BACnet, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRCF16A10003 | such as for example Schneider type: SXWRCF16A10003 | kos | 3
| - I/O modul za RPC krmilnik, 10x relejski izhod, 12x DI, komunikacija Room bus, napajanje 24V DC preko komunikacije, priključek 2xRJ45, tip CRS-HH-REL-10, komplet s pritrditvenim materialom na DIN. | - I/O module for RPC controller, 10x relay output, 12x DI, Room bus communication, 24V DC power supply via communication, 2xRJ45 connector, type CRS-HH-REL-10, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWHHREL10001+SXWDINEND10001 | as for example Schneider tip: SXWHHREL10001+SXWDINEND10001 | kos | 10
| - Razširitveni SMI modul RP-C-EXT-BL-SMI-4-HV-PD za 4 žaluzije, komplet s pritrditvenim materialom na DIN. | - SMI expansion module RP-C-EXT-BL-SMI-4-HV-PD for 4 blinds, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | as for example Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | kos | 14
| - Razširitveni DALI modul RP-C-EXT-DALI-M-PD, komplet s pritrditvenim materialom na DIN. | - DALI Expansion Module RP-C-EXT-DALI-M-PD, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 4
| - Modbus/ KNX modul RP-C-EXT-KNX, komplet s pritrditvenim materialom na DIN. | - Modbus/KNX module RP-C-EXT-KNX, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 4
| - Napajalnik KNX linije MTN684064, komplet s pritrditvenim materialom na DIN. | - Power supply for KNX line MTN684064, complete with DIN mounting material.
| kot naprimer Schneider tip: MTN684064 | such as Schneider type: MTN684064 | kos | 4
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
6.8 | Dobava BMS postaje BMS-N2-4-R.2 (locirana v +BMS-N2-4-R.2), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the BMS station BMS-N2-4-R.2 (located in +BMS-N2-4-R.2), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - krmiljenje ventilatorskih konvektorjev (EC motor, 4-cevni sistem) | - fan coil control (EC motor, 4-pipe system) | kos | 54
| - krmiljenje zunanjih žaluzij s SMI pogoni | - control of external blinds with SMI actuators | kos | 72
| - detekcija odprtosti oken | - window open detection | kos | 37
| - komunikacijske povezave (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | - communication connections (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | kos | 52
| Predvidena konfiguracija BMS postaje BMS-N2-4-R.2 (locirana v omari +BMS-N2-4-R.2), ki bo namenjena računalniškemu nadzoru in vodenju sistema upravljanja zgradb je: | The intended configuration of the BMS station BMS-N2-4-R.2 (located in cabinet +BMS-N2-4-R.2), which will be used for computer control and management of the building management system, is:
| - Napajalnik 24 VAC, 10 W, komplet s pritrditvenim materialom na DIN. | - Power supply 24 VAC, 10 W, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWPS24VX10001 + podnožje SXWTBPSW110001. | such as Schneider type: SXWPS24VX10001 + base SXWTBPSW110001. | kos | 1
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), komplet s pritrditvenim materialom na DIN. | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port), complete with DIN mounting material.
| kot naprimer Schneider tip: SXWASPXXX10001 + podnožje SXWTBASW110002. | such as Schneider type: SXWASPXXX10001 + base SXWTBASW110002. | kos | 1
| - Sobni BACnet krmilnik RPC16A krmilnik, 230 VAC napajanje, 8x I/O, 4x rele, 4x triac, BACnet, komplet s pritrditvenim materialom na DIN. | - Room BACnet controller RPC16A controller, 230 VAC power supply, 8x I/O, 4x relay, 4x triac, BACnet, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRCF16A10003 | such as for example Schneider type: SXWRCF16A10003 | kos | 5
| - I/O modul za RPC krmilnik, 10x relejski izhod, 12x DI, komunikacija Room bus, napajanje 24V DC preko komunikacije, priključek 2xRJ45, tip CRS-HH-REL-10, komplet s pritrditvenim materialom na DIN. | - I/O module for RPC controller, 10x relay output, 12x DI, Room bus communication, 24V DC power supply via communication, 2xRJ45 connector, type CRS-HH-REL-10, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWHHREL10001+SXWDINEND10001 | as for example Schneider tip: SXWHHREL10001+SXWDINEND10001 | kos | 25
| - Razširitveni SMI modul RP-C-EXT-BL-SMI-4-HV-PD za 4 žaluzije, komplet s pritrditvenim materialom na DIN. | - SMI expansion module RP-C-EXT-BL-SMI-4-HV-PD for 4 blinds, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | as for example Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | kos | 19
| - Razširitveni DALI modul RP-C-EXT-DALI-M-PD, komplet s pritrditvenim materialom na DIN. | - DALI Expansion Module RP-C-EXT-DALI-M-PD, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 5
| - Modbus/ KNX modul RP-C-EXT-KNX, komplet s pritrditvenim materialom na DIN. | - Modbus/KNX module RP-C-EXT-KNX, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 5
| - Napajalnik KNX linije MTN684064, komplet s pritrditvenim materialom na DIN. | - Power supply for KNX line MTN684064, complete with DIN mounting material.
| kot naprimer Schneider tip: MTN684064 | such as Schneider type: MTN684064 | kos | 5
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
6.9 | Dobava BMS postaje BMS-N1-1-R.2 (locirana v +BMS-N1-1-R.2), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the BMS station BMS-N1-1-R.2 (located in +BMS-N1-1-R.2), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - krmiljenje ventilatorskih konvektorjev (EC motor, 4-cevni sistem) | - fan coil control (EC motor, 4-pipe system) | kos | 38
| - krmiljenje zunanjih žaluzij s SMI pogoni | - control of external blinds with SMI actuators | kos | 50
| - detekcija odprtosti oken | - window open detection | kos | 15
| - komunikacijske povezave (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | - communication connections (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | kos | 40
| Predvidena konfiguracija BMS postaje BMS-N1-1-R.2 (locirana v omari +BMS-N1-1-R.2), ki bo namenjena računalniškemu nadzoru in vodenju sistema upravljanja zgradb je: | The planned configuration of the BMS station BMS-N1-1-R.2 (located in cabinet +BMS-N1-1-R.2), which will be used for computer control and management of the building management system, is:
| - Napajalnik 24 VAC, 10 W, komplet s pritrditvenim materialom na DIN. | - Power supply 24 VAC, 10 W, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWPS24VX10001 + podnožje SXWTBPSW110001. | such as Schneider type: SXWPS24VX10001 + base SXWTBPSW110001. | kos | 1
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), komplet s pritrditvenim materialom na DIN. | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port), complete with DIN mounting material.
| kot naprimer Schneider tip: SXWASPXXX10001 + podnožje SXWTBASW110002. | such as Schneider type: SXWASPXXX10001 + base SXWTBASW110002. | kos | 1
| - Sobni BACnet krmilnik RPC16A krmilnik, 230 VAC napajanje, 8x I/O, 4x rele, 4x triac, BACnet, komplet s pritrditvenim materialom na DIN. | - Room BACnet controller RPC16A controller, 230 VAC power supply, 8x I/O, 4x relay, 4x triac, BACnet, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRCF16A10003 | such as for example Schneider type: SXWRCF16A10003 | kos | 3
| - I/O modul za RPC krmilnik, 10x relejski izhod, 12x DI, komunikacija Room bus, napajanje 24V DC preko komunikacije, priključek 2xRJ45, tip CRS-HH-REL-10, komplet s pritrditvenim materialom na DIN. | - I/O module for RPC controller, 10x relay output, 12x DI, Room bus communication, 24V DC power supply via communication, 2xRJ45 connector, type CRS-HH-REL-10, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWHHREL10001+SXWDINEND10001 | as for example Schneider tip: SXWHHREL10001+SXWDINEND10001 | kos | 7
| - Razširitveni SMI modul RP-C-EXT-BL-SMI-4-HV-PD za 4 žaluzije, komplet s pritrditvenim materialom na DIN. | - SMI expansion module RP-C-EXT-BL-SMI-4-HV-PD for 4 blinds, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | as for example Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | kos | 14
| - Razširitveni DALI modul RP-C-EXT-DALI-M-PD, komplet s pritrditvenim materialom na DIN. | - DALI Expansion Module RP-C-EXT-DALI-M-PD, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 4
| - Modbus/ KNX modul RP-C-EXT-KNX, komplet s pritrditvenim materialom na DIN. | - Modbus/KNX module RP-C-EXT-KNX, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 4
| - Napajalnik KNX linije MTN684064, komplet s pritrditvenim materialom na DIN. | - Power supply for KNX line MTN684064, complete with DIN mounting material.
| kot naprimer Schneider tip: MTN684064 | such as Schneider type: MTN684064 | kos | 4
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
6.10 | Dobava BMS postaje BMS-N1-2-R.2 (locirana v +BMS-N1-2-R.2), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the BMS station BMS-N1-2-R.2 (located in +BMS-N1-2-R.2), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - krmiljenje ventilatorskih konvektorjev (EC motor, 4-cevni sistem) | - fan coil control (EC motor, 4-pipe system) | kos | 41
| - krmiljenje zunanjih žaluzij s SMI pogoni | - control of external blinds with SMI actuators | kos | 52
| - detekcija odprtosti oken | - window open detection | kos | 14
| - komunikacijske povezave (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | - communication connections (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | kos | 38
| Predvidena konfiguracija BMS postaje BMS-N1-2-R.2 (locirana v omari +BMS-N1-2-R.2), ki bo namenjena računalniškemu nadzoru in vodenju sistema upravljanja zgradb je: | The intended configuration of the BMS station BMS-N1-2-R.2 (located in cabinet +BMS-N1-2-R.2), which will be used for computer control and management of the building management system, is:
| - Napajalnik 24 VAC, 10 W, komplet s pritrditvenim materialom na DIN. | - Power supply 24 VAC, 10 W, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWPS24VX10001 + podnožje SXWTBPSW110001. | such as Schneider type: SXWPS24VX10001 + base SXWTBPSW110001. | kos | 1
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), komplet s pritrditvenim materialom na DIN. | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port), complete with DIN mounting material.
| kot naprimer Schneider tip: SXWASPXXX10001 + podnožje SXWTBASW110002. | such as Schneider type: SXWASPXXX10001 + base SXWTBASW110002. | kos | 1
| - Sobni BACnet krmilnik RPC16A krmilnik, 230 VAC napajanje, 8x I/O, 4x rele, 4x triac, BACnet, komplet s pritrditvenim materialom na DIN. | - Room BACnet controller RPC16A controller, 230 VAC power supply, 8x I/O, 4x relay, 4x triac, BACnet, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRCF16A10003 | such as for example Schneider type: SXWRCF16A10003 | kos | 4
| - I/O modul za RPC krmilnik, 10x relejski izhod, 12x DI, komunikacija Room bus, napajanje 24V DC preko komunikacije, priključek 2xRJ45, tip CRS-HH-REL-10, komplet s pritrditvenim materialom na DIN. | - I/O module for RPC controller, 10x relay output, 12x DI, Room bus communication, 24V DC power supply via communication, 2xRJ45 connector, type CRS-HH-REL-10, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWHHREL10001+SXWDINEND10001 | as for example Schneider tip: SXWHHREL10001+SXWDINEND10001 | kos | 8
| - Razširitveni SMI modul RP-C-EXT-BL-SMI-4-HV-PD za 4 žaluzije, komplet s pritrditvenim materialom na DIN. | - SMI expansion module RP-C-EXT-BL-SMI-4-HV-PD for 4 blinds, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | as for example Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | kos | 13
| - Razširitveni DALI modul RP-C-EXT-DALI-M-PD, komplet s pritrditvenim materialom na DIN. | - DALI Expansion Module RP-C-EXT-DALI-M-PD, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 3
| - Modbus/ KNX modul RP-C-EXT-KNX, komplet s pritrditvenim materialom na DIN. | - Modbus/KNX module RP-C-EXT-KNX, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 3
| - Napajalnik KNX linije MTN684064, komplet s pritrditvenim materialom na DIN. | - Power supply for KNX line MTN684064, complete with DIN mounting material.
| kot naprimer Schneider tip: MTN684064 | such as Schneider type: MTN684064 | kos | 3
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
6.11 | Dobava BMS postaje BMS-N1-3-R.2 (locirana v +BMS-N1-3-R.2), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the BMS station BMS-N1-3-R.2 (located in +BMS-N1-3-R.2), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - krmiljenje ventilatorskih konvektorjev (EC motor, 4-cevni sistem) | - fan coil control (EC motor, 4-pipe system) | kos | 47
| - krmiljenje zunanjih žaluzij s SMI pogoni | - control of external blinds with SMI actuators | kos | 37
| - detekcija odprtosti oken | - window open detection | kos | 23
| - glavne komunikacijske povezave (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | - main communication connections (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | kos | 38
| Predvidena konfiguracija BMS postaje BMS-N1-3-R.2 (locirana v omari +BMS-N1-3-R.2), ki bo namenjena računalniškemu nadzoru in vodenju sistema upravljanja zgradb je: | The intended configuration of the BMS station BMS-N1-3-R.2 (located in cabinet +BMS-N1-3-R.2), which will be used for computer control and management of the building management system, is:
| - Napajalnik 24 VAC, 10 W, komplet s pritrditvenim materialom na DIN. | - Power supply 24 VAC, 10 W, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWPS24VX10001 + podnožje SXWTBPSW110001. | such as Schneider type: SXWPS24VX10001 + base SXWTBPSW110001. | kos | 1
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), komplet s pritrditvenim materialom na DIN. | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port), complete with DIN mounting material.
| kot naprimer Schneider tip: SXWASPXXX10001 + podnožje SXWTBASW110002. | such as Schneider type: SXWASPXXX10001 + base SXWTBASW110002. | kos | 1
| - Sobni BACnet krmilnik RPC16A krmilnik, 230 VAC napajanje, 8x I/O, 4x rele, 4x triac, BACnet, komplet s pritrditvenim materialom na DIN. | - Room BACnet controller RPC16A controller, 230 VAC power supply, 8x I/O, 4x relay, 4x triac, BACnet, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRCF16A10003 | such as for example Schneider type: SXWRCF16A10003 | kos | 4
| - I/O modul za RPC krmilnik, 10x relejski izhod, 12x DI, komunikacija Room bus, napajanje 24V DC preko komunikacije, priključek 2xRJ45, tip CRS-HH-REL-10, komplet s pritrditvenim materialom na DIN. | - I/O module for RPC controller, 10x relay output, 12x DI, Room bus communication, 24V DC power supply via communication, 2xRJ45 connector, type CRS-HH-REL-10, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWHHREL10001+SXWDINEND10001 | as for example Schneider tip: SXWHHREL10001+SXWDINEND10001 | kos | 12
| - Razširitveni SMI modul RP-C-EXT-BL-SMI-4-HV-PD za 4 žaluzije, komplet s pritrditvenim materialom na DIN. | - SMI expansion module RP-C-EXT-BL-SMI-4-HV-PD for 4 blinds, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | as for example Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | kos | 10
| - Razširitveni DALI modul RP-C-EXT-DALI-M-PD, komplet s pritrditvenim materialom na DIN. | - DALI Expansion Module RP-C-EXT-DALI-M-PD, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 4
| - Modbus/ KNX modul RP-C-EXT-KNX, komplet s pritrditvenim materialom na DIN. | - Modbus/KNX module RP-C-EXT-KNX, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 4
| - Napajalnik KNX linije MTN684064, komplet s pritrditvenim materialom na DIN. | - Power supply for KNX line MTN684064, complete with DIN mounting material.
| kot naprimer Schneider tip: MTN684064 | such as Schneider type: MTN684064 | kos | 4
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
6.12 | Dobava BMS postaje BMS-N1-4-R.2 (locirana v +BMS-N1-4-R.2), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the BMS station BMS-N1-4-R.2 (located in +BMS-N1-4-R.2), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - krmiljenje ventilatorskih konvektorjev (EC motor, 4-cevni sistem) | - fan coil control (EC motor, 4-pipe system) | kos | 40
| - krmiljenje zunanjih žaluzij s SMI pogoni | - control of external blinds with SMI actuators | kos | 48
| - detekcija odprtosti oken | - window open detection | kos | 21
| - glavne komunikacijske povezave (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | - main communication connections (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | kos | 40
| Predvidena konfiguracija BMS postaje BMS-N1-4-R.2 (locirana v omari +BMS-N1-4-R.2), ki bo namenjena računalniškemu nadzoru in vodenju sistema upravljanja zgradb je: | The intended configuration of the BMS station BMS-N1-4-R.2 (located in cabinet +BMS-N1-4-R.2), which will be used for computer control and management of the building management system, is:
| - Napajalnik 24 VAC, 10 W, komplet s pritrditvenim materialom na DIN. | - Power supply 24 VAC, 10 W, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWPS24VX10001 + podnožje SXWTBPSW110001. | such as Schneider type: SXWPS24VX10001 + base SXWTBPSW110001. | kos | 1
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), komplet s pritrditvenim materialom na DIN. | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port), complete with DIN mounting material.
| kot naprimer Schneider tip: SXWASPXXX10001 + podnožje SXWTBASW110002. | such as Schneider type: SXWASPXXX10001 + base SXWTBASW110002. | kos | 1
| - Sobni BACnet krmilnik RPC16A krmilnik, 230 VAC napajanje, 8x I/O, 4x rele, 4x triac, BACnet, komplet s pritrditvenim materialom na DIN. | - Room BACnet controller RPC16A controller, 230 VAC power supply, 8x I/O, 4x relay, 4x triac, BACnet, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRCF16A10003 | such as for example Schneider type: SXWRCF16A10003 | kos | 4
| - I/O modul za RPC krmilnik, 10x relejski izhod, 12x DI, komunikacija Room bus, napajanje 24V DC preko komunikacije, priključek 2xRJ45, tip CRS-HH-REL-10, komplet s pritrditvenim materialom na DIN. | - I/O module for RPC controller, 10x relay output, 12x DI, Room bus communication, 24V DC power supply via communication, 2xRJ45 connector, type CRS-HH-REL-10, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWHHREL10001+SXWDINEND10001 | as for example Schneider tip: SXWHHREL10001+SXWDINEND10001 | kos | 8
| - Razširitveni SMI modul RP-C-EXT-BL-SMI-4-HV-PD za 4 žaluzije, komplet s pritrditvenim materialom na DIN. | - SMI expansion module RP-C-EXT-BL-SMI-4-HV-PD for 4 blinds, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | as for example Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | kos | 12
| - Razširitveni DALI modul RP-C-EXT-DALI-M-PD, komplet s pritrditvenim materialom na DIN. | - DALI Expansion Module RP-C-EXT-DALI-M-PD, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 4
| - Modbus/ KNX modul RP-C-EXT-KNX, komplet s pritrditvenim materialom na DIN. | - Modbus/KNX module RP-C-EXT-KNX, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 4
| - Napajalnik KNX linije MTN684064, komplet s pritrditvenim materialom na DIN. | - Power supply for KNX line MTN684064, complete with DIN mounting material.
| kot naprimer Schneider tip: MTN684064 | such as Schneider type: MTN684064 | kos | 4
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
6.13 | Dobava BMS postaje BMS-N1-5-R.2 (locirana v +BMS-N1-5-R.2), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the BMS station BMS-N1-5-R.2 (located in +BMS-N1-5-R.2), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - krmiljenje ventilatorskih konvektorjev (EC motor, 4-cevni sistem) | - fan coil control (EC motor, 4-pipe system) | kos | 20
| - krmiljenje zunanjih žaluzij s SMI pogoni | - control of external blinds with SMI actuators | kos | 34
| - detekcija odprtosti oken | - window open detection | kos | 17
| - komunikacijske povezave (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | - communication connections (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | kos | 26
| Predvidena konfiguracija BMS postaje BMS-N1-5-R.2 (locirana v omari +BMS-N1-5-R.2), ki bo namenjena računalniškemu nadzoru in vodenju sistema upravljanja zgradb je: | The planned configuration of the BMS station BMS-N1-5-R.2 (located in cabinet +BMS-N1-5-R.2), which will be used for computer control and management of the building management system, is:
| - Sobni BACnet krmilnik RPC16A krmilnik, 230 VAC napajanje, 8x I/O, 4x rele, 4x triac, BACnet, komplet s pritrditvenim materialom na DIN. | - Room BACnet controller RPC16A controller, 230 VAC power supply, 8x I/O, 4x relay, 4x triac, BACnet, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRCF16A10003 | such as for example Schneider type: SXWRCF16A10003 | kos | 2
| - I/O modul za RPC krmilnik, 10x relejski izhod, 12x DI, komunikacija Room bus, napajanje 24V DC preko komunikacije, priključek 2xRJ45, tip CRS-HH-REL-10, komplet s pritrditvenim materialom na DIN. | - I/O module for RPC controller, 10x relay output, 12x DI, Room bus communication, 24V DC power supply via communication, 2xRJ45 connector, type CRS-HH-REL-10, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWHHREL10001+SXWDINEND10001 | as for example Schneider tip: SXWHHREL10001+SXWDINEND10001 | kos | 10
| - Razširitveni SMI modul RP-C-EXT-BL-SMI-4-HV-PD za 4 žaluzije, komplet s pritrditvenim materialom na DIN. | - SMI expansion module RP-C-EXT-BL-SMI-4-HV-PD for 4 blinds, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | as for example Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | kos | 9
| - Razširitveni DALI modul RP-C-EXT-DALI-M-PD, komplet s pritrditvenim materialom na DIN. | - DALI Expansion Module RP-C-EXT-DALI-M-PD, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 3
| - Modbus/ KNX modul RP-C-EXT-KNX, komplet s pritrditvenim materialom na DIN. | - Modbus/KNX module RP-C-EXT-KNX, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 3
| - Napajalnik KNX linije MTN684064, komplet s pritrditvenim materialom na DIN. | - Power supply for KNX line MTN684064, complete with DIN mounting material.
| kot naprimer Schneider tip: MTN684064 | such as Schneider type: MTN684064 | kos | 3
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
6.14 | Dobava BMS postaje BMS-N1-6-R.2 (locirana v +BMS-N1-6-R.2), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the BMS station BMS-N1-6-R.2 (located in +BMS-N1-6-R.2), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - krmiljenje ventilatorskih konvektorjev (EC motor, 4-cevni sistem) | - fan coil control (EC motor, 4-pipe system) | kos | 27
| - krmiljenje zunanjih žaluzij s SMI pogoni | - control of external blinds with SMI actuators | kos | 35
| - detekcija odprtosti oken | - window open detection | kos | 16
| - komunikacijske povezave (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | - communication connections (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | kos | 30
| Predvidena konfiguracija BMS postaje BMS-N1-6-R.2 (locirana v omari +BMS-N1-6-R.2), ki bo namenjena računalniškemu nadzoru in vodenju sistema upravljanja zgradb je: | The intended configuration of the BMS station BMS-N1-6-R.2 (located in cabinet +BMS-N1-6-R.2), which will be used for computer control and management of the building management system, is:
| - Sobni BACnet krmilnik RPC16A krmilnik, 230 VAC napajanje, 8x I/O, 4x rele, 4x triac, BACnet, komplet s pritrditvenim materialom na DIN. | - Room BACnet controller RPC16A controller, 230 VAC power supply, 8x I/O, 4x relay, 4x triac, BACnet, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRCF16A10003 | such as for example Schneider type: SXWRCF16A10003 | kos | 2
| - I/O modul za RPC krmilnik, 10x relejski izhod, 12x DI, komunikacija Room bus, napajanje 24V DC preko komunikacije, priključek 2xRJ45, tip CRS-HH-REL-10, komplet s pritrditvenim materialom na DIN. | - I/O module for RPC controller, 10x relay output, 12x DI, Room bus communication, 24V DC power supply via communication, 2xRJ45 connector, type CRS-HH-REL-10, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWHHREL10001+SXWDINEND10001 | as for example Schneider tip: SXWHHREL10001+SXWDINEND10001 | kos | 5
| - Razširitveni SMI modul RP-C-EXT-BL-SMI-4-HV-PD za 4 žaluzije, komplet s pritrditvenim materialom na DIN. | - SMI expansion module RP-C-EXT-BL-SMI-4-HV-PD for 4 blinds, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | as for example Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | kos | 9
| - Razširitveni DALI modul RP-C-EXT-DALI-M-PD, komplet s pritrditvenim materialom na DIN. | - DALI Expansion Module RP-C-EXT-DALI-M-PD, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 3
| - Modbus/ KNX modul RP-C-EXT-KNX, komplet s pritrditvenim materialom na DIN. | - Modbus/KNX module RP-C-EXT-KNX, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 3
| - Napajalnik KNX linije MTN684064, komplet s pritrditvenim materialom na DIN. | - Power supply for KNX line MTN684064, complete with DIN mounting material.
| kot naprimer Schneider tip: MTN684064 | such as Schneider type: MTN684064 | kos | 3
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
6.15 | Dobava BMS postaje BMS-P1-1-R.2 (locirana v +BMS-P1-1-R.2), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the BMS station BMS-P1-1-R.2 (located in +BMS-P1-1-R.2), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - krmiljenje ventilatorskih konvektorjev (EC motor, 4-cevni sistem) | - fan coil control (EC motor, 4-pipe system) | kos | 12
| - krmiljenje zunanjih žaluzij s SMI pogoni | - control of external blinds with SMI actuators | kos | 46
| - detekcija odprtosti oken | - window open detection | kos | 6
| - komunikacijske povezave (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | - communication connections (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | kos | 36
| Predvidena konfiguracija BMS postaje BMS-P1-1-R.2 (locirana v omari +BMS-P1-1-R.2), ki bo namenjena računalniškemu nadzoru in vodenju sistema upravljanja zgradb je: | The planned configuration of the BMS station BMS-P1-1-R.2 (located in cabinet +BMS-P1-1-R.2), which will be used for computer control and management of the building management system, is:
| - Napajalnik 24 VAC, 10 W, komplet s pritrditvenim materialom na DIN. | - Power supply 24 VAC, 10 W, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWPS24VX10001 + podnožje SXWTBPSW110001. | such as Schneider type: SXWPS24VX10001 + base SXWTBPSW110001. | kos | 1
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), komplet s pritrditvenim materialom na DIN. | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port), complete with DIN mounting material.
| kot naprimer Schneider tip: SXWASPXXX10001 + podnožje SXWTBASW110002. | such as Schneider type: SXWASPXXX10001 + base SXWTBASW110002. | kos | 1
| - Sobni BACnet krmilnik RPC16A krmilnik, 230 VAC napajanje, 8x I/O, 4x rele, 4x triac, BACnet, komplet s pritrditvenim materialom na DIN. | - Room BACnet controller RPC16A controller, 230 VAC power supply, 8x I/O, 4x relay, 4x triac, BACnet, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRCF16A10003 | such as for example Schneider type: SXWRCF16A10003 | kos | 1
| - I/O modul za RPC krmilnik, 10x relejski izhod, 12x DI, komunikacija Room bus, napajanje 24V DC preko komunikacije, priključek 2xRJ45, tip CRS-HH-REL-10, komplet s pritrditvenim materialom na DIN. | - I/O module for RPC controller, 10x relay output, 12x DI, Room bus communication, 24V DC power supply via communication, 2xRJ45 connector, type CRS-HH-REL-10, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWHHREL10001+SXWDINEND10001 | as for example Schneider tip: SXWHHREL10001+SXWDINEND10001 | kos | 4
| - Razširitveni SMI modul RP-C-EXT-BL-SMI-4-HV-PD za 4 žaluzije, komplet s pritrditvenim materialom na DIN. | - SMI expansion module RP-C-EXT-BL-SMI-4-HV-PD for 4 blinds, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | as for example Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | kos | 12
| - Razširitveni DALI modul RP-C-EXT-DALI-M-PD, komplet s pritrditvenim materialom na DIN. | - DALI Expansion Module RP-C-EXT-DALI-M-PD, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 3
| - Modbus/ KNX modul RP-C-EXT-KNX, komplet s pritrditvenim materialom na DIN. | - Modbus/KNX module RP-C-EXT-KNX, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 4
| - Napajalnik KNX linije MTN684064, komplet s pritrditvenim materialom na DIN. | - Power supply for KNX line MTN684064, complete with DIN mounting material.
| kot naprimer Schneider tip: MTN684064 | such as Schneider type: MTN684064 | kos | 4
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
6.16 | Dobava BMS postaje BMS-P1-2-R.2 (locirana v +BMS-P1-1-R.2), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the BMS station BMS-P1-2-R.2 (located in +BMS-P1-1-R.2), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - krmiljenje ventilatorskih konvektorjev (EC motor, 4-cevni sistem) | - fan coil control (EC motor, 4-pipe system) | kos | 7
| - krmiljenje zunanjih žaluzij s SMI pogoni | - control of external blinds with SMI actuators | kos | 43
| - detekcija odprtosti oken | - window open detection | kos | 8
| - komunikacijske povezave (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | - communication connections (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | kos | 20
| Predvidena konfiguracija BMS postaje BMS-P1-1-R.2 (locirana v omari +BMS-P1-1-R.2), ki bo namenjena računalniškemu nadzoru in vodenju sistema upravljanja zgradb je: | The planned configuration of the BMS station BMS-P1-1-R.2 (located in cabinet +BMS-P1-1-R.2), which will be used for computer control and management of the building management system, is:
| - Sobni BACnet krmilnik RPC16A krmilnik, 230 VAC napajanje, 8x I/O, 4x rele, 4x triac, BACnet, komplet s pritrditvenim materialom na DIN. | - Room BACnet controller RPC16A controller, 230 VAC power supply, 8x I/O, 4x relay, 4x triac, BACnet, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRCF16A10003 | such as for example Schneider type: SXWRCF16A10003 | kos | 1
| - I/O modul za RPC krmilnik, 10x relejski izhod, 12x DI, komunikacija Room bus, napajanje 24V DC preko komunikacije, priključek 2xRJ45, tip CRS-HH-REL-10, komplet s pritrditvenim materialom na DIN. | - I/O module for RPC controller, 10x relay output, 12x DI, Room bus communication, 24V DC power supply via communication, 2xRJ45 connector, type CRS-HH-REL-10, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWHHREL10001+SXWDINEND10001 | as for example Schneider tip: SXWHHREL10001+SXWDINEND10001 | kos | 2
| - Razširitveni SMI modul RP-C-EXT-BL-SMI-4-HV-PD za 4 žaluzije, komplet s pritrditvenim materialom na DIN. | - SMI expansion module RP-C-EXT-BL-SMI-4-HV-PD for 4 blinds, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | as for example Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | kos | 11
| - Razširitveni DALI modul RP-C-EXT-DALI-M-PD, komplet s pritrditvenim materialom na DIN. | - DALI Expansion Module RP-C-EXT-DALI-M-PD, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 3
| - Modbus/ KNX modul RP-C-EXT-KNX, komplet s pritrditvenim materialom na DIN. | - Modbus/KNX module RP-C-EXT-KNX, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 3
| - Napajalnik KNX linije MTN684064, komplet s pritrditvenim materialom na DIN. | - Power supply for KNX line MTN684064, complete with DIN mounting material.
| kot naprimer Schneider tip: MTN684064 | such as Schneider type: MTN684064 | kos | 3
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
6.17 | Dobava BMS postaje BMS-P1-3-R.2 (locirana v +BMS-P1-3-R.2), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the BMS station BMS-P1-3-R.2 (located in +BMS-P1-3-R.2), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - krmiljenje ventilatorskih konvektorjev (EC motor, 4-cevni sistem) | - fan coil control (EC motor, 4-pipe system) | kos | 60
| - krmiljenje zunanjih žaluzij s SMI pogoni | - control of external blinds with SMI actuators | kos | 50
| - detekcija odprtosti oken | - window open detection | kos | 18
| - komunikacijske povezave (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | - communication connections (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | kos | 50
| Predvidena konfiguracija BMS postaje BMS-P1-3-R.2 (locirana v omari +BMS-P1-3-R.2), ki bo namenjena računalniškemu nadzoru in vodenju sistema upravljanja zgradb je: | The intended configuration of the BMS station BMS-P1-3-R.2 (located in cabinet +BMS-P1-3-R.2), which will be used for computer control and management of the building management system, is:
| - Napajalnik 24 VAC, 10 W, komplet s pritrditvenim materialom na DIN. | - Power supply 24 VAC, 10 W, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWPS24VX10001 + podnožje SXWTBPSW110001. | such as Schneider type: SXWPS24VX10001 + base SXWTBPSW110001. | kos | 1
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), komplet s pritrditvenim materialom na DIN. | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port), complete with DIN mounting material.
| kot naprimer Schneider tip: SXWASPXXX10001 + podnožje SXWTBASW110002. | such as Schneider type: SXWASPXXX10001 + base SXWTBASW110002. | kos | 1
| - Sobni BACnet krmilnik RPC16A krmilnik, 230 VAC napajanje, 8x I/O, 4x rele, 4x triac, BACnet, komplet s pritrditvenim materialom na DIN. | - Room BACnet controller RPC16A controller, 230 VAC power supply, 8x I/O, 4x relay, 4x triac, BACnet, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRCF16A10003 | such as for example Schneider type: SXWRCF16A10003 | kos | 5
| - I/O modul za RPC krmilnik, 10x relejski izhod, 12x DI, komunikacija Room bus, napajanje 24V DC preko komunikacije, priključek 2xRJ45, tip CRS-HH-REL-10, komplet s pritrditvenim materialom na DIN. | - I/O module for RPC controller, 10x relay output, 12x DI, Room bus communication, 24V DC power supply via communication, 2xRJ45 connector, type CRS-HH-REL-10, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWHHREL10001+SXWDINEND10001 | as for example Schneider tip: SXWHHREL10001+SXWDINEND10001 | kos | 18
| - Razširitveni SMI modul RP-C-EXT-BL-SMI-4-HV-PD za 4 žaluzije, komplet s pritrditvenim materialom na DIN. | - SMI expansion module RP-C-EXT-BL-SMI-4-HV-PD for 4 blinds, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | as for example Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | kos | 13
| - Razširitveni DALI modul RP-C-EXT-DALI-M-PD, komplet s pritrditvenim materialom na DIN. | - DALI Expansion Module RP-C-EXT-DALI-M-PD, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 5
| - Modbus/ KNX modul RP-C-EXT-KNX, komplet s pritrditvenim materialom na DIN. | - Modbus/KNX module RP-C-EXT-KNX, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 5
| - Napajalnik KNX linije MTN684064, komplet s pritrditvenim materialom na DIN. | - Power supply for KNX line MTN684064, complete with DIN mounting material.
| kot naprimer Schneider tip: MTN684064 | such as Schneider type: MTN684064 | kos | 5
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
6.18 | Dobava BMS postaje BMS-P1-4-R.2 (locirana v +BMS-P1-4-R.2), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the BMS station BMS-P1-4-R.2 (located in +BMS-P1-4-R.2), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - krmiljenje ventilatorskih konvektorjev (EC motor, 4-cevni sistem) | - fan coil control (EC motor, 4-pipe system) | kos | 40
| - krmiljenje zunanjih žaluzij s SMI pogoni | - control of external blinds with SMI actuators | kos | 30
| - detekcija odprtosti oken | - window open detection | kos | 10
| - komunikacijske povezave (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | - communication connections (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | kos | 35
| Predvidena konfiguracija BMS postaje BMS-P1-4-R.2 (locirana v omari +BMS-N1-1-R.2), ki bo namenjena računalniškemu nadzoru in vodenju sistema upravljanja zgradb je: | The planned configuration of the BMS station BMS-P1-4-R.2 (located in cabinet +BMS-N1-1-R.2), which will be used for computer control and management of the building management system, is:
| - Napajalnik 24 VAC, 10 W, komplet s pritrditvenim materialom na DIN. | - Power supply 24 VAC, 10 W, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWPS24VX10001 + podnožje SXWTBPSW110001. | such as Schneider type: SXWPS24VX10001 + base SXWTBPSW110001. | kos | 1
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), komplet s pritrditvenim materialom na DIN. | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port), complete with DIN mounting material.
| kot naprimer Schneider tip: SXWASPXXX10001 + podnožje SXWTBASW110002. | such as Schneider type: SXWASPXXX10001 + base SXWTBASW110002. | kos | 1
| - Sobni BACnet krmilnik RPC16A krmilnik, 230 VAC napajanje, 8x I/O, 4x rele, 4x triac, BACnet, komplet s pritrditvenim materialom na DIN. | - Room BACnet controller RPC16A controller, 230 VAC power supply, 8x I/O, 4x relay, 4x triac, BACnet, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRCF16A10003 | such as for example Schneider type: SXWRCF16A10003 | kos | 4
| - I/O modul za RPC krmilnik, 10x relejski izhod, 12x DI, komunikacija Room bus, napajanje 24V DC preko komunikacije, priključek 2xRJ45, tip CRS-HH-REL-10, komplet s pritrditvenim materialom na DIN. | - I/O module for RPC controller, 10x relay output, 12x DI, Room bus communication, 24V DC power supply via communication, 2xRJ45 connector, type CRS-HH-REL-10, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWHHREL10001+SXWDINEND10001 | as for example Schneider tip: SXWHHREL10001+SXWDINEND10001 | kos | 13
| - Razširitveni SMI modul RP-C-EXT-BL-SMI-4-HV-PD za 4 žaluzije, komplet s pritrditvenim materialom na DIN. | - SMI expansion module RP-C-EXT-BL-SMI-4-HV-PD for 4 blinds, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | as for example Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | kos | 8
| - Razširitveni DALI modul RP-C-EXT-DALI-M-PD, komplet s pritrditvenim materialom na DIN. | - DALI Expansion Module RP-C-EXT-DALI-M-PD, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 4
| - Modbus/ KNX modul RP-C-EXT-KNX, komplet s pritrditvenim materialom na DIN. | - Modbus/KNX module RP-C-EXT-KNX, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 4
| - Napajalnik KNX linije MTN684064, komplet s pritrditvenim materialom na DIN. | - Power supply for KNX line MTN684064, complete with DIN mounting material.
| kot naprimer Schneider tip: MTN684064 | such as Schneider type: MTN684064 | kos | 4
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
6.19 | Dobava BMS postaje BMS-P1-5-R.2 (locirana v +BMS-P1-5-R.2), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the BMS station BMS-P1-5-R.2 (located in +BMS-P1-5-R.2), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - krmiljenje ventilatorskih konvektorjev (EC motor, 4-cevni sistem) | - fan coil control (EC motor, 4-pipe system) | kos | 33
| - krmiljenje zunanjih žaluzij s SMI pogoni | - control of external blinds with SMI actuators | kos | 34
| - detekcija odprtosti oken | - window open detection | kos | 10
| - komunikacijske povezave (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | - communication connections (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | kos | 35
| Predvidena konfiguracija BMS postaje BMS-P1-5-R.2 (locirana v omari +BMS-P1-5-R.2), ki bo namenjena računalniškemu nadzoru in vodenju sistema upravljanja zgradb je: | The intended configuration of the BMS station BMS-P1-5-R.2 (located in cabinet +BMS-P1-5-R.2), which will be used for computer control and management of the building management system, is:
| - Napajalnik 24 VAC, 10 W, komplet s pritrditvenim materialom na DIN. | - Power supply 24 VAC, 10 W, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWPS24VX10001 + podnožje SXWTBPSW110001. | such as Schneider type: SXWPS24VX10001 + base SXWTBPSW110001. | kos | 1
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), komplet s pritrditvenim materialom na DIN. | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port), complete with DIN mounting material.
| kot naprimer Schneider tip: SXWASPXXX10001 + podnožje SXWTBASW110002. | such as Schneider type: SXWASPXXX10001 + base SXWTBASW110002. | kos | 1
| - Sobni BACnet krmilnik RPC16A krmilnik, 230 VAC napajanje, 8x I/O, 4x rele, 4x triac, BACnet, komplet s pritrditvenim materialom na DIN. | - Room BACnet controller RPC16A controller, 230 VAC power supply, 8x I/O, 4x relay, 4x triac, BACnet, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRCF16A10003 | such as for example Schneider type: SXWRCF16A10003 | kos | 4
| - I/O modul za RPC krmilnik, 10x relejski izhod, 12x DI, komunikacija Room bus, napajanje 24V DC preko komunikacije, priključek 2xRJ45, tip CRS-HH-REL-10, komplet s pritrditvenim materialom na DIN. | - I/O module for RPC controller, 10x relay output, 12x DI, Room bus communication, 24V DC power supply via communication, 2xRJ45 connector, type CRS-HH-REL-10, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWHHREL10001+SXWDINEND10001 | as for example Schneider tip: SXWHHREL10001+SXWDINEND10001 | kos | 10
| - Razširitveni SMI modul RP-C-EXT-BL-SMI-4-HV-PD za 4 žaluzije, komplet s pritrditvenim materialom na DIN. | - SMI expansion module RP-C-EXT-BL-SMI-4-HV-PD for 4 blinds, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | as for example Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | kos | 9
| - Razširitveni DALI modul RP-C-EXT-DALI-M-PD, komplet s pritrditvenim materialom na DIN. | - DALI Expansion Module RP-C-EXT-DALI-M-PD, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 4
| - Modbus/ KNX modul RP-C-EXT-KNX, komplet s pritrditvenim materialom na DIN. | - Modbus/KNX module RP-C-EXT-KNX, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 4
| - Napajalnik KNX linije MTN684064, komplet s pritrditvenim materialom na DIN. | - Power supply for KNX line MTN684064, complete with DIN mounting material.
| kot naprimer Schneider tip: MTN684064 | such as Schneider type: MTN684064 | kos | 4
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
6.20 | Dobava BMS postaje BMS-P1-6-R.2 (locirana v +BMS-P1-6-R.2), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the BMS station BMS-P1-6-R.2 (located in +BMS-P1-6-R.2), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - krmiljenje ventilatorskih konvektorjev (EC motor, 4-cevni sistem) | - fan coil control (EC motor, 4-pipe system) | kos | 31
| - krmiljenje zunanjih žaluzij s SMI pogoni | - control of external blinds with SMI actuators | kos | 44
| - detekcija odprtosti oken | - window open detection | kos | 10
| - glavne komunikacijske povezave (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | - main communication connections (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | kos | 35
| Predvidena konfiguracija BMS postaje BMS-P1-6-R.2 (locirana v omari +BMS-P1-6-R.2), ki bo namenjena računalniškemu nadzoru in vodenju sistema upravljanja zgradb je: | The intended configuration of the BMS station BMS-P1-6-R.2 (located in cabinet +BMS-P1-6-R.2), which will be used for computer control and management of the building management system, is:
| - Sobni BACnet krmilnik RPC16A krmilnik, 230 VAC napajanje, 8x I/O, 4x rele, 4x triac, BACnet, komplet s pritrditvenim materialom na DIN. | - Room BACnet controller RPC16A controller, 230 VAC power supply, 8x I/O, 4x relay, 4x triac, BACnet, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRCF16A10003 | such as for example Schneider type: SXWRCF16A10003 | kos | 4
| - I/O modul za RPC krmilnik, 10x relejski izhod, 12x DI, komunikacija Room bus, napajanje 24V DC preko komunikacije, priključek 2xRJ45, tip CRS-HH-REL-10, komplet s pritrditvenim materialom na DIN. | - I/O module for RPC controller, 10x relay output, 12x DI, Room bus communication, 24V DC power supply via communication, 2xRJ45 connector, type CRS-HH-REL-10, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWHHREL10001+SXWDINEND10001 | as for example Schneider tip: SXWHHREL10001+SXWDINEND10001 | kos | 11
| - Razširitveni SMI modul RP-C-EXT-BL-SMI-4-HV-PD za 4 žaluzije, komplet s pritrditvenim materialom na DIN. | - SMI expansion module RP-C-EXT-BL-SMI-4-HV-PD for 4 blinds, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | as for example Schneider tip: SXWRESMI4HVPD10001+SXWDINEND10001 | kos | 10
| - Razširitveni DALI modul RP-C-EXT-DALI-M-PD, komplet s pritrditvenim materialom na DIN. | - DALI Expansion Module RP-C-EXT-DALI-M-PD, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 4
| - Modbus/ KNX modul RP-C-EXT-KNX, komplet s pritrditvenim materialom na DIN. | - Modbus/KNX module RP-C-EXT-KNX, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 4
| - Napajalnik KNX linije MTN684064, komplet s pritrditvenim materialom na DIN. | - Power supply for KNX line MTN684064, complete with DIN mounting material.
| kot naprimer Schneider tip: MTN684064 | such as Schneider type: MTN684064 | kos | 4
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
6.21 | Dobava BMS postaje BMS-K1-1-R.2 (locirana v +BMS-K1-1-R.2), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the BMS station BMS-K1-1-R.2 (located in +BMS-K1-1-R.2), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - krmiljenje ventilatorskih konvektorjev (EC motor, 4-cevni sistem) | - fan coil control (EC motor, 4-pipe system) | kos | 10
| - glavne komunikacijske povezave (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | - main communication connections (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | kos | 12
| Predvidena konfiguracija BMS postaje BMS-K1-1-R.2 (locirana v omari +BMS-K1-1-R.2), ki bo namenjena računalniškemu nadzoru in vodenju sistema upravljanja zgradb je: | The planned configuration of the BMS station BMS-K1-1-R.2 (located in cabinet +BMS-K1-1-R.2), which will be used for computer control and management of the building management system, is:
| - Napajalnik 24 VAC, 10 W, komplet s pritrditvenim materialom na DIN. | - Power supply 24 VAC, 10 W, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWPS24VX10001 + podnožje SXWTBPSW110001. | such as Schneider type: SXWPS24VX10001 + base SXWTBPSW110001. | kos | 1
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), komplet s pritrditvenim materialom na DIN. | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port), complete with DIN mounting material.
| kot naprimer Schneider tip: SXWASPXXX10001 + podnožje SXWTBASW110002. | such as Schneider type: SXWASPXXX10001 + base SXWTBASW110002. | kos | 1
| - Sobni BACnet krmilnik RPC16A krmilnik, 230 VAC napajanje, 8x I/O, 4x rele, 4x triac, BACnet, komplet s pritrditvenim materialom na DIN. | - Room BACnet controller RPC16A controller, 230 VAC power supply, 8x I/O, 4x relay, 4x triac, BACnet, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRCF16A10003 | such as for example Schneider type: SXWRCF16A10003 | kos | 1
| - I/O modul za RPC krmilnik, 10x relejski izhod, 12x DI, komunikacija Room bus, napajanje 24V DC preko komunikacije, priključek 2xRJ45, tip CRS-HH-REL-10, komplet s pritrditvenim materialom na DIN. | - I/O module for RPC controller, 10x relay output, 12x DI, Room bus communication, 24V DC power supply via communication, 2xRJ45 connector, type CRS-HH-REL-10, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWHHREL10001+SXWDINEND10001 | as for example Schneider tip: SXWHHREL10001+SXWDINEND10001 | kos | 2
| - Razširitveni DALI modul RP-C-EXT-DALI-M-PD, komplet s pritrditvenim materialom na DIN. | - DALI Expansion Module RP-C-EXT-DALI-M-PD, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 4
| - Modbus/ KNX modul RP-C-EXT-KNX, komplet s pritrditvenim materialom na DIN. | - Modbus/KNX module RP-C-EXT-KNX, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 4
| - Napajalnik KNX linije MTN684064, komplet s pritrditvenim materialom na DIN. | - Power supply for KNX line MTN684064, complete with DIN mounting material.
| kot naprimer Schneider tip: MTN684064 | such as Schneider type: MTN684064 | kos | 4
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
6.22 | Dobava BMS postaje BMS-K1-2-R.2 (locirana v +BMS-K1-2-R.2), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of the BMS station BMS-K1-2-R.2 (located in +BMS-K1-2-R.2), manufacturing, programming, installation, testing and commissioning of the application software for the PLC station according to the requirements of the electrical project, the mechanical engineering project and the investor in the following scope: |  |  | kpl | 1 |  | 0
| - krmiljenje ventilatorskih konvektorjev (EC motor, 4-cevni sistem) | - fan coil control (EC motor, 4-pipe system) | kos | 8
| - glavne komunikacijske povezave (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | - main communication connections (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | kos | 12
| Predvidena konfiguracija BMS postaje BMS-K1-2-R.2 (locirana v omari +BMS-K1-2-R.2), ki bo namenjena računalniškemu nadzoru in vodenju sistema upravljanja zgradb je: | The intended configuration of the BMS station BMS-K1-2-R.2 (located in cabinet +BMS-K1-2-R.2), which will be used for computer control and management of the building management system, is:
| - Napajalnik 24 VAC, 10 W, komplet s pritrditvenim materialom na DIN. | - Power supply 24 VAC, 10 W, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWPS24VX10001 + podnožje SXWTBPSW110001. | such as Schneider type: SXWPS24VX10001 + base SXWTBPSW110001. | kos | 1
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), komplet s pritrditvenim materialom na DIN. | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port), complete with DIN mounting material.
| kot naprimer Schneider tip: SXWASPXXX10001 + podnožje SXWTBASW110002. | such as Schneider type: SXWASPXXX10001 + base SXWTBASW110002. | kos | 1
| - Sobni BACnet krmilnik RPC16A krmilnik, 230 VAC napajanje, 8x I/O, 4x rele, 4x triac, BACnet, komplet s pritrditvenim materialom na DIN. | - Room BACnet controller RPC16A controller, 230 VAC power supply, 8x I/O, 4x relay, 4x triac, BACnet, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRCF16A10003 | such as for example Schneider type: SXWRCF16A10003 | kos | 1
| - I/O modul za RPC krmilnik, 10x relejski izhod, 12x DI, komunikacija Room bus, napajanje 24V DC preko komunikacije, priključek 2xRJ45, tip CRS-HH-REL-10, komplet s pritrditvenim materialom na DIN. | - I/O module for RPC controller, 10x relay output, 12x DI, Room bus communication, 24V DC power supply via communication, 2xRJ45 connector, type CRS-HH-REL-10, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWHHREL10001+SXWDINEND10001 | as for example Schneider tip: SXWHHREL10001+SXWDINEND10001 | kos | 2
| - Razširitveni DALI modul RP-C-EXT-DALI-M-PD, komplet s pritrditvenim materialom na DIN. | - DALI Expansion Module RP-C-EXT-DALI-M-PD, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 4
| - Modbus/ KNX modul RP-C-EXT-KNX, komplet s pritrditvenim materialom na DIN. | - Modbus/KNX module RP-C-EXT-KNX, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 4
| - Napajalnik KNX linije MTN684064, komplet s pritrditvenim materialom na DIN. | - Power supply for KNX line MTN684064, complete with DIN mounting material.
| kot naprimer Schneider tip: MTN684064 | such as Schneider type: MTN684064 | kos | 4
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
6.23 | Dobava BMS postaje BMS-K1-3-R.2 (locirana v +BMS-K2-1-R.2), izdelava, programiranje, inštalacija, testiranje in spuščanje v pogon aplikacijske programske opreme za PLC postajo po zahtevah elektro projekta, strojno-tehnološkega projekta in investitorja v naslednjem obsegu: | Supply of BMS station BMS-K1-3-R.2 (located in +BMS-K2-1-R.2), manufacturing, programming, installation, testing and commissioning of application software for PLC station according to the requirements of the electrical project, mechanical engineering project and investor in the following scope: |  |  | kpl | 1 |  | 0
| - krmiljenje ventilatorskih konvektorjev (EC motor, 4-cevni sistem) | - fan coil control (EC motor, 4-pipe system) | kos | 6
| - glavne komunikacijske povezave (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | - main communication connections (Ethernet, ModBus, KNX, DALI-2, RoomBus, SMI) | kos | 10
| Predvidena konfiguracija BMS postaje BMS-K1-3-R.2 (locirana v omari +BMS-K1-3-R.2), ki bo namenjena računalniškemu nadzoru in vodenju sistema upravljanja zgradb je: | The intended configuration of the BMS station BMS-K1-3-R.2 (located in cabinet +BMS-K1-3-R.2), which will be used for computer control and management of the building management system, is:
| - Napajalnik 24 VAC, 10 W, komplet s pritrditvenim materialom na DIN. | - Power supply 24 VAC, 10 W, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWPS24VX10001 + podnožje SXWTBPSW110001. | such as Schneider type: SXWPS24VX10001 + base SXWTBPSW110001. | kos | 1
| - CPU modul (s serijskimi porti RS485, 10/100 Mbit/Ethernet port), komplet s pritrditvenim materialom na DIN. | - CPU module (with RS485 serial ports, 10/100 Mbit/Ethernet port), complete with DIN mounting material.
| kot naprimer Schneider tip: SXWASPXXX10001 + podnožje SXWTBASW110002. | such as Schneider type: SXWASPXXX10001 + base SXWTBASW110002. | kos | 1
| - Sobni BACnet krmilnik RPC16A krmilnik, 230 VAC napajanje, 8x I/O, 4x rele, 4x triac, BACnet, komplet s pritrditvenim materialom na DIN. | - Room BACnet controller RPC16A controller, 230 VAC power supply, 8x I/O, 4x relay, 4x triac, BACnet, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWRCF16A10003 | such as for example Schneider type: SXWRCF16A10003 | kos | 1
| - I/O modul za RPC krmilnik, 10x relejski izhod, 12x DI, komunikacija Room bus, napajanje 24V DC preko komunikacije, priključek 2xRJ45, tip CRS-HH-REL-10, komplet s pritrditvenim materialom na DIN. | - I/O module for RPC controller, 10x relay output, 12x DI, Room bus communication, 24V DC power supply via communication, 2xRJ45 connector, type CRS-HH-REL-10, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWHHREL10001+SXWDINEND10001 | as for example Schneider tip: SXWHHREL10001+SXWDINEND10001 | kos | 2
| - Razširitveni DALI modul RP-C-EXT-DALI-M-PD, komplet s pritrditvenim materialom na DIN. | - DALI Expansion Module RP-C-EXT-DALI-M-PD, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 4
| - Modbus/ KNX modul RP-C-EXT-KNX, komplet s pritrditvenim materialom na DIN. | - Modbus/KNX module RP-C-EXT-KNX, complete with DIN mounting material.
| kot naprimer Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | as for example Schneider tip: SXWREDAMPD10001 + SXWDINEND10001 | kos | 4
| - Napajalnik KNX linije MTN684064, komplet s pritrditvenim materialom na DIN. | - Power supply for KNX line MTN684064, complete with DIN mounting material.
| kot naprimer Schneider tip: MTN684064 | such as Schneider type: MTN684064 | kos | 4
| OPOMBA: izdelana programska oprema mora biti ustrezno dokumentirana in predana naročniku na zapisljivem mediju! | NOTE: The software produced must be properly documented and handed over to the client on a recordable medium!
6.24 | Dobava, Izdelava, inštalacija, testiranje in spuščanje v pogon sistemske programske opreme PLC in SCADA za sisteme nadzora BMS v skladu s funkcijskimi zahtevami in zahtevami naročnika oziroma uporabnika. OPOMBA: SCADA nadzorni sistem je potrebno izdelati skupen za cel objekt in možnost ločenega prikaza in vodenja za posamezni oddelek. | Supply, Manufacture, installation, testing and commissioning of PLC and SCADA system software for BMS control systems in accordance with the functional and customer/user requirements. NOTE: The SCADA control system should be common for the whole building and the possibility of separate display and management for each department. |  |  | kpl | 1 |  | 0
| - izdelava vizualizacijskih prikazov na SCADA sistemu-skupen; | - creating visualisation displays on a SCADA system - common; | kos | 5
| - izdelava vizualizacijskih prikazov na SCADA sistemu-posamezni laboratoriski oddelek; ocenjeno | - creation of visualisation displays on SCADA system - individual laboratory department; evaluated | kos | 35
| - parametriranje signalov, alarmov in zgodovine; | - parameterisation of signals, alarms and history; | kpl | 1
| - izdelava in vzpostavitev delovanja celotnega sistema preko preglednih grafičnih prikazov in sinoptičnih slik, izdelanih v skladu z zahtevami s strani naročnika; | - the production and set-up of the entire system through clear graphical displays and synoptic images, produced in accordance with the customer's requirements; | kpl | 1
| - izdelava podatkovne baze, | - creation of a database, | kpl | 1
| - izdelava gonilnikov za povezavo sistemov na SCADA sistem. Dodati vizualizacijske prikaze, dodati bazo podatkov, alarmov in zgodovino za sistem; | - creation of drivers to connect the systems to the SCADA system. Add visualisation displays, add database, alarms and history for the system; | kpl | 1
| - izdelava in dokumentiranje xDS - Design Specification (FS - Functional Specification, HDS - Hardware Design Specification in SDS - Software Design Specification); | - creation and documentation of xDS - Design Specification (FS - Functional Specification, HDS - Hardware Design Specification and SDS - Software Design Specification); | kpl | 1
| - izvedba in dokumentiranje IQ/OQ/QTZ/ZP; | - iQ/OQ/QTZ/ZP implementation and documentation; | kpl | 1
| - dobava vseh potrebnih SW licenc za SCADA sistem; | - supply of all necessary software licences for the SCADA system; | kpl | 1
| - izvedba komunikacijskega vmesnika s samostojnimi napravami za potrebe delovanja in nadzora in prikaz osnovnih statusov delovanja na SCADA sistemu; | - implementation of a communication interface with stand-alone devices for operation and control purposes and display of basic operational statuses on the SCADA system; | kpl | 1
| - izvedba komunikacijskega vmesnika in integracije v centralni Historian za naslednje podatke -Procesne vrednosti | - implementation of a communication interface and integration into the central Historian for the following data -Process values | kpl | 1
| OPOMBA: pred izdelavo sistemske programske opreme je potrebno v sodelovanju z investitorjem izdelati detajlno funkcionalno specifikacijo. | NOTE: Before the system software can be developed, a detailed functional specification must be drawn up in cooperation with the investor.
| OPOMBA: izdelana programska oprema mora zadovoljevati zahteve strojno-tehnološkega projekta, elektro projekta, investitorja ter mora biti ustrezno dokumentirana na zapisljivem mediju! | NOTE: The software developed must satisfy the requirements of the mechanical engineering project, the electrical project, the investor and must be properly documented on a recordable medium!
| OPOMBA: računalnik za SCADA nadzorni sistem s OS win10 dobavi naročnik. | NOTE: The computer for the SCADA control system with win10 OS shall be supplied by the customer.
| Sistem upravljanja stavb (HW & SW) | Building Management System (HW & SW) | [5 empty] | 0

## 3.13.7_Ostalo
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
3.13 | ELEKTRO DELA | ELECTRICAL WORKS
3.13.7 | OSTALO | OTHER |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
7 | OSTALO | OTHER
7.1 | Priprava podlog za izdelavo PID projekta. Vnos sprememb, do katerih pride med izvedbo, v en izvod PZI projekta. | Preparation of the basis for the PID project. Entry of changes that occur during implementation in one copy of the PID project. | kpl | 1 |  | 0
7.2 | Izvedba meritev in funkcionalnega pregleda elektroinstalacij z izdelavo zapisnikov in poročil za celoten sistem v sestavi : | Carrying out measurements and functional inspection of the electrical installations, producing minutes and reports for the entire system as a whole: | kpl | 1 |  | 0
| - merjenje izolacijske upornosti | - insulation resistance measurement
| - funkcionalni preizkus | - functional test
| - nastavitev zaščit | - setting safeguards
7.3 | Pozitivne ocene, atesti, certifikati in potrdila ustreznih inštitucij za dokazovanje primerne kakovosti vgrajenih naprav, napeljav, materialov in montažnih del (EIMV, IVD, ZAG, SIQ in podobno). | Positive evaluations, attestations, certificates and attestations of the relevant institutions to prove the adequate quality of the installed devices, installations, materials and assembly works (EIMV, IVD, ZAG, SIQ, etc.). | kpl | 1 |  | 0
| Izdelava tesnjenja prehodov kablov in kabelskih inštalacij skozi požarne sektorje, ki ga z ustreznimi materiali izvede izvajalec z licenco ter na koncu izda ustrezni certifikat (izvedba in uporabljen material v skladu s standardom DIN 4102, skladno s smernico SZPV 408, skladno s NPV (EI90) in po navodilih proizvajalca), cca: Φ 90 mm, kot naprimer Protecta, za stene do debeline 400 mm OPOMBA: tesnenje mora biti takšnega tipa, ki omogoča naknadno vstavljanje kablov. | Sealing of cable and cable installation penetrations through fire sectors, carried out by a licensed contractor using appropriate materials and finally certified (execution and material used in accordance with DIN 4102, in accordance with SZPV 408, in accordance with NPV (EI90) and according to the manufacturer's instructions), approx.: Φ 90 mm, such as Protecta, for walls up to 400 mm thick NOTE: The sealing shall be of a type to allow subsequent insertion of cables. | kpl | 85 |  | 0
| Izdelava tesnjenja prehodov kablov in kabelskih inštalacij skozi požarne sektorje, ki ga z ustreznimi materiali izvede izvajalec z licenco ter na koncu izda ustrezni certifikat (izvedba in uporabljen material v skladu s standardom DIN 4102, skladno s smernico SZPV 408, skladno s NPV (EI90) in po navodilih proizvajalca), cca: fi 90 mm, kot naprimer Hilti, za stene debelejše od 400 mm OPOMBA: tesnenje mora biti takšnega tipa, ki omogoča naknadno vstavljanje kablov. | Sealing of cable and cable installation penetrations through fire sectors, carried out by a licensed contractor using appropriate materials and finally certified (execution and material used in accordance with DIN 4102, in accordance with SZPV 408, in accordance with NPV (EI90) and according to the manufacturer's instructions), approx.: fi 90 mm, such as Hilti, for walls thicker than 400 mm NOTE: The sealing shall be of a type to allow subsequent insertion of cables. | kpl | 10 |  | 0
| Izdelava tesnjenja prehodov kablov in kabelskih inštalacij skozi požarne sektorje, ki ga z ustreznimi materiali izvede izvajalec z licenco ter na koncu izda ustrezni certifikat (izvedba in uporabljen material v skladu s standardom DIN 4102, skladno s smernico SZPV 408, skladno s NPV (EI90) in po navodilih proizvajalca), cca: Φ 150 mm, kot naprimer Hilti, za stene debelejše od 400 mm OPOMBA: tesnenje mora biti takšnega tipa, ki omogoča naknadno vstavljanje kablov. | Sealing of cable and cable installation penetrations through fire sectors, carried out by a licensed contractor using appropriate materials and finally certified (execution and material used in accordance with DIN 4102, in accordance with SZPV 408, in accordance with NPV (EI90) and according to the manufacturer's instructions), approx.: Φ 150 mm, such as Hilti, for walls thicker than 400 mm NOTE: The sealing shall be of a type to allow subsequent insertion of cables. | kpl | 8 |  | 0
| Izdelava tesnjenja prehodov kablov in kabelskih inštalacij skozi požarne sektorje, ki ga z ustreznimi materiali izvede izvajalec z licenco ter na koncu izda ustrezni certifikat (izvedba in uporabljen material v skladu s standardom DIN 4102, skladno s smernico SZPV 408, skladno s NPV (EI90) in po navodilih proizvajalca), cca: 600 x 100 mm, kot naprimer Hilti OPOMBA: tesnenje mora biti takšnega tipa, ki omogoča naknadno vstavljanje kablov. | Sealing of cable and cable installation penetrations through fire sectors, carried out by a licensed contractor using appropriate materials and finally certified (execution and material used in accordance with DIN 4102, in accordance with SZPV 408, in accordance with NPV (EI90) and according to the manufacturer's instructions), approx.: 600 x 100 mm, such as Hilti NOTE: The sealing shall be of a type to allow subsequent insertion of cables. | kpl | 3 |  | 0
| Vrtanje odprtin v stenah in ploščah, do premera Φ 150 mm | Drilling of holes in walls and panels, up to a diameter of Φ 150 mm | kos | 185 |  | 0
| Izdelava tesnjenja horizontalnih prehodov kablov in kabelskih inštalacij skozi stene, do Φ 40 mm. | Sealing of horizontal passages for cables and cable installations through walls, up to Φ 40 mm. | kpl | 30 |  | 0
| Izdelava tesnjenja horizontalnih prehodov kablov in kabelskih inštalacij skozi stene, do Φ 90 mm. | Sealing of horizontal passages for cables and cable installations through walls, up to Φ 90 mm. | kpl | 25 |  | 0
| Izdelava tesnjenja horizontalnih prehodov kablov in kabelskih inštalacij skozi stene, do Φ 150 mm. | Sealing of horizontal passages for cables and cable installations through walls, up to Φ 150 mm. | kpl | 15 |  | 0
7.4 | Razna nepredvidena dela, ki se obračunajo po urah s potrditvijo nadzornika v gradbenem dnevniku. | Miscellaneous unforeseen work, billed by the hour with the supervisor's approval in the construction logbook. | ur | 150 |  | 0
| Opomba: | Remark:
| Dobavitelj opreme prilagodi projekt za izvedbo PZI na izbrano oziroma ponujeno opremo! | The equipment supplier adapts the PZI project to the equipment selected or offered!
| OSTALO | OTHER |  |  |  | 0