## 0_Naslovnica
OPOZORILO! Vsi prevodi v angleščino so strojno izdelani in zgolj informativne narave. V primeru kakršnekoli nejasnosti ali dvoma izključno velja izvirno besedilo v slovenščini. WARNING! All translations into English have been produced by machine translation and are provided for informational purposes only. In the event of any ambiguity or uncertainty, the original Slovenian text shall prevail exclusively.
| / | / | [5 empty] | /
| Sprem./Rev.: | Opis spremembe/Description of Changes: | [5 empty] | Datum/Date: | Podpis/Signature:
| Investitor/Investor: |  |  |  |  | Gradnja/Facility
|  |  | Univerza v Ljubljani Kongresni trg 12 1000 Ljubljana, Slovenija |  |  | Fakulteta za strojništvo/Faculty of Mechanical Engineering
| Projektant/Design Engineer: |  |  |  |  | Del objekta/sistem/Building/System:
|  |  | VAREN d.o.o. Dogoška cesta 35 2000 Maribor, Slovenija |  |  | ZAKLONIŠČE/SHELTER
| Projektant/Design Engineer: |  |  |  |  | Vrsta načrta/Documentation:
4 NAČRT S PODROČJA STROJNIŠTVA/ DOC. IN THE FIELD OF MECHANICAL ENGINEERING
|  | Ime in priimek/Name and Surname: |  |  | Id. št./Id. No: | Vsebina risbe (dokumenta)/Document Title:
| Vodja proj./ Des. Manager: | Boštjan Vuga, univ. dipl. inž. arh., grad. dip. (AA) |  |  | ZAPS 0035 PA PPN | PR. POPIS STROJNIH DEL/BOQ OF MECHANICAL WORKS 4/1 Zaklonišče/Shelter
| Poobl. strok./ Cert. Profess.: | Marko Lubej, univ. dipl. inž. str. |  |  | IZS S-0739
| Poobl. strok./ Cert. Profess.: |  |  |  |  | Št. proj./ Proj. No.: | 362-19 |  | Vrsta dokument./ Document. Type: | DZR
| Izdelal/ Creator: | Marko Lubej, univ. dipl. inž. str. |  |  | IZS S-0739 | Klas. ozn./ Class. No.: | -- |  | Stran/ Page: | 1/*
| Datum/ Date: | maj/May 2026 |  | Merilo/ Scale: | / | Ident. ozn./ Id. No: | JULFS--6S0103P

## 0_Osebe
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
POOBLAŠČENI STROKOVNJAKI, ODGOVORNI ZA IZDELAVO PROJEKTANTSKEGA POPISA:
Id. št. ZAPS/IZS | Pooblaščeni strokovnjak | Strokovno področje
IZS S-0739 | Marko Lubej, univ. dipl. inž. str. | Strojništvo
SODELAVCI PRI IZDELAVI PROJEKTANTSKEGA POPISA:
/ | Hinko Samec | Tehnologija zaklonišča
CERTIFIED EXPERTS RESPONSIBLE FOR ELABORATING THE BILL OF QUANTITIES:
Id. No ZAPS/IZS | Certified Expert | Area of Expertise
IZS S-0739 | Marko Lubej, univ. dipl. inž. str. | Mechanical Engineering
COLABORATORS IN THE ELABORATING THE BILL OF QUANTITIES:
/ | Hinko Samec | Shelter technology

## 0.1_Uvod-STP
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
0.1 | SPLOŠNI TEHNIČNI POGOJI | GENERAL TECHNICAL CONDITIONS
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic operator with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
0.1.1 | Izvajalec se obveže, da bo upošteval veljavno zakonodajo, ki ureja graditev objektov v Republiki Sloveniji, vključno s povezanimi podzakonskimi akti, predpisi, tehničnimi smernicami, standardi, pravili stroke in dobro gradbeno prakso. Prav tako mora izvajalec upoštevati vse zahteve izdanega integralnega gradbenega dovoljenja in vsa dela izvesti skladno s projektno dokumentacijo ter ostalimi pogoji, objavljenimi v razpisni dokumentaciji. | The Contractor undertakes to comply with the applicable legislation governing the construction of buildings in the Republic of Slovenia, including related by-laws, regulations, technical guidelines, standards, professional rules and good construction practice. The Contractor shall also comply with all the requirements of the integral building permit issued and shall carry out all works in accordance with the project documentation and other conditions published in the tender documentation.
0.1.2 | Dela lahko izvaja samo izvajalec, ki je registriran za opravljanje gradbene dejavnosti in ima za tovrstna dela ustrezno zavarovanje za škodo, certifikate, tehnično izobražen kader, sredstva ter je usposobljen za samostojno pripravo in izvedbo del. | The work may only be carried out by a contractor who is registered to carry out construction work and who has the appropriate insurance for such work, certificates, technically trained staff, resources and is qualified to prepare and carry out the work independently.
0.1.3 | Izvajalec odgovarja za kakovost izvedbe vseh del. | The Contractor shall be responsible for the quality of the execution of all works.
0.1.4 | Izvajalec nosi vso odgovornost za nesreče in škodo, ki nastane na objektu ali v okolici zaradi njegovega dela. | The Contractor shall bear all liability for accidents and damage to the installation or the surrounding area caused by his work.
0.1.5 | Pred oddajo ponudbe se je izvajalec dolžan seznaniti z območjem predvidenim za gradnjo in temu prilagoditi vsa potrebna dela, kar mora biti zajeto v ponudbi. V neposredni bližini predvidene gradnje se nahajajo stavbe, v katerih potekajo izobraževalni in raziskovalni procesi. Zato bo izvajalec moral izvajati kontrolo hrupa in kontrolo vibracij. Dela, ki so hrupna in dela, ki povzročajo vibracije bo izvajalec moral preprečiti oziroma jih izvesti na način, da povzročajo minimalne vplive. Tehnologijo rušenja, pilotiranja in tehnologijo izvedbe ostalih del bo izvajalec moral prilagoditi tako, da bo vpliv minimalen. Izvajalec mora preprečiti in zmanjšati emisije delcev iz gradbišča na najmanjšo možno mero. | Before submitting a tender, the contractor is obliged to familiarise himself with the area to be constructed and to adapt any necessary works accordingly, which must be included in the tender. In the immediate vicinity of the proposed construction, there are buildings in which educational and research processes take place. The contractor will therefore be required to carry out noise and vibration control. Noise and vibration works will have to be avoided or carried out in such a way as to minimise the impact. Demolition, piling and other works will have to be adapted to minimise the impact. The contractor must avoid and minimise the emission of particulates emitted from the construction site as far as is reasonably practicable.
0.1.6 | Izvajalec je pred oddajo ponudbe dolžan pregledati projektno dokumentacijo in ostale pogoje, ki so del razpisne dokumentacije V primeru morebitnih napak in neskladij je izvajalec dolžan na to opozoriti naročnika pred oddajo ponudbe. | The Contractor is obliged to review the project documentation and other conditions forming part of the tender documentation before submitting the tender In case of any errors or inconsistencies, the Contractor is obliged to bring these to the attention of the Contracting Authority before submitting the tender.
0.1.7 | Pred oddajo ponudbe je izvajalec dolžan preveriti ustreznost popisov del in količin v teh popisih ter njihovo skladnost z ostalimi dokumenti projektne dokumentacije, ki so del razpisne dokumentacije. Prav tako je izvajalec dolžan preveriti vse detajle in sheme. Vse izmere je potrebno preveriti po posameznih projektih oz. načrtih, ki sestavljajo razpisno dokumentacijo. V primeru ugotovljenih neskladij je v času priprave ponudbe obvezan o tem obvestiti naročnika. | Before submitting a tender, the Contractor shall check the adequacy of the inventories of works and quantities in these Bills of Quantities and their conformity with the other documents of the project documentation forming part of the tender documentation. The Contractor shall also check all details and diagrams. All measurements shall be checked against the individual projects or plans forming part of the tender documentation. In the event of any discrepancies, the Contractor shall inform the Contracting Authority at the time of preparing the tender.
0.1.8 | Pred oddajo ponudbe je izvajalec dolžan v tem popisu preveriti zmnožke in seštevke ter prenose le-teh v rekapitulacijo. Izvajalec se s pripravo ponudbe obvezuje, da je prebral vse celice in elemente celotnega popisa, vključno z vsemi postavkami in splošnimi navodili ali določili in je preveril pravilnost preračuna ter s tem zagotavlja ponudbeno vrednost. | Before submitting a tender, the Contractor is required to check the products and totals in this Bill of Quantities (BoQ) and their transfer to the recapitulation. The Contractor undertakes, by preparing a tender, to have read all the cells and elements of the complete BoQ, including all headings and general instructions or provisions, and to have checked the correctness of the conversion, thereby guaranteeing the value of the tender.
0.1.9 | Dela bo izvajalec moral izvajati po predloženi projektni dokumentaciji, detajlih in z upoštevanjem navodil in potrditev projektanta, nadzornika in investitorja. Vso potrebno delavniško dokumentacijo zagotovi izvajalec del v okviru ponujene cene. | The Contractor shall carry out the works in accordance with the submitted design documents, details and subject to the instructions and approvals of the Designer, the Supervisor and the Investor. All necessary workshop documentation shall be provided by the Contractor within the scope of the price quoted.
0.1.10 | Pred izvedbo posameznih del je izvajalec dolžan pregledati projektno dokumentacijo za izvedbo gradnje (PZI) in elaborate. Na morebitne napake v dokumentaciji ali neskladja med posameznimi načrti ali deli načrtov (popisi del, tehnična poročila, lokacijski in tehnični prikazi) izvajalec opozori nadzornika in projektanta, in se z njima pravočasno uskladi. | The Contractor shall review the Detailed Design documentation (PZI) and the studies before carrying out the individual works. The Contractor shall draw the attention of the Supervisor and the Designer to any errors in the documentation or discrepancies between the individual designs or parts of designs (BoQ, technical reports, location and technical drawings) and shall coordinate with them in good time.
0.1.11 | Tehnični opisi, prikazi, detajli, sheme ter ostali dokumenti v PZI dokumentaciji predstavljajo dodaten opis popisnih postavk gradbeno obrtniških in inštalacijskih del ter jih je potrebno dosledno upoštevati skupaj s popisom del. | The technical descriptions, illustrations, details, diagrams and other documents in the Detailed Design documentation (PZI) are additional descriptions of the BoQ inventory items of the building, construction and installation works and must be strictly followed together with the BoQ.
0.1.12 | Specifikacije in zahteve, navedene v popisu, se ne smejo upoštevati kot edine zahteve. Izvajalec je dolžan v ceni zajeti in dobaviti vse elemente opreme ter opraviti dela in storitve, ki niso eksplicitno navedeni, a so bistvenega pomena za funkcionalnost, skladnost s predpisi ter kontinuirano, zanesljivo in varno obratovanje opreme. | The specifications and requirements set out in the BoQ shall not be taken as the only requirements. The Contractor shall be obliged to include in the price and supply all items of equipment and to carry out works and services which are not expressly mentioned but which are essential for the functionality, regulatory compliance and continuous, reliable and safe operation of the equipment.
0.1.13 | Vsa dela morajo biti izvedena kvalitetno in iz materialov z zahtevanimi lastnostmi, izvedena skladno z veljavno zakonodajo in z upoštevanjem navodil za vgradnjo za izbrane materiale in opremo, s predložitvijo predpisanih izjav o lastnostih in/ali certifikatov. Vsi gradbeni proizvodi (GP) morajo biti označeni s CE oznako. | All work shall be of good quality and be executed with materials of the required characteristics, in accordance with the applicable legislation and in compliance with the installation instructions for the materials and equipment selected, and shall be accompanied by the prescribed declarations of performance and/or certificates. All construction products (GP) shall bear the CE marking.
0.1.14 | Za vsako opisano delo v popisu je potrebno upoštevati celotno potrebno delo, ves osnovni in pomožni material, prevoz materiala in orodja na objekt, notranje transporte, delovne in pomožne odre, zaključno čiščenje in odstranitev odpadkov po dovršenem delu. | For each work described in the inventory, the total work required, all basic and ancillary materials, the transport of materials and tools to the site, internal transports, working and ancillary scaffolding, final cleaning and the disposal of waste after the work has been completed must be taken into account.
0.1.15 | Vsa delovna sredstva, organizacija in koordinacija del, pripravljalna, spremljajoča in zaključna dela, potrebni montažni in tesnilni materiali ter podkonstrukcije so sestavni del posameznih postavk. | All labour, organisation and coordination of the works, preparatory, accompanying and finishing works, necessary prefabrication and sealing materials and substructures are part of the individual items.
0.1.16 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - načrt organizacije gradbišča s podrobnim terminskim planom in izvedba vseh pripravljalnih del, postavitev, organizacija, zaščita in prijava gradbišča, gradbiščnih objektov, ureditev začasnih deponij, tekoče vzdrževanje, skupaj s plačilom splošnih stroškov pristojbin in davkov upravnih organov, pridobivanju raznih dovoljenj in soglasij za izvedbo, ograditev gradbišča in postavitev gradbene table in prometne signalizacije, zagotavljanje ustrezne varnosti na gradbišču, tekoče vzdrževanje in končna odstranitev gradbišča; - zagotovitev potrebnih začasnih površin za transportne poti in gradnjo izven območja gradbišča s plačilom stroškov za sanacijo in vzpostavitev okoliških zemljišč in objektov v prvotno stanje (soglasja, odškodnine, itd.); - začasni odvoz, deponiranje in vračanje izkopanega materiala, ki ga ne bo možno deponirati na gradbišču; - odvoz in zagotovitev odstranjevanja odpadnega gradbenega materiala skladno z zakonodajo na področju ravnanja z odpadki (odvoz na urejene deponije s plačilom komunalnih prispevkov in taks itd.); - oteženi izkop v mokrem terenu, izkop v vodi, odvod meteorne vode iz gradbene jame in vode, ki se izceja iz bočnih strani izkopov; - ustrezno varovanje izkopa gradbene jame za objekt in ostalih manjših posameznih izkopov za izvedbo komunalne infrastrukture brez posegov na sosednja zemljišča; - ustrezno varovanje obstoječih objektov, infrastrukture in okolice v času gradnje ter dokumentiranje vseh morebitnih škodnih dogodkov; - pripravljalna, spremljajoča in zaključna dela (zakoličbe, zagotovitev potrebnih komunalnih priključkov za potrebe izvajanja gradnje, izvedba začasnih inštalacij, označevanje podzemnih vodov, postavljanje in vzdrževanje zakoličbenih profilov, izvedba in označevanje novih in starih križanj ter morebitna zaščita križanj komunalnih vodov, geodetski posnetki in izdajanje vmesnih posnetkov izvedene infrastrukture naročniku, izdelava zbirnih kart, itd.), v kolikor ni to drugače določeno; - pridobivanje soglasij in izvedba morebitnih zapor na vseh cestah s plačilom stroškov, nadomestil in pristojbin; - zagotovitev oz. postavitev in končna odstranitev po zaključku gradnje začasnih skladišč in začasnega pisarniškega kontejnerskega objekta vključno z opremo za dve delovni mesti in za skupne operativne sestanke vel. ca. 40 m2 za potrebe naročnika, s tekočim vzdrževanjem in čiščenjem. | The following must also be included or taken into account in the uniform prices for individual items: - a construction site organisation plan with a detailed timetable and the execution of all preparatory works, the setting-up, organisation, protection and registration of the construction site, site facilities, the arrangement of temporary storage facilities, ongoing maintenance, including the payment of general costs of fees and taxes of the administrative authorities, the obtaining of various permits and consents for the execution, the fencing of the site and the erection of construction signs and traffic signals, the provision of adequate security on the site, ongoing maintenance and the final dismantling of the construction site; - provision of the necessary temporary areas for transport routes and off-site construction, with costs for restoration and reinstatement of surrounding land and buildings (consents, compensation, etc.); - temporary removal, storage and return of excavated material that cannot be stored on site; - removing and disposing of waste building materials in accordance with waste management legislation (removal to regulated landfill sites with payment of municipal fees and charges, etc.); - difficult excavation in wet ground, excavation in water, drainage of rainwater from the construction pit and water draining from the sides of excavations; - adequate protection of the excavation of the construction pit for the building and other small individual excavations for the implementation of the utility infrastructure without encroaching on neighbouring land; - adequate protection of existing facilities, infrastructure and the surrounding area during construction, and documentation of any damage incidents; - preparatory, accompanying and finishing works (stake-out, provision of the necessary utility connections for the needs of construction, execution of temporary installations, marking of underground lines, installation and maintenance of stake-out profiles, execution and marking of new and old crossings and possible protection of crossings of utility lines, geodetic surveys and issuing of intermediate images of the completed infrastructure to the client, production of summary maps, etc.), unless otherwise specified; - obtaining consents and implementing any road closures, with costs, compensation and fees; - provision or erection and final removal on completion of construction of temporary storage and temporary office container building including equipment for two workstations and for joint operational meetings of approx. 40 m2 for the needs of the client, with ongoing maintenance and cleaning.
0.1.17 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - izdelava montažne tehnične dokumentacije, detajlov izvedbe in vse druge potrebne delavniške dokumentacije (s področja arhitekture, gradbeništva, elektrotehnike, strojništva in zunanje ter krajinske ureditve) ter pridobitev obvezne potrditve s strani projektanta, nadzornika in investitorja; - odprava vseh vrst inštalacijskih kolizij z izvajanjem potrebnih premikov inštalacij in njihovim usklajevanjem na mestu montaže, vse v obsegu, ki ne vpliva na projektirano rešitev ali tip inštalacij oz. opreme; - zagotavljanje kompletnosti elektro-instalacijskih sistemov s področja avtomatike za doseganje njihove popolne funkcionalnosti delovanja; - stroški za nadzor in koordinacijo izvedbe vseh elektro napeljav, ki so predmet končne instalacije proizvoda (senčila, vrata, okna,…); - izdelava montažnih skic in detajlov za izvedbo v dogovoru z vodjo gradnje in nadzornikom; - izdelava in predstavitev vzorcev v ustrezni velikosti za potrditev projektanta, nadzornika in investitorja; - zagotavljanje varnosti in zdravja pri delu, zlasti izvajanje vseh del, ki izhajajo in ukrepov, ki izhajajo iz določil veljavnih predpisov varstva pri delu in zahtev Varnostnega načrta;- stroški garancij, ki jih mora izvajalec predložiti naročniku. | The following must also be included or taken into account in the uniform prices for individual items: - preparation of prefabricated technical documentation, construction details and all other necessary workshop documentation (architectural, civil, electrical, mechanical, exterior and landscaping) and obtaining the mandatory approval of the designer, the supervisor and the investor; - elimination of all types of installation conflicts by carrying out the necessary relocation of installations and their coordination at the installation site, all to the extent that it does not affect the design solution or the type of installation or equipment; - ensuring the completeness of electrical installation systems in the automation sector to achieve their full operational functionality; - the cost of supervising and coordinating the installation of all the electrical installations that are the subject of the final installation of the product (blinds, doors, windows, etc.); - preparation of erection drawings and details for implementation in agreement with the construction manager and supervisor; - production and presentation of samples in appropriate sizes for the approval of the designer, the supervisor and the investor; - ensuring health and safety at work, in particular the implementation of all the works arising from and the measures resulting from the provisions of the applicable occupational safety regulations and the requirements of the Safety Plan; - the cost of the guarantees to be provided by the contractor to the client.
0.1.18 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - strošek vodje del glavnega izvajalca, ki bo izvajal tudi koordinacijo s podizvajalci in z drugimi izvajalci, ki jih bo izbral naročnik in bo opravljal delo vodje gradbišča; - koordinacija del z ostalimi izvajalci oz. podizvajalci del, projektantom, nadzornikom in investitorjem pri medsebojnem usklajevanju organizacije gradbišča in časovnega načrta del ter pri usklajevanju izdelave plana montaže, potrjenih s strani vseh udeležencev gradnje; - stroški koordinacije, sodelovanja in usklajevanja z dobavitelji tehnološke, laboratorijske, eksperimentalne in vse ostale pohištvene ter multimedijske opreme ter z vsemi ostalimi dobavitelji oz. podizvajalci na objektu; - stroški izdelave situacij; - stroški zavarovanja objekta v času izvedbe del in delavcev ter materiala na gradbišču v času izvajanja del, od začetka del do pridobitve uporabnega dovoljenja za objekt. Zavarovanje mora biti sklenjeno pri ustrezni zavarovalni družbi najmanj v višini pogodbene vrednosti ali v zakonsko predpisani vrednosti (v kolikor zavarovanje v višini pogodbene vrednosti presega zakonsko dovoljeno), za ves čas trajanja izvedbe del do uspešne primopredaje objekta; - preizkušanje kvalitete materiala, ki se vgrajuje in dokazovanje kvalitete s certifikati oz. tehničnimi soglasji; - izvedba vseh zahtevanih testov in preizkusov (npr. tlačni preizkusi, termografski pregledi, meritve elektromagnetnega sevanja, hrupa, itd.), poskusnega obratovanja celotnega objekta s poudarkom na vseh inštalacijah ter izvajanje predpisanega monitoringa v skladu s Poročilom o vplivih na okolje (pred gradnjo, med gradnjo in po končani gradnji); - izdelava izkaza požarne varnosti, vključno s sprotnim spremljanjem gradnje in izvajanjem požarnovarnostnih zahtev ter izdelava Požarnega reda z obveznimi prilogami; - izdelava Izkaza zaščite pred hrupom v stavbah; - izdelava Izkaza energijskih lastnosti stavbe in energetske izkaznice; - sodelovanje z izvajalci gradbenega in projektantskega nadzora in investitorjem za izvedbo tehničnega pregleda in priprava primopredaje, ki mora vsebovati vso zahtevano dokumentacijo, predvsem pa: izjave o skladnosti, požarni izkaz in ostale izkaze ter obvezne tabele, dokazilo o zanesljivosti objekta (DZO), certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo in vzdrževanje ter vse ostale dokumente v skladu s predpisi in pogodbenimi določili. | The following must also be included or taken into account in the uniform prices of the individual items: - the cost of a works manager for the main contractor, who will also coordinate with subcontractors and other contractors selected by the client and act as site manager; - coordination of the works with other contractors or subcontractors, the designer, the supervisor and the investor in coordinating the organisation of the construction site and the timetable for the works, and in coordinating the production of an installation plan approved by all the participants in the construction; - the costs of coordination, cooperation and coordination with suppliers of technological, laboratory, experimental and all other furniture and multimedia equipment, as well as with all other suppliers or subcontractors on the site; - the cost of drawing up situations; - the cost of insuring the building during the execution of the works and the workers and materials on site during the execution of the works, from the start of the works until the building has been licensed for occupation. The insurance must be taken out with a suitable insurance company for at least the contract value or the legal value (if the insurance for the contract value exceeds the legal value), for the entire duration of the works until the successful handover of the building; - testing the quality of the material to be installed and proving it with certificates or technical approvals; - carrying out all required tests and trials (e.g. pressure tests, thermographic inspections, electromagnetic radiation measurements, noise measurements, etc.), trial operation of the entire building, with emphasis on all installations, and carrying out the required monitoring in accordance with the Environmental Impact Assessment Report (before, during and after construction); - preparation of a fire safety statement, including ongoing monitoring of construction and implementation of fire safety requirements, and preparation of a Fire Safety Order with mandatory annexes; - preparation of a Noise Protection Statement for buildings; - preparation of the Building Energy Performance Report and Energy Performance Certificate; - cooperation with the construction and design supervision contractors and the investor to carry out the technical inspection and prepare the handover, which must include all the required documentation, in particular: declarations of conformity, fire and other statements and mandatory tables, proof of reliability of the building (DZO), certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use and maintenance, and all other documents in accordance with the regulations and the contractual provisions.
0.1.19 | V enotnih cenah posameznih postavk, ki se nanašajo na opremo in posamezne sisteme, mora biti zajeto oz. upoštevano tudi naslednje: - dobava oz. transport, - stroški za vse delovne stroje za dvigovanje bremen in delovne košare za dostope do delovišč; - morebitni stroški povzročeni upravljavcem GJI, ki bi nastali v zvezi s predmetno gradnjo; - montaža, vključno s pomožnim montažnim materialom (vezni, tesnilni in pritrdilni material, sidra, nosilni profili, podkonstrukcije in podobno) in navodili proizvajalca, - odprava vseh kolizij sistemov s stenami in med sistemi, - izvedba vseh potrebnih tesnjenj, - priključitev in nastavitve, vključno z morebitnim kalibriranjem, - zagon, testiranje in meritve, vključno s poročili, - šolanje uporabnikov oz. vzdrževalnega osebja za uporabo in vzdrževanje sistemov, - navodila za obratovanje in vzdrževanje, - vsi potrebni certifikati, izjave o skladnosti oz. potrdila ter - vsa druga pomožna dela in material, da se zagotovi funkcionalnost posamezne postavke popisa. | The following must also be included or taken into account in the uniform prices for individual items relating to equipment and individual systems: - delivery/transport, - the cost of all lifting machines and work baskets for access to work sites; - any costs incurred to the operators of utility infrastructure (GJI) in connection with the subject construction; - installation, including ancillary installation materials (bonding, sealing and fixing materials, anchors, support profiles, substructures, etc.) and manufacturer's instructions, - eliminating all system-to-wall and system-to-system collisions, - all necessary sealing work, - connection and set-up, including calibration if necessary, - commissioning, testing and measurements, including reports, - training users or maintenance staff in the use and maintenance of the systems, - operating and maintenance instructions, - any necessary certificates, declarations of conformity or attestations; and - all other ancillary works and materials to ensure the functionality of each inventory item.
0.1.20 | Vsi odri morajo biti upoštevani v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All scaffolding must be included in the uniform prices of the items listed, except where specifically mentioned.
0.1.21 | Vsi delovni in pomožni odri, lestve in ostala potrebna pomožna sredstva, kot tudi čiščenje vseh elementov po končanih delih, mora biti upoštevano v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All working and auxiliary scaffolding, ladders and other necessary ancillaries, as well as the cleaning of all elements after completion of the works, shall be included in the uniform prices of the items listed, except those specifically mentioned.
0.1.22 | Delavniško dokumentacijo za vse nosilne jeklene konstrukcije in podkonstrukcije izdela izvajalec, strošek izdelave delavniške dokumentacije se upošteva v ponujenih cenah in se ne obračuna posebej. | The cost of the shop drawings for all steelwork and substructures shall be included in the prices quoted and shall not be charged separately.
0.1.23 | V enotnih cenah postavk mora biti vključeno tudi vgrajevanje vseh instalacijskih razvodov v opaže armirano betonskih elementov in izdelava prehodov inštalacij ter dodatno izrezovanje utorov in prebojev v kamnite, zidane ali armirano-betonske stene, ponovno demontiranje in montiranje vseh vrst montažnih sten, vsa dodatna dela za zagotavljanje primernih križanj med posameznimi instalacijskimi vodi, izdelava vseh vrst ojačitev konstrukcij in podobna dela, ki zagotavljajo kakovostno vgradnjo vseh vrst instalacijskih vodov in niso posebej navedena v popisu GOI del. V ponudbi morajo biti upoštevana vsa drobna strojna in elektro instalacijska dela in transporti. | The installation of all installation ducts in the formwork of reinforced concrete elements and the construction of installation penetrations, as well as the additional cutting of grooves and penetrations in stone, masonry or reinforced concrete walls, the reassembly and reinstallation of all types of prefabricated walls, all additional work to ensure adequate crossings between individual installation ducts, the construction of all types of structural reinforcement and similar work to ensure the quality installation of all types of installation ducts and not specifically mentioned in the BoQ of the Construction, installation and finishing works (GOI) shall also be included in the uniform prices of the items. The tender shall take into account all minor mechanical and electrical installation work and transport.
0.1.24 | Vsi kovinski elementi in konstrukcije, ki bi lahko bili izpostavljeni atmosferskim in ostalim korozijskim vplivom, morajo biti ustrezno protikorozijsko zaščiteni. | All metallic elements and structures that could be exposed to atmospheric and other corrosive influences must be adequately protected against corrosion.
0.1.25 | Za vse večje jeklene dele se skladno s predpisi, izdelajo ustrezne ozemljitve, nevidno pritrjene in speljane na splošno ozemljitev objekta. | For all major steel parts, appropriate earth connections shall be made in accordance with the regulations, invisibly attached and connected to the general earth of the building.
0.1.26 | Za vse vidne elemente in serijske elemente je obvezna predhodna uskladitev obdelav, barv in materialov s projektantom na podlagi dostavljenih vzorcev v ustrezni velikosti. Obvezna je preveritev dejanskih mer na licu mesta in posledična prilagoditev elementov in njihove montaže. | For all visible elements and serial elements, it is mandatory to coordinate the finishes, colours and materials with the designer beforehand on the basis of the supplied samples in the appropriate size. It is mandatory to check the actual dimensions on site and to adjust the elements and their installation accordingly.
0.1.27 | Dimenzije obrtniških izdelkov in količine je potrebno pred naročanjem preveriti na objektu. Potrebna je uskladitev vseh elementov (kljuke, okovje, detajlne konstrukcije in obdelave, itd.) s projektantom, nadzornikom in investitorjem. Izvajalec je dolžan pred izdelavo predložiti projektantu v potrditev ustrezne delavniške načrte in detajle. | The dimensions of the workmanship and quantities must be checked on site before ordering. All elements (hooks, fittings, detailed construction and finishes, etc.) must be coordinated with the designer, the supervisor and the investor. The contractor is obliged to submit the relevant workshop plans and details to the designer for approval before manufacture.
0.1.28 | V posameznih postavkah popisa so navedeni proizvajalci in/ali tipi posameznih sistemov, materialov ali opreme, s čimer so zgolj natančno opredeljene zahtevane tehnične lastnosti. Izvajalec del lahko ponudi nadomesten sistem, material ali opremo drugega proizvajalca in tipa, pri čemer morajo biti tehnične lastnosti ponujenega sistema, materiala ali opreme enakovredne ali boljše od opredeljenih v popisu, dimenzijsko pa ne smejo presegati projektiranih dimenzij. Vse funkcijske in tehnične karakteristike nadomestnih sistemov, materialov ali opreme mora izvajalec dokazati z ustrezno dokumentacijo. Vse morebitne posledice zaradi spremembe sistemov, materialov ali opreme vključno z morebitnimi spremembami oz. dopolnitvami BIM modelov in projektne dokumentacije, stroškovno in časovno bremenijo izvajalca. | The individual items of the Inventory shall specify the manufacturers and/or types of the individual systems, materials or equipment, thereby merely specifying the required technical characteristics. The Contractor may offer a substitute system, material or equipment of a different manufacturer and type, provided that the technical characteristics of the offered system, material or equipment shall be equivalent to or better than those specified in the BoQ, and shall not exceed the design dimensions. All functional and technical characteristics of the substitute systems, materials or equipment shall be demonstrated by the Contractor with appropriate documentation. Any consequences resulting from changes to systems, materials or equipment, including any changes or additions to the BIM models and project documentation, shall be borne by the Contractor in terms of cost and time.
0.1.29 | Vsako zamenjavo, uporabo in končni izbor nadomestnih sistemov, materialov, proizvodov in opreme morajo obvezno in pravočasno (pred dobavo in vgradnjo) pisno potrditi projektant (vseh sodelujočih strok), nadzornik in investitor. | Any replacement, use and final selection of alternative systems, materials, products and equipment must be approved in writing by the designer (of all disciplines involved), the supervisor and the investor in a timely manner (prior to delivery and installation).
0.1.30 | Izvajalec mora v ponudbeno ceno vključiti tudi: - ves čas gradnje sprotno beleženje sprememb oz. odstopanj od PZI dokumentacije, vključno z izdelavo tekstualnega opisa sprememb, - pripravo podlog na nivoju PZI, ki so potrebne za posodobitev oz. uskladitev BIM modela z izvedenim stanjem (LOD 500) in izdelavo projektne dokumentacije izvedenih del (PID), - mesečno predajanje potrjenih sprememb opreme in materiala, ki vplivajo na BIM model, v formatu IFC, - vzdrževanje in uporabljanje pri izvedbi zadnje veljavne revizije PZI dokumentacije, vključno z dopolnitvami PZI načrtov, ki so nastali zaradi sprememb med gradnjo. | The contractor must also include in the tender price: - keeping a record of changes or deviations from the construction documentation (PZI) throughout construction, including a textual description of the changes, - preparation of the Detailed Design (PZI) level documents required to update or align the BIM model with the as-built condition (LOD 500) and the preparation of the as-built project documentation for the works (PID), - monthly submission of approved equipment and material changes affecting the BIM model in IFC format, - maintenance and use in the execution of the last valid revision of the construction documentation (PZI), including additions to the construction design documentation (PZI) resulting from changes during construction.
| OPOMBE: | REMARKS:
0.1.31 | Tribune vzhodnega trga (na severni strani objekta zaklonišča), ki so oz. bodo služile kot vhod na športno igrišče, obsip objekta na V in J strani objekta, humuziranje in zatravitev, so predmet projekta št. 380-20 (Skupni uvoz in zunanja ureditev območja FS in FFA) in niso upoštevane v tem popisu. | The stands of the eastern square (on the north side of the shelter building), which are or will be used as the entrance to the sports ground, the building envelope on the E and S sides of the building, the humidification and the grassing, are the subject of project No 380-20 (Joint access and external landscaping of the FS and FFA areas) and are not included in this bill of quantities.
0.1.32 | Vsa predvidena oprema mora biti skladna s Pravilnikom o tehničnih normativih za zaklonišča in zaklonilnike (Uradni list RS, št. 17/98, 26/98 – popr., 25/00, 38/01 in 66/06). | All equipment must comply with the Regulation on Technical Standards for Shelters and Defenders (Official Gazette of the Republic of Slovenia, No. 17/98, 26/98 - corrected, 25/00, 38/01 and 66/06).

## 0.2_Uvod-DGNB
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
0.2 | SPLOŠNI TEHNIČNI POGOJI ZA PODROČJE DGNB CERTIFICIRANJA | GENERAL TECHNICAL CONDITIONS FOR DGNB CERTIFICATION
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic entity with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
| Splošni pogoji za področje DGNB certificiranja predstavljajo dopolnilo splošnim tehničnim pogojem in ne odpravljajo drugih obveznosti in odgovornosti, ki jih ima izvajalec v skladu s predpisi in pogodbo. | The General Conditions for DGNB Certification are complementary to the General Technical Conditions and do not exclude other obligations and responsibilities that the Contractor has under the Regulations and the Contract.
0.2.1 | Izvajalec mora v svojih ponudbah upoštevati, da se bo objekt certificiral v skladu z zahtevami DGNB sistema certificiranja trajnostne gradnje, ter pravočasno (vsaj 60 dni pred vgradnjo posameznega produkta) dostaviti vso ustrezno dokumentacijo za vse v ponudbi zajete materiale, elemente in opremo. Zahtevana je uporaba materialov, elementov ali opreme, ki so okolju in ljudem prijazni, energetsko učinkoviti in obenem ustrezajo zahtevam DGNB sistema. Zahtevan nivo certifikata je: ZLATI CERTIFIKAT | The Contractor shall take into account in its tenders that the building will be certified in accordance with the requirements of the DGNB Sustainable Building Certification Scheme and shall deliver all relevant documentation for all materials, elements and equipment included in the tender in a timely manner (at least 60 days before the installation of each product). The use of materials, elements or equipment that are environmentally and human friendly, energy efficient and at the same time meet the requirements of the DGNB system is required. The required level of certification is: GOLD CERTIFICATE
0.2.2 | Podrobnejši opis DGNB sistema in navodila za posamezne kriterije so dostopna v dokumentu"DGNB Criteria Set New Construction Buildings, Version 2020 International", ki je na voljo na DGNB spletni strani https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria | A more detailed description of the DGNB system and guidance on the individual criteria is available in the document "DGNB Criteria Set New Construction Buildings, Version 2020 International", available on the DGNB website https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria
0.2.3 | Izvajalec mora v svojih ponudbah upoštevati, da je potrebno skladno z določili DGNB certifikacijskega sistema, pravočasno (pred pričetkom gradnje) dostaviti vso ustrezno dokumentacijo, za vse v ponudbi zajete materiale, elemente in opremo (tehnični list, varnostni list, izjava o lastnostih, tehnična navodila za ravnanje, servisiranje, vzdrževanje,...) v slovenskem jeziku. Vgradnja kakršnihkoli materialov, elementov ali opreme, se izvede zgolj na podlagi predhodne preveritve posredovane dokumentacije in obenem potrditve s strani nadzornika. | The Contractor must take into account in its tenders that, in accordance with the provisions of the DGNB certification system, all relevant documentation for all materials, elements and equipment included in the tender (technical data sheet, safety data sheet, declaration of properties, technical instructions for handling, servicing, maintenance,...) must be delivered on time (prior to the start of construction) in the Slovene language (in accordance with the provisions of the DGNB certification system). The installation of any materials, elements or equipment shall be subject to prior checking of the submitted documentation and, at the same time, to the approval of the Supervisor.
0.2.4 | Izbrani materiali, elementi, naprave, sistemi in oprema morajo prispevati k večji trajnosti stavbe v smeri zagotavljanja energetske učinkovitosti, ekonomičnega in enostavnega vzdrževanja ter čiščenja, dolge življenjske dobe, uporabe okolju prijaznih materialov ipd. | The materials, elements, appliances, systems and equipment chosen must contribute to the sustainability of the building in terms of energy efficiency, economic and easy maintenance and cleaning, long lifetime, use of environmentally friendly materials, etc.
0.2.5 | Predloženi dokumenti za vse uporabljene materiale, elemente in opremo morajo izpolnjevati zahteve najmanj kakovostne stopnje QS3 (zaželeno QS4), iz dokumenta: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001) | The documents submitted for all materials, components and equipment used shall meet the requirements of at least quality level QS3 (preferably QS4) of the document DGNB Quality Grades for Materials, Components and Equipment (JULFS--7X9001)
0.2.6 | V kolikor izbrani materiali oz. elementi, navedeni v posameznih postavkah, ne ustrezajo vsaj kakovostni stopnji QS3 iz seznama: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), je izvajalec dolžan na to opozoriti projektanta, nadzor in investitorja ter podati predlog ustreznega materiala oz. elementa. | If the selected materials or elements listed in the individual items do not meet at least quality level QS3 of the list of DGNB quality classes for materials, elements and equipment (JULFS--7X9001), the Contractor shall draw this to the attention of the Designer, the Supervisor and the Investor, and shall make a proposal for a suitable material or element.
0.2.7 | Izvajalec lahko v svoji ponudbi predlaga alternativne produkte in rešitve glede na predvidene s projektom, pod pogojem, da le-te prav tako izpolnjujejo vse navedene zahteve. Pri morebitnih predlaganih alternativnih produktih oz. rešitvah je potrebno upoštevati najmanj enake ali boljše lastnosti v smislu življenjske dobe, obstojnosti, ter enostavnosti in stroška čiščenja ter vzdrževanja v primerjavi s projektom predpisanimi rešitvami. Za alternativne rešitve izvajalec pridobi soglasje projektanta, nadzornika in investitorja pred pričetkom gradnje. | The Contractor may propose alternative products and solutions to those envisaged by the project in its tender, provided that they also meet all the requirements set out above. Any alternative products or solutions proposed shall have at least the same or better characteristics in terms of service life, durability, and ease and cost of cleaning and maintenance compared to the solutions envisaged by the project. For alternative solutions, the contractor shall obtain the agreement of the designer, the supervisor and the investor before starting construction.
0.2.8 | Izvajalec med gradnjo dnevno beleži vsa eventualna odstopanja od PZI projektne dokumentacije ter podatke pravočasno posreduje naročniku, nadzoru in projektantu. Potrjene spremembe vnese v podlage za izdelavo PID in posodobitev BIM modelov. | During construction, the Contractor shall record on a daily basis any deviations from the Detailed Design documentation (PZI) and shall provide the information to the Client, Supervision and the Designer in a timely manner. Confirmed changes shall be entered into the basis for the As-built documentation (PID) and BIM model updates.
0.2.9 | Izvajalec med gradnjo sproti izpolnjuje Seznam vseh konstrukcijskih sestav s pripadajočimi vgrajenimi gradbenimi materiali in dokumentira naslednje podatke o vgrajenih materialih (v slovenskem jeziku): - Varnostni list - Tehnični list - Izjavo o lastnostih (če je relevantno) - Izkazovanje morebiti obstoječega okoljskega certifikata (Tip I - okoljski znak ali Tip III - okoljska produktna deklaracija /EPD) - Izjavo proizvajalca ali dobavitelja, da produkt ustreza zahtevam ENV1.2 - Tehnična navodila za ravnanje, servisiranje, vzdrževanje oziroma ostale, z zakonom predpisane dokumente in dokumentacijo. | During construction, the Contractor shall keep a List of all structural assemblies with their associated construction materials and document the following information on the materials installed (in Slovene language): - Safety Data Sheet - Technical Data Sheet - Declaration of performance (if applicable) - Demonstration of any existing environmental certification (Type I - Ecolabel or Type III - Environmental Product Declaration /EPD) - A declaration by the manufacturer or supplier that the product complies with the requirements of ENV1.2 - Technical instructions for handling, servicing, maintenance or other documents and documentation required by law.
0.2.10 | Za vse vgrajene bistvene tehnične sisteme mora izvajalec zagotoviti obstoj pooblaščenega servisa, ki deluje na območju Republike Slovenije, da ima investitor možnost skleniti ustrezno pogodbo o vzdrževanju. Med bistvene tehnične sisteme sodijo npr.: sistemi ogrevanja in hlajenja, priprava tehnoloških medijev, prezračevanje in klimatizacija, sistemi detekcije in gašenja požara, sistemi tehničnega varovanja, BMS in CNS sistemi upravljanja stavbe, razsvetljava, komunikacijski in WI-FI sistemi,... | For all installed essential technical systems, the contractor must ensure the existence of an authorised service centre operating in the territory of the Republic of Slovenia, so that the investor has the possibility of concluding an appropriate maintenance contract. The essential technical systems include, for example: heating and cooling systems, technological media preparation, ventilation and air conditioning, fire detection and extinguishing systems, technical security systems, BMS and CNS building management systems, lighting, communication and WI-FI systems,...
0.2.11 | Zaželeno je, da imajo uporabljeni elementi in materiali okoljsko oznako Tip I. (kot npr. ENCODE, BLUE ANGEL, ipd...). | It is preferable that the elements and materials used have a Type I environmental label (such as ENCODE, BLUE ANGEL, etc...).
0.2.12 | Izvajalec bo za elemente iz lesa moral dokazovati izvor z navedbo izvorne države in tipa lesa, FSC / PEFC certifikat z dodatnim pripadajočim potrdilom Chain of custody-trgovski certifikat dobavitelja - ta se dokazuje z dobavnicami, računi ali enakovredno. Za izdelke iz naravnega kamna iz EU držav je potrebna deklaracija, da je izvor in procesiranje teh izdelkov v celoti v EU državah. Za izdelke iz naravnega kamna, ki prihajajo iz držav izven EU, je potrebno predložiti dokazilo o izpolnjevanju ILO konvencije 182, ki vključuje neodvisna inšpekcijska poročila. | For wood elements, the contractor will be required to provide proof of origin, indicating the country of origin and the type of wood, FSC/PEFC certification with an additional Chain of Custody certificate - the supplier's trade certificate - this shall be evidenced by delivery notes, invoices or equivalent. For natural stone products from EU countries, a declaration that the sourcing and processing of these products is entirely in EU countries is required. For natural stone products from non-EU countries, proof of compliance with ILO Convention 182, including independent inspection reports, is required.
0.2.13 | Izobraževanje udeležencev pri gradnji Izvajalec je dolžan vse udeležence pri gradnji podrobneje seznaniti tudi z relevantnimi koncepti, študijami, elaborati, ki opredelujejo trajnostni način gradnje za naslednja področja: - zaščita pred hrupom (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)) - zaščita pred prašenjem - zaščita tal in podzemne vode (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)), Analiza tveganja za onesnaženje vodnega telesa podzemne vode št. 0346-023/2023, maj 2023 (Geološko projektiranje d.o.o.)) - ravnanje z gradbenimi odpadki (Načrt gospodarjenja z gradbenimi odpadki) Izobraževanja se izvajajo skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.1 1.2, 2.2, 3.2 in 4.2 Training for the parties implementing the construction work | Training of construction participants The contractor is also obliged to inform all construction participants in detail about relevant concepts, studies, elaborations defining sustainable construction methods for the following areas: - noise protection (Environmental Impact Assessment Report No 100123-11523, dated 11.5.2023, supplemented on 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.)) - dust protection - protection of soil and groundwater (Environmental Impact Assessment Report No. 100123-11523, dated 11.5.2023, supplemented 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.), Risk analysis for contamination of the groundwater No. 0346-023/2023, May 2023 (Geološko projektiranje d.o.o.)) - construction waste management (Construction Waste Management Plan) The training shall be carried out in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.1 1.2, 2.2, 3.2 and 4.2 Training for the parties implementing the construction work
0.2.14 | Navodila za obratovanje in vzdrževanje objekta Izvajalec pripravi Navodila za obratovanje in vzdrževanje objekta skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilih: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual | Instructions for the operation and maintenance of the facility The Contractor shall prepare the Operation and Maintenance Instructions for the Facility in accordance with the applicable Slovenian legislation and the DGNB System Instructions specified in the Criteria: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual
0.2.15 | Meritve kontrole kakovosti gradnje Izvajalec mora upoštevati, da se bodo po koncu gradnje izvedle naslednje meritve: - meritve zrakotesnosti - meritve s termokamero (termografija) - meritve akustike - meritve zvočne zaščite ovoja stavbe - meritve zvočne zaščite ločilnih elementov med posameznimi prostori različnih namembnosti - meritve udarnega zvoka - meritve vlažnosti vgrajenih elementov, pred vgradnjo finalnih tlakov - test odvoda dima in toplote Meritve morajo opraviti ustrezno usposobljeni preskusni organi ali strokovnjaki ter rezultate oceniti in primerjati z zahtevami. Obseg opravljenih meritev mora biti sorazmeren z velikostjo zgradbe in mora ustrezno odražati cilj preverjanja kakovosti zgradbe. Smiselno je, da izvajalec del tekom gradnje za sprotno kontrolo kakovosti vgrajenih materialov, elementov in opreme, sam izvaja meritve. Končne meritve (ob primopredaji) izvede tretja oseba kot neodvisna potrditev doseganja zahtev. Meritve se izvajajo skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 2. Quality control measurements | Construction quality control measurements The contractor must take into account that the following measurements will be carried out after completion of the construction: - airtightness measurements - thermal camera measurements (thermography) - acoustics measurements - measurements of the sound insulation of the building envelope - measurements of the sound insulation of the separating elements between different rooms of different uses - impact sound measurements - moisture measurements of the installed elements, prior to the installation of the final flooring - smoke and heat extraction test The measurements shall be carried out by suitably qualified test bodies or experts and the results evaluated and compared with the requirements. The extent of the measurements carried out shall be proportionate to the size of the building and shall adequately reflect the objective of the building quality verification. It is reasonable for the contractor to carry out his own measurements during construction to check the quality of the materials, elements and equipment installed. Final measurements (at handover) are carried out by a third party as an independent confirmation of compliance with the requirements. The measurements shall be carried out in accordance with the applicable Slovenian legislation and the DGNB system instructions specified in the benchmark: PRO 2.2 2. Quality control measurements
0.2.16 | Zagotavljanje kakovosti za uporabljene gradbene proizvode Izvajalec mora zagotavljati izvajanje primerjav med definiranim in dejansko uporabljenim materialom, elementom ali opremo skladno seznamom: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), vključno z dokazno dokumentacijo ugotovitev primerjav ter skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 3.1 Quality assurance for the used construction products | Quality assurance for the construction products used The Contractor shall ensure that comparisons are made between the defined and the actual material, element or equipment used in accordance with the list: DGNB Quality Grades of Installed Materials, Elements and Equipment (JULFS--7X9001), including supporting documentation of the findings of the comparisons, and in accordance with the DGNB system instructions defined in the Criterion: PRO 2.2 3.1 Quality assurance for the used construction products
0.2.17 | Zaščita pred vlago Izvajalec predloži dokumentacijo, ki dokazuje, da je bil izveden program prezračevanja, prilagojen stavbi, s čimer se zagotovi pogoje, da so vgrajeni gradbeni elementi ustrezno suhi, skladno z navodili DGNB opredeljenimi v merilu: PRO 2.2 4.1 Mould prevention | Protection against moisture The Contractor shall provide documentation demonstrating that a building-specific ventilation programme has been implemented to ensure that the building elements installed are adequately dry, in accordance with the DGNB guidelines specified in the criteria: PRO 2.2 4.1 Mould prevention
0.2.18 | Preizkusi delovanja sistemov Izvajalec sodeluje pri izvedbi predhodnega in končnega preizkusa delovanja vseh bistvenih tehničnih komponent stavbe in pripravi ustrezne dokazne dokumentacije ter pri usposabljanju vzdrževalcev/upravljalcev stavbe, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators | System performance tests The Contractor shall be involved in the performance of the preliminary and final performance tests of all essential technical components of the building and the preparation of the relevant supporting documentation, as well as in the training of the maintenance/management staff of the building, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators
0.2.19 | Poročilo o zagonu objekta Izvajalec sodeluje pri pripravi končnega poročila o zagonu objekta, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 5.1 Creation of a detailed final report | Commissioning report The Contractor shall be involved in the preparation of the final commissioning report, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 5.1 Creation of a detailed final report
0.2.20 | Koncept celovitega delovanja sistemov v stavbi Izvajalec sodeluje pri procesu implementiranja stalnega nadzora in nastavitev delovanja stavbe ter usposabljanju vzdrževalcev/upravljalcev stavbe. Navedeno se izvede v skladu z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 6.1 Creation and handover of an integral operating concept | The concept of integrated building systems The contractor is involved in the process of implementing the building's continuous monitoring and settings and training the building's maintenance/management staff. This shall be done in accordance with the DGNB system instructions defined in the benchmark: PRO 2.3 6.1 Creation and handover of an integral operating concept
0.2.21 | Prilagoditev nastavitev sistemov po začetni fazi uporabe objekta Izvajalec sodeluje pri ponovnem pregledu delovanja vseh bistvenih tehničnih sistemov ter eventualni ponovni prilagoditvi teh sistemov s strani strokovnjaka oz. (neodvisne) tretje osebe. Postopek se izvede po približno 10–14 mesecih po zaključku gradnje, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 7.1 Readjustment of the system following initial operating phase | Adjusting system settings after the initial phase of use of the building The Contractor shall be involved in the re-examination of the functioning of all essential technical systems and the possible re-adjustment of these systems by an expert or (independent) third party. The procedure shall be carried out approximately 10-14 months after completion of construction, in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.3 7.1 Readjustment of the system following initial operating phase

## 0.3_Uvod-Zaklonišče
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
0.3 | SPLOŠNI TEHNIČNI POGOJI ZA POPIS ZAKLONIŠČA | GENERAL TECHNICAL CONDITIONS FOR THE SHELTER BILL OF QUANTITIES
| Splošne opombe, veljavne za celotno obdobje gradnje in za vse sodelujoče pri gradnji zaklonišča | General notes applicable to the entire construction period and to all those involved in the construction of the shelter
0.3.0.1 | V prvi fazi del - ob opaženju in betoniranju spodnje plošče in sten zaklonišča - morajo biti dobavljeni in vgrajeni vsi deli in naprave, ki so v popisu točk 1.0 in 2.0. | During the first phase of the works - the formwork and concreting of the bottom slab and the shelter walls - all the parts and appliances listed in items 1.0 and 2.0 shall be supplied and installed.
0.3.0.2 | V drugi fazi del se dobavijo in vgradijo vsi deli in naprave, ki so v popisu točk 3.0 in 4.0. | In the second phase of the works, all the parts and appliances listed under items 3.0 and 4.0 shall be supplied and installed.
0.3.0.3 | Dejavnosti iz točke 5.0 se izvajajo sprotno. | The activities referred to in point 5.0 shall be carried out on an ongoing basis.
| Opombe za pozicije točke 1.0 (prva faza gradnje zaklonišča) | Notes for the items of point 1.0 (first phase of shelter construction)
0.3.1.1 | Vse cevi morajo biti vstavljene med opaže pred betoniranjem. Puščanje odprtin za naknadno vgradnjo cevi ni dovoljeno, ker ne zagotavlja ustrezne protiudarne trdnosti in plinotesnosti zaklonišča. | All pipes must be inserted between the formwork before concreting. Leaving openings for the subsequent installation of pipes is not permitted as it does not ensure adequate impact strength and gas tightness of the shelter.
0.3.1.2 | Vsi jekleni deli morajo biti v celoti vroče cinkani, imeti morajo ustrezne prirobnice (DIN 2501) za nadgradnjo ventilov in cevnih podaljškov ter nastavke za pritrditev med opaže. | All steel parts must be fully hot-dip galvanised, have suitable flanges (DIN 2501) for valve and pipe extension superstructures and fittings for fixing between the formwork.
0.3.1.3 | Beton, ki se ob betoniranju sten in zgornje plošče zateče v cevi, je potrebno, po razopaženju, takoj odstraniti in vse cevi očistiti tudi znotraj. | Concrete that gets stuck in the pipes during the concreting of the walls and the top slab must be removed immediately after formwork removal and all pipes must be cleaned inside.
0.3.1.4 | Sledove posušenega cementnega mleka je potrebno, po razopaženju, takoj obrisati, da ne bi prišlo do najedanja površine jeklenih delov in površinske zaščite. | Traces of dried cement milk should be wiped off immediately after formwork removal to avoid corrosion of the surface of the steel parts and the surface protection.
0.3.1.5 | Cevi za prehode in tesnjenje kablov se vgradijo v vodoravni legi 200 mm pod stropom. | The conduits for cable passage and sealing shall be installed horizontally 200 mm below the ceiling.
0.3.1.6 | Ravne in zalomljene cevi se vgradijo tako, da imajo prirobnice navpično lego. | Straight and curved pipes shall be installed so that the flanges are vertical.
0.3.1.7 | Zalomljene cevi se vgrajujejo v legi daljše središčnice vodoravno, navpično ali pod kotom 45°. | Curved pipes shall be installed in the position of the longer centreline horizontally, vertically or at an angle of 45°.
0.3.1.8 | Cevi, ki so predvidene za dovod in odvod zraka z ventili in loputami, na katerih je potrebno ročno posredovanje, se vgradijo tako, da je ročno posredovanje omogočeno odrasli osebi s tal (v prostoru z napravami, v smeri zapore vhoda in v smeri skladišča odpadkov in odplak). Medsebojna lega teh cevi je takšna, da je posredovanje na ventilih in loputah z ročicami medsebojno nemoteno. Lego in vgradnjo cevi mora prilagoditi dobavitelj sistema za zračenje v zaščitni funkciji glede na tip izbranih ventilov in loput. | Pipes provided for the supply and extract of air with valves and dampers requiring manual intervention shall be installed in such a way that manual intervention is possible for an adult from the floor (in the appliance room, in the direction of the entrance barrier and in the direction of the waste and sewage storage). The relative position of these pipes shall be such that the intervention at valves and dampers with levers is mutually unobstructed. The positioning and installation of the pipes shall be adapted by the supplier of the ventilation system in the protective function according to the type of valves and dampers selected.
| Opombe za pozicije točke 2.0 (prva faza gradnje zaklonišča): | Notes for the items of point 2.0 (first phase of shelter construction):
0.3.2.1 | Vsa zapiralna sredstva morajo biti vstavljena med opaže pred betoniranjem. Puščanje odprtin za naknadno vgradnjo zapiralnih sredstev ni dovoljeno, ker ne zagotavlja ustrezne protiudarne trdnosti in plinotesnosti zaklonišča; za vgradnjo navadnih vrat za sanitarije in umivalnice za funkcijo zaklonišča za drugi namen se prehodne odprtine smejo pustiti, ta vrata je dopustno vgraditi pozneje; navadna vrata, ki so predvidena samo za funkcijo zaklonišča za drugi namen, v tem popisu niso zajeta. | All closing means must be inserted between the formwork before concreting. Leaving openings for the subsequent installation of closing means is not permitted as it does not provide adequate impact strength and gas-tightness of the shelter; for the installation of ordinary doors for toilets and washbasins for the function of the shelter for another purpose, the passage openings may be left and these doors may be installed at a later date; ordinary doors intended only for the function of a shelter for another purpose are not covered by this BoQ.
0.3.2.2 | Izvajalec gradbenih del mora ob dobavi zapiralnih sredstev dobiti vsa potrebna navodila za vgradnjo. | The building contractor must be provided with all necessary installation instructions at the time of delivery of the closures.
0.3.2.3 | Pred dobavo in vgradnjo je potrebno ponovno preveriti ustreznost smeri odpiranja vratnih kril vseh zapiralnih sredstev. | Before delivery and installation, all door closers must be rechecked to ensure that the direction of opening of the door leaf is correct.
0.3.2.4 | Dobavitelj armiranobetonskih zapiralnih sredstev mora dobaviti okvirje in krila z vso potrebno armaturo, krila pa opaži in z betonom zapolni izvajalec gradbenih del po navodilih in ob prisotnosti dobavitelja. | The supplier of the reinforced concrete closures shall supply the frames and leaves with all necessary reinforcement, and the leaves shall be formworked and filled with concrete by the contractor as directed and in the presence of the supplier.
0.3.2.5 | Izvajalec gradbenih del mora v svoji ponudbi zajeti tudi opaženje in betoniranje vratnih kril armiranobetonskih vrat (poz.: 2.0.1 in 2.0.2). | The contractor shall also include in his tender the formwork and concreting of the reinforced concrete door leaves (items.: 2.0.1 and 2.0.2).
0.3.2.6 | Vsa armiranobetonska vrata morajo imeti jeklene dele zaščitene pred korozijo s temeljnim premazom, pred tehničnim preizkusom je te dele potrebno prebarvati s končnim premazom, ki ga določi arhitekt. | All reinforced concrete doors shall have the steel parts protected against corrosion by a primer, and shall be repainted with a finish to be specified by the architect prior to the technical test.
0.3.2.7 | Izbrani premaz po osušitvi ne sme biti škodljiv za zdravje v vročem stanju (pri 363 K). | The selected coating shall not be harmful to health when hot (at 363 K) after drying.
0.3.2.8 | Vsa jeklena vrata morajo biti pocinkana, zato dodatni premaz ni potreben, je pa dopusten. | All steel doors must be galvanised, so an additional coating is not necessary but is acceptable.
0.3.2.9 | Pri barvanju je potrebno zaščititi gumijasta tesnila, laminat za požarno zaščito tesnil, deklaracijske tablice ter nastavke za mazanje tečajev. | When painting, the rubber seals, the laminate for fire protection of the seals, the declaration plates and the hinge grease fittings must be protected.
0.3.2.10 | Vsa med gradnjo poškodovana tesnila in trakove laminata za požarno zaščito tesnil je potrebno zamenjati z originalnimi materiali. Vsa nova tesnila morajo biti v enem kosu. | All gaskets and laminate strips for fire protection of gaskets damaged during construction shall be replaced with original materials. All new gaskets shall be in one piece.
| Opombe za pozicije točke 3.0 (druga faza gradnje zaklonišča): | Notes for the items of point 3.0 (second phase of shelter construction):
0.3.3.1 | Ob posameznih pozicijah mora biti že zajeta potrebna količina tesnilnega, mazalnega pritrdilnega in povezovalnega materiala, skladnega s tipi posameznih delov in naprav. | The necessary quantities of sealing, lubricating, fastening and joining materials, corresponding to the types of individual parts and appliances, shall already be included in each item.
0.3.3.2 | Jekleni deli morajo biti vroče cinkani (razen litoželeznih) ali na kvalitetno primerljiv način zaščiteni pred korozijo. | Steel parts shall be hot-dip galvanised (except cast iron) or protected against corrosion in a comparable quality manner.
| Opombe za pozicije točke 4.0 (druga faza gradnje zaklonišča): | Notes for the items of point 4.0 (second phase of shelter construction):
0.3.4.1 | V posameznih pozicijah mora biti zajet ves potreben pritrdilni in povezovalni material, skladen s tipi naprav in opreme. | All necessary fixing and connecting material, compatible with the types of installations and equipment, shall be included in the individual items.
0.3.4.2 | Po prilogi A je potrebno zaklonišča opremiti še z nosilnimi okvirji za suha stranišča, kar pa velja le v primeru, ko so v zaklonišču vgrajena mokra stranišča z odtoki, ki jih je na ta način potrebno preurediti v suha stranišča. V tem zaklonišču mokra stranišča niso vgrajena, zato v popisu teh nosilnih okvirjev ni. | Annex A requires that the shelters also be fitted with support frames for dry toilets, but this is only the case if the shelter has wet toilets with drains that need to be converted to dry toilets. In this shelter, the wet toilets are not fitted, so these support frames are not included in the BoQ.
0.3.4.3 | Po prilogi A je potrebno vsako zaklonišče, ki ima ambulanto, opremiti tudi s papirjem za medicinske potrebe (5 zavitkov za zaklonišče do 100 zaklonilnih mest oziroma 10 zavitkov za zaklonišče nad 100 do 300 zaklonilnih mest). V zaklonišču v tem objektu ni ambulante, zato dobava papirja za medicinske potrebe ni potrebna in ga popis ne zajema. | According to Annex A, each shelter with a medical room must also be supplied with medical paper (5 rolls for shelters up to 100 shelter places or 10 rolls for shelters above 100 shelter places up to 300 shelter places). There is no medical room in the shelter in this facility, therefore the supply of medical paper is not required and is not covered by the BoQ.
0.3.4.4 | Sedežno-ležalne in ležalne konstrukcije morajo biti dobavljene in vgrajene demontažno v količini za 2/3 zaklonilnih mest kot sedeži in za 1/3 zaklonilnih mest kot ležišča, z vmesnimi vzdolžnimi in prečnimi hodniki, skladno z zahtevami predpisa; če bodo vgrajene postelje in sedišča s platni, morajo biti iz snovi, ki ne plesni (samougasljiva umetna vlakna); dobavitelj mora ta del popisa prilagoditi svojim kataloškim podatkom in v celoti zahtevam predpisa. | The seat-bed and bed structures shall be supplied and installed dismantled in a quantity of 2/3 of the shelter places as seats and 1/3 of the shelter places as beds, with longitudinal and transverse aisles in between, in accordance with the requirements of the Regulation; if beds and seats with canvas are to be installed, they shall be made of non-mould-resistant material (self-extinguishing plastic fibres); the supplier shall adapt this part of the BoQ to his catalogue data and to the full requirements of the Regulation.
| Opombe za pozicije točke 5.0 (obe fazi gradnje zaklonišča): | Notes for the items of point 5.0 (both phases of shelter construction):
0.3.5.1 | Nepredvidena dela se opravijo po predhodnem naročilu, načrtu in dogovoru o vrednosti teh del, s potrditvijo nadzorne organizacije. | Unforeseen works shall be carried out after prior order, design and agreement on the value of the works, with the approval of the Supervisory Organisation.
0.3.5.2 | V poziciji 5.0.4 mora biti zajeta tudi demontaža in urejeno vskladiščenje bivalne, sanitarne in pomožne (zakloniščne) opreme zaradi sprostitve prostorov za funkcijo za drugi (mirnodobni) namen zaklonišča - po pozitivnem tehničnem preizkusu zaklonišča! | Item 5.0.4 must also include the dismantling and orderly storage of the living, sanitary and auxiliary (shelter) equipment in order to free the premises for the other (peacetime) function of the shelter - after a positive technical test of the shelter!

## 4.1.0_Rekapitulacija
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
| REKAPITULACIJA STROŠKOV STROJNIH DEL | COST SUMMARY OF MECHANICAL WORKS
| 4 NAČRT S PODROČJA STROJNIŠTVA | 4 DOCUMENTATION IN THE FIELD OF MECHANICAL ENGINEERING
| 4/1 Zaklonišče | 4/1 Shelter
4.1 | STROJNA DELA | MECHANICAL WORKS
4.1.1 | STROJNA DELA - VEČJE ZAKLONIŠČE S 300 ZAKLONILNIMI MESTI | MECHANICAL WORKS - LARGE SHELTER WITH 300 SHELTER SPACES | 0
0% | NEPREDVIDENA DELA | UNFORSEEN WORKS | 0
4.1.2 | STROJNA DELA - MANJŠE ZAKLONIŠČE Z 200 ZAKLONILNIMI MESTI | MECHANICAL WORKS - SMALLER SHELTER WITH 200 SHELTER SPACES | 0
0% | NEPREDVIDENA DELA | UNFORSEEN WORKS | 0
| SKUPAJ STROJNA DELA | TOTAL MECHANICAL WORKS | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT

## 4.1.1.0_Rekapitulacija 300
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
| REKAPITULACIJA STROŠKOV STROJNIH DEL | COST SUMMARY OF MECHANICAL WORKS
| 4 NAČRT S PODROČJA STROJNIŠTVA | 4 DOCUMENTATION IN THE FIELD OF MECHANICAL ENGINEERING
| 4/1 Zaklonišče | 4/1 Shelter
4.1.1 | STROJNA DELA - VEČJE ZAKLONIŠČE S 300 ZAKLONILNIMI MESTI | MECHANICAL WORKS - LARGE SHELTER WITH 300 SHELTER SPACES
4.1.1.1 | VGRADNI DELI | BUILDING WORKS | 0
4.1.1.2 | ZAPIRALNA SREDSTVA IN PRIBOR | CLOSURES AND ACCESSORIES | 0
4.1.1.3 | SISTEM ZA ZRAČENJE ZAKLONIŠČA V ZAŠČITNI FUNKCIJI IN UVODNICE ZA TESNJENJE KABLOV | SHELTER VENTILATION SYSTEM IN PROTECTIVE FUNCTION AND CABLE SEALING GLANDS | 0
4.1.1.4 | BIVALNA, SANITARNA IN POMOŽNA OPREMA | LIVING, SANITARY AND ANCILLARY EQUIPMENT | 0
4.1.1.5 | VGRADNJA NAPRAV, NAPELJAV IN OPREME TER OSTALE DEJAVNOSTI | INSTALLATION OF PLANT, FIXTURES AND FITTINGS AND OTHER ACTIVITIES | 0
0
0 | NEPREDVIDENA DELA | UNFORSEEN WORKS | 0
| SKUPAJ STROJNA DELA - VEČJE ZAKLONIŠČE S 300 ZAK. MESTI | TOTAL MECHANICAL WORKS - LARGE SHELTER WITH 300 SHELTER SPACES | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT

## 4.1.1.1_300_1.0
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
4.1.1 | STROJNA DELA - VEČJE ZAKLONIŠČE S 300 ZAKLONILNIMI MESTI | MECHANICAL WORKS - LARGE SHELTER WITH 300 SHELTER SPACES
4.1.1.1 | VGRADNI DELI | BUILDING WORKS |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
1.0 | VGRADNI DELI | BUILDING WORKS
1.0.1 | Ravna jeklena cev z nastavkom za vgradnjo protiudarnega ventila (vel. 4) - DN 200/750 z dvema prirobnicama kot npr.: KROBATH tip MF Gr. 4 DN 200/750 2F | Straight steel pipe with spigot for installation of backflow preventer (size 4) - DN 200/750 with two flanges as e.g. KROBATH type MF Gr. 4 DN 200/750 2F | kos | 3 |  | 0
1.0.2 | Ravna jeklena cev za dovod zraka na prezračevalno napravo pri zaščitnem zračenju DN 150/400 z eno prirobnico IZDELANO PO DETAJLU DOBAVITELJA | Flat steel pipe for air supply to the ventilation unit for protective ventilation DN 150/400 with one flange MADE TO SUPPLIER'S DETAIL | kos | 3 |  | 0
1.0.3 | Zalomljena jeklena cev za dovod zraka na prezračevalno napravo pri normalnem zračenju DN 200/400 z eno prirobnico, Z-zalom IZDELANO PO DETAJLU DOBAVITELJA | Broken steel pipe for air supply to the ventilation unit during normal ventilation DN 200/400 with one flange, Z-end MADE TO SUPPLIER'S DETAIL | kos | 2 |  | 0
1.0.4 | Zalomljena jeklena cev za dovod zraka na prezračevalno napravo pri normalnem zračenju DN 200/400 z eno prirobnico, U-zalom IZDELANO PO DETAJLU DOBAVITELJA | Broken steel pipe for air supply to the ventilation unit during normal ventilation DN 200/400 with one flange, U-joint MADE TO SUPPLIER'S DETAIL | kos | 1 |  | 0
1.0.5 | Zalomljena jeklena cev za ventil za regulacijo nadtlaka DN 150/750 z eno prirobnico (za odvod zraka iz bivalnega prostora v smeri zapore vhoda) IZDELANO PO DETAJLU DOBAVITELJA | Broken steel pipe for overpressure control valve DN 150/750 with one flange (for air extraction from the living space in the direction of the entrance barrier) MADE TO SUPPLIER'S DETAIL | kos | 4 |  | 0
1.0.6 | Ravna jeklena cev za ventil za regulacijo nadtlaka DN 150/300 z eno prirobnico (za odvod zraka iz sanitarij v smeri skladišča odpadkov in odplak) IZDELANO PO DETAJLU DOBAVITELJA | Flat steel pipe for overpressure control valve DN 150/300 with one flange (for air discharge from the toilet towards the waste and sewage storage) MADE TO SUPPLIER'S DETAIL | kos | 3 |  | 0
1.0.7 | Zalomljena jeklena cev za odvod zraka pri zaščitnem in normalnem zračenju DN 150/750 z dvema prirobnicama, Z-zalom (odvod zraka iz zapore vhoda) IZDELANO PO DETAJLU DOBAVITELJA | Fused steel pipe for air exhaust for protective and normal ventilation DN 150/750 with two flanges, Z-end (air exhaust from the entrance barrier) MADE TO SUPPLIER'S DETAIL | kos | 4 |  | 0
1.0.8 | Zalomljena jeklena cev za odvod zraka pri zaščitnem in normalnem zračenju DN 150/750 z dvema prirobnicama, Z-zalom (odvod zraka iz skladišča odpadkov in odplak) IZDELANO PO DETAJLU DOBAVITELJA | Fused steel pipe for protective and normal ventilation air discharge DN 150/750 with two flanges, Z-end (air discharge from waste and sewage storage) MADE TO SUPPLIER'S DETAIL | kos | 3 |  | 0
1.0.9 | Ravna jeklena cev za odvod kondenzne vode z navojnim nastavkom za zasun DN 25/600 IZDELANO PO DETAJLU DOBAVITELJA | Flat steel condensate drain pipe with threaded plug DN 25/600 MADE TO SUPPLIER'S DETAIL | kos | 1 |  | 0
1.0.10 | Ravna jeklena cev za tesnjenje kablov DN 100/300 z nastavki za pritrditev med opaže IZDELANO PO DETAJLU DOBAVITELJA | Flat steel cable sealing hose DN 100/300 with fittings for fixing between the formwork MADE TO SUPPLIER'S DETAIL | kos | 2 |  | 0
1.0.11 | Ravna jeklena cev za tesnjenje kablov DN 100/400 z nastavki za pritrditev med opaže IZDELANO PO DETAJLU DOBAVITELJA | Flat steel cable sealing hose DN 100/400 with fittings for fixing between the formwork MADE TO SUPPLIER'S DETAIL | kos | 4 |  | 0
1.0.12 | Ravna jeklena cev za tesnjenje kablov DN 100/750 z nastavki za pritrditev med opaže IZDELANO PO DETAJLU DOBAVITELJA | Flat steel cable sealing hose DN 100/750 with fittings for fixing between the formwork MADE TO SUPPLIER'S DETAIL | kos | 4 |  | 0
1.0.13 | Ravna jeklena cev za pretok zraka in kondenzne vode med komorami peščenega predfiltra DN 150/400 z nastavki za pritrditev med opaže IZDELANO PO DETAJLU DOBAVITELJA | Flat steel pipe for air and condensate water flow between the sand pre-filter chambers DN 150/400 with fittings for fixing between the formwork MADE TO SUPPLIER'S DETAIL | kos | 9 |  | 0
1.0.14 | Ravna jeklena cev za prehod vodovodne napeljave skozi steno DN 25/750 – obojestransko z navojno tuljavo za zaščitno funkcijo zaklonišča IZDELANO PO DETAJLU DOBAVITELJA | Flat steel pipe for the passage of the water supply through the wall DN 25/750 - both sides with threaded sleeve for the shelter protection function MADE TO SUPPLIER'S DETAIL | kos | 1 |  | 0
1.0.15 | Ravna jeklena cev za prehod vodovodne napeljave skozi steno DN 20/300 – obojestransko z navojno tuljavo za zaščitno funkcijo zaklonišča IZDELANO PO DETAJLU DOBAVITELJA | Flat steel pipe for the passage of the water supply through the wall DN 20/300 - both sides with threaded sleeve for the shelter protection function MADE TO SUPPLIER'S DETAIL | kos | 2 |  | 0
| VGRADNI DELI | BUILDING WORKS |  |  |  | 0

## 4.1.1.2_300_2.0
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
4.1.1 | STROJNA DELA - VEČJE ZAKLONIŠČE S 300 ZAKLONILNIMI MESTI | MECHANICAL WORKS - LARGE SHELTER WITH 300 SHELTER SPACES
4.1.1.2 | ZAPIRALNA SREDSTVA IN PRIBOR | CLOSURES AND ACCESSORIES |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
2.0 | ZAPIRALNA SREDSTVA IN PRIBOR | CLOSURES AND ACCESSORIES
2.0.1 | Armiranobetonska protiudarna vrata, plinotesna in požarna (EI-90), s priborom za odmik ruševin, za nadtlak 300 kPa, z vgrajenim gumijastim tesnilom, z zapiralnim in blokadnim mehanizmom, z obojestransko označenimi smermi odpiranja in zapiranja, v zapori vhoda, z dimenzijami 1200/2050/200 mm – leva kot npr.: KROBATH tip DT-B 1200 L | Reinforced concrete anti-ram door, gas-tight and fire-resistant (EI-90), with debris deflection fittings, for an overpressure of 300 kPa, with integrated rubber seal, with closing and locking mechanism, with opening and closing directions marked on both sides, in the entrance barrier, with dimensions 1200/2050/200 mm - left such as KROBATH type DT-B 1200 L | kpl | 2 |  | 0
2.0.2 | Armiranobetonska protiudarna vrata, plinotesna in požarna (EI-90), s priborom za odmik ruševin, za nadtlak 300 kPa, z vgrajenim gumijastim tesnilom, z zapiralnim in blokadnim mehanizmom, z obojestransko označenimi smermi odpiranja in zapiranja, v zapori zasilnega izhoda, z dimenzijami 825/2050/200 mm – leva kot npr.: KROBATH tip DT-B 825 L | Reinforced concrete anti-accident door, gas-tight and fire-resistant (EI-90), with debris deflection fittings, for an overpressure of 300 kPa, with built-in rubber seal, with closing and locking mechanism, with opening and closing directions marked on both sides, in emergency exit barrier, dimensions 825/2050/200 mm - left such as KROBATH type DT-B 825 L | kpl | 1 |  | 0
2.0.3 | Jeklena, plinotesna in požarna vrata (EI-90), za nadtlak 10 kPa, z vgrajenim gumijastim tesnilom, z zapiralnim mehanizmom, z obojestransko označenimi smermi odpiranja in zapiranja, v zapori vhoda, z dimenzijami 1200/2050/100 mm – desna kot npr.: KROBATH tip GT 1200 R | Steel, gas-tight and fire-resistant door (EI-90), for overpressure of 10 kPa, with integrated rubber seal, with closing mechanism, with opening and closing directions marked on both sides, in the entrance barrier, with dimensions 1200/2050/100 mm - right such as KROBATH type GT 1200 R | kpl | 2 |  | 0
2.0.4 | Jeklena, plinotesna in požarna vrata (EI-90), za nadtlak 10 kPa, z vgrajenim gumijastim tesnilom, z zapiralnim mehanizmom, z obojestransko označenimi smermi odpiranja in zapiranja, v skladišču odpadkov in odplak, z dimenzijami 825/2050/100 mm – leva kot npr.: KROBATH tip GT 825 L | Steel, gas-tight and fire-resistant door (EI-90), for overpressure of 10 kPa, with integrated rubber seal, with closing mechanism, with opening and closing directions marked on both sides, in waste and sewage storage, dimensions 825/2050/100 mm - left such as KROBATH type GT 825 L | kpl | 1 |  | 0
2.0.5 | Jeklena, plinotesna in požarna vrata (EI-90), za nadtlak 10 kPa, z vgrajenim gumijastim tesnilom, z zapiralnim mehanizmom, z obojestransko označenimi smermi odpiranja in zapiranja, v zapori zasilnega izhoda, z dimenzijami 825/2050/100 mm – leva kot npr.: KROBATH tip GT 825 L | Steel, gas-tight and fire-resistant door (EI-90), for overpressure 10 kPa, with integrated rubber seal, with closing mechanism, with opening and closing directions marked on both sides, in emergency exit barrier, dimensions 825/2050/100 mm - left such as KROBATH type GT 825 L | kpl | 1 |  | 0
2.0.6 | Jeklena, plinotesna in požarna vratca (EI-90), za nadtlak 10 kPa, z vgrajenim gumijastim tesnilom, z zapiralnim mehanizmom, z obojestransko označenimi smermi odpiranja in zapiranja, v peščeni predfilter, z dimenzijami 600/800/100 mm – desna kot npr.: KROBATH tip GKL 90 R | Steel, gas-tight and fire-resistant door (EI-90), for 10 kPa overpressure, with integrated rubber seal, with closing mechanism, with opening and closing directions marked on both sides, in sand pre-filter, dimensions 600/800/100 mm - right such as KROBATH type GKL 90 R | kpl | 1 |  | 0
2.0.7 | Jeklena navadna notranja vrata, odporna na tresljaje konstrukcije, z vgrajeno rešetko za izenačevanje zračnega tlaka med notranjimi prostori, z dimenzijami 825/2050 mm – desna – za vstop v prostor z napravami kot npr.: KROBATH tip IT 825 R | Structural vibration-resistant plain steel interior door with integrated grille for air pressure equalisation between interior spaces, dimensions 825/2050 mm - right-hand - for access to the equipment room such as KROBATH type IT 825 R | kpl | 1 |  | 0
2.0.8 | Jeklena navadna notranja vrata, odporna na tresljaje konstrukcije, z vgrajeno rešetko za izenačevanje zračnega tlaka med notranjimi prostori, s samozapiralnim mehanizmom, z dimenzijami 825/2050 mm – leva – za vstop v sanitarije kot npr.: KROBATH tip IT 825 L | Steel ordinary internal door, resistant to structural vibrations, with integrated grille to equalise the air pressure between the internal compartments, with self-closing mechanism, dimensions 825/2050 mm - left-hand - for entrance to sanitary facilities such as KROBATH type IT 825 L | kpl | 1 |  | 0
2.0.9 | Jeklena navadna notranja vrata, odporna na tresljaje konstrukcije, z vgrajeno rešetko za izenačevanje zračnega tlaka med notranjimi prostori, z dimenzijami 825/2050 mm – leva – za vstop v shrambo vode in opreme kot npr.: KROBATH tip IT 825 L | Steel ordinary internal door, resistant to structural vibration, with integrated grille to equalise air pressure between internal spaces, dimensions 825/2050 mm - left - for access to water and equipment storage such as KROBATH type IT 825 L | kpl | 1 |  | 0
2.0.10 | Jeklena lestev za dostop do prostora peščenega predfiltra, s priborom za montažno pritrditev DOBAVLJIVO V SLO | Steel ladder for access to the sand pre-filter compartment, with mounting accessories AVAILABLE IN SLO | kpl | 2 |  | 0
| ZAPIRALNA SREDSTVA IN PRIBOR | CLOSURES AND ACCESSORIES |  |  |  | 0

## 4.1.1.3_300_3.0
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
4.1.1 | STROJNA DELA - VEČJE ZAKLONIŠČE S 300 ZAKLONILNIMI MESTI | MECHANICAL WORKS - LARGE SHELTER WITH 300 SHELTER SPACES
4.1.1.3 | SISTEM ZA ZRAČENJE ZAKLONIŠČA V ZAŠČITNI FUNKCIJI IN UVODNICE ZA TESNJENJE KABLOV | SHELTER VENTILATION SYSTEM IN PROTECTIVE FUNCTION AND CABLE SEALING GLANDS |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
3.0 | SISTEM ZA ZRAČENJE ZAKLONIŠČA V ZAŠČITNI FUNKCIJI IN UVODNICE ZA TESNJENJE KABLOV | SHELTER VENTILATION SYSTEM IN PROTECTIVE FUNCTION AND CABLE SEALING GLANDS
3.0.1 | Protiudarni ventil (vel. 4) za dovod zraka s prigrajenim filtrom za grobi prah DN 200 kot npr.: KROBATH tip ESV GR. 4 | Air inlet check valve (size 4) with coarse dust filter DN 200 such as KROBATH type ESV GR. 4 | kpl | 3 |  | 0
3.0.2 | Nadtlačni protiudarni ventil za odvod zraka skozi zaporo vhoda in skozi skladišče odpadkov DN 150 kot npr.: KROBATH tip ÜV-ESV 75 | Overpressure backdraft valve for air outlet through the entrance barrier and through the waste storage DN 150 such as KROBATH type ÜV-ESV 75 | kpl | 7 |  | 0
3.0.3 | Regulacijski ventil za odvod zraka DN 150 kot npr.: KROBATH tip ALV 150 | Control valve for air outlet DN 150 such as KROBATH type ALV 150 | kpl | 7 |  | 0
3.0.4 | Vroče cinkana rešetka za peščeni predfilter kot npr.: KROBAT SFR VERZ. | Hot-dip galvanised grating for sand pre-filter such as KROBAT SFR VERZ. | m2 | 6.7 |  | 0
3.0.5 | Certificirani ostrorobi peščeni granulat, eruptivnega porekla, odprašen, zrna granulacije 4-8 mm, embaliran v vrečah s težo največ 30 kg v SLO pri dobavitelju peska asfaltnim bazam | Certified coarse sandy granulate, eruptive origin, dust-free, grain size 4-8 mm, packed in bags weighing not more than 30 kg in SLO, supplier of sand to asphalt bases | m3 | 9.4 |  | 0
3.0.6 | Vmesna zalomljena cev DN 150 za dovod zraka na prezračevalno napravo pri zaščitnem zračenju, z dvema prirobnicama, L-zalom DOBAVLJIVO V SLO | Intermediate broken pipe DN 150 for air supply to the ventilation unit in protective ventilation, with two flanges, L-bend AVAILABLE IN SLO | kpl | 3 |  | 0
3.0.7 | Vmesna zalomljena cev DN 200 za dovod zraka na prezračevalno napravo pri normalnem zračenju, z dvema prirobnicama, L-zalom DOBAVLJIVO V SLO | Intermediate broken pipe DN 200 for air supply to the ventilation unit under normal ventilation, with two flanges, L-shaped AVAILABLE IN SLO | kpl | 3 |  | 0
3.0.8 | Krogelni ventil za zapiranje odvoda kondenzne vode DN 25 iz prostora peščenega predfiltra DOBAVLJIVO V SLO | Ball valve for closing the condensate drain DN 25 from the sand pre-filter compartment AVAILABLE IN SLO | kos | 1 |  | 0
3.0.9 | Plinotesna loputa z ročico DN 200-RS DOBAVLJIVO V SLO | Gas-tight butterfly valve with handle DN 200-RS AVAILABLE IN SLO | kpl | 3 |  | 0
3.0.10 | Plinotesna loputa z ročico DN 150-RS DOBAVLJIVO V SLO | Gas-tight butterfly valve with handle DN 150-RS AVAILABLE IN SLO | kpl | 10 |  | 0
3.0.11 | Prezračevalna naprava z ročnim in električnim pogonom (400 V, 50 Hz, 400 W, IP 54), pogonsko ročico, stikalom, prikazovalnikom pretoka zraka (načina zračenja), z navodilom za uporabo v različnih načinih zračenja, za nazivni pretok najmanj 600 m3/h kot npr.: KROBATH tip VA-300 | Ventilation appliance with manual and electric drive (400 V, 50 Hz, 400 W, IP 54), drive lever, switch, air flow display (ventilation mode), with instructions for use in different ventilation modes, for a nominal flow of at least 600 m3/h such as KROBATH type VA-300 | kpl | 3 |  | 0
3.0.12 | Filter za RBK-zaščito s priključnima prirobnicama, s podnožjem za vgradnjo in pritrditev, za nazivni pretok 200 m3/h in padec tlaka največ 600 Pa; filter mora imeti veljavni certifikat in nalepko KI Ljubljana kot npr.: COLF tip ECS-250 | RBK-protection filter with two connection flanges, with mounting and fixing base, for a nominal flow of 200 m3/h and a pressure drop of maximum 600 Pa; the filter must have a valid certificate and a label from KI Ljubljana such as COLF type ECS-250 | kpl | 3 |  | 0
3.0.13 | Razstavljiva spojka s prirobnicama in gibljivimi cevmi za hitro priključitev filtra za RBK-zaščito, vse skladno s tipom dobavljenega filtra kot npr.: KROBATH tip SKU | Expandable coupling with flanges and flexible hoses for quick connection of the RBC protection filter, all according to the type of filter supplied such as KROBATH type SKU | kpl | 3 |  | 0
3.0.14 | Tekočinski merilnik nadtlaka (U-cevka) z merilnim območjem najmanj 1500 Pa kot npr.: KROBATH tip SRM-7031 | Liquid pressure gauge (U-tube) with a measuring range of at least 1500 Pa such as KROBATH type SRM-7031 | kpl | 1 |  | 0
3.0.15 | Pribor za neprekinjeno cevno povezavo merilnika nadtlaka v hodnik zasilnega izhoda, z ventilom DOBAVLJIVO V SLO | Accessories for continuous hose connection of an overpressure gauge to the emergency exit corridor, with valve AVAILABLE IN SLO | kpl | 1 |  | 0
3.0.16 | Merilnik temperature zraka (od 0 do + 40 °C) in relativne vlažnosti zraka (od 20 do 100 %) DOBAVLJIVO V SLO | Air temperature gauge (0 to + 40 °C) and relative humidity (from 20 to 100%) AVAILABLE IN SLO | kpl | 1 |  | 0
3.0.17 | Jeklena spiro cev za razvod zraka s potrebnimi fazonskimi kosi DN 200 DOBAVLJIVO V SLO - PICHLER | Steel spiro pipe for air distribution with necessary phasing pieces DN 200 AVAILABLE IN SLO - PICHLER | m | 95 |  | 0
3.0.18 | Jeklena spiro cev za razvod zraka s potrebnimi fazonskimi kosi DN 160 DOBAVLJIVO V SLO - PICHLER | Steel spiro pipe for air distribution with necessary phasing pieces DN 160 AVAILABLE IN SLO - PICHLER | m | 30 |  | 0
3.0.19 | Jeklena spiro cev za razvod zraka s potrebnimi fazonskimi kosi DN 100 DOBAVLJIVO V SLO - PICHLER | Steel spiro pipe for air distribution with necessary phasing pieces DN 100 AVAILABLE IN SLO - PICHLER | m | 20 |  | 0
3.0.20 | Prezračevalni ventil za dovod zraka DN 160 DOBAVLJIVO V SLO - PICHLER | Ventilation valve for air inlet DN 160 AVAILABLE IN SLO - PICHLER | kpl | 22 |  | 0
3.0.21 | Prezračevalni ventil za dovod zraka DN 100 DOBAVLJIVO V SLO - PICHLER | Ventilation valve for air inlet DN 100 AVAILABLE IN SLO - PICHLER | kpl | 20 |  | 0
3.0.22 | Pribor za vertikalno elastično obešanje spiro cevi DN 200 za razvod zraka SESTAVLJENO PO DETAJLU | Accessories for vertical elastic suspension of spiro tubes DN 200 for air distribution ASSEMBLED IN DETAIL | kpl | 62 |  | 0
3.0.23 | Pribor za vertikalno elastično obešanje spiro cevi DN 160 za razvod zraka SESTAVLJENO PO DETAJLU | Accessories for vertical elastic suspension of spiro tubes DN 160 for air distribution ASSEMBLED IN DETAIL | kpl | 20 |  | 0
3.0.24 | Pribor za vertikalno elastično obešanje spiro cevi DN 100 za razvod zraka SESTAVLJENO PO DETAJLU | Accessories for vertical elastic suspension of spiro tubes DN 100 for air distribution ASSEMBLED IN DETAIL | kpl | 14 |  | 0
3.0.25 | Regulacijska loputa DN 200 DOBAVLJIVO V SLO - PICHLER | Regulating flap DN 200 AVAILABLE IN SLO - PICHLER | kpl | 9 |  | 0
3.0.26 | Regulacijska loputa DN 100 DOBAVLJIVO V SLO - PICHLER | Regulating flap DN 100 AVAILABLE IN SLO - PICHLER | kpl | 4 |  | 0
3.0.27 | Tesnilna uvodnica s polnilnimi kosi za tesnjenje kablov DN 100 kot npr.: KROBATH tip RGP-100 | Sealing gland with filler pieces for sealing cables DN 100 such as KROBATH type RGP-100 | kpl | 20 |  | 0
3.0.28 | Zaščitna plošča z mrežico za zunanjo stran cevi za odvod zraka DN 150 SESTAVLJENO PO DETAJLU DOBAVITELJA | Protective plate with mesh for the outside of the air outlet pipe DN 150 ASSEMBLED TO SUPPLIER'S DETAIL | kpl | 7 |  | 0
3.0.29 | Zaščitna plošča z mrežico za zunanjo stran cevi za dovod zraka DN 200 SESTAVLJENO PO DETAJLU DOBAVITELJA | Protective plate with mesh for the outside of the air inlet pipe DN 200 ASSEMBLED TO SUPPLIER'S DETAIL | kpl | 3 |  | 0
3.0.30 | Vmesna spiro cevna povezava z dušilno loputo za priključitev prezračevalne naprave na dovodna priključka normalnega in zaščitnega zračenja DN 200/150 DOBAVLJIVO V SLO - PICHLER | Intermediate spiro hose connection with throttle valve for the connection of the ventilation appliance to the normal and protective ventilation inlet connections DN 200/150 AVAILABLE IN SLO - PICHLER | kpl | 3 |  | 0
3.0.31 | Ravna vmesna cev za nadgradnjo plinotesne lopute nad ventilom za regulacijo nadtlaka DN 150 z dvema prirobnicama PO DETAJLU DOBAVITELJA | Straight intermediate pipe for the gas-tight hatch upgrade above the pressure relief valve DN 150 with two flanges AS DETAILED BY THE SUPPLIER | kos | 7 |  | 0
3.0.32 | Detektor ogljikovega monoksida (s kabelsko povezavo krmilno-signalnega dela in senzorja), z napajalnima električnima priključkoma 230 in 24 V, s svetlobnim in zvočnim alarmom, kalibriran na alarmni prag 50 ppm CO, z navodilom za uporabo kot npr.: FISCHER tip LIFE GM 040-6 + FRFCO | Carbon monoxide detector (with cable connection of the control-signalling part and the sensor), with 230 and 24 V power supply, with light and sound alarm, calibrated to an alarm threshold of 50 ppm CO, with instruction manual such as FISCHER type LIFE GM 040-6 + FRFCO | kpl | 1 |  | 0
3.0.33 | Jekleni čep DN 25 za obojestransko plinotesno zatesnitev cevi vodovodne napeljave do uporabe vodovodnega priključka DOBAVLJIVO V SLO | Steel plug DN 25 for double-sided gas-tight sealing of the water supply pipe until the water connection is used AVAILABLE IN SLO | kos | 2 |  | 0
3.0.34 | Jekleni čep DN 20 za obojestransko plinotesno zatesnitev cevi vodovodne napeljave do uporabe vodovodnega priključka DOBAVLJIVO V SLO | Steel plug DN 20 for double-sided gas-tight sealing of the water supply pipe until the water connection is used AVAILABLE IN SLO | kos | 4 |  | 0
| SISTEM ZA ZRAČENJE ZAKLONIŠČA V ZAŠČITNI FUNKCIJI IN UVODNICE ZA TESNJENJE KABLOV | SHELTER VENTILATION SYSTEM IN PROTECTIVE FUNCTION AND CABLE SEALING GLANDS |  |  |  | 0

## 4.1.1.4_300_4.0
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
4.1.1 | STROJNA DELA - VEČJE ZAKLONIŠČE S 300 ZAKLONILNIMI MESTI | MECHANICAL WORKS - LARGE SHELTER WITH 300 SHELTER SPACES
4.1.1.4 | BIVALNA, SANITARNA IN POMOŽNA OPREMA | LIVING, SANITARY AND ANCILLARY EQUIPMENT |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
4.0 | BIVALNA, SANITARNA IN POMOŽNA OPREMA | LIVING, SANITARY AND ANCILLARY EQUIPMENT
| Sedežno-ležalne in ležalne konstrukcije morajo biti dobavljene in vgrajene demontažno v količini za 2/3 zaklonilnih mest kot sedeži in za 1/3 zaklonilnih mest kot ležišča, z vmesnimi vzdolžnimi in prečnimi hodniki, skladno z zahtevami predpisa; če bodo vgrajene postelje in sedišča s platni, morajo biti iz snovi, ki ne plesni (samougasljiva umetna vlakna); dobavitelj mora ta del popisa prilagoditi svojim kataloškim podatkom in v celoti zahtevam predpisa, za zaklonišče za 300 oseb. | The seating and bedding structures shall be supplied and installed dismantled in a quantity for 2/3 of the shelter positions as seats and for 1/3 of the shelter positions as beds, with longitudinal and transverse corridors in between, in accordance with the requirements of the Regulation; if beds and seats with canvas are to be installed, they shall be made of non-mould-resistant material (self-extinguishing plastic fibres); the supplier shall adapt this part of the inventory to his catalogue data and to the full requirements of the Regulation, for a shelter for 300 persons.
4.0.1 | Demontažna sedišča SESTAVLJENO PO DETAJLU DOBAVITELJA | Dismantling seating ASSEMBLED TO SUPPLIER'S DETAIL | kpl | 200 |  | 0
4.0.2 | Demontažna ležišča SESTAVLJENO PO DETAJLU DOBAVITELJA | Dismantling mattresses ASSEMBLED TO SUPPLIER'S DETAIL | kpl | 100 |  | 0
4.0.3 | Odprti kovinski regal za hrano in pribor, sestavljiv z vijačnimi zvezami DOBAVLJIVO V SLO | Open metal food and cutlery rack, assemblable with screw ties AVAILABLE IN SLO | kpl | 3 |  | 0
4.0.4 | Kovinska omara za pribor in potrošni material DOBAVLJIVO V SLO | Metal cabinet for cutlery and consumables AVAILABLE IN SLO | kpl | 1 |  | 0
4.0.5 | Omarica s kompletom za prvo pomoč DOBAVLJIVO V SLO | First aid kit AVAILABLE IN SLO | kpl | 6 |  | 0
4.0.6 | Plastična posoda s pokrovom - za odplake, s prostornino 27 litrov za skupno potrebno prostornino (1 liter na dan za osebo za sedem dni = 2100 litrov) DOBAVLJIVO V SLO | Plastic container with lid - for sewage, with a capacity of 27 litres for the total required capacity (1 litre per person per day for seven days = 2100 litres) AVAILABLE IN SLO | kos | 78 |  | 0
4.0.7 | Plastična posoda s pokrovom - za fekalije, s prostornino 27 litrov za skupno potrebno prostornino (1,3 litra na dan za osebo za sedem dni = 2730 litrov) DOBAVLJIVO V SLO | Plastic container with lid - for faeces, with a capacity of 27 litres for the total required capacity (1.3 litres per person per day for seven days = 2730 litres) AVAILABLE IN SLO | kos | 102 |  | 0
4.0.8 | Plastična posoda s pokrovom - za odpadke, s prostornino 27 litrov za skupno potrebno prostornino (2 litra na dan za osebo za sedem dni = 4200 litrov) DOBAVLJIVO V SLO | Plastic container with lid - for waste, with a capacity of 27 litres for the total required capacity (2 litres per person per day for seven days = 4200 litres) AVAILABLE IN SLO | kos | 156 |  | 0
4.0.9 | Plastična posoda s pipico - za pitno vodo, s prostornino 20 litrov za skupno potrebno prostornino v zaklonišču (3 litre na dan za osebo za sedem dni = 6300 litrov) DOBAVLJIVO V SLO | Plastic container with tap - for drinking water, with a capacity of 20 litres for the total required shelter capacity (3 litres per person per day for seven days = 6300 litres) AVAILABLE IN SLO | kos | 315 |  | 0
4.0.10 | Suho stranišče s podnožjem DOBAVLJIVO V SLO | Dry toilet with base AVAILABLE IN SLO | kpl | 9 |  | 0
4.0.11 | Nosilec posode za vodo in vedro, emajlirani umivalnik za stensko pritrditev, z odtokom v vedro SESTAVLJENO PO DETAJLU DOBAVITELJA | Water tank and bucket holder, enamelled washbasin for wall mounting, with drain into bucket ASSEMBLED TO SUPPLIER'S DETAIL | kpl | 3 |  | 0
4.0.12 | Tablice za označitev dostopa in namembnosti prostorov v zaklonišču PO DETAJLU DOBAVITELJA | Signs to indicate access and use of shelter spaces AS DETAILED BY THE SUPPLIER | kos | 30 |  | 0
4.0.13 | Zakloniščni red z načrtom zaklonišča in z označenimi potmi umika iz zaklonišča – 2 × plastificirani A3 PO DETAJLU DOBAVITELJA | Shelter order with shelter plan and marked escape routes - 2 × laminated A3 AS DETAILED BY THE SUPPLIER | kpl | 12 |  | 0
4.0.14 | Montažne predelne stene s povezovalnim in pritrdilnim priborom za ureditev straniščnih kabin DOBAVLJIVO V SLO | Prefabricated partitions with connecting and fixing accessories for toilet cubicle arrangements AVAILABLE IN SLO | m2 | 60 |  | 0
4.0.15 | Pribor za vrata v montažnih predelnih stenah straniščnih kabin DOBAVLJIVO V SLO | Door accessories in prefabricated toilet cubicle partitions AVAILABLE IN SLO | kpl | 9 |  | 0
4.0.16 | Komplet gasilske in samoreševalne opreme za reševanje iz zaklonišča (po prilogi A, Ur. l. RS št. 26/98 in 38/01): | Firefighting and self-rescue equipment kit for shelter rescue (according to Annex A, Official Journal of the RS No 26/98 and 38/01):
| gasilni aparat na vodo V9 | v9 water extinguisher | kpl | 4 |  | 0
| rezervna tesnila za vrata (SR) (v zavitku) | spare door seals (SR) (in a pack) | kos | 2 |  | 0
| nosila za poškodovance | stretchers for the injured | kpl | 2 |  | 0
| zložljiva nosila za poškodovance | foldable stretchers for injured persons | kpl | 2 |  | 0
| nosilni okvir za suho stranišče (ni potrebno, ker v tem zaklonišču ni mokrih stranišč) | a support frame for a dry toilet (not necessary as there are no wet toilets in this shelter) | kpl | 0 |  | 0
| črne PVC vrečke za suho stranišče (po 100 kosov za eno stranišče ) | black PVC bags for dry toilets (100 pieces per toilet) | kos | 900 |  | 0
| toplotno - odporna tesnilna vrv (bela) (v zvitku) | heat-resistant sealing rope (white) (roll) | kos | 2 |  | 0
| dvigalka 100 kN | 100 kN hoist | kpl | 2 |  | 0
| papir za medicinske potrebe (ni potrebno, ker v tem zaklonišču ni ambulante) (v zavitku) | medical paper (not needed as there is no clinic in this shelter) (in a roll) | kos | 0 |  | 0
| rezervne vrečke za posodo z odpadki za 30 litrov vsebine (po 10 kosov na eno posodo z odpadki, v tem zaklonišču je 336 posod) | spare waste bin bags for 30 litres (10 per bin, 336 bins in this shelter) | kpl | 3360 |  | 0
| sredstvo za konzervacijo pitne vode (za celotni volumen posod za pitno vodo, odmerjeno v zavitkih za posamezno posodo, v količini za celotno število posod; v tem zaklonišču je predvidenih 315 posod) (v zavitku) | drinking water preservative (for the total volume of drinking water containers, measured in packs per container, in the quantity for the total number of containers; 315 containers are foreseen in this shelter) (per pack) | kos | 315 |  | 0
| dodatno pa še osnovni komplet na plošči, ki se namesti na steno v zapori vhoda ter v zapori zasilnega izhoda in vsebuje sledeče predpisano ročno orodje: - kladivo 1500 g (1 kos) - kladivo 2000 g (1 kos) - klini iz trdega lesa (250×80×40) mm, (6 kosov) - matični ključ (46 mm, 1 kos) - zložljiva lopata (1 kos) - sekač za beton – koničasti 400 mm (1 kos) - sekač za beton – koničasti 500 mm (1 kos) - sekač za beton – ravni 500 mm (1 kos) - obod žage za kovino – 300 mm (1 kos) - sekira navadna – večja (1 kos) - kramp (1 kos) - lomilni drog 1,2 m (1 kos) - sekira manjša z nastavkom za izruvanje žebljev (1 kos) - lističi za žago za kovino (300×22) mm, (10 kosov) - ročna žaga za les 500 mm VSE DOBAVLJIVO V SLO | in addition, a basic kit on a panel to be mounted on the wall in the entrance and emergency exit barriers, containing the following prescribed hand tools: - hammer 1500 g (1 piece) - hammer 2000 g (1 piece) - hardwood dowels (250×80×40) mm, (6 pieces) - wrench (46 mm, 1 piece) - folding shovel (1 piece) - concrete cutter - pointed 400 mm (1 piece) - concrete cutter - pointed 500 mm (1 piece) - concrete chisel - straight 500 mm (1 piece) - metal saw rim - 300 mm (1 piece) - hatchet - larger (1 piece) - pick (1 piece) - breaking bar 1,2 m (1 piece) - small axe with grubbing attachment nails (1 piece) - metal saw blades (300×22) mm, (10 pcs.) - hand-held wood saw 500 mm ALL AVAILABLE IN SLO | kpl | 2 |  | 0
| BIVALNA, SANITARNA IN POMOŽNA OPREMA | LIVING, SANITARY AND ANCILLARY EQUIPMENT |  |  |  | 0

## 4.1.1.5_300_5.0
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
4.1.1 | STROJNA DELA - VEČJE ZAKLONIŠČE S 300 ZAKLONILNIMI MESTI | MECHANICAL WORKS - LARGE SHELTER WITH 300 SHELTER SPACES
4.1.1.5 | VGRADNJA NAPRAV, NAPELJAV IN OPREME TER OSTALE DEJAVNOSTI | INSTALLATION OF PLANT, FIXTURES AND FITTINGS AND OTHER ACTIVITIES |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
5.0 | VGRADNJA NAPRAV, NAPELJAV IN OPREME TER OSTALE DEJAVNOSTI | INSTALLATION OF PLANT, FIXTURES AND FITTINGS AND OTHER ACTIVITIES
5.0.1 | Namestitev vgradnih delov v opaže - pozicije od 1.01 do 1.15 DOBAVITELJ TEHNIKE IN OPREME ZAKLONIŠČA | Installing fittings in the formwork - positions 1.01 to 1.15 SUPPLIER OF SHELTER EQUIPMENT | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
5.0.2 | Vgradnja zapiralnih sredstev in pribora v opaže in na stene - pozicije od 2.01 do 2.10 DOBAVITELJ TEHNIKE IN OPREME ZAKLONIŠČA | Installation of closures and fittings in sheathing and on walls - positions 2.01 to 2.10 SUPPLIER OF SHELTER EQUIPMENT | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
5.0.3 | Vgradnja sistema za zračenje zaklonišča v zaščitni funkciji in uvodnice za tesnjenje kablov - pozicije od 3.01 do 3.34 DOBAVITELJ TEHNIKE IN OPREME ZAKLONIŠČA | Installation of a shelter ventilation system in protective function and cable glands - positions 3.01 to 3.34 SUPPLIER OF SHELTER EQUIPMENT | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
5.0.4 | Vgradnja bivalne, sanitarne in pomožne opreme - pozicije od 4.01 do 4.16 DOBAVITELJ TEHNIKE IN OPREME ZAKLONIŠČA | Installation of living, sanitary and ancillary equipment - positions 4.01 to 4.16 SUPPLIER OF SHELTER EQUIPMENT | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
5.0.5 | Izdelava navodil za uporabo, servisiranje in vzdrževanje sistema za zračenje in zaklonišča kot celote v zaščitni funkciji (projekt za obratovanje in vzdrževanje - POV) DOBAVITELJ TEHNIKE IN OPREME ZAKLONIŠČA | Preparation of instructions for the use, servicing and maintenance of the ventilation system and the shelter as a whole in its protective function (Operation and Maintenance Project - O&M Project) SUPPLIER OF SHELTER EQUIPMENT | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
5.0.6 | Nastavitve prezračevalnih količin in tlakov sistema za zračenje v zaščitni funkciji zaklonišča DOBAVITELJ TEHNIKE IN OPREME ZAKLONIŠČA | Settings of ventilation volumes and pressures of the ventilation system in the shelter protection function SUPPLIER OF SHELTER EQUIPMENT | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
5.0.7 | Predhodni preizkus celotnega zaklonišča in priprava zaklonišča na tehnični preizkus (za vse izvajalce v zaklonišču - brez izdaje javne listine) DOBAVITELJ TEHNIKE IN OPREME ZAKLONIŠČA | Preliminary test of the entire shelter and preparation of the shelter for the technical test (for all shelter operators - without issuing a public charter) SUPPLIER OF SHELTER EQUIPMENT | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
5.0.8 | Tehnični preizkus zaklonišča kot celote za pridobitev javne listine (potrdila o opravljenem tehničnem preizkusu zaklonišča), kar izvede pooblaščeni zavod POOBLAŠČENI ZAVOD | Technical test of the shelter as a whole to obtain a public document (certificate of completion of the technical test of the shelter), carried out by an approved institute AUTHORISED INSTITUTION | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
5.0.9 | Izdelava elaborata o preureditvi zaklonišča iz funkcije za drugi namen v zaščitno funkcijo DOBAVITELJ TEHNIKE IN OPREME ZAKLONIŠČA | Preparation of a study on the conversion of a shelter from a function for another purpose to a protective function SUPPLIER OF SHELTER EQUIPMENT | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
5.0.10 | Dobava, nastavitev in izpolnitev knjige vzdrževanja z začetnimi podatki DOBAVITELJ TEHNIKE IN OPREME ZAKLONIŠČA | Supply, setup and completion of the maintenance book with initial data SUPPLIER OF SHELTER EQUIPMENT | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
5.0.11 | Seznanitev predstavnika uporabnika z načini uporabe in vzdrževanja zaklonišča DOBAVITELJ TEHNIKE IN OPREME ZAKLONIŠČA | Briefing the user representative on how to use and maintain the shelter SUPPLIER OF SHELTER EQUIPMENT | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
5.0.12 | Izdelava posnetka in projekta izvedenih del za zaklonišče v obsegu dobave in del po tem popisu (PID) DOBAVITELJ TEHNIKE IN OPREME ZAKLONIŠČA | Preparation of a survey and design of the works to be carried out for the shelter to the extent of the supply and the works according to this Inventory (PID) SUPPLIER OF SHELTER EQUIPMENT | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
5.0.13 | Kompletiranje vse potrebne in spremljajoče dokazne dokumentacije (certifikati, izjave o skladnosti, navodila, garancijski listi, poročila in zapisniki o meritvah, itd.) v obsegu dobave in del po tem popisu DOBAVITELJ TEHNIKE IN OPREME ZAKLONIŠČA | Completion of all necessary and accompanying supporting documentation (certificates, declarations of conformity, instructions, warranty certificates, reports and records of measurements, etc.) within the scope of the supply and the works according to this Inventory SUPPLIER OF SHELTER EQUIPMENT | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
5.0.14 | Sodelovanje na operativnih sestankih na gradbišču DOBAVITELJ TEHNIKE IN OPREME ZAKLONIŠČA | Participation in operational meetings on site SUPPLIER OF SHELTER EQUIPMENT | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
5.0.15 | Stroški transporta, souporabe pomožnih objektov, napeljav in zavarovanja na gradbišču DOBAVITELJ TEHNIKE IN OPREME ZAKLONIŠČA | Costs of transport, sharing of ancillary facilities, installations and on-site insurance SUPPLIER OF SHELTER EQUIPMENT | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
| VGRADNJA NAPRAV, NAPELJAV IN OPREME TER OSTALE DEJAVNOSTI | INSTALLATION OF PLANT, FIXTURES AND FITTINGS AND OTHER ACTIVITIES |  |  | Skupni znesek pozicij te točke mora biti zajet v enotnih cenah posameznih pozicij točk od 1.0 do 4.0!

## 4.1.2.0_Rekapitulacija 200
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
| REKAPITULACIJA STROŠKOV STROJNIH DEL | COST SUMMARY OF MECHANICAL WORKS
| 4 NAČRT S PODROČJA STROJNIŠTVA | 4 DOCUMENTATION IN THE FIELD OF MECHANICAL ENGINEERING
| 4/1 Zaklonišče | 4/1 Shelter
4.1.2 | STROJNA DELA - MANJŠE ZAKLONIŠČE Z 200 ZAKLONILNIMI MESTI | MECHANICAL WORKS - SMALLER SHELTER WITH 200 SHELTER SPACES
4.1.2.1 | VGRADNI DELI | BUILDING WORKS | 0
4.1.2.2 | ZAPIRALNA SREDSTVA IN PRIBOR | CLOSURES AND ACCESSORIES | 0
4.1.2.3 | SISTEM ZA ZRAČENJE ZAKLONIŠČA V ZAŠČITNI FUNKCIJI IN UVODNICE ZA TESNJENJE KABLOV | SHELTER VENTILATION SYSTEM IN PROTECTIVE FUNCTION AND CABLE SEALING GLANDS | 0
4.1.2.4 | BIVALNA, SANITARNA IN POMOŽNA OPREMA | LIVING, SANITARY AND ANCILLARY EQUIPMENT | 0
4.1.2.5 | VGRADNJA NAPRAV, NAPELJAV IN OPREME TER OSTALE DEJAVNOSTI | INSTALLATION OF PLANT, FIXTURES AND FITTINGS AND OTHER ACTIVITIES | 0
0
0 | NEPREDVIDENA DELA | UNFORSEEN WORKS | 0
| SKUPAJ STROJNA DELA - MANJŠE ZAKLONIŠČE Z 200 ZAK. MESTI | TOTAL MECHANICAL WORKS - SMALLER SHELTER WITH 200 SHELTER SPACES | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT

## 4.1.2.1_200_1.0
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
4.1.2 | STROJNA DELA - MANJŠE ZAKLONIŠČE Z 200 ZAKLONILNIMI MESTI | MECHANICAL WORKS - SMALLER SHELTER WITH 200 SHELTER SPACES
4.1.2.1 | VGRADNI DELI | BUILDING WORKS |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
1.0 | VGRADNI DELI | BUILDING WORKS
1.0.1 | Ravna jeklena cev z nastavkom za vgradnjo protiudarnega ventila (vel. 4) - DN 200/750 z dvema prirobnicama kot npr.: KROBATH tip MF Gr. 4 DN 200/750 2F | Straight steel pipe with spigot for installation of backflow preventer (size 4) - DN 200/750 with two flanges as e.g. KROBATH type MF Gr. 4 DN 200/750 2F | kos | 2 |  | 0
1.0.2 | Ravna jeklena cev za dovod zraka na prezračevalno napravo pri zaščitnem zračenju DN 150/400 z eno prirobnico IZDELANO PO DETAJLU DOBAVITELJA | Flat steel pipe for air supply to the ventilation unit for protective ventilation DN 150/400 with one flange MADE TO SUPPLIER'S DETAIL | kos | 2 |  | 0
1.0.3 | Zalomljena jeklena cev za dovod zraka na prezračevalno napravo pri normalnem zračenju DN 200/400 z eno prirobnico, Z-zalom IZDELANO PO DETAJLU DOBAVITELJA | Broken steel pipe for air supply to the ventilation unit during normal ventilation DN 200/400 with one flange, Z-end MADE TO SUPPLIER'S DETAIL | kos | 2 |  | 0
1.0.4 | Zalomljena jeklena cev za ventil za regulacijo nadtlaka DN 150/750 z eno prirobnico (za odvod zraka iz bivalnega prostora v smeri zapore vhoda), U-zalom IZDELANO PO DETAJLU DOBAVITELJA | Fused steel pipe for overpressure control valve DN 150/750 with one flange (for air exhaust from the living space in the direction of the entrance barrier), U-joint MADE TO SUPPLIER'S DETAIL | kos | 3 |  | 0
1.0.5 | Ravna jeklena cev za ventil za regulacijo nadtlaka DN 150/300 z eno prirobnico (za odvod zraka iz sanitarij v smeri skladišča odpadkov in odplak) IZDELANO PO DETAJLU DOBAVITELJA | Flat steel hose for overpressure control valve DN 150/300 with one flange (for air discharge from toilets towards waste and sewage storage) MADE TO SUPPLIER'S DETAIL | kos | 2 |  | 0
1.0.6 | Zalomljena jeklena cev za odvod zraka iz zapore vhoda pri zaščitnem in normalnem zračenju DN 150/750 z dvema prirobnicama, Z-zalom IZDELANO PO DETAJLU DOBAVITELJA | Fused steel pipe for air outlet from the entrance barrier for protective and normal ventilation DN 150/750 with two flanges, Z-end MADE TO SUPPLIER'S DETAIL | kos | 3 |  | 0
1.0.7 | Zalomljena jeklena cev za odvod zraka iz skladišča odpadkov in odplak pri zaščitnem in normalnem zračenju DN 150/750 z dvema prirobnicama, Z-zalom IZDELANO PO DETAJLU DOBAVITELJA | Fused steel waste and sewage storage air pipe for protective and normal ventilation DN 150/750 with two flanges, Z-end MADE TO SUPPLIER'S DETAIL | kos | 2 |  | 0
1.0.8 | Ravna jeklena cev za odvod kondenzne vode z navojnim nastavkom za zasun DN 25/600 IZDELANO PO DETAJLU DOBAVITELJA | Flat steel condensate drain pipe with threaded plug DN 25/600 MADE TO SUPPLIER'S DETAIL | kos | 1 |  | 0
1.0.9 | Ravna jeklena cev za tesnjenje kablov DN 100/750 z nastavki za pritrditev med opaže IZDELANO PO DETAJLU DOBAVITELJA | Flat steel cable sealing hose DN 100/750 with fittings for fixing between the formwork MADE TO SUPPLIER'S DETAIL | kos | 4 |  | 0
1.0.10 | Ravna jeklena cev za tesnjenje kablov DN 100/400 z nastavki za pritrditev med opaže IZDELANO PO DETAJLU DOBAVITELJA | Flat steel cable sealing hose DN 100/400 with fittings for fixing between the formwork MADE TO SUPPLIER'S DETAIL | kos | 4.1 |  | 0
1.0.11 | Ravna jeklena cev za tesnjenje kablov DN 100/300 z nastavki za pritrditev med opaže IZDELANO PO DETAJLU DOBAVITELJA | Flat steel cable sealing hose DN 100/300 with fittings for fixing between the formwork MADE TO SUPPLIER'S DETAIL | kos | 3 |  | 0
1.0.12 | Ravna jeklena cev za pretok zraka in kondenzne vode med komorami peščenega predfiltra DN 150/400 z nastavki za pritrditev med opaže IZDELANO PO DETAJLU DOBAVITELJA | Flat steel pipe for the flow of air and condensate water between the sand pre-filter chambers DN 150/400 with fittings for fixing between the formwork MADE TO SUPPLIER'S DETAIL | kos | 5 |  | 0
1.0.13 | Ravna jeklena cev za prehod vodovodne napeljave skozi steno DN 25/750 – obojestransko z navojno tuljavo za zaščitno funkcijo zaklonišča IZDELANO PO DETAJLU DOBAVITELJA | Flat steel pipe for the passage of the water supply through the wall DN 25/750 - both sides with threaded sleeve for the shelter protection function MADE TO SUPPLIER'S DETAIL | kos | 1 |  | 0
1.0.14 | Ravna jeklena cev za prehod vodovodne napeljave skozi steno DN 20/300 – obojestransko z navojno tuljavo za zaščitno funkcijo zaklonišča IZDELANO PO DETAJLU DOBAVITELJA | Flat steel pipe for the passage of the water supply through the wall DN 20/300 - both sides with threaded sleeve for the protective function of the shelter MADE TO SUPPLIER'S DETAIL | kos | 2 |  | 0
| VGRADNI DELI | BUILDING WORKS |  |  |  | 0

## 4.1.2.2_200_2.0
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
4.1.2 | STROJNA DELA - MANJŠE ZAKLONIŠČE Z 200 ZAKLONILNIMI MESTI | MECHANICAL WORKS - SMALLER SHELTER WITH 200 SHELTER SPACES
4.1.2.2 | ZAPIRALNA SREDSTVA IN PRIBOR | CLOSURES AND ACCESSORIES |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
2.0 | ZAPIRALNA SREDSTVA IN PRIBOR | CLOSURES AND ACCESSORIES
2.0.1 | Armiranobetonska protiudarna vrata, plinotesna in požarna (EI-90), s priborom za odmik ruševin, za nadtlak 300 kPa, z vgrajenim gumijastim tesnilom, z zapiralnim in blokadnim mehanizmom, z obojestransko označenimi smermi odpiranja in zapiranja, v zapori vhoda, z dimenzijami 1200/2050/200 mm – desna kot npr.: KROBATH tip DT-B 1200 R | Reinforced concrete anti-ram door, gas-tight and fire-resistant (EI-90), with debris deflection fittings, for an overpressure of 300 kPa, with integrated rubber seal, with closing and locking mechanism, with opening and closing directions marked on both sides, in the entrance barrier, with dimensions 1200/2050/200 mm - right such as KROBATH type DT-B 1200 R | kpl | 1 |  | 0
2.0.2 | Armiranobetonska protiudarna vrata, plinotesna in požarna (EI-90), s priborom za odmik ruševin, za nadtlak 300 kPa, z vgrajenim gumijastim tesnilom, z zapiralnim in blokadnim mehanizmom, z obojestransko označenimi smermi odpiranja in zapiranja, v zapori zasilnega izhoda, z dimenzijami 825/2050/200 mm – desna kot npr.: KROBATH tip DT-B 825 R | Reinforced concrete anti-accident door, gas-tight and fire-resistant (EI-90), with debris deflection fittings, for an overpressure of 300 kPa, with built-in rubber seal, with closing and locking mechanism, with opening and closing directions marked on both sides, in emergency exit barrier, dimensions 825/2050/200 mm - right such as KROBATH type DT-B 825 R | kpl | 1 |  | 0
2.0.3 | Jeklena, plinotesna in požarna vrata (EI-90), za nadtlak 10 kPa, z vgrajenim gumijastim tesnilom, z zapiralnim mehanizmom, z obojestransko označenimi smermi odpiranja in zapiranja, v zapori vhoda, z dimenzijami 1200/2050/100 mm – leva kot npr.: KROBATH tip GT 1200 L | Steel, gas-tight and fire-resistant door (EI-90), for overpressure of 10 kPa, with integrated rubber seal, with closing mechanism, with opening and closing directions marked on both sides, in the entrance barrier, with dimensions 1200/2050/100 mm - left such as KROBATH type GT 1200 L | kpl | 1 |  | 0
2.0.4 | Jeklena, plinotesna in požarna vrata (EI-90), za nadtlak 10 kPa, z vgrajenim gumijastim tesnilom, z zapiralnim mehanizmom, z obojestransko označenimi smermi odpiranja in zapiranja, v skladišču odpadkov in odplak, z dimenzijami 825/2050/100 mm – desna kot npr.: KROBATH tip GT 825 R | Steel, gas-tight and fire-resistant door (EI-90), for overpressure of 10 kPa, with integrated rubber seal, with closing mechanism, with opening and closing directions marked on both sides, in waste and sewage storage, dimensions 825/2050/100 mm - right such as KROBATH type GT 825 R | kpl | 1 |  | 0
2.0.5 | Jeklena, plinotesna in požarna vrata (EI-90), za nadtlak 10 kPa, z vgrajenim gumijastim tesnilom, z zapiralnim mehanizmom, z obojestransko označenimi smermi odpiranja in zapiranja, v zapori zasilnega izhoda, z dimenzijami 825/2050/100 mm – desna kot npr.: KROBATH tip GT 825 R | Steel, gas-tight and fire-resistant door (EI-90), for overpressure of 10 kPa, with integrated rubber seal, with closing mechanism, with opening and closing directions marked on both sides, in emergency exit barrier, dimensions 825/2050/100 mm - right such as KROBATH type GT 825 R | kpl | 1 |  | 0
2.0.6 | Jeklena, plinotesna in požarna vratca (EI-90), za nadtlak 10 kPa, z vgrajenim gumijastim tesnilom, z zapiralnim mehanizmom, z obojestransko označenimi smermi odpiranja in zapiranja, v peščeni predfilter, z dimenzijami 600/800/100 mm – leva kot npr.: KROBATH tip GKL 90 L | Steel, gas-tight and fire-tight door (EI-90), for 10 kPa overpressure, with integrated rubber seal, with closing mechanism, opening and closing directions marked on both sides, in sand pre-filter, dimensions 600/800/100 mm - left such as KROBATH type GKL 90 L | kpl | 1 |  | 0
2.0.7 | Jeklena navadna notranja vrata, odporna na tresljaje konstrukcije, z vgrajeno rešetko za izenačevanje zračnega tlaka med notranjimi prostori, z dimenzijami 825/2050 mm – leva – za vstop v prostor z napravami kot npr.: KROBATH tip IT 825 L | Structural vibration-resistant plain steel interior door with integrated grille to equalise air pressure between interior spaces, dimensions 825/2050 mm - left - for access to the equipment room such as KROBATH type IT 825 L | kpl | 1 |  | 0
2.0.8 | Jeklena navadna notranja vrata, odporna na tresljaje konstrukcije, z vgrajeno rešetko za izenačevanje zračnega tlaka med notranjimi prostori, s samozapiralnim mehanizmom, z dimenzijami 825/2050 mm – leva – za vstop v sanitarije kot npr.: KROBATH tip IT 825 L | Steel ordinary internal door, resistant to structural vibrations, with integrated grille to equalise the air pressure between the internal compartments, with self-closing mechanism, dimensions 825/2050 mm - left-hand - for entrance to sanitary facilities such as KROBATH type IT 825 L | kpl | 1 |  | 0
2.0.9 | Jeklena navadna notranja vrata, odporna na tresljaje konstrukcije, z vgrajeno rešetko za izenačevanje zračnega tlaka med notranjimi prostori, z dimenzijami 825/2050 mm – desna – za vstop v shrambo vode in opreme kot npr.: KROBATH tip IT 825 R | Steel ordinary internal door, resistant to structural vibrations, with integrated grille to equalise air pressure between internal spaces, dimensions 825/2050 mm - right - for access to water and equipment storage such as KROBATH type IT 825 R | kpl | 1 |  | 0
2.0.10 | Jeklena lestev za dostop do prostora peščenega predfiltra, s priborom za montažno pritrditev DOBAVLJIVO V SLO | Steel ladder for access to the sand pre-filter compartment, with mounting accessories AVAILABLE IN SLO | m | 2 |  | 0
| ZAPIRALNA SREDSTVA IN PRIBOR | CLOSURES AND ACCESSORIES |  |  |  | 0

## 4.1.2.3_200_3.0
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
4.1.2 | STROJNA DELA - MANJŠE ZAKLONIŠČE Z 200 ZAKLONILNIMI MESTI | MECHANICAL WORKS - SMALLER SHELTER WITH 200 SHELTER SPACES
4.1.2.3 | SISTEM ZA ZRAČENJE ZAKLONIŠČA V ZAŠČITNI FUNKCIJI IN UVODNICE ZA TESNJENJE KABLOV | SHELTER VENTILATION SYSTEM IN PROTECTIVE FUNCTION AND CABLE SEALING GLANDS |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
3.0 | SISTEM ZA ZRAČENJE ZAKLONIŠČA V ZAŠČITNI FUNKCIJI IN UVODNICE ZA TESNJENJE KABLOV | SHELTER VENTILATION SYSTEM IN PROTECTIVE FUNCTION AND CABLE SEALING GLANDS
3.0.1 | Protiudarni ventil (vel. 4) za dovod zraka s prigrajenim filtrom za grobi prah DN 200 kot npr.: KROBATH tip ESV GR. 4 | Air inlet check valve (size 4) with coarse dust filter DN 200 such as KROBATH type ESV GR. 4 | kpl | 2 |  | 0
3.0.2 | Nadtlačni protiudarni ventil za odvod zraka skozi zaporo vhoda in skozi skladišče odpadkov DN 150 kot npr.: KROBATH tip ÜV-ESV 75 | Overpressure backdraft valve for air outlet through the entrance barrier and through the waste storage DN 150 such as KROBATH type ÜV-ESV 75 | kpl | 5 |  | 0
3.0.3 | Regulacijski ventil za odvod zraka DN 150 kot npr.: KROBATH tip ALV 150 | Control valve for air outlet DN 150 such as KROBATH type ALV 150 | kpl | 5 |  | 0
3.0.4 | Vroče cinkana rešetka za peščeni predfilter kot npr.: KROBAT SFR VERZ. | Hot-dip galvanised grating for sand pre-filter such as KROBAT SFR VERZ. | m2 | 5.03 |  | 0
3.0.5 | Certificirani ostrorobi peščeni granulat, eruptivnega porekla, odprašen, zrna granulacije 4-8 mm, embaliran v vrečah s težo največ 30 kg v SLO pri dobavitelju peska asfaltnim bazam | Certified coarse sandy granulate, eruptive origin, dust-free, grain size 4-8 mm, packed in bags weighing not more than 30 kg in SLO, supplier of sand to asphalt bases | m3 | 7.1 |  | 0
3.0.6 | Vmesna zalomljena cev DN 150 za dovod zraka na prezračevalno napravo pri zaščitnem zračenju, z dvema prirobnicama, L-zalom DOBAVLJIVO V SLO | Intermediate broken pipe DN 150 for air supply to the ventilation unit in protective ventilation, with two flanges, L-bend AVAILABLE IN SLO | kpl | 2 |  | 0
3.0.7 | Vmesna zalomljena cev DN 200 za dovod zraka na prezračevalno napravo pri normalnem zračenju, z dvema prirobnicama, L-zalom DOBAVLJIVO V SLO | Intermediate broken pipe DN 200 for air supply to the ventilation unit under normal ventilation, with two flanges, L-shaped AVAILABLE IN SLO | kpl | 2 |  | 0
3.0.8 | Krogelni ventil za zapiranje odvoda kondenzne vode DN 25 iz prostora peščenega predfiltra DOBAVLJIVO V SLO | Ball valve for closing the condensate drain DN 25 from the sand pre-filter compartment AVAILABLE IN SLO | kos | 1 |  | 0
3.0.9 | Plinotesna loputa z ročico DN 200-RS DOBAVLJIVO V SLO | Gas-tight butterfly valve with handle DN 200-RS AVAILABLE IN SLO | kpl | 2 |  | 0
3.0.10 | Plinotesna loputa z ročico DN 150-RS DOBAVLJIVO V SLO | Gas-tight butterfly valve with handle DN 150-RS AVAILABLE IN SLO | kpl | 7 |  | 0
3.0.11 | Prezračevalna naprava z ročnim in električnim pogonom (400 V, 50 Hz, 400 W, IP 54), pogonsko ročico, stikalom, prikazovalnikom pretoka zraka (načina zračenja), z navodilom za uporabo v različnih načinih zračenja, za nazivni pretok najmanj 600 m3/h kot npr.: KROBATH tip VA-300 | Ventilation appliance with manual and electric drive (400 V, 50 Hz, 400 W, IP 54), drive lever, switch, air flow display (ventilation mode), with instructions for use in different ventilation modes, for a nominal flow of at least 600 m3/h such as KROBATH type VA-300 | kpl | 2 |  | 0
3.0.12 | Filter za RBK-zaščito s priključnima prirobnicama, s podnožjem za vgradnjo in pritrditev, za nazivni pretok 200 m3/h in padec tlaka največ 600 Pa; filter mora imeti veljavni certifikat in nalepko KI Ljubljana kot npr.: COLF tip ECS-250 | RBK-protection filter with two connection flanges, with mounting and fixing base, for a nominal flow of 200 m3/h and a pressure drop of maximum 600 Pa; the filter must have a valid certificate and a label from KI Ljubljana such as COLF type ECS-250 | kpl | 2 |  | 0
3.0.13 | Razstavljiva spojka s prirobnicama in gibljivimi cevmi za hitro priključitev filtra za RBK-zaščito, vse skladno s tipom dobavljenega filtra kot npr.: KROBATH tip SKU | Expandable coupling with flanges and flexible hoses for quick connection of the RBC protection filter, all according to the type of filter supplied such as KROBATH type SKU | kpl | 2 |  | 0
3.0.14 | Tekočinski merilnik nadtlaka (U-cevka) z merilnim območjem najmanj 1500 Pa kot npr.: KROBATH tip SRM-7031 | Liquid pressure gauge (U-tube) with a measuring range of at least 1500 Pa such as KROBATH type SRM-7031 | kpl | 1 |  | 0
3.0.15 | Pribor za neprekinjeno cevno povezavo merilnika nadtlaka v hodnik zasilnega izhoda, z ventilom DOBAVLJIVO V SLO | Accessories for continuous hose connection of an overpressure gauge to the emergency exit corridor, with valve AVAILABLE IN SLO | kpl | 1 |  | 0
3.0.16 | Merilnik temperature zraka (od 0 do + 40 °C) in relativne vlažnosti zraka (od 20 do 100 %) DOBAVLJIVO V SLO | Air temperature gauge (0 to + 40 °C) and relative humidity (from 20 to 100%) AVAILABLE IN SLO | kpl | 1 |  | 0
3.0.17 | Jeklena spiro cev za razvod zraka s potrebnimi fazonskimi kosi DN 200 DOBAVLJIVO V SLO - PICHLER | Steel spiro pipe for air distribution with necessary phasing pieces DN 200 AVAILABLE IN SLO - PICHLER | m | 60 |  | 0
3.0.18 | Jeklena spiro cev za razvod zraka s potrebnimi fazonskimi kosi DN 160 DOBAVLJIVO V SLO - PICHLER | Steel spiro pipe for air distribution with necessary phasing pieces DN 160 AVAILABLE IN SLO - PICHLER | m | 30 |  | 0
3.0.19 | Jeklena spiro cev za razvod zraka s potrebnimi fazonskimi kosi DN 100 DOBAVLJIVO V SLO - PICHLER | Steel spiro pipe for air distribution with necessary phasing pieces DN 100 AVAILABLE IN SLO - PICHLER | m | 15 |  | 0
3.0.20 | Prezračevalni ventil za dovod zraka DN 160 DOBAVLJIVO V SLO - PICHLER | Ventilation valve for air inlet DN 160 AVAILABLE IN SLO - PICHLER | kpl | 15 |  | 0
3.0.21 | Prezračevalni ventil za dovod zraka DN 100 DOBAVLJIVO V SLO - PICHLER | Ventilation valve for air inlet DN 100 AVAILABLE IN SLO - PICHLER | kpl | 8 |  | 0
3.0.22 | Pribor za vertikalno elastično obešanje spiro cevi DN 200 za razvod zraka SESTAVLJENO PO DETAJLU | Accessories for vertical elastic suspension of spiro tubes DN 200 for air distribution ASSEMBLED IN DETAIL | kpl | 40 |  | 0
3.0.23 | Pribor za vertikalno elastično obešanje spiro cevi DN 160 za razvod zraka SESTAVLJENO PO DETAJLU | Accessories for vertical elastic suspension of spiro tubes DN 160 for air distribution ASSEMBLED IN DETAIL | kpl | 20 |  | 0
3.0.24 | Pribor za vertikalno elastično obešanje spiro cevi DN 100 za razvod zraka SESTAVLJENO PO DETAJLU | Accessories for vertical elastic suspension of spiro tubes DN 100 for air distribution ASSEMBLED IN DETAIL | kpl | 10 |  | 0
3.0.25 | Regulacijska loputa DN 200 DOBAVLJIVO V SLO - PICHLER | Regulating flap DN 200 AVAILABLE IN SLO - PICHLER | kpl | 6 |  | 0
3.0.26 | Regulacijska loputa DN 100 DOBAVLJIVO V SLO - PICHLER | Regulating flap DN 100 AVAILABLE IN SLO - PICHLER | kpl | 3 |  | 0
3.0.27 | Tesnilna uvodnica s polnilnimi kosi za tesnjenje kablov DN 100 kot npr.: KROBATH tip RGP-100 | Sealing gland with filler pieces for sealing cables DN 100 such as KROBATH type RGP-100 | kpl | 22 |  | 0
3.0.28 | Zaščitna plošča z mrežico za zunanjo stran cevi za odvod zraka DN 150 SESTAVLJENO PO DETAJLU DOBAVITELJA | Protective plate with mesh for the outside of the air outlet pipe DN 150 ASSEMBLED TO SUPPLIER'S DETAIL | kpl | 5 |  | 0
3.0.29 | Zaščitna plošča z mrežico za zunanjo stran cevi za dovod zraka DN 200 SESTAVLJENO PO DETAJLU DOBAVITELJA | Protective plate with mesh for the outside of the air inlet pipe DN 200 ASSEMBLED TO SUPPLIER'S DETAIL | kpl | 2 |  | 0
3.0.30 | Vmesna spiro cevna povezava z dušilno loputo za priključitev prezračevalne naprave na dovodna priključka normalnega in zaščitnega zračenja DN 200/150 DOBAVLJIVO V SLO - PICHLER | Intermediate spiro hose connection with throttle valve for the connection of the ventilation appliance to the normal and protective ventilation inlet connections DN 200/150 AVAILABLE IN SLO - PICHLER | kpl | 2 |  | 0
3.0.31 | Ravna vmesna cev za nadgradnjo plinotesne lopute nad ventilom za regulacijo nadtlaka DN 150 z dvema prirobnicama PO DETAJLU DOBAVITELJA | Straight intermediate pipe for the gas-tight hatch upgrade above the pressure relief valve DN 150 with two flanges AS DETAILED BY THE SUPPLIER | kos | 5 |  | 0
3.0.32 | Detektor ogljikovega monoksida (s kabelsko povezavo krmilno-signalnega dela in senzorja), z napajalnima električnima priključkoma 230 in 24 V, s svetlobnim in zvočnim alarmom, kalibriran na alarmni prag 50 ppm CO, z navodilom za uporabo kot npr.: FISCHER tip LIFE GM 040-6 + FRFCO | Carbon monoxide detector (with cable connection of the control-signalling part and the sensor), with 230 and 24 V power supply, with light and sound alarm, calibrated to an alarm threshold of 50 ppm CO, with instruction manual such as FISCHER type LIFE GM 040-6 + FRFCO | kpl | 1 |  | 0
3.0.33 | Jekleni čep DN 25 za obojestransko plinotesno zatesnitev cevi vodovodne napeljave do uporabe vodovodnega priključka DOBAVLJIVO V SLO | Steel plug DN 25 for double-sided gas-tight sealing of the water supply pipe until the water connection is used AVAILABLE IN SLO | kos | 2 |  | 0
3.0.34 | Jekleni čep DN 20 za obojestransko plinotesno zatesnitev cevi vodovodne napeljave do uporabe vodovodnega priključka DOBAVLJIVO V SLO | Steel plug DN 20 for double-sided gas-tight sealing of the water supply pipe until the water connection is used AVAILABLE IN SLO | kos | 4 |  | 0
| SISTEM ZA ZRAČENJE ZAKLONIŠČA V ZAŠČITNI FUNKCIJI IN UVODNICE ZA TESNJENJE KABLOV | SHELTER VENTILATION SYSTEM IN PROTECTIVE FUNCTION AND CABLE SEALING GLANDS |  |  |  | 0

## 4.1.2.4_200_4.0
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
4.1.2 | STROJNA DELA - MANJŠE ZAKLONIŠČE Z 200 ZAKLONILNIMI MESTI | MECHANICAL WORKS - SMALLER SHELTER WITH 200 SHELTER SPACES
4.1.2.4 | BIVALNA, SANITARNA IN POMOŽNA OPREMA | LIVING, SANITARY AND ANCILLARY EQUIPMENT |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
4.0 | BIVALNA, SANITARNA IN POMOŽNA OPREMA | LIVING, SANITARY AND ANCILLARY EQUIPMENT
| Sedežno-ležalne in ležalne konstrukcije morajo biti dobavljene in vgrajene demontažno v količini za 2/3 zaklonilnih mest kot sedeži in za 1/3 zaklonilnih mest kot ležišča, z vmesnimi vzdolžnimi in prečnimi hodniki, skladno z zahtevami predpisa; če bodo vgrajene postelje in sedišča s platni, morajo biti iz snovi, ki ne plesni (samougasljiva umetna vlakna); dobavitelj mora ta del popisa prilagoditi svojim kataloškim podatkom in v celoti zahtevam predpisa, za zaklonišče za 250 oseb. | The seating and bedding structures shall be supplied and installed dismantled in a quantity of 2/3 of the shelter positions as seats and 1/3 of the shelter positions as beds, with longitudinal and transverse corridors in between, in accordance with the requirements of the Regulation; if beds and seats with canvas are to be installed, they shall be of non-mould-resistant material (self-extinguishing plastic fibres); the supplier shall adapt this part of the inventory to his own catalogue and to the full requirements of the Regulation, for a shelter for 250 persons.
4.0.1 | Demontažna sedišča SESTAVLJENO PO DETAJLU DOBAVITELJA | Dismantling seating ASSEMBLED TO SUPPLIER'S DETAIL | kpl | 134 |  | 0
4.0.2 | Demontažna ležišča SESTAVLJENO PO DETAJLU DOBAVITELJA | Dismantling mattresses ASSEMBLED TO SUPPLIER'S DETAIL | kpl | 67 |  | 0
4.0.3 | Odprti kovinski regal za hrano in pribor, sestavljiv z vijačnimi zvezami DOBAVLJIVO V SLO | Open metal food and cutlery rack, assemblable with screw ties AVAILABLE IN SLO | kpl | 2 |  | 0
4.0.4 | Kovinska omara za pribor in potrošni material DOBAVLJIVO V SLO | Metal cabinet for cutlery and consumables AVAILABLE IN SLO | kpl | 1 |  | 0
4.0.5 | Omarica s kompletom za prvo pomoč DOBAVLJIVO V SLO | First aid kit AVAILABLE IN SLO | kpl | 4 |  | 0
4.0.6 | Plastična posoda s pokrovom - za odplake, s prostornino 27 litrov za skupno potrebno prostornino (1 liter na dan za osebo za sedem dni = 1400 litrov) DOBAVLJIVO V SLO | Plastic container with lid - for sewage, with a capacity of 27 litres for the total required capacity (1 litre per person per day for seven days = 1400 litres) AVAILABLE IN SLO | kos | 52 |  | 0
4.0.7 | Plastična posoda s pokrovom - za fekalije, s prostornino 27 litrov za skupno potrebno prostornino (1,3 litra na dan za osebo za sedem dni = 1820 litrov) DOBAVLJIVO V SLO | Plastic container with lid - for faeces, with a capacity of 27 litres for the total required capacity (1.3 litres per person per day for seven days = 1820 litres) AVAILABLE IN SLO | kos | 68 |  | 0
4.0.8 | Plastična posoda s pokrovom - za odpadke, s prostornino 27 litrov za skupno potrebno prostornino (2 litra na dan za osebo za sedem dni = 2800 litrov) DOBAVLJIVO V SLO | Plastic container with lid - for waste, with a capacity of 27 litres for the total required capacity (2 litres per person per day for seven days = 2800 litres) AVAILABLE IN SLO | kos | 104 |  | 0
4.0.9 | Plastična posoda s pipico - za pitno vodo, s prostornino 20 litrov za skupno potrebno prostornino v zaklonišču (3 litre na dan za osebo za sedem dni = 4200 litrov) DOBAVLJIVO V SLO | Plastic container with tap - for drinking water, with a capacity of 20 litres for the total required shelter capacity (3 litres per person per day for seven days = 4200 litres) AVAILABLE IN SLO | kos | 210 |  | 0
4.0.10 | Suho stranišče s podnožjem DOBAVLJIVO V SLO | Dry toilet with base AVAILABLE IN SLO | kpl | 6 |  | 0
4.0.11 | Nosilec posode za vodo in vedro, emajlirani umivalnik za stensko pritrditev, z odtokom v vedro SESTAVLJENO PO DETAJLU DOBAVITELJA | Water tank and bucket holder, enamelled washbasin for wall mounting, with drain into bucket ASSEMBLED TO SUPPLIER'S DETAIL | kpl | 2 |  | 0
4.0.12 | Tablice za označitev dostopa in namembnosti prostorov v zaklonišču PO DETAJLU DOBAVITELJA | Signs to indicate access and use of shelter spaces AS DETAILED BY THE SUPPLIER | kos | 22 |  | 0
4.0.13 | Zakloniščni red z načrtom zaklonišča in z označenimi potmi umika iz zaklonišča – 2 × plastificirani A3 PO DETAJLU DOBAVITELJA | Shelter order with shelter plan and marked escape routes - 2 × laminated A3 AS DETAILED BY THE SUPPLIER | kpl | 10 |  | 0
4.0.14 | Montažne predelne stene s povezovalnim in pritrdilnim priborom za ureditev straniščnih kabin DOBAVLJIVO V SLO | Prefabricated partitions with connecting and fixing accessories for toilet cubicle arrangements AVAILABLE IN SLO | m2 | 32 |  | 0
4.0.15 | Pribor za vrata v montažnih predelnih stenah straniščnih kabin DOBAVLJIVO V SLO | Door accessories in prefabricated toilet cubicle partitions AVAILABLE IN SLO | kpl | 6 |  | 0
4.0.16 | Komplet gasilske in samoreševalne opreme za reševanje iz zaklonišča (po prilogi A, Ur. l. RS št. 26/98 in 38/01): | Firefighting and self-rescue equipment kit for shelter rescue (according to Annex A, Official Journal of the RS No 26/98 and 38/01):
| gasilni aparat na vodo V9 | v9 water extinguisher | kpl | 4 |  | 0
| rezervna tesnila za vrata (SR) (v zavitku) | spare door seals (SR) (in a pack) | kos | 2 |  | 0
| nosila za poškodovance | stretchers for the injured | kpl | 2 |  | 0
| zložljiva nosila za poškodovance | foldable stretchers for injured persons | kpl | 2 |  | 0
| nosilni okvir za suho stranišče (ni potrebno, ker v tem zaklonišču ni mokrih stranišč) | a support frame for a dry toilet (not necessary as there are no wet toilets in this shelter) | kpl | 0 |  | 0
| črne PVC vrečke za suho stranišče (po 100 kosov za eno stranišče ) | black PVC bags for dry toilets (100 pieces per toilet) | kos | 600 |  | 0
| toplotno - odporna tesnilna vrv (bela) (v zvitku) | heat-resistant sealing rope (white) (roll) | kos | 2 |  | 0
| dvigalka 100 kN | 100 kN hoist | kpl | 2 |  | 0
| papir za medicinske potrebe (ni potrebno, ker v tem zaklonišču ni ambulante) (v zavitku) | medical paper (not needed as there is no clinic in this shelter) (in a roll) | kos | 0 |  | 0
| rezervne vrečke za posodo z odpadki za 30 litrov vsebine (po 10 kosov na eno posodo z odpadki, v tem zaklonišču je 224 posod) | spare waste bin bags for 30 litres of waste (10 per bin, 224 bins in this shelter) | kpl | 2240 |  | 0
| sredstvo za konzervacijo pitne vode (za celotni volumen posod za pitno vodo, odmerjeno v zavitkih za posamezno posodo, v količini za celotno število posod; v tem zaklonišču je predvidenih 210 posod) (v zavitku) | drinking water preservative (for the total volume of drinking water containers, measured in packs for each container, in the quantity for the total number of containers; 210 containers are foreseen in this shelter) (in a pack) | kos | 210 |  | 0
| dodatno pa še osnovni komplet na plošči, ki se namesti na steno v zapori vhoda ter v zapori zasilnega izhoda in vsebuje sledeče predpisano ročno orodje: - kladivo 1500 g (1 kos) - kladivo 2000 g (1 kos) - klini iz trdega lesa (250×80×40) mm, (6 kosov) - matični ključ (46 mm, 1 kos) - zložljiva lopata (1 kos) - sekač za beton – koničasti 400 mm (1 kos) - sekač za beton – koničasti 500 mm (1 kos) - sekač za beton – ravni 500 mm (1 kos) - obod žage za kovino – 300 mm (1 kos) - sekira navadna – večja (1 kos) - kramp (1 kos) - lomilni drog 1,2 m (1 kos) - sekira manjša z nastavkom za izruvanje žebljev (1 kos) - lističi za žago za kovino (300×22) mm, (10 kosov) - ročna žaga za les 500 mm VSE DOBAVLJIVO V SLO | in addition, a basic kit on a panel to be mounted on the wall in the entrance and emergency exit barriers, containing the following prescribed hand tools: - hammer 1500 g (1 piece) - hammer 2000 g (1 piece) - hardwood dowels (250×80×40) mm, (6 pieces) - wrench (46 mm, 1 piece) - folding shovel (1 piece) - concrete cutter - pointed 400 mm (1 piece) - concrete cutter - pointed 500 mm (1 piece) - concrete chisel - straight 500 mm (1 piece) - metal saw rim - 300 mm (1 piece) - hatchet - larger (1 piece) - pick (1 piece) - breaking bar 1,2 m (1 piece) - small axe with grubbing attachment nails (1 piece) - metal saw blades (300×22) mm, (10 pcs.) - hand-held wood saw 500 mm ALL AVAILABLE IN SLO | kpl | 2 |  | 0
| BIVALNA, SANITARNA IN POMOŽNA OPREMA | LIVING, SANITARY AND ANCILLARY EQUIPMENT |  |  |  | 0

## 4.1.2.5_200_5.0
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | ZAKLONIŠČE | SHELTER
4.1.2 | STROJNA DELA - MANJŠE ZAKLONIŠČE Z 200 ZAKLONILNIMI MESTI | MECHANICAL WORKS - SMALLER SHELTER WITH 200 SHELTER SPACES
4.1.2.5 | VGRADNJA NAPRAV, NAPELJAV IN OPREME TER OSTALE DEJAVNOSTI | INSTALLATION OF PLANT, FIXTURES AND FITTINGS AND OTHER ACTIVITIES |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
5.0 | VGRADNJA NAPRAV, NAPELJAV IN OPREME TER OSTALE DEJAVNOSTI | INSTALLATION OF PLANT, FIXTURES AND FITTINGS AND OTHER ACTIVITIES
5.0.1 | Namestitev vgradnih delov v opaže - pozicije od 1.01 do 1.14 DOBAVITELJ TEHNIKE IN OPREME ZAKLONIŠČA | Installing fittings in the formwork - positions 1.01 to 1.14 SUPPLIER OF SHELTER EQUIPMENT | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
5.0.2 | Vgradnja zapiralnih sredstev in pribora v opaže in na stene - pozicije od 2.01 do 2.10 DOBAVITELJ TEHNIKE IN OPREME ZAKLONIŠČA | Installation of closures and fittings in sheathing and on walls - positions 2.01 to 2.10 SUPPLIER OF SHELTER EQUIPMENT | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
5.0.3 | Vgradnja sistema za zračenje zaklonišča v zaščitni funkciji in uvodnice za tesnjenje kablov - pozicije od 3.01 do 3.34 DOBAVITELJ TEHNIKE IN OPREME ZAKLONIŠČA | Installation of a shelter ventilation system in protective function and cable glands - positions 3.01 to 3.34 SUPPLIER OF SHELTER EQUIPMENT | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
5.0.4 | Vgradnja bivalne, sanitarne in pomožne opreme - pozicije od 4.01 do 4.16 DOBAVITELJ TEHNIKE IN OPREME ZAKLONIŠČA | Installation of living, sanitary and ancillary equipment - positions 4.01 to 4.16 SUPPLIER OF SHELTER EQUIPMENT | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
5.0.5 | Izdelava navodil za uporabo, servisiranje in vzdrževanje sistema za zračenje in zaklonišča kot celote v zaščitni funkciji (projekt za obratovanje in vzdrževanje - POV) DOBAVITELJ TEHNIKE IN OPREME ZAKLONIŠČA | Preparation of instructions for the use, servicing and maintenance of the ventilation system and the shelter as a whole in its protective function (Operation and Maintenance Project - O&M Project) SUPPLIER OF SHELTER EQUIPMENT | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
5.0.6 | Nastavitve prezračevalnih količin in tlakov sistema za zračenje v zaščitni funkciji zaklonišča DOBAVITELJ TEHNIKE IN OPREME ZAKLONIŠČA | Settings of ventilation volumes and pressures of the ventilation system in the shelter protection function SUPPLIER OF SHELTER EQUIPMENT | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
5.0.7 | Predhodni preizkus celotnega zaklonišča in priprava zaklonišča na tehnični preizkus (za vse izvajalce v zaklonišču - brez izdaje javne listine) DOBAVITELJ TEHNIKE IN OPREME ZAKLONIŠČA | Preliminary test of the entire shelter and preparation of the shelter for the technical test (for all shelter operators - without issuing a public charter) SUPPLIER OF SHELTER EQUIPMENT | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
5.0.8 | Tehnični preizkus zaklonišča kot celote za pridobitev javne listine (potrdila o opravljenem tehničnem preizkusu zaklonišča), kar izvede pooblaščeni zavod POOBLAŠČENI ZAVOD | Technical test of the shelter as a whole to obtain a public document (certificate of completion of the technical test of the shelter), carried out by an approved institute AUTHORISED INSTITUTION | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
5.0.9 | Izdelava elaborata o preureditvi zaklonišča iz funkcije za drugi namen v zaščitno funkcijo DOBAVITELJ TEHNIKE IN OPREME ZAKLONIŠČA | Preparation of a study on the conversion of a shelter from a function for another purpose to a protective function SUPPLIER OF SHELTER EQUIPMENT | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
5.0.10 | Dobava, nastavitev in izpolnitev knjige vzdrževanja z začetnimi podatki DOBAVITELJ TEHNIKE IN OPREME ZAKLONIŠČA | Supply, setup and completion of the maintenance book with initial data SUPPLIER OF SHELTER EQUIPMENT | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
5.0.11 | Seznanitev predstavnika uporabnika z načini uporabe in vzdrževanja zaklonišča DOBAVITELJ TEHNIKE IN OPREME ZAKLONIŠČA | Briefing the user representative on how to use and maintain the shelter SUPPLIER OF SHELTER EQUIPMENT | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
5.0.12 | Izdelava posnetka in projekta izvedenih del za zaklonišče v obsegu dobave in del po tem popisu (PID) DOBAVITELJ TEHNIKE IN OPREME ZAKLONIŠČA | Preparation of a survey and design of the works to be carried out for the shelter to the extent of the supply and the works according to this Inventory (PID) SUPPLIER OF SHELTER EQUIPMENT | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
5.0.13 | Kompletiranje vse potrebne in spremljajoče dokazne dokumentacije (certifikati, izjave o skladnosti, navodila, garancijski listi, poročila in zapisniki o meritvah, itd.) v obsegu dobave in del po tem popisu DOBAVITELJ TEHNIKE IN OPREME ZAKLONIŠČA | Completion of all necessary and accompanying supporting documentation (certificates, declarations of conformity, instructions, warranty certificates, reports and records of measurements, etc.) within the scope of the supply and the works according to this Inventory SUPPLIER OF SHELTER EQUIPMENT | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
5.0.14 | Sodelovanje na operativnih sestankih na gradbišču DOBAVITELJ TEHNIKE IN OPREME ZAKLONIŠČA | Participation in operational meetings on site SUPPLIER OF SHELTER EQUIPMENT | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
5.0.15 | Stroški transporta, souporabe pomožnih objektov, napeljav in zavarovanja na gradbišču DOBAVITELJ TEHNIKE IN OPREME ZAKLONIŠČA | Costs of transport, sharing of ancillary facilities, installations and on-site insurance SUPPLIER OF SHELTER EQUIPMENT | kpl | 1 | Že zajeto v cenah 1.0 do 4.0
| VGRADNJA NAPRAV, NAPELJAV IN OPREME TER OSTALE DEJAVNOSTI | INSTALLATION OF PLANT, FIXTURES AND FITTINGS AND OTHER ACTIVITIES |  |  | Skupni znesek pozicij te točke mora biti zajet v enotnih cenah posameznih pozicij točk od 1.0 do 4.0!