## 0_Naslovnica
OPOZORILO! Vsi prevodi v angleščino so strojno izdelani in zgolj informativne narave. V primeru kakršnekoli nejasnosti ali dvoma izključno velja izvirno besedilo v slovenščini. WARNING! All translations into English have been produced by machine translation and are provided for informational purposes only. In the event of any ambiguity or uncertainty, the original Slovenian text shall prevail exclusively.
| / | / | [5 empty] | /
| Sprem./Rev.: | Opis spremembe/Description of Changes: | [5 empty] | Datum/Date: | Podpis/Signature:
| Investitor/Investor: |  |  |  |  | Gradnja/Facility
|  |  | Univerza v Ljubljani Kongresni trg 12 1000 Ljubljana, Slovenija |  |  | Fakulteta za strojništvo/Faculty of Mechanical Engineering
| Projektant/Design Engineer: |  |  |  |  | Del objekta/sistem/Building/System:
|  |  | IBE, svetovanje, projektiranje in inženiring Ljubljana, Slovenija |  |  | STAVBA FAKULTETE/FACULTY BUILDING
| Projektant/Design Engineer: |  |  |  |  | Vrsta načrta/Documentation:
4 NAČRT S PODROČJA STROJNIŠTVA/ DOC. IN THE FIELD OF MECHANICAL ENGINEERING
|  | Ime in priimek/Name and Surname: |  |  | Id. št./Id. No: | Vsebina risbe (dokumenta)/Document Title:
| Vodja proj./ Des. Manager: | Boštjan Vuga, univ. dipl. inž. arh., grad. dip. (AA) |  |  | ZAPS 0035 PA PPN | PR. POPIS STROJNIH DEL/BOQ OF MECH. WORKS 4/4 Prezr. in klima. ped. in ostalih prostorov/ Vent. and Air Cond. of Educat. and Other Rooms
| Poobl. strok./ Cert. Profess.: | Veđi Husić univ. dipl. inž. str. |  |  | IZS S-1591
| Poobl. strok./ Cert. Profess.: |  |  |  |  | Št. proj./ Proj. No.: | 362-19 |  | Vrsta dokument./ Document. Type: | DZR
| Izdelal/ Creator: | Veđi Husić univ. dipl. inž. str. |  |  | IZS S-1591 | Klas. ozn./ Class. No.: | -- |  | Stran/ Page: | 1/*
| Datum/ Date: | maj/May 2026 |  | Merilo/ Scale: | / | Ident. ozn./ Id. No: | JULFS--6S0402P

## 0_Osebe
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
POOBLAŠČENI STROKOVNJAKI, ODGOVORNI ZA IZDELAVO PROJEKTANTSKEGA POPISA:
Id. št. ZAPS/IZS | Pooblaščeni strokovnjak | Strokovno področje
IZS S-1591 | Veđi Husić univ. dipl. inž. str. | Prezračevanje in klimatizacija pedagoških in ostalih prostorov
SODELAVCI PRI IZDELAVI PROJEKTANTSKEGA POPISA:
CERTIFIED EXPERTS RESPONSIBLE FOR ELABORATING THE BILL OF QUANTITIES:
Id. No ZAPS/IZS | Certified Expert | Area of Expertise
IZS S-1591 | Veđi Husić univ. dipl. inž. str. | Ventilation and air-conditioning of teaching and other areas
COLABORATORS IN THE ELABORATING THE BILL OF QUANTITIES:

## 0.1_Uvod-STP
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
0.1 | SPLOŠNI TEHNIČNI POGOJI | GENERAL TECHNICAL CONDITIONS
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic operator with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
0.1.1 | Izvajalec se obveže, da bo upošteval veljavno zakonodajo, ki ureja graditev objektov v Republiki Sloveniji, vključno s povezanimi podzakonskimi akti, predpisi, tehničnimi smernicami, standardi, pravili stroke in dobro gradbeno prakso. Prav tako mora izvajalec upoštevati vse zahteve izdanega integralnega gradbenega dovoljenja in vsa dela izvesti skladno s projektno dokumentacijo ter ostalimi pogoji, objavljenimi v razpisni dokumentaciji. | The Contractor undertakes to comply with the applicable legislation governing the construction of buildings in the Republic of Slovenia, including related by-laws, regulations, technical guidelines, standards, professional rules and good construction practice. The Contractor shall also comply with all the requirements of the integral building permit issued and shall carry out all works in accordance with the project documentation and other conditions published in the tender documentation.
0.1.2 | Dela lahko izvaja samo izvajalec, ki je registriran za opravljanje gradbene dejavnosti in ima za tovrstna dela ustrezno zavarovanje za škodo, certifikate, tehnično izobražen kader, sredstva ter je usposobljen za samostojno pripravo in izvedbo del. | The work may only be carried out by a contractor who is registered to carry out construction work and who has the appropriate insurance for such work, certificates, technically trained staff, resources and is qualified to prepare and carry out the work independently.
0.1.3 | Izvajalec odgovarja za kakovost izvedbe vseh del. | The Contractor shall be responsible for the quality of the execution of all works.
0.1.4 | Izvajalec nosi vso odgovornost za nesreče in škodo, ki nastane na objektu ali v okolici zaradi njegovega dela. | The Contractor shall bear all liability for accidents and damage to the installation or the surrounding area caused by his work.
0.1.5 | Pred oddajo ponudbe se je izvajalec dolžan seznaniti z območjem predvidenim za gradnjo in temu prilagoditi vsa potrebna dela, kar mora biti zajeto v ponudbi. V neposredni bližini predvidene gradnje se nahajajo stavbe, v katerih potekajo izobraževalni in raziskovalni procesi. Zato bo izvajalec moral izvajati kontrolo hrupa in kontrolo vibracij. Dela, ki so hrupna in dela, ki povzročajo vibracije bo izvajalec moral preprečiti oziroma jih izvesti na način, da povzročajo minimalne vplive. Tehnologijo rušenja, pilotiranja in tehnologijo izvedbe ostalih del bo izvajalec moral prilagoditi tako, da bo vpliv minimalen. Izvajalec mora preprečiti in zmanjšati emisije delcev iz gradbišča na najmanjšo možno mero. | Before submitting a tender, the contractor is obliged to familiarise himself with the area to be constructed and to adapt any necessary works accordingly, which must be included in the tender. In the immediate vicinity of the proposed construction, there are buildings in which educational and research processes take place. The contractor will therefore be required to carry out noise and vibration control. Noise and vibration works will have to be avoided or carried out in such a way as to minimise the impact. Demolition, piling and other works will have to be adapted to minimise the impact. The contractor must avoid and minimise the emission of particulates emitted from the construction site as far as is reasonably practicable.
0.1.6 | Izvajalec je pred oddajo ponudbe dolžan pregledati projektno dokumentacijo in ostale pogoje, ki so del razpisne dokumentacije V primeru morebitnih napak in neskladij je izvajalec dolžan na to opozoriti naročnika pred oddajo ponudbe. | The Contractor is obliged to review the project documentation and other conditions forming part of the tender documentation before submitting the tender In case of any errors or inconsistencies, the Contractor is obliged to bring these to the attention of the Contracting Authority before submitting the tender.
0.1.7 | Pred oddajo ponudbe je izvajalec dolžan preveriti ustreznost popisov del in količin v teh popisih ter njihovo skladnost z ostalimi dokumenti projektne dokumentacije, ki so del razpisne dokumentacije. Prav tako je izvajalec dolžan preveriti vse detajle in sheme. Vse izmere je potrebno preveriti po posameznih projektih oz. načrtih, ki sestavljajo razpisno dokumentacijo. V primeru ugotovljenih neskladij je v času priprave ponudbe obvezan o tem obvestiti naročnika. | Before submitting a tender, the Contractor shall check the adequacy of the inventories of works and quantities in these Bills of Quantities and their conformity with the other documents of the project documentation forming part of the tender documentation. The Contractor shall also check all details and diagrams. All measurements shall be checked against the individual projects or plans forming part of the tender documentation. In the event of any discrepancies, the Contractor shall inform the Contracting Authority at the time of preparing the tender.
0.1.8 | Pred oddajo ponudbe je izvajalec dolžan v tem popisu preveriti zmnožke in seštevke ter prenose le-teh v rekapitulacijo. Izvajalec se s pripravo ponudbe obvezuje, da je prebral vse celice in elemente celotnega popisa, vključno z vsemi postavkami in splošnimi navodili ali določili in je preveril pravilnost preračuna ter s tem zagotavlja ponudbeno vrednost. | Before submitting a tender, the Contractor is required to check the products and totals in this Bill of Quantities (BoQ) and their transfer to the recapitulation. The Contractor undertakes, by preparing a tender, to have read all the cells and elements of the complete BoQ, including all headings and general instructions or provisions, and to have checked the correctness of the conversion, thereby guaranteeing the value of the tender.
0.1.9 | Dela bo izvajalec moral izvajati po predloženi projektni dokumentaciji, detajlih in z upoštevanjem navodil in potrditev projektanta, nadzornika in investitorja. Vso potrebno delavniško dokumentacijo zagotovi izvajalec del v okviru ponujene cene. | The Contractor shall carry out the works in accordance with the submitted design documents, details and subject to the instructions and approvals of the Designer, the Supervisor and the Investor. All necessary workshop documentation shall be provided by the Contractor within the scope of the price quoted.
0.1.10 | Pred izvedbo posameznih del je izvajalec dolžan pregledati projektno dokumentacijo za izvedbo gradnje (PZI) in elaborate. Na morebitne napake v dokumentaciji ali neskladja med posameznimi načrti ali deli načrtov (popisi del, tehnična poročila, lokacijski in tehnični prikazi) izvajalec opozori nadzornika in projektanta, in se z njima pravočasno uskladi. | The Contractor shall review the Detailed Design documentation (PZI) and the studies before carrying out the individual works. The Contractor shall draw the attention of the Supervisor and the Designer to any errors in the documentation or discrepancies between the individual designs or parts of designs (BoQ, technical reports, location and technical drawings) and shall coordinate with them in good time.
0.1.11 | Tehnični opisi, prikazi, detajli, sheme ter ostali dokumenti v PZI dokumentaciji predstavljajo dodaten opis popisnih postavk gradbeno obrtniških in inštalacijskih del ter jih je potrebno dosledno upoštevati skupaj s popisom del. | The technical descriptions, illustrations, details, diagrams and other documents in the Detailed Design documentation (PZI) are additional descriptions of the BoQ inventory items of the building, construction and installation works and must be strictly followed together with the BoQ.
0.1.12 | Specifikacije in zahteve, navedene v popisu, se ne smejo upoštevati kot edine zahteve. Izvajalec je dolžan v ceni zajeti in dobaviti vse elemente opreme ter opraviti dela in storitve, ki niso eksplicitno navedeni, a so bistvenega pomena za funkcionalnost, skladnost s predpisi ter kontinuirano, zanesljivo in varno obratovanje opreme. | The specifications and requirements set out in the BoQ shall not be taken as the only requirements. The Contractor shall be obliged to include in the price and supply all items of equipment and to carry out works and services which are not expressly mentioned but which are essential for the functionality, regulatory compliance and continuous, reliable and safe operation of the equipment.
0.1.13 | Vsa dela morajo biti izvedena kvalitetno in iz materialov z zahtevanimi lastnostmi, izvedena skladno z veljavno zakonodajo in z upoštevanjem navodil za vgradnjo za izbrane materiale in opremo, s predložitvijo predpisanih izjav o lastnostih in/ali certifikatov. Vsi gradbeni proizvodi (GP) morajo biti označeni s CE oznako. | All work shall be of good quality and be executed with materials of the required characteristics, in accordance with the applicable legislation and in compliance with the installation instructions for the materials and equipment selected, and shall be accompanied by the prescribed declarations of performance and/or certificates. All construction products (GP) shall bear the CE marking.
0.1.14 | Za vsako opisano delo v popisu je potrebno upoštevati celotno potrebno delo, ves osnovni in pomožni material, prevoz materiala in orodja na objekt, notranje transporte, delovne in pomožne odre, zaključno čiščenje in odstranitev odpadkov po dovršenem delu. | For each work described in the inventory, the total work required, all basic and ancillary materials, the transport of materials and tools to the site, internal transports, working and ancillary scaffolding, final cleaning and the disposal of waste after the work has been completed must be taken into account.
0.1.15 | Vsa delovna sredstva, organizacija in koordinacija del, pripravljalna, spremljajoča in zaključna dela, potrebni montažni in tesnilni materiali ter podkonstrukcije so sestavni del posameznih postavk. | All labour, organisation and coordination of the works, preparatory, accompanying and finishing works, necessary prefabrication and sealing materials and substructures are part of the individual items.
0.1.16 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - načrt organizacije gradbišča s podrobnim terminskim planom in izvedba vseh pripravljalnih del, postavitev, organizacija, zaščita in prijava gradbišča, gradbiščnih objektov, ureditev začasnih deponij, tekoče vzdrževanje, skupaj s plačilom splošnih stroškov pristojbin in davkov upravnih organov, pridobivanju raznih dovoljenj in soglasij za izvedbo, ograditev gradbišča in postavitev gradbene table in prometne signalizacije, zagotavljanje ustrezne varnosti na gradbišču, tekoče vzdrževanje in končna odstranitev gradbišča; - zagotovitev potrebnih začasnih površin za transportne poti in gradnjo izven območja gradbišča s plačilom stroškov za sanacijo in vzpostavitev okoliških zemljišč in objektov v prvotno stanje (soglasja, odškodnine, itd.); - začasni odvoz, deponiranje in vračanje izkopanega materiala, ki ga ne bo možno deponirati na gradbišču; - odvoz in zagotovitev odstranjevanja odpadnega gradbenega materiala skladno z zakonodajo na področju ravnanja z odpadki (odvoz na urejene deponije s plačilom komunalnih prispevkov in taks itd.); - oteženi izkop v mokrem terenu, izkop v vodi, odvod meteorne vode iz gradbene jame in vode, ki se izceja iz bočnih strani izkopov; - ustrezno varovanje izkopa gradbene jame za objekt in ostalih manjših posameznih izkopov za izvedbo komunalne infrastrukture brez posegov na sosednja zemljišča; - ustrezno varovanje obstoječih objektov, infrastrukture in okolice v času gradnje ter dokumentiranje vseh morebitnih škodnih dogodkov; - pripravljalna, spremljajoča in zaključna dela (zakoličbe, zagotovitev potrebnih komunalnih priključkov za potrebe izvajanja gradnje, izvedba začasnih inštalacij, označevanje podzemnih vodov, postavljanje in vzdrževanje zakoličbenih profilov, izvedba in označevanje novih in starih križanj ter morebitna zaščita križanj komunalnih vodov, geodetski posnetki in izdajanje vmesnih posnetkov izvedene infrastrukture naročniku, izdelava zbirnih kart, itd.), v kolikor ni to drugače določeno; - pridobivanje soglasij in izvedba morebitnih zapor na vseh cestah s plačilom stroškov, nadomestil in pristojbin; - zagotovitev oz. postavitev in končna odstranitev po zaključku gradnje začasnih skladišč in začasnega pisarniškega kontejnerskega objekta vključno z opremo za dve delovni mesti in za skupne operativne sestanke vel. ca. 40 m2 za potrebe naročnika, s tekočim vzdrževanjem in čiščenjem. | The following must also be included or taken into account in the uniform prices for individual items: - a construction site organisation plan with a detailed timetable and the execution of all preparatory works, the setting-up, organisation, protection and registration of the construction site, site facilities, the arrangement of temporary storage facilities, ongoing maintenance, including the payment of general costs of fees and taxes of the administrative authorities, the obtaining of various permits and consents for the execution, the fencing of the site and the erection of construction signs and traffic signals, the provision of adequate security on the site, ongoing maintenance and the final dismantling of the construction site; - provision of the necessary temporary areas for transport routes and off-site construction, with costs for restoration and reinstatement of surrounding land and buildings (consents, compensation, etc.); - temporary removal, storage and return of excavated material that cannot be stored on site; - removing and disposing of waste building materials in accordance with waste management legislation (removal to regulated landfill sites with payment of municipal fees and charges, etc.); - difficult excavation in wet ground, excavation in water, drainage of rainwater from the construction pit and water draining from the sides of excavations; - adequate protection of the excavation of the construction pit for the building and other small individual excavations for the implementation of the utility infrastructure without encroaching on neighbouring land; - adequate protection of existing facilities, infrastructure and the surrounding area during construction, and documentation of any damage incidents; - preparatory, accompanying and finishing works (stake-out, provision of the necessary utility connections for the needs of construction, execution of temporary installations, marking of underground lines, installation and maintenance of stake-out profiles, execution and marking of new and old crossings and possible protection of crossings of utility lines, geodetic surveys and issuing of intermediate images of the completed infrastructure to the client, production of summary maps, etc.), unless otherwise specified; - obtaining consents and implementing any road closures, with costs, compensation and fees; - provision or erection and final removal on completion of construction of temporary storage and temporary office container building including equipment for two workstations and for joint operational meetings of approx. 40 m2 for the needs of the client, with ongoing maintenance and cleaning.
0.1.17 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - izdelava montažne tehnične dokumentacije, detajlov izvedbe in vse druge potrebne delavniške dokumentacije (s področja arhitekture, gradbeništva, elektrotehnike, strojništva in zunanje ter krajinske ureditve) ter pridobitev obvezne potrditve s strani projektanta, nadzornika in investitorja; - odprava vseh vrst inštalacijskih kolizij z izvajanjem potrebnih premikov inštalacij in njihovim usklajevanjem na mestu montaže, vse v obsegu, ki ne vpliva na projektirano rešitev ali tip inštalacij oz. opreme; - zagotavljanje kompletnosti elektro-instalacijskih sistemov s področja avtomatike za doseganje njihove popolne funkcionalnosti delovanja; - stroški za nadzor in koordinacijo izvedbe vseh elektro napeljav, ki so predmet končne instalacije proizvoda (senčila, vrata, okna,…); - izdelava montažnih skic in detajlov za izvedbo v dogovoru z vodjo gradnje in nadzornikom; - izdelava in predstavitev vzorcev v ustrezni velikosti za potrditev projektanta, nadzornika in investitorja; - zagotavljanje varnosti in zdravja pri delu, zlasti izvajanje vseh del, ki izhajajo in ukrepov, ki izhajajo iz določil veljavnih predpisov varstva pri delu in zahtev Varnostnega načrta;- stroški garancij, ki jih mora izvajalec predložiti naročniku. | The following must also be included or taken into account in the uniform prices for individual items: - preparation of prefabricated technical documentation, construction details and all other necessary workshop documentation (architectural, civil, electrical, mechanical, exterior and landscaping) and obtaining the mandatory approval of the designer, the supervisor and the investor; - elimination of all types of installation conflicts by carrying out the necessary relocation of installations and their coordination at the installation site, all to the extent that it does not affect the design solution or the type of installation or equipment; - ensuring the completeness of electrical installation systems in the automation sector to achieve their full operational functionality; - the cost of supervising and coordinating the installation of all the electrical installations that are the subject of the final installation of the product (blinds, doors, windows, etc.); - preparation of erection drawings and details for implementation in agreement with the construction manager and supervisor; - production and presentation of samples in appropriate sizes for the approval of the designer, the supervisor and the investor; - ensuring health and safety at work, in particular the implementation of all the works arising from and the measures resulting from the provisions of the applicable occupational safety regulations and the requirements of the Safety Plan; - the cost of the guarantees to be provided by the contractor to the client.
0.1.18 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - strošek vodje del glavnega izvajalca, ki bo izvajal tudi koordinacijo s podizvajalci in z drugimi izvajalci, ki jih bo izbral naročnik in bo opravljal delo vodje gradbišča; - koordinacija del z ostalimi izvajalci oz. podizvajalci del, projektantom, nadzornikom in investitorjem pri medsebojnem usklajevanju organizacije gradbišča in časovnega načrta del ter pri usklajevanju izdelave plana montaže, potrjenih s strani vseh udeležencev gradnje; - stroški koordinacije, sodelovanja in usklajevanja z dobavitelji tehnološke, laboratorijske, eksperimentalne in vse ostale pohištvene ter multimedijske opreme ter z vsemi ostalimi dobavitelji oz. podizvajalci na objektu; - stroški izdelave situacij; - stroški zavarovanja objekta v času izvedbe del in delavcev ter materiala na gradbišču v času izvajanja del, od začetka del do pridobitve uporabnega dovoljenja za objekt. Zavarovanje mora biti sklenjeno pri ustrezni zavarovalni družbi najmanj v višini pogodbene vrednosti ali v zakonsko predpisani vrednosti (v kolikor zavarovanje v višini pogodbene vrednosti presega zakonsko dovoljeno), za ves čas trajanja izvedbe del do uspešne primopredaje objekta; - preizkušanje kvalitete materiala, ki se vgrajuje in dokazovanje kvalitete s certifikati oz. tehničnimi soglasji; - izvedba vseh zahtevanih testov in preizkusov (npr. tlačni preizkusi, termografski pregledi, meritve elektromagnetnega sevanja, hrupa, itd.), poskusnega obratovanja celotnega objekta s poudarkom na vseh inštalacijah ter izvajanje predpisanega monitoringa v skladu s Poročilom o vplivih na okolje (pred gradnjo, med gradnjo in po končani gradnji); - izdelava izkaza požarne varnosti, vključno s sprotnim spremljanjem gradnje in izvajanjem požarnovarnostnih zahtev ter izdelava Požarnega reda z obveznimi prilogami; - izdelava Izkaza zaščite pred hrupom v stavbah; - izdelava Izkaza energijskih lastnosti stavbe in energetske izkaznice; - sodelovanje z izvajalci gradbenega in projektantskega nadzora in investitorjem za izvedbo tehničnega pregleda in priprava primopredaje, ki mora vsebovati vso zahtevano dokumentacijo, predvsem pa: izjave o skladnosti, požarni izkaz in ostale izkaze ter obvezne tabele, dokazilo o zanesljivosti objekta (DZO), certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo in vzdrževanje ter vse ostale dokumente v skladu s predpisi in pogodbenimi določili. | The following must also be included or taken into account in the uniform prices of the individual items: - the cost of a works manager for the main contractor, who will also coordinate with subcontractors and other contractors selected by the client and act as site manager; - coordination of the works with other contractors or subcontractors, the designer, the supervisor and the investor in coordinating the organisation of the construction site and the timetable for the works, and in coordinating the production of an installation plan approved by all the participants in the construction; - the costs of coordination, cooperation and coordination with suppliers of technological, laboratory, experimental and all other furniture and multimedia equipment, as well as with all other suppliers or subcontractors on the site; - the cost of drawing up situations; - the cost of insuring the building during the execution of the works and the workers and materials on site during the execution of the works, from the start of the works until the building has been licensed for occupation. The insurance must be taken out with a suitable insurance company for at least the contract value or the legal value (if the insurance for the contract value exceeds the legal value), for the entire duration of the works until the successful handover of the building; - testing the quality of the material to be installed and proving it with certificates or technical approvals; - carrying out all required tests and trials (e.g. pressure tests, thermographic inspections, electromagnetic radiation measurements, noise measurements, etc.), trial operation of the entire building, with emphasis on all installations, and carrying out the required monitoring in accordance with the Environmental Impact Assessment Report (before, during and after construction); - preparation of a fire safety statement, including ongoing monitoring of construction and implementation of fire safety requirements, and preparation of a Fire Safety Order with mandatory annexes; - preparation of a Noise Protection Statement for buildings; - preparation of the Building Energy Performance Report and Energy Performance Certificate; - cooperation with the construction and design supervision contractors and the investor to carry out the technical inspection and prepare the handover, which must include all the required documentation, in particular: declarations of conformity, fire and other statements and mandatory tables, proof of reliability of the building (DZO), certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use and maintenance, and all other documents in accordance with the regulations and the contractual provisions.
0.1.19 | V enotnih cenah posameznih postavk, ki se nanašajo na opremo in posamezne sisteme, mora biti zajeto oz. upoštevano tudi naslednje: - dobava oz. transport, - stroški za vse delovne stroje za dvigovanje bremen in delovne košare za dostope do delovišč; - morebitni stroški povzročeni upravljavcem GJI, ki bi nastali v zvezi s predmetno gradnjo; - montaža, vključno s pomožnim montažnim materialom (vezni, tesnilni in pritrdilni material, sidra, nosilni profili, podkonstrukcije in podobno) in navodili proizvajalca, - odprava vseh kolizij sistemov s stenami in med sistemi, - izvedba vseh potrebnih tesnjenj, - priključitev in nastavitve, vključno z morebitnim kalibriranjem, - zagon, testiranje in meritve, vključno s poročili, - šolanje uporabnikov oz. vzdrževalnega osebja za uporabo in vzdrževanje sistemov, - navodila za obratovanje in vzdrževanje, - vsi potrebni certifikati, izjave o skladnosti oz. potrdila ter - vsa druga pomožna dela in material, da se zagotovi funkcionalnost posamezne postavke popisa. | The following must also be included or taken into account in the uniform prices for individual items relating to equipment and individual systems: - delivery/transport, - the cost of all lifting machines and work baskets for access to work sites; - any costs incurred to the operators of utility infrastructure (GJI) in connection with the subject construction; - installation, including ancillary installation materials (bonding, sealing and fixing materials, anchors, support profiles, substructures, etc.) and manufacturer's instructions, - eliminating all system-to-wall and system-to-system collisions, - all necessary sealing work, - connection and set-up, including calibration if necessary, - commissioning, testing and measurements, including reports, - training users or maintenance staff in the use and maintenance of the systems, - operating and maintenance instructions, - any necessary certificates, declarations of conformity or attestations; and - all other ancillary works and materials to ensure the functionality of each inventory item.
0.1.20 | Vsi odri morajo biti upoštevani v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All scaffolding must be included in the uniform prices of the items listed, except where specifically mentioned.
0.1.21 | Vsi delovni in pomožni odri, lestve in ostala potrebna pomožna sredstva, kot tudi čiščenje vseh elementov po končanih delih, mora biti upoštevano v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All working and auxiliary scaffolding, ladders and other necessary ancillaries, as well as the cleaning of all elements after completion of the works, shall be included in the uniform prices of the items listed, except those specifically mentioned.
0.1.22 | Delavniško dokumentacijo za vse nosilne jeklene konstrukcije in podkonstrukcije izdela izvajalec, strošek izdelave delavniške dokumentacije se upošteva v ponujenih cenah in se ne obračuna posebej. | The cost of the shop drawings for all steelwork and substructures shall be included in the prices quoted and shall not be charged separately.
0.1.23 | V enotnih cenah postavk mora biti vključeno tudi vgrajevanje vseh instalacijskih razvodov v opaže armirano betonskih elementov in izdelava prehodov inštalacij ter dodatno izrezovanje utorov in prebojev v kamnite, zidane ali armirano-betonske stene, ponovno demontiranje in montiranje vseh vrst montažnih sten, vsa dodatna dela za zagotavljanje primernih križanj med posameznimi instalacijskimi vodi, izdelava vseh vrst ojačitev konstrukcij in podobna dela, ki zagotavljajo kakovostno vgradnjo vseh vrst instalacijskih vodov in niso posebej navedena v popisu GOI del. V ponudbi morajo biti upoštevana vsa drobna strojna in elektro instalacijska dela in transporti. | The installation of all installation ducts in the formwork of reinforced concrete elements and the construction of installation penetrations, as well as the additional cutting of grooves and penetrations in stone, masonry or reinforced concrete walls, the reassembly and reinstallation of all types of prefabricated walls, all additional work to ensure adequate crossings between individual installation ducts, the construction of all types of structural reinforcement and similar work to ensure the quality installation of all types of installation ducts and not specifically mentioned in the BoQ of the Construction, installation and finishing works (GOI) shall also be included in the uniform prices of the items. The tender shall take into account all minor mechanical and electrical installation work and transport.
0.1.24 | Vsi kovinski elementi in konstrukcije, ki bi lahko bili izpostavljeni atmosferskim in ostalim korozijskim vplivom, morajo biti ustrezno protikorozijsko zaščiteni. | All metallic elements and structures that could be exposed to atmospheric and other corrosive influences must be adequately protected against corrosion.
0.1.25 | Za vse večje jeklene dele se skladno s predpisi, izdelajo ustrezne ozemljitve, nevidno pritrjene in speljane na splošno ozemljitev objekta. | For all major steel parts, appropriate earth connections shall be made in accordance with the regulations, invisibly attached and connected to the general earth of the building.
0.1.26 | Za vse vidne elemente in serijske elemente je obvezna predhodna uskladitev obdelav, barv in materialov s projektantom na podlagi dostavljenih vzorcev v ustrezni velikosti. Obvezna je preveritev dejanskih mer na licu mesta in posledična prilagoditev elementov in njihove montaže. | For all visible elements and serial elements, it is mandatory to coordinate the finishes, colours and materials with the designer beforehand on the basis of the supplied samples in the appropriate size. It is mandatory to check the actual dimensions on site and to adjust the elements and their installation accordingly.
0.1.27 | Dimenzije obrtniških izdelkov in količine je potrebno pred naročanjem preveriti na objektu. Potrebna je uskladitev vseh elementov (kljuke, okovje, detajlne konstrukcije in obdelave, itd.) s projektantom, nadzornikom in investitorjem. Izvajalec je dolžan pred izdelavo predložiti projektantu v potrditev ustrezne delavniške načrte in detajle. | The dimensions of the workmanship and quantities must be checked on site before ordering. All elements (hooks, fittings, detailed construction and finishes, etc.) must be coordinated with the designer, the supervisor and the investor. The contractor is obliged to submit the relevant workshop plans and details to the designer for approval before manufacture.
0.1.28 | V posameznih postavkah popisa so navedeni proizvajalci in/ali tipi posameznih sistemov, materialov ali opreme, s čimer so zgolj natančno opredeljene zahtevane tehnične lastnosti. Izvajalec del lahko ponudi nadomesten sistem, material ali opremo drugega proizvajalca in tipa, pri čemer morajo biti tehnične lastnosti ponujenega sistema, materiala ali opreme enakovredne ali boljše od opredeljenih v popisu, dimenzijsko pa ne smejo presegati projektiranih dimenzij. Vse funkcijske in tehnične karakteristike nadomestnih sistemov, materialov ali opreme mora izvajalec dokazati z ustrezno dokumentacijo. Vse morebitne posledice zaradi spremembe sistemov, materialov ali opreme vključno z morebitnimi spremembami oz. dopolnitvami BIM modelov in projektne dokumentacije, stroškovno in časovno bremenijo izvajalca. | The individual items of the Inventory shall specify the manufacturers and/or types of the individual systems, materials or equipment, thereby merely specifying the required technical characteristics. The Contractor may offer a substitute system, material or equipment of a different manufacturer and type, provided that the technical characteristics of the offered system, material or equipment shall be equivalent to or better than those specified in the BoQ, and shall not exceed the design dimensions. All functional and technical characteristics of the substitute systems, materials or equipment shall be demonstrated by the Contractor with appropriate documentation. Any consequences resulting from changes to systems, materials or equipment, including any changes or additions to the BIM models and project documentation, shall be borne by the Contractor in terms of cost and time.
0.1.29 | Vsako zamenjavo, uporabo in končni izbor nadomestnih sistemov, materialov, proizvodov in opreme morajo obvezno in pravočasno (pred dobavo in vgradnjo) pisno potrditi projektant (vseh sodelujočih strok), nadzornik in investitor. | Any replacement, use and final selection of alternative systems, materials, products and equipment must be approved in writing by the designer (of all disciplines involved), the supervisor and the investor in a timely manner (prior to delivery and installation).
0.1.30 | Izvajalec mora v ponudbeno ceno vključiti tudi: - ves čas gradnje sprotno beleženje sprememb oz. odstopanj od PZI dokumentacije, vključno z izdelavo tekstualnega opisa sprememb, - pripravo podlog na nivoju PZI, ki so potrebne za posodobitev oz. uskladitev BIM modela z izvedenim stanjem (LOD 500) in izdelavo projektne dokumentacije izvedenih del (PID), - mesečno predajanje potrjenih sprememb opreme in materiala, ki vplivajo na BIM model, v formatu IFC, - vzdrževanje in uporabljanje pri izvedbi zadnje veljavne revizije PZI dokumentacije, vključno z dopolnitvami PZI načrtov, ki so nastali zaradi sprememb med gradnjo. | The contractor must also include in the tender price: - keeping a record of changes or deviations from the construction documentation (PZI) throughout construction, including a textual description of the changes, - preparation of the Detailed Design (PZI) level documents required to update or align the BIM model with the as-built condition (LOD 500) and the preparation of the as-built project documentation for the works (PID), - monthly submission of approved equipment and material changes affecting the BIM model in IFC format, - maintenance and use in the execution of the last valid revision of the construction documentation (PZI), including additions to the construction design documentation (PZI) resulting from changes during construction.

## 0.2_Uvod-DGNB
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
0.2 | SPLOŠNI TEHNIČNI POGOJI ZA PODROČJE DGNB CERTIFICIRANJA | GENERAL TECHNICAL CONDITIONS FOR DGNB CERTIFICATION
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic entity with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
| Splošni pogoji za področje DGNB certificiranja predstavljajo dopolnilo splošnim tehničnim pogojem in ne odpravljajo drugih obveznosti in odgovornosti, ki jih ima izvajalec v skladu s predpisi in pogodbo. | The General Conditions for DGNB Certification are complementary to the General Technical Conditions and do not exclude other obligations and responsibilities that the Contractor has under the Regulations and the Contract.
0.2.1 | Izvajalec mora v svojih ponudbah upoštevati, da se bo objekt certificiral v skladu z zahtevami DGNB sistema certificiranja trajnostne gradnje, ter pravočasno (vsaj 60 dni pred vgradnjo posameznega produkta) dostaviti vso ustrezno dokumentacijo za vse v ponudbi zajete materiale, elemente in opremo. Zahtevana je uporaba materialov, elementov ali opreme, ki so okolju in ljudem prijazni, energetsko učinkoviti in obenem ustrezajo zahtevam DGNB sistema. Zahtevan nivo certifikata je: ZLATI CERTIFIKAT | The Contractor shall take into account in its tenders that the building will be certified in accordance with the requirements of the DGNB Sustainable Building Certification Scheme and shall deliver all relevant documentation for all materials, elements and equipment included in the tender in a timely manner (at least 60 days before the installation of each product). The use of materials, elements or equipment that are environmentally and human friendly, energy efficient and at the same time meet the requirements of the DGNB system is required. The required level of certification is: GOLD CERTIFICATE
0.2.2 | Podrobnejši opis DGNB sistema in navodila za posamezne kriterije so dostopna v dokumentu"DGNB Criteria Set New Construction Buildings, Version 2020 International", ki je na voljo na DGNB spletni strani https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria | A more detailed description of the DGNB system and guidance on the individual criteria is available in the document "DGNB Criteria Set New Construction Buildings, Version 2020 International", available on the DGNB website https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria
0.2.3 | Izvajalec mora v svojih ponudbah upoštevati, da je potrebno skladno z določili DGNB certifikacijskega sistema, pravočasno (pred pričetkom gradnje) dostaviti vso ustrezno dokumentacijo, za vse v ponudbi zajete materiale, elemente in opremo (tehnični list, varnostni list, izjava o lastnostih, tehnična navodila za ravnanje, servisiranje, vzdrževanje,...) v slovenskem jeziku. Vgradnja kakršnihkoli materialov, elementov ali opreme, se izvede zgolj na podlagi predhodne preveritve posredovane dokumentacije in obenem potrditve s strani nadzornika. | The Contractor must take into account in its tenders that, in accordance with the provisions of the DGNB certification system, all relevant documentation for all materials, elements and equipment included in the tender (technical data sheet, safety data sheet, declaration of properties, technical instructions for handling, servicing, maintenance,...) must be delivered on time (prior to the start of construction) in the Slovene language (in accordance with the provisions of the DGNB certification system). The installation of any materials, elements or equipment shall be subject to prior checking of the submitted documentation and, at the same time, to the approval of the Supervisor.
0.2.4 | Izbrani materiali, elementi, naprave, sistemi in oprema morajo prispevati k večji trajnosti stavbe v smeri zagotavljanja energetske učinkovitosti, ekonomičnega in enostavnega vzdrževanja ter čiščenja, dolge življenjske dobe, uporabe okolju prijaznih materialov ipd. | The materials, elements, appliances, systems and equipment chosen must contribute to the sustainability of the building in terms of energy efficiency, economic and easy maintenance and cleaning, long lifetime, use of environmentally friendly materials, etc.
0.2.5 | Predloženi dokumenti za vse uporabljene materiale, elemente in opremo morajo izpolnjevati zahteve najmanj kakovostne stopnje QS3 (zaželeno QS4), iz dokumenta: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001) | The documents submitted for all materials, components and equipment used shall meet the requirements of at least quality level QS3 (preferably QS4) of the document DGNB Quality Grades for Materials, Components and Equipment (JULFS--7X9001)
0.2.6 | V kolikor izbrani materiali oz. elementi, navedeni v posameznih postavkah, ne ustrezajo vsaj kakovostni stopnji QS3 iz seznama: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), je izvajalec dolžan na to opozoriti projektanta, nadzor in investitorja ter podati predlog ustreznega materiala oz. elementa. | If the selected materials or elements listed in the individual items do not meet at least quality level QS3 of the list of DGNB quality classes for materials, elements and equipment (JULFS--7X9001), the Contractor shall draw this to the attention of the Designer, the Supervisor and the Investor, and shall make a proposal for a suitable material or element.
0.2.7 | Izvajalec lahko v svoji ponudbi predlaga alternativne produkte in rešitve glede na predvidene s projektom, pod pogojem, da le-te prav tako izpolnjujejo vse navedene zahteve. Pri morebitnih predlaganih alternativnih produktih oz. rešitvah je potrebno upoštevati najmanj enake ali boljše lastnosti v smislu življenjske dobe, obstojnosti, ter enostavnosti in stroška čiščenja ter vzdrževanja v primerjavi s projektom predpisanimi rešitvami. Za alternativne rešitve izvajalec pridobi soglasje projektanta, nadzornika in investitorja pred pričetkom gradnje. | The Contractor may propose alternative products and solutions to those envisaged by the project in its tender, provided that they also meet all the requirements set out above. Any alternative products or solutions proposed shall have at least the same or better characteristics in terms of service life, durability, and ease and cost of cleaning and maintenance compared to the solutions envisaged by the project. For alternative solutions, the contractor shall obtain the agreement of the designer, the supervisor and the investor before starting construction.
0.2.8 | Izvajalec med gradnjo dnevno beleži vsa eventualna odstopanja od PZI projektne dokumentacije ter podatke pravočasno posreduje naročniku, nadzoru in projektantu. Potrjene spremembe vnese v podlage za izdelavo PID in posodobitev BIM modelov. | During construction, the Contractor shall record on a daily basis any deviations from the Detailed Design documentation (PZI) and shall provide the information to the Client, Supervision and the Designer in a timely manner. Confirmed changes shall be entered into the basis for the As-built documentation (PID) and BIM model updates.
0.2.9 | Izvajalec med gradnjo sproti izpolnjuje Seznam vseh konstrukcijskih sestav s pripadajočimi vgrajenimi gradbenimi materiali in dokumentira naslednje podatke o vgrajenih materialih (v slovenskem jeziku): - Varnostni list - Tehnični list - Izjavo o lastnostih (če je relevantno) - Izkazovanje morebiti obstoječega okoljskega certifikata (Tip I - okoljski znak ali Tip III - okoljska produktna deklaracija /EPD) - Izjavo proizvajalca ali dobavitelja, da produkt ustreza zahtevam ENV1.2 - Tehnična navodila za ravnanje, servisiranje, vzdrževanje oziroma ostale, z zakonom predpisane dokumente in dokumentacijo. | During construction, the Contractor shall keep a List of all structural assemblies with their associated construction materials and document the following information on the materials installed (in Slovene language): - Safety Data Sheet - Technical Data Sheet - Declaration of performance (if applicable) - Demonstration of any existing environmental certification (Type I - Ecolabel or Type III - Environmental Product Declaration /EPD) - A declaration by the manufacturer or supplier that the product complies with the requirements of ENV1.2 - Technical instructions for handling, servicing, maintenance or other documents and documentation required by law.
0.2.10 | Za vse vgrajene bistvene tehnične sisteme mora izvajalec zagotoviti obstoj pooblaščenega servisa, ki deluje na območju Republike Slovenije, da ima investitor možnost skleniti ustrezno pogodbo o vzdrževanju. Med bistvene tehnične sisteme sodijo npr.: sistemi ogrevanja in hlajenja, priprava tehnoloških medijev, prezračevanje in klimatizacija, sistemi detekcije in gašenja požara, sistemi tehničnega varovanja, BMS in CNS sistemi upravljanja stavbe, razsvetljava, komunikacijski in WI-FI sistemi,... | For all installed essential technical systems, the contractor must ensure the existence of an authorised service centre operating in the territory of the Republic of Slovenia, so that the investor has the possibility of concluding an appropriate maintenance contract. The essential technical systems include, for example: heating and cooling systems, technological media preparation, ventilation and air conditioning, fire detection and extinguishing systems, technical security systems, BMS and CNS building management systems, lighting, communication and WI-FI systems,...
0.2.11 | Zaželeno je, da imajo uporabljeni elementi in materiali okoljsko oznako Tip I. (kot npr. ENCODE, BLUE ANGEL, ipd...). | It is preferable that the elements and materials used have a Type I environmental label (such as ENCODE, BLUE ANGEL, etc...).
0.2.12 | Izvajalec bo za elemente iz lesa moral dokazovati izvor z navedbo izvorne države in tipa lesa, FSC / PEFC certifikat z dodatnim pripadajočim potrdilom Chain of custody-trgovski certifikat dobavitelja - ta se dokazuje z dobavnicami, računi ali enakovredno. Za izdelke iz naravnega kamna iz EU držav je potrebna deklaracija, da je izvor in procesiranje teh izdelkov v celoti v EU državah. Za izdelke iz naravnega kamna, ki prihajajo iz držav izven EU, je potrebno predložiti dokazilo o izpolnjevanju ILO konvencije 182, ki vključuje neodvisna inšpekcijska poročila. | For wood elements, the contractor will be required to provide proof of origin, indicating the country of origin and the type of wood, FSC/PEFC certification with an additional Chain of Custody certificate - the supplier's trade certificate - this shall be evidenced by delivery notes, invoices or equivalent. For natural stone products from EU countries, a declaration that the sourcing and processing of these products is entirely in EU countries is required. For natural stone products from non-EU countries, proof of compliance with ILO Convention 182, including independent inspection reports, is required.
0.2.13 | Izobraževanje udeležencev pri gradnji Izvajalec je dolžan vse udeležence pri gradnji podrobneje seznaniti tudi z relevantnimi koncepti, študijami, elaborati, ki opredelujejo trajnostni način gradnje za naslednja področja: - zaščita pred hrupom (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)) - zaščita pred prašenjem - zaščita tal in podzemne vode (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)), Analiza tveganja za onesnaženje vodnega telesa podzemne vode št. 0346-023/2023, maj 2023 (Geološko projektiranje d.o.o.)) - ravnanje z gradbenimi odpadki (Načrt gospodarjenja z gradbenimi odpadki) Izobraževanja se izvajajo skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.1 1.2, 2.2, 3.2 in 4.2 Training for the parties implementing the construction work | Training of construction participants The contractor is also obliged to inform all construction participants in detail about relevant concepts, studies, elaborations defining sustainable construction methods for the following areas: - noise protection (Environmental Impact Assessment Report No 100123-11523, dated 11.5.2023, supplemented on 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.)) - dust protection - protection of soil and groundwater (Environmental Impact Assessment Report No. 100123-11523, dated 11.5.2023, supplemented 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.), Risk analysis for contamination of the groundwater No. 0346-023/2023, May 2023 (Geološko projektiranje d.o.o.)) - construction waste management (Construction Waste Management Plan) The training shall be carried out in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.1 1.2, 2.2, 3.2 and 4.2 Training for the parties implementing the construction work
0.2.14 | Navodila za obratovanje in vzdrževanje objekta Izvajalec pripravi Navodila za obratovanje in vzdrževanje objekta skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilih: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual | Instructions for the operation and maintenance of the facility The Contractor shall prepare the Operation and Maintenance Instructions for the Facility in accordance with the applicable Slovenian legislation and the DGNB System Instructions specified in the Criteria: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual
0.2.15 | Meritve kontrole kakovosti gradnje Izvajalec mora upoštevati, da se bodo po koncu gradnje izvedle naslednje meritve: - meritve zrakotesnosti - meritve s termokamero (termografija) - meritve akustike - meritve zvočne zaščite ovoja stavbe - meritve zvočne zaščite ločilnih elementov med posameznimi prostori različnih namembnosti - meritve udarnega zvoka - meritve vlažnosti vgrajenih elementov, pred vgradnjo finalnih tlakov - test odvoda dima in toplote Meritve morajo opraviti ustrezno usposobljeni preskusni organi ali strokovnjaki ter rezultate oceniti in primerjati z zahtevami. Obseg opravljenih meritev mora biti sorazmeren z velikostjo zgradbe in mora ustrezno odražati cilj preverjanja kakovosti zgradbe. Smiselno je, da izvajalec del tekom gradnje za sprotno kontrolo kakovosti vgrajenih materialov, elementov in opreme, sam izvaja meritve. Končne meritve (ob primopredaji) izvede tretja oseba kot neodvisna potrditev doseganja zahtev. Meritve se izvajajo skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 2. Quality control measurements | Construction quality control measurements The contractor must take into account that the following measurements will be carried out after completion of the construction: - airtightness measurements - thermal camera measurements (thermography) - acoustics measurements - measurements of the sound insulation of the building envelope - measurements of the sound insulation of the separating elements between different rooms of different uses - impact sound measurements - moisture measurements of the installed elements, prior to the installation of the final flooring - smoke and heat extraction test The measurements shall be carried out by suitably qualified test bodies or experts and the results evaluated and compared with the requirements. The extent of the measurements carried out shall be proportionate to the size of the building and shall adequately reflect the objective of the building quality verification. It is reasonable for the contractor to carry out his own measurements during construction to check the quality of the materials, elements and equipment installed. Final measurements (at handover) are carried out by a third party as an independent confirmation of compliance with the requirements. The measurements shall be carried out in accordance with the applicable Slovenian legislation and the DGNB system instructions specified in the benchmark: PRO 2.2 2. Quality control measurements
0.2.16 | Zagotavljanje kakovosti za uporabljene gradbene proizvode Izvajalec mora zagotavljati izvajanje primerjav med definiranim in dejansko uporabljenim materialom, elementom ali opremo skladno seznamom: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), vključno z dokazno dokumentacijo ugotovitev primerjav ter skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 3.1 Quality assurance for the used construction products | Quality assurance for the construction products used The Contractor shall ensure that comparisons are made between the defined and the actual material, element or equipment used in accordance with the list: DGNB Quality Grades of Installed Materials, Elements and Equipment (JULFS--7X9001), including supporting documentation of the findings of the comparisons, and in accordance with the DGNB system instructions defined in the Criterion: PRO 2.2 3.1 Quality assurance for the used construction products
0.2.17 | Zaščita pred vlago Izvajalec predloži dokumentacijo, ki dokazuje, da je bil izveden program prezračevanja, prilagojen stavbi, s čimer se zagotovi pogoje, da so vgrajeni gradbeni elementi ustrezno suhi, skladno z navodili DGNB opredeljenimi v merilu: PRO 2.2 4.1 Mould prevention | Protection against moisture The Contractor shall provide documentation demonstrating that a building-specific ventilation programme has been implemented to ensure that the building elements installed are adequately dry, in accordance with the DGNB guidelines specified in the criteria: PRO 2.2 4.1 Mould prevention
0.2.18 | Preizkusi delovanja sistemov Izvajalec sodeluje pri izvedbi predhodnega in končnega preizkusa delovanja vseh bistvenih tehničnih komponent stavbe in pripravi ustrezne dokazne dokumentacije ter pri usposabljanju vzdrževalcev/upravljalcev stavbe, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators | System performance tests The Contractor shall be involved in the performance of the preliminary and final performance tests of all essential technical components of the building and the preparation of the relevant supporting documentation, as well as in the training of the maintenance/management staff of the building, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators
0.2.19 | Poročilo o zagonu objekta Izvajalec sodeluje pri pripravi končnega poročila o zagonu objekta, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 5.1 Creation of a detailed final report | Commissioning report The Contractor shall be involved in the preparation of the final commissioning report, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 5.1 Creation of a detailed final report
0.2.20 | Koncept celovitega delovanja sistemov v stavbi Izvajalec sodeluje pri procesu implementiranja stalnega nadzora in nastavitev delovanja stavbe ter usposabljanju vzdrževalcev/upravljalcev stavbe. Navedeno se izvede v skladu z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 6.1 Creation and handover of an integral operating concept | The concept of integrated building systems The contractor is involved in the process of implementing the building's continuous monitoring and settings and training the building's maintenance/management staff. This shall be done in accordance with the DGNB system instructions defined in the benchmark: PRO 2.3 6.1 Creation and handover of an integral operating concept
0.2.21 | Prilagoditev nastavitev sistemov po začetni fazi uporabe objekta Izvajalec sodeluje pri ponovnem pregledu delovanja vseh bistvenih tehničnih sistemov ter eventualni ponovni prilagoditvi teh sistemov s strani strokovnjaka oz. (neodvisne) tretje osebe. Postopek se izvede po približno 10–14 mesecih po zaključku gradnje, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 7.1 Readjustment of the system following initial operating phase | Adjusting system settings after the initial phase of use of the building The Contractor shall be involved in the re-examination of the functioning of all essential technical systems and the possible re-adjustment of these systems by an expert or (independent) third party. The procedure shall be carried out approximately 10-14 months after completion of construction, in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.3 7.1 Readjustment of the system following initial operating phase

## 0.3_Uvod-STP-HVAC
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
0.3 | SPLOŠNI TEHNIČNI POGOJI ZA PREZRAČEVALNE SISTEME | GENERAL TECHNICAL CONDITIONS FOR VENTILATION SYSTEMS
0.3.1 | Klimatske naprave za dovod in odvod notranje modulne izvedbe | Indoor modular supply and extract air conditioners
| Dobava in montaža klimatov EUROCLIMA, SYSTEMAIR ali OC IMP Klima ali enakovredno po SIST EN 16798-3, CEN/TR 16798-4, SIST EN 13053:2020 in VDI 3803-1:2020, skupaj s fleksibilnimi priključki, gumijastimi protivibracijskimi podložkami, zunanjost jeklena pocinkana pločevina zaščitena z ZnAlMg, notranjost: dno in vodila iz pocinkane pločevine zaščita ZnAlMg Debelina pokrova 50mm, izolacija mineralna volna 100kg/m3. Tesnila na vseh posluževalnih vratih morajo biti izvedena z dvojnim tesnenjem (dvojno prekrivanje). Čelni stiki klimata morajo biti gladki, vse skladno s SIST EN 1886:2008. | Supply and installation of EUROCLIMA, SYSTEMAIR or OC IMP Klima air conditioners or equivalent according to SIST EN 16798-3, CEN/TR 16798-4, SIST EN 13053:2020 and VDI 3803-1:2020, including flexible connectors, rubber anti-vibration washers, exterior galvanised sheet steel protected with ZnAlMg, interior: bottom and guides made of galvanised sheet steel, protected with ZnAlMg, cover thickness 50mm, insulation mineral wool 100kg/m3. Seals on all service doors must be double sealed (double overlapping). The front joints of the air conditioner must be smooth, all in accordance with SIST EN 1886:2008.
| Tesnost klimata mora biti razreda L1 (nadtlak +700Pa in podtlak -400Pa), toplotna izolativnost ohišja panelov razreda T2, faktor toplotnih mostov razreda TB2 in mehanska stabilnost razred D1, vse skladno s SIST EN 1886:2008 in z veljavnim EUROVENT certifikatom. | The airtightness of the climate shall be class L1 (overpressure +700Pa and underpressure -400Pa), the thermal insulation of the panel enclosure shall be class T2, the thermal bridging factor shall be class TB2 and the mechanical stability shall be class D1, all in accordance with SIST EN 1886:2008 and with a valid EUROVENT certificate.
| Korekcijski faktor zunanjega zraka zaradi puščanja skozi enoto za vračanje odpadnega zraka ne sme biti večja od OACF razred 2 po SIST EN 16798-3:2017. | The ambient air correction factor for leakage through the exhaust air return unit shall not be greater than OACF Class 2 according to SIST EN 16798-3:2017.
| Filtri v klimatskih napravah so skladni s SIST EN ISO 16890-1. | Filters in air-conditioning systems shall comply with SIST EN ISO 16890-1.
| Naprava mora biti uvrščena v hitrostni razred max. V3 (max. 1,8-2m/s skozi prosti čelni presek) ali nižje po SIST EN 13053:2020. | The device must be classified in speed class max. V3 (max. 1.8-2m/s through free frontal section) or lower according to SIST EN 13053:2020.
| Učinkovitost mešalnih enot mora biti v razredu min. M2 (ni≥85%) po SIST EN 13053:2020 | The efficiency of the mixing units must be in class M2 (not ≥ 85%) according to SIST EN 13053:2020
| Vrednosti zmanjšanja jakosti zvoka v skladu s standardom SIST EN 1886: | Sound intensity reduction values according to SIST EN 1886:
| -Srednja frekvenca oktave (Hz) 125 250 500 1000 2000 4000 8000 | -Mean octave frequency (Hz) 125 250 500 1000 2000 4000 8000
| Zmanjšanje jakosti zvoka min. R' (dB) 14 13 13 17 25 36 45 | Sound intensity reduction min. R' (dB) 14 13 13 17 25 36 45
| Skladno s standardom SIST EN 13053 mora učinkovitost vračanja odpadne toplote ustrezati razredu H1. Prezračevalna naprava mora biti skladna z ErP 2018. | In accordance with SIST EN 13053, the waste heat recovery efficiency must comply with class H1. The ventilation plant must comply with ErP 2018.
| Razred tesnosti okvirjev filtrov mora ustrezati razredu L1 t.j. minimalno razredu ISO ePM1>80% po VDI 3803:2020. Vse filterne enote morajo biti opremljene s filtri, rezervnim kompletom filtrov ISO Coarse, ePm, presostati za merjenje uporov filtrov, dodatnimi odjemi tlaka za priključitev presostatov. | The tightness class of the filter frames must correspond to class L1, i.e. minimum ISO class ePM1>80% according to VDI 3803:2020.All filter units must be equipped with filters, spare set of ISO Coarse, ePm, presstats for measuring filter resistances, additional pressure taps for connecting the presstats.
| Vrečasti filter s filtracijo ePm mora biti vpet v nosilni okvir z vpenjalnimi vzmetmi. Vrečasti filtri so na voljo v dolžinah (do 600 mm) in so lahko izdelani iz dveh različnih materialov: steklenih ali sintetičnih vlaken, ki so temperaturno obstojna do ≈ 70°C. Točno temperaturno obstojnost določi proizvajalec. Razredi filtrov so predvideni v skladu s standardom SIST EN ISO 16890. Enota s filtrom mora biti opremljena z okvirjem glede na izbiro iz pocinkane jeklene pločevine, nerjavne jeklene pločevine AISI 304 (Hygienik) ali barvane jeklene pločevine. Okvir naj bo tesnjen proti ohišju s trajno elastičnim kitom. Na okvirju naj bo predviden tesnilni trak, na katerega so pritisnjene kasete. Posluževanje filtra za hygienik naprave je obvezno prek prazne enote na »umazani« strani filtra. Enota mora imeti kontrolno okno, svetilko ter stikalo za luč. | The bag filter with ePm filtration shall be clamped in a support frame with clamping springs. Bag filters are available in lengths (up to 600 mm) and can be made of two different materials: glass fibre or synthetic fibre, which are temperature resistant up to ≈ 70°C. The exact temperature resistance is determined by the manufacturer. Filter classes are provided in accordance with SIST EN ISO 16890. The filter unit shall be fitted with a frame made of galvanised steel sheet, stainless steel sheet AISI 304 (Hygienic) or painted steel sheet, depending on the choice. The frame shall be sealed against the casing with a permanently elasticated putty. A sealing strip shall be provided on the frame to which the cassettes are pressed. The filter for the hygienic device must be operated via the empty unit on the 'dirty' side of the filter. The unit shall have a control window, a lamp and a light switch.
| Kasetni filter s filtracijo Coarse ali ePm po SIST EN ISO 16890 je predviden dolžine do 150mm, vgrajen v fiksen okvir iz jeklene pocinkane ali nerjaveče pločevine. Posluževanje filtra za hygienik naprave je obvezno prek prazne enote na »umazani« strani filtra. Enota mora imeti kontrolno okno, svetilko ter stikalo za luč. | A cassette filter with Coarse or ePm filtration according to SIST EN ISO 16890 shall be provided with a length of up to 150 mm, mounted in a fixed frame made of galvanised steel or stainless steel sheet. The filter for the hygienic unit must be operated via the empty unit on the 'dirty' side of the filter. The unit shall be equipped with a control window, a lamp and a light switch.
| Dušilniki zvoka so iz kulis debeline 200 mm in dolžine 750 do1140 mm. Dušilne kulise so postavljene na vodila iz pocinkane pločevine, pritrjena na ohišje. Zvočno izolacijski material kulis je mineralna volna, ki ustreza požarnemu standardu razred A1 po SIST EN 13501-1:2011. Okvir in resonančna pločevina kulis sta izdelana iz pocinkane pločevine. | The silencers shall be made of 200 mm thick and 750 to 140 mm long spheres. The silencers shall be mounted on galvanised sheet metal rails fixed to the enclosure. The sound insulation material of the spheres shall be mineral wool complying with the fire standard class A1 according to SIST EN 13501-1:2011. The frame and the resonant sheet metal of the spheres shall be made of galvanised sheet metal.
| Vodni grelnik je sestavljen iz okvira, lamelnega paketa s cevmi ter zbiralne in razdelilne cevi. Spoj lamel in cevi je izveden z mehanskim ekspandiranjem. Vodni grelnik je v enoti postavljen na vodila iz nerjavne pločevine, pritrjena na ohišje. Zbiralna in razdelilna cev imata navojni priključek. | The water heater shall consist of a frame, a fin package with tubing, a header and a distribution hose. The joint between the fins and the hose shall be made by mechanical expansion. The water heater shall be mounted in the unit on stainless steel guides fixed to the casing. The header and the distribution hose shall have a threaded connection.
| Vodni hladilnik je sestavljen iz okvira, lamelnega paketa s cevmi ter zbiralne in razdelilne cevi. Spoj lamel in cevi je izveden z mehanskim ekspandiranjem. Vodni (glikolni) hladilnik je v enoti postavljen na vodila iz pocinkane pločevine, pritrjena na ohišje. Zbiralna in razdelilna cev imata navojni priključek. Eliminator vodnih kapljic je izdelan iz okvira iz pocinkane pločevine, v katerega so v enakomernem razmaku vstavljene plastične lamele iz polipropilena za lovljenje in izločanje vodnih kapljic. Okvir eliminatorja je izvlačljiv, kar omogoča njegovo redno periodično čiščenje. | The water cooler shall consist of a frame, a louvre package with tubing, and a collection and distribution hose. The joint between the louvres and the hose shall be made by mechanical expansion. The water (glycol) cooler shall be mounted in the unit on galvanised sheet metal rails fixed to the housing. The collection and distribution hose shall have a threaded connection. The water droplet eliminator shall consist of a galvanised sheet metal frame in which plastic polypropylene louvres are inserted at regular intervals to trap and expel the water droplets. The frame of the water droplet eliminator shall be extendable to allow for periodic periodic periodic cleaning of the eliminator.
| Glikolni rekuperator je sestavljen iz okvira, lamelnega paketa, zbiralnih cevi z navojnimi priključki po ISO R7 ter priključki za praznjenje in odzračevanje. Register stoji na vodilih in je prosto izvlečljiv. Pod hladilnikom je banja s tristranskim nagibom za zbiranje in hitrejši odvod kondenzata iz nerjavečega materiala. Z grelnikom je v celoto povezan s cevnim tokokrogom, ki vsebuje obtočno črpalko in vse potrebne elemente kot pr.: ventili, raztezna posoda, varnostni ventil, itd. Cevni tokokrog ni sestavni del naprave. | The glycol recuperator consists of a frame, a lamella pack, collection pipes with threaded connections according to ISO R7 and connections for emptying and venting. The register is mounted on rails and is freely extendable. Under the condenser there is a tank with a three-sided inclination for collecting and faster draining of the condensate made of stainless material. It is connected to the heater as a whole by a piping circuit containing a circulation pump and all the necessary elements such as: valves, expansion tank, safety valve, etc. The piping circuit is not an integral part of the appliance.
| Izvedba hladilnikov/sušilnikov mora biti omejena z višino 1140mm, višji hladilniki morajo imeti izvedbo deljenih hladilnih registrov, skladno z ''ASHRAE Handbook HVAC Systems and equipment'', deljeni morajo biti tudi eliminatorji kapljic zaradi boljšega odvajanja kondenza in lažjega kasnejšega servisiranja. Skladno s VDI 3803 morajo biti izvedena tudi lovilna korita za odvodnjavanje, odtočni priključki kondenzata imajo vsi premer min. Ø40. Višine deljenih registrov so lahko tudi višje - skladno s tehničnimi navodili posameznega proizvajalca! | The design of the chillers/dryers must be limited to a height of 1140mm, taller chillers must have split register design in accordance with the ''ASHRAE Handbook HVAC Systems and equipment'', droplet eliminators must also be split to improve condensate drainage and ease subsequent servicing. Drainage traps must also be fitted in accordance with VDI 3803, condensate drain connections must all be a minimum diameter of Ø40. Heights of the split registers can also be taller - in accordance with the manufacturer's technical instructions!
| Upori na vodni strani za grelnike so lahko do 20kPa, hladilnike do 30kPa in glikol rekuperatorji do 120kPa. | Water-side resistances for heaters can be up to 20kPa, chillers up to 30kPa and glycol recuperators up to 120kPa.
| Toplotni izmenjevalci glikolnih rekuperatorjev (grelniki in hladilniki) so skonstruirani za povečanje protitoka medija in zraka, kar omogoča povečan prenos toplote in višji izkoristek vračanja toplote (High efficiency run around coils). | The heat exchangers (heaters and coolers) of glycol recuperators are designed to increase the counterflow of the medium and air, allowing increased heat transfer and higher heat recovery efficiency (High efficiency run around coils).
| Rekuperativna enota je sestavljena iz ploščnega rekuperatorja, sestavljenega iz vložkov iz ravnih aluminijastih lamel. Rekuperator je v ohišje enote vstavljen diagonalno. Sveži in odpadni zrak se gibljeta skozi rekuperator v križnem toku. Na izstopu odpadnega zraka iz enote je vgrajen eliminator vodnih kapljic, izdelan iz okvira iz pocinkane pločevine, v katerega so v enakomernem razmaku vstavljene plastične lamele iz polipropilena za lovljenje in izločanje vodnih kapljic. Okvir eliminatorja je izvlačljiv, kar omogoča njegovo redno periodično čiščenje. Enota je opremljena z obvodom zraka na strani svežega zraka. Obvod zraka je opremljen s povezanima, protismerno delujočima žaluzijama razreda tesnosti 3 po SIST EN 1751. Za odtok kondenzata sta v enoti na straneh dovodnega in odvodnega zraka nameščeni koriti iz nerjaveče pločevine 1.4301 s priključkom za odtok Ø 40 mm in sifonom. | The recuperative unit shall consist of a plate recuperator composed of inserts of flat aluminium fins. The recuperator shall be inserted diagonally into the unit casing. Fresh and waste air shall move through the recuperator in a cross flow. A water droplet eliminator shall be installed at the outlet of the waste air from the unit and shall consist of a galvanised sheet metal frame in which plastic fins made of polypropylene are inserted at regular intervals to trap and filter out water droplets. The frame of the eliminator is retractable, which allows periodic cleaning. The unit is equipped with an air bypass on the fresh air side. The air bypass is equipped with two connected, counteracting louvres of leakage tightness class 3 according to SIST EN 1751. For condensate drainage, the unit is fitted with 1.4301 stainless steel troughs on the supply and extract air sides with a 40 mm Ø drain connection and a siphon trap.
| Enota za parno vlaženje je prazna komora s posluževalnimi vrati, z banjo z odtokom za zbiranje in odtok kondenzata in z notranjimi površinami iz nerjaveče jeklene pločevine, namenjena vgradnji cevi za distribucijo pare. Enota ima kontrolno okno, svetilko ter stikalo za luč. | The steam humidification unit shall be an empty chamber with a service door, a drain with a drain for the collection and discharge of condensate and stainless steel internal surfaces for the installation of steam distribution pipes. The unit shall have a control window, a lamp and a light switch.
| V enotah je vgrajen kontaktni vlažilnik, izdelan v nerjaveči izvedbi. Izvedba mora biti v izvedbi skladni s VDI 6022/1:2018 in VDI 3803:2020. Vlažilna kaseta kontaktnega vlažilnika debeline min. 200 mm ima visoko sposobnost absorpcije vode in veliko kontaktno površino med tokoma zraka in kaseto. Medij v vlažilni kaseti je samočistljiv, izdelan iz negorljivega materiala in montiran v nerjavečem ohišju. Za odtok vode je v enoti vgrajeno korito iz nerjaveče pločevine 1.4301 s priključkom za odtok Ø 40mm in sifonom. Vlažilnik obratuje v obtočnem načinu (potopna črpalka dovaja izhlapelo količino vode za vlaženje). Kontaktni vlažilnik ima najmanj dve stopnji delovanja z zapiranjem dela kasete preko el. mag. ventila. Dovod vode je izveden preko tovarniško vgrajenega el. mag. ventila ter nivojsko reguliran preko tovarniško vgrajene nivojske sonde. Korito je opremljeno še z el. motornim ventilom za kaluženje sistema preko zaznavala prevodnosti vode (QIC) (izpust vode po 4h ne delovanja). Učinkovitost vlaženja η=ca. 60%. Enota ima kontrolno okno, svetilko ter stikalo za luč. | The units shall be equipped with a contact humidifier, manufactured in stainless steel. The design shall be in accordance with VDI 6022/1:2018 and VDI 3803:2020. The humidifying cassette of the contact humidifier shall have a minimum thickness of 200 mm and shall have a high water absorption capacity and a large contact surface between the air flow and the cassette. The medium in the humidifying cassette shall be self-cleaning, made of flame-retardant material and mounted in a stainless steel casing. For the water outlet, the unit is fitted with a 1.4301 stainless steel trough with a Ø 40 mm outlet connection and a siphon. The humidifier operates in circulation mode (a submersible pump supplies the evaporated water for humidification). The contact humidifier has at least two stages of operation, with the cassette part closing via an electrically operated mag. valve. The water supply is via a factory-fitted electric mag valve and level regulated via a factory-fitted level probe. The trough is also equipped with an electric motorised valve for tempering the system via a water conductivity sensor (QIC) (water discharge after 4 h of non-operation). The humidification efficiency η= approx. 60%. The unit is equipped with a control window, a lamp and a light switch.
| V enoti je nameščen prostotekoči ventilator z nazaj zakrivljenimi lopaticami. Motor ventilatorja je montiran na nosilni plošči, ki je pritrjena na okvir ventilatorja. Rotor ventilatorja je dinamično balansiran po DIN ISO 1940 del 1 - G 2.5. Ventilatorski sklop je montiran na nosilnem okvirju iz vzdolžnih in prečnih profilov in preko izolatorjev vibracij elastično pritrjen na ohišje enote. Ventilator mora biti dobavljen z odjemom tlaka na sesalnem ustju ventilatorja, izvedenimi priključki za meritev pretoka na steni klimata. Enota ima kontrolno okno, svetilko ter stikalo za luč. | The unit shall be fitted with a free-flowing fan with backward curved blades. The fan motor shall be mounted on a support plate fixed to the fan frame. The fan rotor shall be dynamically balanced in accordance with DIN ISO 1940 Part 1 - G 2.5. The fan assembly shall be mounted on a support frame made of longitudinal and transverse sections and elastically fixed to the unit casing via vibration isolators. The fan shall be supplied with a pressure tap at the fan inlet, with connections for flow measurement on the air-conditioning wall. The unit shall be fitted with a control window, a lamp and a light switch.
| Elektromotor ventilatorja primeren za vodenje s frekvenčnim pretvornikom, razreda učinkovitosti vsaj IE3 skladno s SIST EN 60034-30:2014. Z dodatno temperaturno PTC sondo v navitju za izvedbo primarne temperaturne zaščite navitja. Kabel temperaturne sonde mora biti v zaščitni cevi - zaščita pred vodo pri pranju. Servisno stikalo za vklop elektro motorja je v dobavi elektro inštalacij. Vsi prehodi v/iz prezračevalne naprave morajo biti preko ustreznih uvodnic. | Fan electric motor suitable for frequency converter control, efficiency class at least IE3 according to SIST EN 60034-30:2014. With additional PTC temperature probe in the winding to perform primary temperature protection of the winding. The temperature probe cable must be in a protective hose - protection against water during washing. A service switch for switching on the electric motor is included in the supply of the electrical installation. All passages to/from the ventilation unit must be via suitable inlets.
| Vsi sistemi so predvideni s servisnimi stikali. Priključki za tlačna tipala in stikala so v notranjosti klimatske naprave. | All systems are provided with service switches. Connections for pressure sensors and switches are located inside the air-conditioning unit.
| Fleksibilni priključek razreda tesnosti C po SIST EN13810 in po SIST EN 1507 v območju od ±1500 Pa, je sestavljen iz dveh prirobničnih okvirjev iz pocinkane jeklene pločevine z integriranim tesnilnim trakom iz EPDM gume in fleksibilnega dela iz nehigroskopskega materiala, uporabnega v območju od -10 do+80°C. | The flexible connector of tightness class C according to SIST EN13810 and according to SIST EN 1507 in the range of ±1500 Pa, consists of two flange frames made of galvanised steel sheet with integrated EPDM rubber sealing strip and a flexible part made of non-hygroscopic material, usable in the range from -10 to +80°C.
| Zobniška regulacijska žaluzija razreda tesnosti 2 po SIST EN 1751, z zunanje ležečimi zobniki iz polipropilena, z okvirom in loputami iz aluminija, s tesnenjem med loputami s tesnilnim trakom iz EPDM materiala in s pogonsko osjo iz pocinkanega jekla. Vgrajene so na zunanjii strani ohišja in pripravljene za vgradnjo motornega pogona. | Gear-operated control louvre of leakage tightness class 2 according to SIST EN 1751, with externally mounted polypropylene gears, aluminium frame and flaps, sealing between the flaps with EPDM sealing tape and galvanised steel drive axle. Mounted on the outside of the housing and ready for installation of the motor drive.
| Vgradnja optičnih manometrov je izvedena skladno z navodili proizvajalca Dwayer ali WIKA | Installation of optical pressure gauges shall be carried out in accordance with the Dwayer or WIKA manufacturer's instructions
| Pred dobavo naj se iz risb preverijo strani posluževanja posameznih enot ter ustreznost dimenzij za postavitev na pod ter še enkrat preverijo obtežbe! | Before delivery, check the service sides of the individual units from the drawings, check that the dimensions are suitable for the floor and check the loads again!
| Višina podstavka klimatov je 200mm. | The height of the base of the air conditioners is 200mm.
| Za kompletno napravo je potrebno zagotoviti še potrebna navodila za montažo, obratovanje in vzdrževanje, s seznamom rezervnih delov. | The complete installation must be accompanied by the necessary installation, operating and maintenance instructions, including a list of spare parts.
0.3.2 | Kanalski dogrelniki, ki so zapisani pod periferno opremo so sestavljeni iz okvirja, lamelnega paketa s cevmi ter zbiralne in razdelilne cevi. Spoj lamel in cevi je izveden z mehanskim ekspandiranjem. Vsi kanalski dogrelniki s priključki do vključno DN 50 morajo biti navojni, opremljeni s holandčnim spojem. | The duct heaters listed under peripheral equipment shall consist of a frame, a louvre package with pipes and a collection and distribution pipe. The joint between the louvre and the pipe shall be made by mechanical expansion. All duct heaters with connections up to and including DN 50 shall be threaded, fitted with a Dutch joint.
0.3.3 | Požarne lopute naj bodo okrogle ali pravokotne izvedbe, za vgradnjo v suhomontažno ali betonsko steno s požarno odpornostjo EI 90-S. Krmiljenje lopute od zunanjega signala z elektromotornim pogonom (24 VAC) z mikrostikali za signalizacijo položaja lopute odprto/zaprto, komplet z dvema termičnima tipaloma Tf1 in Tf2 z aktiviranjem nad 72 st. C, če termičn otipalo zazna povišanje temperature v okolici ali v notranjosti kanala. Požarna loputa mora imeti deklarirane lastnosti skladno s SIST EN 15650:2010 in mora biti skladna s standardom SIST EN 1366/2. Klasifikacija požarne odpornosti mora biti skladna s SIST EN 13501-3. Priklop in izvedba prezračevalnih kanalov na požarno loputo se izvede v skladu z ONORM H 6031. | The fire dampers shall be of circular or rectangular design, for installation in dry-walled or concrete walls with fire resistance EI 90-S. Control of the damper from an external signal by means of an electromotor drive (24 VAC) with micro-switches for signalling the open/closed position of the damper, complete with two thermal sensors Tf1 and Tf2, activated above 72 °C if the thermal sensor detects an increase in the temperature of the surroundings or the interior of the duct. The fire damper shall have declared characteristics in accordance with SIST EN 15650:2010 and shall comply with SIST EN 1366/2. The fire resistance classification shall comply with SIST EN 13501-3. The connection and design of the ventilation ducts to the fire damper shall be in accordance with ONORM H 6031.
0.3.4 | Obtočne črpalke so enostopenjske z mokrotekočim ali suhim rotorjem s sesalnimi in tlačnimi priključki v isti liniji, priključki so navojni po ISO 228-1, oz. prirobnični po SIST EN 1092-2 za NP10. Razreda učinkovitosti vsaj IE3 skladno s SIST EN 60034-30:2014. V kolikor ima črpalka frekvenčni pretvornik mora imeti tudi možnost povezave oz. nadgradnje na hišno komunikacijo preko lokalnega omrežja LAN Ethernet wiring (ISO 8802-3) in sicer po odprtem protokolu (Mod BUS, profibus, BACnet...) skladno s SIST EN 14908-1:2014 in SIST EN 14908-2:2014. Črpalke morajo ustrezati do temperature min. 100°C. | The circulators shall be single-stage with wet-running or dry-running impeller with suction and pressure connections in the same line, the connections shall be threaded according to ISO 228-1, or flanged according to SIST EN 1092-2 for NP10. They shall have an efficiency class of at least IE3 according to SIST EN 60034-30:2014. If the pump has a frequency converter, it must also have the possibility of connecting or upgrading to the house communication via the local LAN Ethernet wiring (ISO 8802-3) using an open protocol protocol (Mod BUS, profibus, BACnet, etc.) in accordance with SIST EN 14908-1:2014 and SIST EN 14908-2:2014. The pump shall be suitable for a temperature of at least 100°C.
0.3.5 | Obtočna črpalka za glykol medij pri sistemu rekuperacije toplote je vertikalna večstopenjska s sesalnim in tlačnim priključkom v isti liniji za postavitev na pod, priključki so navojni po ISO 228-1, oz. prirobnični po SIST EN 1092-2 za NP10. Razreda učinkovitosti vsaj IE3, skladno s SIST EN 60034-30:2014. Črpalka ima tovarniško prigrajen frekvenčni pretvornik in diferenčno tlačno zaznavalo in s tem tudi možnost povezave oz. nadgradnje na hišno komunikacijo preko lokalnega omrežja LAN Ethernet wiring (ISO 8802-3) in sicer po odprtem protokolu (Mod BUS, profibus, BACnet...) skladno s SIST EN 14908-1:2014 in SIST EN 14908-2:2014. Črpalke morajo ustrezati od -10°C do temperature min. 100°C. | The circulator for the glycol medium in the heat recovery system shall be a vertical multistage pump with suction and pressure connections in the same line for floor mounting, the connections shall be threaded according to ISO 228-1, or flanged according to SIST EN 1092-2 for NP10. Efficiency class at least IE3, according to SIST EN 60034-30:2014. The pump has a factory-fitted frequency converter and differential pressure sensor and thus also the possibility of connection or upgrade to house communication via LAN Ethernet wiring (ISO 8802-3) using an open protocol (Mod BUS, Profibus, BACnet, etc.) in accordance with SIST EN 14908-1:2014 and SIST EN 14908-2:2014.The pumps must be suitable for temperatures from -10°C up to a minimum of 100°C.
0.3.6 | Obtočne črpalke za mešanico glykol/voda morajo biti dobavljene z ustreznimi tesnili za etylen glykol! | Glycol/water mix circulators must be supplied with suitable seals for ethylene glycol!
0.3.7 | Senzorji za montažo na cev ali rezervoar morajo biti dobavljeni vključno z zaščitno tulko Ms63 PN10. | Sensors for mounting on a pipe or tank must be supplied including a Ms63 PN10 protective sleeve.
0.3.8 | Aktivno kombinirano tipalo temperature in vlage za zunanjo stensko montažo (vremenska postaja TIC/MIC) namenjen za merjenje fizikalnih veličin, kot so: temperatura, relativna vlaga, temperatura rosišča, temperatura vlažnega termometra, absolutna vlažnost in entalpija. Tehnologija senzorja je polimerni kapacitivni senzor z mrežastim filtrom iz nerjavečega jekla. | Active combined temperature and humidity sensor for external wall mounting (TIC/MIC weather station) designed to measure physical quantities such as: temperature, relative humidity, dew point temperature, wet bulb temperature, absolute humidity and enthalpy. The sensor technology is a polymer capacitive sensor with a stainless steel mesh filter.
0.3.9 | Aktivna tipala temperature in vlage ali kombinirana tipala za vgradnjo v kanal mora biti dobavljena vključno z montažnim in pritrdilnim materialom. | Active temperature and humidity sensors or combined sensors for duct mounting shall be supplied including mounting and fixing material.
0.3.10 | Diferenčna tipala razlike tlaka morajo biti dobavljena vključno z vsem pritrdilnim in montažnim materialom. | Differential pressure sensors must be supplied including all fixing and mounting material.
0.3.11 | Regulacijski ventili (Belimo ali IMI TA) do DN50 so navojni po ISO 228-1, nad to dimenzijo pa prirobnični, skladno s SIST EN 1092-2. Nazivna napetost motornih pogonov je AC/DC24V; Zvezni signal 2-10V. Ventili morajo ustrezati do temperature min. 100°C. | Control valves (Belimo or IMI TA) up to DN50 are threaded according to ISO 228-1, above this dimension are flanged valves according to SIST EN 1092-2. The nominal voltage of the motor drives is AC/DC24V; the interface signal is 2-10V. The valves have to be suitable up to a minimum temperature of 100°C.
0.3.12 | Regulacijski mešalni ventil za regulacijo toplotne moči na sistemu glikolne rekuperacije (Belimo energy valve ali IMI TA Smart), ki izpolnjuje zahteve po SIST EN 1434 in obsega regulacijski ventil s pogonom z logaritemsko karakteristiko, senzorskim modulom, logičnim modulom ter integriranim in eksternim senzorjem. Enota z integriranim senzorjem vsebuje tudi ultra zvočni merilnik pretoka. Izvedba vsebuje logično enoto z vgrajenim dT kontrolnikom, kotrolnikom moči, pretoka ali omejevalnika povratne temperature. Sistem ima možnost povezave oz. nadgradnje na hišno komunikacijo preko lokalnega omrežja LAN Ethernet wiring (ISO 8802-3) in sicer po odprtem protokolu (Mod BUS, profibus, BACnet...) skladno s SIST EN 14908-1:2014 in SIST EN 14908-2:2014. Ventili morajo ustrezati od -10°C do min. 100°C. Regulacijski ventili do DN50 so navojni po ISO 228-1, nad to dimenzijo pa prirobnični, skladno s SIST EN 1092-2. Nazivna napetost motornih pogonov je AC/DC24V; Zvezni signal 2-10V. Ventili morajo ustrezati od -10°C do temperature min. 100°C. | Control mixing valve for heat output control on a glycol recovery system (Belimo energy valve or IMI TA Smart), meeting the requirements of SIST EN 1434, comprising a logarithmic actuated control valve, sensor module, logic module and integrated and external sensors. The integrated sensor unit also includes an ultra-sonic flow meter. The version includes a logic unit with integrated dT controller, power, flow or return temperature limiter. The system has the possibility of connection or upgrade to the house communication via LAN Ethernet wiring (ISO 8802-3) using an open protocol (Mod BUS, profibus, BACnet, etc.) in accordance with SIST EN 14908-1:2014 and SIST EN 14908-2:2014. The valves must be suitable from -10°C to min. 100°C. The control valves up to DN50 are threaded in accordance with ISO 228-1, and above this dimension they are flanged in accordance with SIST EN 1092-2. The rated voltage of the motor drives is AC/DC24V; the interface signal is 2-10V. The valves must be suitable from -10°C up to a minimum temperature of 100°C.
0.3.13 | Elektronski volumski regulatorji pretoka okrogle izvedbe za variabilen pretok - VAV so narejeni iz ohišja iz jeklene pocinkane pločevine na konceh z nastavkom in tesnilom za montažo na okrogli kanal po SIST EN 1506:2007, vključno z merilnim profilom za merjenje dinamičnega tlaka Pdin, regulacijsko loputo ter regulacijskim sklopom z zveznim motornim pogonom. Napajanje: 24V AC/DC, krmiljenje: 0(2)-10V. | Electronic volumetric flow controllers of round design for variable flow - VAV shall be made of galvanised sheet steel casing with spigot and gasket on the ends for mounting on a round duct according to SIST EN 1506:2007, including dynamic pressure measuring profile Pdin, control damper and control assembly with continuous motor drive. Power supply: 24V AC/DC, control: 0(2)-10V.
0.3.14 | Elektronski volumski regulatorji pretoka pravokotne izvedbe za variabilen pretok - VAV so narejeni iz ohišja iz jeklene pocinkane pločevine ter na obeh konceh z jekleno pocinkano prirobnico MEZ, vključno z merilnim profilom za merjenje dinamičnega tlaka Pdin, regulacijsko loputo ter regulacijskim sklopom z zveznim motornim pogonom. Napajanje: 24V AC/DC, krmiljenje: 0(2)-10V. | The electronic rectangular volume flow controllers for variable flow - VAV are made of galvanised sheet steel housing with galvanised steel flange MEZ at both ends, including dynamic pressure measuring profile Pdin, control damper and control assembly with continuous motor drive. Power supply: 24V AC/DC, control: 0(2)-10V.
0.3.15 | Mehanski volumski regulatorji pretoka okrogle izvedbe - CAV so narejeni iz ohišja iz jeklene pocinkane pločevine na konceh z nastavkom in tesnilom za montažo na okrogli kanal po SIST EN 1506:2007, regulacija pretoka je mehanska preko regulacijske plošče, ki je obojestransko uležajena, in preko sistemov vzvodov z nastavno vzmetjo. | Mechanical volume flow control valves of circular design - CAV are made of galvanised sheet steel casing with spigot and gasket on the ends for mounting on a circular duct according to SIST EN 1506:2007, the flow control is mechanical through a control plate, which is moulded on both sides, and through a lever system with an adjusting spring.
0.3.16 | Mehanski volumski regulatorji pretoka pravokotne izvedbe - CAV so narejeni iz ohišja iz jeklene pocinkane pločevine ter na obeh konceh z jekleno pocinkano prirobnico MEZ, regulacija pretoka je mehanska preko regulacijske plošče, ki je obojestransko uležajena, in preko sistemov vzvodov z nastavno vzmetjo. Kasnejša morebitna nadgradnja mora omogočiti vgradnjo dodatnih motornih pogonov. Nastavitev pretoka je ročna. | Mechanical rectangular volume flow controllers - CAV are made of galvanised sheet steel casing with galvanised steel MEZ flange at both ends, flow control is mechanical via a control plate, which is grooved on both sides, and via lever systems with adjustable spring. Subsequent possible upgrading must allow the installation of additional motor drives. Flow adjustment is manual.
0.3.17 | Regulatorji konstantnega volumskega pretoka okrogle izvedbe - CAV iz materiala PP-s ali PP-s-el, zasnova je prilagojena konstantnim volumskim pretokom v območje kemično onesnaženega izhodnega zraka in pri dovodu čistega zraka. Minimalna debelina stene je 3mm, skladno z DIN 4741, razred tesnenja po SIST EN 12237. Volumenski pretok se ohranja konstanten v določenem območju tlaka s posebna membrana in vložki so zasnovani za specifični volumski pretok. Prilagodijo se na tovarniško nastavitev | Constant volume flow controllers of round design - CAV made of PP-s or PP-s-el material, the design is adapted to constant volume flows in the chemically contaminated zone of the outlet air and in the clean air inlet. The minimum wall thickness is 3mm, according to DIN 4741, sealing class according to SIST EN 12237. The volume flow is kept constant in a specific pressure range by a special diaphragm and inserts are designed for a specific volume flow. They can be adjusted to the factory setting
0.3.18 | Plastični radialni strešni ventilator, odporen proti koroziji, z ohišjem v stabilni, rotacijsko sintrani izvedbi iz PP-s ali PPs-el (ATEX), enostransko sesanje, z zaščito pred drobci v skladu s predpisi za preprečevanje nesreč od velikosti 160 kot plastificirana žična mreža. V primeru pokončne montaže se odpadni zrak izpihuje navpično v skladu z zahtevami za agresiven zrak. Vsi deli, ki so izpostavljeni izpušnemu zraku, izdelani iz plastike ali zaprti s plastiko. Tekač z nazaj ukrivljenimi lopaticami v brizgani različici, nameščen s stožčasto zaklepno pušo na gredi motorja, statično in dinamično uravnotežen, v brizgani različici, nameščen s stožčasto zaklepno pušo na gredi motorja, statično in dinamično uravnotežen, kakovost uravnoteženja najmanj G 6.3 (DIN ISO 21940-11). Vključno z notranje nameščenim motorjem, zaprtim proti dostavni medij in zunanje nameščeno stikalo za popravilo v primeru standardnih motorjev (brez zaščite pred eksploatacijo) oz. Zunanje prezračevanje motorja preko navzven nameščenih kanalov. Izvedba mora biti dobavljena vključno s tipskim podstavkom za montažo na streho ter vsem pritrdilnim in montažnim materialom. ATEX izvedba mora ustrezati direktivi 2014/34/EU II 2/3G IIB T4. Sistem ima možnost povezave oz. nadgradnje na hišno komunikacijo preko lokalnega omrežja LAN Ethernet wiring (ISO 8802-3) in sicer po odprtem protokolu (Mod BUS, profibus, BACnet...) skladno s SIST EN 14908-1:2014 in SIST EN 14908-2:2014. | Corrosion-resistant plastic radial roof fan with housing in stable, rotationally sintered PP-s or PPs-el (ATEX), single-sided suction, with protection against splinters in accordance with accident prevention regulations from size 160 as plasticised wire mesh. In the case of upright mounting, exhaust air shall be exhausted vertically in accordance with the requirements for aggressive air. All parts exposed to exhaust air shall be made of plastic or sealed with plastic. Runner with backward curved blades in the injection moulded version, mounted with a conical locking bush on the motor shaft, statically and dynamically balanced, in the injection moulded version, mounted with a conical locking bush on the motor shaft, statically and dynamically balanced, balancing quality at least G 6.3 (DIN ISO 21940-11). Including internally mounted motor, sealed against the delivery medium, and externally mounted repair switch in the case of standard motors (without service protection) or external ventilation of the motor via externally mounted ducts. The version shall be supplied including a standard roof-mounting pedestal, and including all fixing and mounting material. The ATEX version must comply with Directive 2014/34/EU II 2/3G IIB T4.The system has the possibility of connection or upgrade to house communication via LAN Ethernet wiring (ISO 8802-3) using an open protocol (Mod BUS, Profibus, BACnet...) in accordance with SIST EN 14908-1:2014 and SIST EN 14908-2:2014.
0.3.19 | Centrifugalni ventilator z direktnim pogonom. Plastični radialni ventilator, odporen proti koroziji, s stranskim dovodom in vertikalnim odvodom, ohišje iz disipativnega in ognjevarnega PP-s, brizgana in tesno varjena različica, s tesnilom in maščobno zaporo na prehodu gredi. Tekač v električno prevodni PPs-el z lopaticami, nameščenimi na zadnji strani rotorja za razbremenitev pri prehodu gredi. Vsi deli izpostavljeni zračnemu toku so izdelani iz plastike ali zaprti s plastiko. Motor zaprt proti mediju, z zaščito pred preobremenitvijo v celotnem območju moči. Okvir ventilatorja iz prašno lakirane jeklene pločevine za montažo na streho, vključno s fleksibilnim priključkom ter vremensko zaščito. | Direct-drive centrifugal fan. Corrosion-resistant plastic radial fan with side inlet and vertical outlet, housing in dissipative and refractory PP-s, injection-moulded and close-welded version, with seal and grease interlock at shaft passage. Runner in electrically conductive PPs-el with blades mounted on the back of the rotor for relief at shaft passage. All parts exposed to the air flow made of plastic or sealed with plastic. Motor sealed against the medium, with overload protection throughout the power range. Fan frame in powder-coated steel sheet for roof mounting, including flexible connector and weatherproofing protection.
0.3.20 | Kanalski ventilator centrifugalne ''in-line'' izvedbe iz ohišja z jeklene pocinkane pločevine ter na obeh koncih z jekleno pocinkano prirobnico MEZ. Izvedba je narejena iz tekača z nazaj zakrivljenimi lopaticami iz pocinkane pločevine. Motor je nasajen direktno na tekač, ki je dinamično balansiran skladno z DIN ISO 1940. El. motor in tekač sta umeščena direktno v zračnem toku, kar zvišuje njuno življensko dobo. Ventilator mora biti skladen z ErP 2018. Izvedba je dobavljiva vključno z mehansko protipovratno žaluzijo ter vsem montažnim in pritrdilnim materialom. | Centrifugal "in-line" ducted fan made of galvanised sheet steel housing with galvanised steel MEZ flange at both ends. The version is made of a runner with backward curved galvanised sheet steel blades. The motor is mounted directly on the runner, which is dynamically balanced in accordance with DIN ISO 1940. The electric motor and the runner are positioned directly in the air flow, which increases their lifetime. The fan shall comply with ErP 2018. The version is supplied including a mechanical backdraught preventer, all mounting and fixing materials.
0.3.21 | Strešni ventilatorji morajo biti dobavljeni skupaj z mehansko protipovratno loputo ter strešnim podstavkom za montažo. Ohišje je predvideno iz aluminija s 50 mm izolacijo iz mineralne volne za nizko raven hrupa, osnovni okvir iz pocinkanega jekla. Zaščita motorja je vgrajena v elektroniko motorja, dodatna zunanja zaščita motorja ni potrebna. Izvedba mora imeti vgrajene tlačne senzorje, elektronika pa je programirana za delovanje s konstantnim tlakom. Nazaj ukrivljeni tekači izdelani iz poliamida PA za velikost 190 in 225. Od 315 do 710 tekači izdelani iz polipropilena PP. Motor mora biti izven toka zraka, z nazaj zakrivljenimi lopaticami, balansiran skladno z DIN ISO 1940. Ventilator mora biti dobavljen z vsem pritrdilnim in montažnim materialom. | The roof fans shall be supplied with a mechanical backdraft damper and a roof mounting pedestal. The housing shall be aluminium with 50 mm mineral wool insulation for low noise level, the base frame shall be galvanised steel. The motor protection shall be integrated in the motor electronics, no additional external motor protection is required. The design shall have pressure sensors integrated and the electronics shall be programmed for constant pressure operation. Backward curved runners made of polyamide PA for sizes 190 and 225. 315 to 710 runners made of polypropylene PP. The motor shall be out of the air flow, with backward curved blades, balanced in accordance with DIN ISO 1940. The fan shall be supplied with all fixing and mounting material.
0.3.22 | Izdelava in tesnenje prebojev pri prehodu zračnih kanalov med požarnimi sektorji z ustrezno atestirano sistemsko maso/kitom/izolacijo požarne odpornosti EI90, proizvod kot npr. HILTI, PROMAT, PIROFIX-PFT.Vsak prehod mora biti označen z nalepko ali tablico z osnovnimi požarnimi podatki. | Making and sealing of penetrations at the passage of air ducts between fire sectors with a suitable certified system compound/kit/insulation of fire resistance EI90, product such as e.g. HILTI, PROMAT, PIROFIX-PFT.Each passage must be marked with a sticker or a plaque with basic fire information.
0.3.23 | Izvajalec del mora pred pričetkom izvedbe del natančno pregledati skupne vstope/izstope instalacij v/iz jaškov ter razvode v njih. Obvezno mora prikazati delavniško risbo čelnega pogleda na vstop/izstop v jaške ali na ozkih prehodih skozi požarne stene za vse instalacije, upoštevajoč ustrezne odmike med njimi. Odmiki med požarnimi loputami in cevovodi mora biti skladna s SIST EN 1366-3:2021. Navadno imajo EU proizvajalci požarnih loput zahtevan odmik min. 200mm, v kolikor to ne bo mogoče, je potrebno narediti vmesno pregradno požarno odporno steno iz silikatnega materiala, v tem primeru so lahko instalacije nameščene tudi bližje kot 200mm! | The contractor must thoroughly inspect the common entrances/exits of the installations to/from the shafts and the piping in them before starting the works. He must show a shop drawing of the frontal view of the entry/exit to the shafts or at the narrow passages through the fire walls for all the installations, taking into account the appropriate spacing between them. The spacing between the fire dampers and the piping must be in accordance with SIST EN 1366-3:2021. Usually the EU manufacturers of the fire dampers have a minimum required spacing of 200mm, if this is not possible an intermediate fire-resistance barrier wall made of a siliceous material is required in which case the installations may be installed even closer than 200mm!

## 4.4.0_Rekapitulacija
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
| REKAPITULACIJA STROŠKOV STROJNIH DEL | COST SUMMARY OF MECHANICAL WORKS
| 4 NAČRT S PODROČJA STROJNIŠTVA | 4 DOCUMENTATION IN THE FIELD OF MECHANICAL ENGINEERING
| 4/4 Prezračevanje in klimatizacija pedagoških in ostalih prostorov | 4/4 Ventilation and Air Conditioning of Educational and Other Rooms
4.4 | STROJNA DELA | MECHANICAL WORKS
4.4.1 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS01 | VENTILATION AND AIR CONDITIONING SYSTEM KS01 | 0
4.4.2 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS02 | VENTILATION AND AIR CONDITIONING SYSTEM KS02 | 0
4.4.3 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS03 | VENTILATION AND AIR CONDITIONING SYSTEM KS03 | 0
4.4.4 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS04 | VENTILATION AND AIR CONDITIONING SYSTEM KS04 | 0
4.4.5 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS05 | VENTILATION AND AIR CONDITIONING SYSTEM KS05 | 0
4.4.6 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS06 | VENTILATION AND AIR CONDITIONING SYSTEM KS06 | 0
4.4.7 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS07 | VENTILATION AND AIR CONDITIONING SYSTEM KS07 | 0
4.4.8 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS08 | VENTILATION AND AIR CONDITIONING SYSTEM KS08 | 0
4.4.9 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS14 | VENTILATION AND AIR CONDITIONING SYSTEM KS14 | 0
4.4.10 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS15 | VENTILATION AND AIR CONDITIONING SYSTEM KS15 | 0
4.4.11 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS17 | VENTILATION AND AIR CONDITIONING SYSTEM KS17 | 0
4.4.12 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS18 | VENTILATION AND AIR CONDITIONING SYSTEM KS18 | 0
4.4.13 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM VS21 | VENTILATION AND AIR CONDITIONING SYSTEM VS21 | 0
4.4.14 | SKUPNE POSTAVKE | COMMON ITEMS | 0
0
0% | NEPREDVIDENA DELA | UNFORSEEN WORKS | 0
| SKUPAJ STROJNA DELA: | TOTAL MECHANICAL WORKS: | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT

## 4.4.1_PrKlim KS01
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.4 | STROJNA DELA | MECHANICAL WORKS
4.4.1 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS01 | VENTILATION AND AIR CONDITIONING SYSTEM KS01 |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
1 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS01 | VENTILATION AND AIR CONDITIONING SYSTEM KS01
1.1 | Klimatska naprava za dovod in odvod zraka KD01/KO01 - glej tudi zavihek Zahteve klimati. | KD01/KO01 supply and extract air conditioner - see also Climate requirements tab.
| Tehnične karakteristike naprave (opis v smeri toka zraka): | Technical characteristics of the appliance (description downstream):
| Dovod: Vdov = 12400 m3/h | Input: Vdov = 12400 m3/h
| - posluževanje dovod: desno v smeri toka zraka! | - inlet: right in the direction of the air flow!
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 10 60% po ISO 16890 (M5 po SIST EN 779), s fleksibilnim čelnim priključkom, za pretok zraka 12400m3/h. Maksimalni končni padec tlaka 200Pa. Oznaka: F01.100 | - Filter unit with bag filter cartridge of filtration level ePM 10 60% according to ISO 16890 (M5 according to SIST EN 779), with flexible front connection, for an air flow of 12400m3/h. Maximum final pressure drop 200Pa. Code: F01.100
| - Prazna enota z regulacijskimi žaluzijami 2x 1533x618x125 za pretok zraka 12400m3/h. | - Empty unit with 2x 1533x618x125 control louvres for an air flow of 12400m3/h.
| - Prazna enota z AMS merilno mrežo STRA-R1250X625MM vgrajeno v zgornji del enote, pred rototermom. | - Empty unit with AMS measuring grid STRA-R1250X625MM built into the top of the unit, in front of the rototherm.
| - Rotacijska regeneratorska enota za prenos senzibilne in latentne toplote, z ON/OFF žaluzijami obtoka zraka 2x 1485x210x125. Tehnični podatki za zimsko obdobje: - pretok zraka 3900/3300m3/h - stopnja vračanja občutene toplote: 74,5% - stopnja vračanja latentne toplote: 77,8% - vračanje toplotne energije: 46,10kW - stanje dovodnega zr. pred enoto: -13,00°C/90,0% - stanje dovodnega zraka za enoto: 13,10°C/50,6% Tehnični podatki za poletno obdobje: - pretok zraka 3900/3300m3/h - stopnja vračanja občutene toplote: 74,5% - stopnja vračanja latentne toplote: 75,8% - vračanje toplotne energije: 18,30kW - stanje dovodnega zr. pred enoto: 34,50°C/40,0% - stanje dovodnega zraka za enoto: 28,20°C/45,3% Oznaka: RE01.191 | - Rotary regenerative unit for sensible and latent heat transfer, with ON/OFF airflow shutters 2x 1485x210x125. technical data for the winter period: - air flow 3900/3300m3/h - sensible heat recovery rate: 74.5% - latent heat recovery rate: 77.8% - heat energy recovery: 46.10kW - supply air condition upstream of the unit: -13.00°C/90.0% - supply air condition for the unit: 13.10°C/50.6% Technical data for the summer period: - air flow 3900/3300m3/h - sensible heat recovery rate: 74.5% - latent heat recovery rate: 75.8% - heat energy recovery: 18.30kW - supply air condition upstream of the unit: 34.50°C/40.0% - supply air condition for the unit: 28.20°C/45.3% Code: RE01.191
| - Mešalna enota za mešanje zunajnega in prostorskega zraka, z vgrajenimi mešalnimi cevmi za zagotavljanje ustreznega mešanja zraka, z regulacijsko žaluzijo 1390x410x125. | - Mixing unit for mixing outside and indoor air, with integrated mixing pipes to ensure adequate air mixing, with control louvre 1390x410x125.
| - Enota pred-grelnika zraka s protizmrzovalno zaščito. - pretok zraka 12400m3/h - grelna moč Qg=19,7kW - temperaturni režim ogrevnega medija 50/40°C - pretok ogrevnega medija 0,476 l/s - padec tlaka na zračni strani 8Pa - temperatura zraka vstop 19,20°C - temperatura zraka izstop 23,90°C - padec tlaka na strani ogr. medija (voda) 10,87kPa - priključka navojna 1" - tlačna stopnja PN16 Oznaka: HE01.106 | - Air preheater unit with anti-freeze protection. - air flow 12400m3/h - heating power Qg=19,7kW - heating medium temperature 50/40°C - heating medium flow rate 0,476 l/s - 8Pa pressure drop on the air side - air temperature inlet 19,20°C - air temperature outlet 23,90°C - pressure drop on the heating medium side (water) 10,87kPa - 1" threaded connectors - pressure rating PN16 Code: HE01.106
| - Vlažilna enota s kontaktnim vlaženjem zraka. Dovod sveže pripravljene demineralizirane vode, z materialom kontaktnega vlažilnika impregniranim srebrom, črpalko, potrebno merilno regulacijsko opremo, ventili na dovodu sveže vode ter ventilom na odvodu vode iz banje, s funkcijo samodejnega praznjenja banje vlažilnika in polnjenja s svežo pripravljeno mehčano vodo glede na prevodnost vode v banji, oziroma glede na čas ko vlažilnik ni v funkciji. Odvod kondenzata s sifonom z vodno in mehansko smardno zaporo. - pretok zraka 12400m3/h - priključna električna moč 0,06kW, 3x400V, 50Hz - padec tlaka na zračni strani dpz=27Pa - temperatura zraka vstop 23,9°C - relativna vlaga zraka vstop 27,7% - temperatura zraka izstop 22,15°C - relativna vlaga izstop 35% - izkoristek vlaženja 16,02% - vlaženje 14,8 kg/h - tipalo prevodonsti vode QICCD01.108 - tipalo zgornjega nivoja vode LICH01.108 - tipalo spodnjega nivoja vode LICL01.108 - elektromagnetni ventil za praznenje VD01.108 - elektromagnetni ventil za dovod sveže vode VD01.208 Oznaka: SH01.108 | - Humidification unit with contact humidification. Freshly prepared demineralised water supply, with silver-impregnated contact humidifier material, pump, necessary metering control equipment, valves at the fresh water inlet and at the water outlet of the humidifier tank, with automatic emptying of the humidifier tank and refilling with freshly prepared softened water according to the conductivity of the water in the tank, or according to the time when the humidifier is not in operation. Condensate drainage with siphon with water and mechanical odour trap. - air flow 12400m3/h - connection power 0,06kW, 3x400V, 50Hz - pressure drop on the air side dpz=27Pa - air temperature entering 23,9°C - relative humidity 27.7% - air temperature outlet 22,15°C - relative humidity 35% exit - humidification efficiency 16.02% - humidification 14,8 kg/h - water conductivity sensor QICCD01.108 - upper water level sensor LICH01.108 - lower water level sensor LICL01.108 - solenoid valve for emptying VD01.108 - fresh water inlet solenoid valve VD01.208 Code: SH01.108
| - Enota hladilnika z eliminatorjem kapljic in koritom za odvod kondenzata. - pretok zraka 12400m3/h - hladilna moč Qhtot=74,2kW - temperaturni režim hladilnega medija 9/14°C - pretok hladilnega medija 3,543 l/s - padec tlaka na zračni strani 84/78Pa - temperatura zraka vstop 26,70°C - temperatura zraka izstop 12,50°C - padec tlaka na strani hl. medija (voda) 28,58kPa - priključka navojna 2" - tlačna stopnja PN16 Oznaka: HE01.109 | - Refrigerator unit with drip eliminator and condensate drain. - air flow 12400m3/h - cooling power Qhtot=74,2kW - cooling medium temperature 9/14°C - coolant flow rate 3,543 l/s - pressure drop on the air side 84/78Pa - air temperature inlet 26,70°C - air temperature outlet 12,50°C - pressure drop on the medium side (water) 28,58kPa - 2" threaded connectors - pressure rating PN16 Code: HE01.109
| - Ventilatorska enota s prostotekočim rotorjem. Elektromotor je EC-motor, s 100% zvezno regulacijo vrtljajev preko potenciometra (0-10V), ki omogoča nastavitev delovanja ventilatorja na ustrezno delovno točko. Enota vsebuje: okence O150 in svetilko s stikalom ter servisno stikalo. - pretok zraka 12400m3/h - eksterni statični padec tlaka dpext=450Pa - priključna električna moč 2x3,7kW, 3x400V, 50Hz - razred izkoristka elektromotorja IE5/EC - zaščita IP55 Oznaka: FA01.110 | - Fan unit with free-flowing rotor. The electric motor is an EC motor, with 100% continuous speed control via a potentiometer (0-10V), which allows the fan to be set to the appropriate operating point. The unit contains: an O150 window and a lamp with switch and a service switch. - air flow 12400m3/h - external static pressure drop dpext=450Pa - connection power 2x3,7kW, 3x400V, 50Hz - electric motor efficiency class IE5/EC - iP55 protection Code: FA01.110
| - Enota do-grelnika zraka. - pretok zraka 12400m3/h - grelna moč Qg=35,8kW - temperaturni režim ogrevnega medija 50/40°C - pretok ogrevnega medija 0,865 l/s - padec tlaka na zračni strani 13Pa - temperatura zraka vstop 12,50°C - temperatura zraka izstop 21°C - padec tlaka na strani ogr. medija (voda) 14,23kPa - priključka navojna 1 1/4" - tlačna stopnja PN16 Oznaka: HE01.111 | - Do-it-yourself air heater unit. - air flow 12400m3/h - heating power Qg=35,8kW - heating medium temperature 50/40°C - heating medium flow rate 0,865 l/s - air side pressure drop 13Pa - air temperature inlet 12,50°C - air temperature outlet 21°C - pressure drop on the heating medium side (water) 14,23kPa - 1 1/4" threaded connectors - pressure rating PN16 Code: HE01.111
| - Dušilna enota. - pretok zraka 12400m3/h - padec tlaka dp=12Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 7 17 18 21 15 11 12 Oznaka: DZ01.112 | - Throttle unit. - air flow 12400m3/h - pressure drop dp=12Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 7 17 18 21 15 11 12 Code: DZ01.112
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 1 75% po ISO 16890 (F8 po SIST EN 779, s fleksibilnim čelnim priključkom, za pretok zraka 12400m3/h. Maksimalni končni padec tlaka 300Pa. Oznaka: F01.113 | - Filter unit with bag filter cartridge of filtration level ePM 1 75% according to ISO 16890 (F8 according to SIST EN 779, with flexible front connection, for air flow of 12400m3/h. Maximum final pressure drop 300Pa. Code: F01.113
| Dolžina: 8,71m | Length: 8,71m
| Širina: 1,665m | Width: 1,665m
| Višina: 1.485m | Height: 1.485m
| Kompletno z dobavo dodatne opreme: | Complete with supply of accessories:
| - odtočni sifoni | - drain traps
| - jadrovinasti nastavki | - sailplane spigots
| - s spojnim, tesnilnim in pritrdilnim materialom in priključki za senzorje, | - with jointing, sealing and fixing materials and sensor connections,
| Odvod: Vodv = 11800 m3/h | Discharge: waterv = 11800 m3/h
| - posluževanje odvod: levo v smeri toka zraka! | - serving outlet: left in the direction of the air flow!
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 10 60% po ISO 16890 (M5 po SIST EN 779), s fleksibilnim čelnim priključkom, za pretok zraka 12400m3/h. Maksimalni končni padec tlaka 200Pa. Oznaka: F01.207 | - Filter unit with bag filter cartridge of filtration level ePM 10 60% according to ISO 16890 (M5 according to SIST EN 779), with flexible front connection, for an air flow of 12400m3/h. Maximum final pressure drop 200Pa. Code: F01.207
| - Dušilna enota. - pretok zraka 11800m3/h - padec tlaka dp=11Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 7 17 18 21 15 11 12 Oznaka: DZ01.206 | - Throttle unit. - air flow 11800m3/h - pressure drop dp=11Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 7 17 18 21 15 11 12 Code: DZ01.206
| - Ventilatorska enota s prostotekočim rotorjem. Elektromotor je EC-motor, s 100% zvezno regulacijo vrtljajev preko potenciometra (0-10V), ki omogoča nastavitev delovanja ventilatorja na ustrezno delovno točko. Enota vsebuje: okence O150 in svetilko s stikalom ter servisno stikalo. - pretok zraka 11800m3/h - eksterni statični padec tlaka dpext=450Pa - priključna električna moč 2x2.5kW, 3x400V, 50Hz - razred izkoristka elektromotorja IE5/EC - zaščita IP55 Oznaka: FA01.205 | - Fan unit with free-flowing rotor. The electric motor is an EC motor, with 100% continuous speed control via a potentiometer (0-10V), which allows the fan to be set to the appropriate operating point. The unit contains: an O150 window and a lamp with switch and a service switch. - air flow 11800m3/h - external static pressure drop dpext=450Pa - connection power 2x2.5kW, 3x400V, 50Hz - electric motor efficiency class IE5/EC - iP55 protection Code: FA01.205
| - Dušilna enota. - pretok zraka 11800m3/h - padec tlaka dp=11Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 7 17 18 21 15 11 12 Oznaka: DZ01.204 | - Throttle unit. - air flow 11800m3/h - pressure drop dp=11Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 7 17 18 21 15 11 12 Code: DZ01.204
| - Sesalna tlačna enota z regulacijsko žaluzijo 1533x1248x125, fleksibilnim čelnim priključkom, za pretok zraka 11800m3/h. | - Suction pressure unit with control shutter 1533x1248x125, flexible front connection, for air flow 11800m3/h.
| Dolžina: 4,97m | Length: 4,97m
| Širina: 1,665m | Width: 1,665m
| Višina: 1.360m | Height: 1.360m
| Kompletno z dobavo dodatne opreme: | Complete with supply of accessories:
| - postavitvene noge, gumirane, višine 100-200mm | - rubberised feet, height 100-200mm
| - odtočni sifoni | - drain traps
| - jadrovinasti nastavki | - sailplane spouts
| - postavitev klimata na antivibracijski dušilnik (gumo) za preprečevanje prenosa vibracij in hrupa na konstrukcijo objekta. Dušilniki morajo biti preračunani glede na lastnosti klimata (teža in vrtilna frekvenca ventilatorjev). | - installation of the air conditioner on an anti-vibration damper (rubber) to prevent the transmission of vibrations and noise to the structure of the building. The dampers must be calculated according to the characteristics of the air conditioner (weight and speed of the fans).
| - s spojnim, tesnilnim in pritrdilnim materialom in priključki za senzorje, | - with jointing, sealing and fixing materials and sensor connections,
| Teža: 3.361kg | Weight: 3.361kg
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR | - SYSTEMAIR | kpl | 1 |  | 0
1.2 | Zunanja zaščitna rešetka za dovod zraka narejene iz jeklene pocinkane pločevine z zaščitno mrežo, z vgrajenim električnim grelnim kablom z zaščitno funkcijo proti zamrzovanju in termostatom za vklop pri +5 °C, pritrditev z vijaki na vzidan okvir iz jeklenega kotnika, barve v skladu z zahtevam načrta arhitekture, s pritrdilnim in tesnilnim materialom tipa: | External air intake grille made of galvanised sheet steel with protective mesh, with built-in electric heating cable with anti-freeze protection function and thermostat for switching on at +5 °C, bolted to a steel angle frame, colour according to architectural design requirements, with fixing and sealing material type:
| - dimenzije B=920/H=2920 | - dimensions B=920/H=2920
| - dimenzija prosta za pretok zraka B=920/H=1820 | - dimension free for air flow B=920/H=1820
| - H=600mm nad terenom zaprta rešetka z betonsko steno | - H=600mm above ground closed grid with concrete wall
| - H=500mm od vrha rešetke zaprta rešetka z betonsko steno | - H=500mm from top of grille closed grille with concrete wall
| - pretok q = 7955 m3/h | - flow rate q = 7955 m3/h
| - padec tlaka Δp = 8 Pa | - pressure drop Δp = 8 Pa
| - prost prerez Aef=1.323 m2 | - free cross-section Aef=1.323 m2
| - električna moč grelca od 1.88 do 3.77 kW, 3x400 V, 50Hz, na preseku za pretok zraka B=920/H=1820 | - heater electrical power from 1.88 to 3.77 kW, 3x400 V, 50Hz, at air flow cross section B=920/H=1820
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - OC IMP KLIMA tip JZR-6 920x2920 | - OC IMP KLIMA tip JZR-6 920x2920
| Oznaka: ZR01.901; ZR01.902 | Code: ZR01.901; ZR01.902 | kpl | 2 |  | 0
1.3 | Zunanja zaščitna rešetka za odvod zraka narejena iz jeklene pocinkane pločevine z zaščitno mrežo, pritrditev z vijaki na vzidan okvir iz jeklenega kotnika, barve v skladu z zahtevam načrta arhitekture, s pritrdilnim in tesnilnim materialom tipa: | External air grille made of galvanised sheet steel with protective mesh, bolted to a steel angle angle frame, colour according to the architectural plan, with fixing and sealing material of the type:
| - dimenzije B=920/H=2920 | - dimensions B=920/H=2920
| - dimenzija prosta za pretok zraka B=920/H=1820 | - dimension free for air flow B=920/H=1820
| - H=600mm nad terenom zaprta rešetka z betonsko steno | - H=600mm above ground closed grid with concrete wall
| - H=500mm od vrha rešetke zaprta rešetka z betonsko steno | - H=500mm from top of grille closed grille with concrete wall
| - pretok q = 15120 m3/h | - flow rate q = 15120 m3/h
| - padec tlaka Δp = 26 Pa | - pressure drop Δp = 26 Pa
| - prost prerez Aef=1.323 m2 | - free cross-section Aef=1.323 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - OC IMP KLIMA tip JZR-6 920x2920 | - OC IMP KLIMA tip JZR-6 920x2920
| Oznaka: ZR01.801 | Code: ZR01.801 | kpl | 1 |  | 0
1.4 | Okrogli prezračevalni kanali izdelani iz pocinkane pločevine po SIST EN 1506, vključno z revizijskimi odprtinami, oblikovnimi kosi, debeline po standardu. V ceni na enoto (m) je potrebno upoštevati ves spojni in pritrdilni material (prirobnice, odrez, spone, vijaki, tesnila, ojačitve, vključno z obešalnim in pritrdilnim materialom sistemskega proizvajalca z lastnostmi odgovarjajoč zahtevam SIST EN 12236: 2002, vključno pleskanje vseh kovinskih korozijsko nezaščitenih delov, po temeljitem predhodnem čiščenju do kovinskega sijaja. Antikorozijska zaščita se izvaja v skladu z EN 12944 za naslednje pogoje: • Življenjska doba več kot 15 let. • Stopnja korozijske atmosfere C4 (visoka). | Round ventilation ducts made of galvanised sheet metal according to SIST EN 1506, including inspection openings, shaped pieces, thickness according to the standard. The unit price (m) must take into account all joining and fixing material (flanges, cut-offs, clamps, bolts, gaskets, reinforcements, including hanging and fixing material of the system manufacturer with properties according to the requirements of SIST EN 12236: 2002, including painting of all metal corrosion-protected parts, after thorough cleaning to a metallic gloss. The corrosion protection shall be carried out in accordance with EN12944, for the following conditions: - Lifetime over 15 years. - Corrosive atmosphere C4 (high).
| - Okrogli prezračevalni kanali Ø630 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø630 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 25 |  | 0
| - Okrogli prezračevalni kanali Ø710 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø710 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 10 |  | 0
1.5 | Pravokotni prezračevalni kanali izdelani iz pocinkane pločevine po SIST EN 1505:1999, debeline po DIN 24190, klase tesnosti B po SIST EN 1507:2006, vključno z revizijskimi odprtinami, oblikovnimi kosi. V ceni na enoto (m2) je potrebno upoštevati ves spojni in pritrdilni material (prirobnice, odrez, spone, vijaki, tesnila, usmerjevalniki, ojačitve, vključno z obešalnim in pritrdilnim materialom sistemskega proizvajalca z lastnostmi odgovarjajoč zahtevam SIST EN 12236: 2002, vključno pleskanje vseh kovinskih korozijsko nezaščitenih delov, po temeljitem predhodnem čiščenju do kovinskega sijaja. Antikorozijska zaščita se izvaja v skladu z EN 12944 za naslednje pogoje: • Življenjska doba več kot 15 let. • Stopnja korozijske atmosfere C4 (visoka). | Rectangular ventilation ducts made of galvanised sheet metal according to SIST EN 1505:1999, thickness according to DIN 24190, tightness class B according to SIST EN 1507:2006, including inspection openings, shaped pieces. The unit price (m2) must take into account all joining and fixing material (flanges, cut-off, clamps, bolts, gaskets, guides, reinforcements, including hanging and fixing material of the system manufacturer with properties corresponding to the requirements of SIST EN 12236:2002, including the painting of all metal corrosion-protected parts, after thorough preliminary cleaning to a metallic gloss. The anticorrosive protection shall be performed in accordance with EN 12944 for the following conditions: - Lifetime over 15 years. - Corrosive atmosphere C4 (high). | m2 | 540 |  | 0
1.6 | Toplotna izolacija zajemnih, izpušnih ter vtočnih kanalov s parozapornimi ploščami izdelanimi iz sintetičnega kavčuka z zaprto celično strukturo, toplotne prevodnosti manjše ali enake 0,033W/mK pri srednji temperaturi 0 °C, koeficient upora difuziji vodene pare večji ali enak 10000 testirano v skladu z EN 13469 za cevi in EN 12086 za plošče, požarna klasifikacija B/BL-s3,d0 po DIN 4102, oziroma po SIST EN 13501-1. | Thermal insulation of intake, exhaust and inlet ducts with vapour control panels made of synthetic rubber with closed cell structure, thermal conductivity less than or equal to 0,033 W/mK at a mean temperature of 0 °C, resistance coefficient to diffusion of water vapour greater than or equal to 10000 tested in accordance with EN 13469 for pipes and EN 12086 for panels, fire classification B/BL-s3,d0 according to DIN 4102, or according to SIST EN 13501-1.
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - ARMACELL tip: Armaflex AF | - ARMACELL tip: Armaflex AF
| Toplotna izolacija zajemnih kanalov na vtočni strani (ZUZ-ODA), debeline s = 50 mm, + original lepilo | Thermal insulation of the inlet side of the intake ducts (ZUZ-ODA), thickness s = 50 mm, + original adhesive | m2 | 3 |  | 0
| Toplotna izolacija notranjih kanalov na vtočni strani (VTZ-SUP), debeline s = 19 mm, + original lepilo | Thermal insulation of internal ducts on the inlet side (VTZ-SUP), thickness s = 19 mm, + original adhesive | m2 | 270 |  | 0
| Toplotna izolacija izpušnih kanalov (ZAZ-EHA), debeline s = 19 mm, + original lepilo | Exhaust duct insulation (ZAZ-EHA), thickness s = 19 mm, + original adhesive | m2 | 150 |  | 0
1.7 | Požarna izolacija namenjena požarni izolaciji prezračevalnih kanalov, požarne odpornost EI90 po EN 13501, ustrezna za montažo od zunaj ter izdelana na način, da je odporna na zunanje vremenske vplive, vključno z vsem potrebnim pritrdilnim in montažnim materialom. | Fire insulation designed for the fire insulation of ventilation ducts, fire-resistance rating EI90 according to EN 13501, suitable for external installation and manufactured to withstand external weathering, including all necessary fixing and installation materials.
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - PROMAT, KNAUF | - PROMAT, KNAUF
| Požrna izolacija | Fire insulation | m2 | 46 |  | 0
1.8 | Talna rešetka za dovod zraka, aluminijasta s fiksnimi vodoravnimi usmerniki pod kotom 0 stopinj, izdelana iz vlečenih Al profilov, pritrjena na vgradni okvir z vidnimi vijaki, nastavni del s protismernimi lamelami za regulacijo količine zraka, skupaj z montažnim materialom, barve v skladu z zahtevam načrta arhitekture, tipa: | Floor air inlet grille, aluminium with fixed horizontal rectifiers at an angle of 0 degrees, made of drawn Al profiles, fixed to the mounting frame with visible screws, adjusting part with anti-air volume control louvres, including mounting material, colour according to the requirements of the architectural plan, type:
| - dimenzije B=500/H=100 | - dimensions B=500/H=100
| - pretok q = 150 m3/h | - flow rate q = 150 m3/h
| - prost prerez Aef=0,017 m2 | - free cross-section Aef=0,017 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - TECNOVENTIL tip BP5/CTX 500x100 | - TECNOVENTIL tip BP5/CTX 500x100
| Oznaka: / | Tag: / | kpl | 5 |  | 0
1.9 | Vrtinčni difutor, primeren za navpično montažo v stopnice, sestavljena iz okrogle vrtinčne difuzorske plošče in pritrdilnega obroča za hitro montažo, z radialno razporejenimi lamelami za usmerjanje zraka in izjemno hitro zmanjšanje hitrosti zraka ter temperaturne razlike, izdelan iz jeklene pločevine, skupaj z montažnim materialom, barve v skladu z zahtevam načrta arhitekture, tipa: | Vortex diffuser, suitable for vertical installation in stairs, consisting of a circular vortex diffuser plate and a fastening ring for quick installation, with radially arranged slats to direct the air and reduce air velocity and temperature difference extremely quickly, made of sheet steel, complete with mounting material, colour according to the requirements of the architectural plan, type:
| - dimenzije Ø60/Ø35 | - dimensions Ø60/Ø35
| - pretok q = 7,53 m3/h | - flow rate q = 7,53 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SCHAKO tip SAR-060 | - SCHAKO type SAR-060
| Oznaka: / | Tag: / | kpl | 1534 |  | 0
1.10 | Rešetka za dovod zraka, izdelana iz aluminijskih profilov, sestavljena iz nosilnega okvirja z vodoravnim in navpičnim nastavljivim lamelam, dodatkom za nastavitev količine zraka, pritrditev rešetke na prezračevalni kanal, z ugradim okvirjem, vključno z vsem pritrdilnim in montažnim materialom, barva v skladu z zahtevam načrta arhitekture, tipa: | Air inlet grille made of aluminium profiles, consisting of a support frame with horizontal and vertical adjustable slats, air volume adjustment accessory, grille attachment to the ventilation duct, with a framed frame, including all fixing and mounting material, colour in accordance with the requirements of the architectural plan, type:
| - dimenzije B=800/H=400 | - dimensions B=800/H=400
| - pretok q = 1025 m3/h | - flow rate q = 1025 m3/h
| - prost prerez Aef=0,194 m2 | - free cross-section Aef=0,194 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-A-2-2-800x400-R1 | - SYSTEMAIR tip NOVA-A-2-2-800x400-R1
| Oznaka: / | Tag: / | kpl | 11 |  | 0
1.11 | Rešetka za dovod zraka, izdelana iz aluminijskih profilov, sestavljena iz nosilnega okvirja z vodoravnim in navpičnim nastavljivim lamelam, dodatkom za nastavitev količine zraka, pritrditev rešetke na prezračevalni kanal, z ugradim okvirjem, vključno z vsem pritrdilnim in montažnim materialom, barva v skladu z zahtevam načrta arhitekture, tipa: | Air inlet grille made of aluminium profiles, consisting of a support frame with horizontal and vertical adjustable slats, air volume adjustment accessory, grille attachment to the ventilation duct, with a framed frame, including all fixing and mounting material, colour in accordance with the requirements of the architectural plan, type:
| - dimenzije B=400/H=400 | - dimensions B=400/H=400
| - pretok q = 512/513 m3/h | - flow rate q = 512/513 m3/h
| - prost prerez Aef=0,095 m2 | - free cross-section Aef=0,095 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-A-2-2-400x400-R1 | - SYSTEMAIR tip NOVA-A-2-2-400x400-R1
| Oznaka: / | Tag: / | kpl | 2 |  | 0
1.12 | Rešetka za dovod zraka, izdelana iz aluminijskih profilov, sestavljena iz nosilnega okvirja z vodoravnim in navpičnim fiksnim lamelam, dodatkom za nastavitev količine zraka, pritrditev rešetke na prezračevalni kanal, z ugradim okvirjem, vključno z vsem pritrdilnim in montažnim materialom, barva v skladu z zahtevam načrta arhitekture, tipa: | Air inlet grille made of aluminium profiles, consisting of a support frame with horizontal and vertical fixed slats, air volume adjustment accessory, grille attachment to the ventilation duct, with a framed frame, including all fixing and mounting material, colour in accordance with the requirements of the architectural plan, type:
| - dimenzije B=200/H=100 | - dimensions B=200/H=100
| - pretok q = 100 m3/h | - flow rate q = 100 m3/h
| - prost prerez Aef=0,013 m2 | - free cross-section Aef=0,013 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-E-2-200x100-R1 | - SYSTEMAIR tip NOVA-E-2-200x100-R1
| Oznaka: / | Tag: / | kpl | 1 |  | 0
1.13 | Rešetka za odvod zraka, izdelana iz jeklene pocinkane pločevine, sestavljena iz nosilnega okvirja z navpičnim nastavljivim lamelam, dodatkom za nastavitev količine zraka, pritrditev rešetke na prezračevalni kanal, z ugradim okvirjem, vključno z vsem pritrdilnim in montažnim materialom, barva v skladu z zahtevam načrta arhitekture, tipa: | Air outlet grille made of galvanised sheet steel, consisting of a support frame with vertical adjustable slats, air volume adjustment accessory, grille attachment to the ventilation duct, with a framed frame, including all fixing and mounting material, colour according to the requirements of the architectural plan, type:
| - dimenzije B=825/H=225 | - dimensions B=825/H=225
| - pretok q = 850 m3/h | - flow rate q = 850 m3/h
| - prost prerez Aef=0,134 m2 | - free cross-section Aef=0,134 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-C-1-825x225-R1 | - SYSTEMAIR tip NOVA-C-1-825x225-R1
| Oznaka: / | Tag: / | kpl | 8 |  | 0
1.14 | Rešetka za odvod zraka, izdelana iz jeklene pocinkane pločevine, sestavljena iz nosilnega okvirja z navpičnim nastavljivim lamelam, dodatkom za nastavitev količine zraka, pritrditev rešetke na prezračevalni kanal, z ugradim okvirjem, vključno z vsem pritrdilnim in montažnim materialom, barva v skladu z zahtevam načrta arhitekture, tipa: | Air outlet grille made of galvanised sheet steel, consisting of a support frame with vertical adjustable slats, air volume adjustment accessory, grille attachment to the ventilation duct, with a framed frame, including all fixing and mounting material, colour according to the requirements of the architectural plan, type:
| - dimenzije B=1025/H=225 | - dimensions B=1025/H=225
| - pretok q = 1225 m3/h | - flow rate q = 1225 m3/h
| - prost prerez Aef=0,168 m2 | - free cross-section Aef=0,168 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-C-1-1025x225-R1 | - SYSTEMAIR tip NOVA-C-1-1025x225-R1
| Oznaka: / | Tag: / | kpl | 4 |  | 0
1.15 | Rešetka za odvod zraka, izdelana iz aluminijskih profilov, sestavljena iz nosilnega okvirja z vodoravnim in navpičnim fiksnim lamelam, dodatkom za nastavitev količine zraka, pritrditev rešetke na prezračevalni kanal, z ugradim okvirjem, vključno z vsem pritrdilnim in montažnim materialom, barva v skladu z zahtevam načrta arhitekture, tipa: | Air outlet grille made of aluminium profiles, consisting of a support frame with horizontal and vertical fixed slats, air volume adjustment accessory, grille attachment to the ventilation duct, with a framed frame, including all fixing and mounting material, colour in accordance with the requirements of the architectural plan, type:
| - dimenzije B=200/H=100 | - dimensions B=200/H=100
| - pretok q = 100 m3/h | - flow rate q = 100 m3/h
| - prost prerez Aef=0,013 m2 | - free cross-section Aef=0,013 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-E-2-200x100-R1 | - SYSTEMAIR tip NOVA-E-2-200x100-R1
| Oznaka: / | Tag: / | kpl | 1 |  | 0
1.16 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije B=1400/H=650 | - dimensions B=1400/H=650
| - pretok q = 12300 m3/h | - flow rate q = 12300 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-1400x650 | - SYSTEMAIR tip FDS-1400x650
| Oznaka: KFD01.311; KFD01.312 | Code: KFD01.311; KFD01.312 | kpl | 2 |  | 0
1.17 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study with fastening and sealing material type:
| - dimenzije B=1400/H=750 | - dimensions B=1400/H=750
| - pretok q = 11700 m3/h | - flow rate q = 11700 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-1400x750 | - SYSTEMAIR tip FDS-1400x750
| Oznaka: KFD01.411 | Code: KFD01.411 | kpl | 1 |  | 0
1.18 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije Ø630 | - dimensions Ø630
| - pretok q = 3600 m3/h | - flow rate q = 3600 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-630 | - SYSTEMAIR tip FDR-3G-630
| Oznaka: KFD01.412; KFD01.414 | Code: KFD01.412; KFD01.414 | kpl | 2 |  | 0
1.19 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije Ø710 | - ø710 dimensions
| - pretok q = 4500 m3/h | - flow rate q = 4500 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-710 | - SYSTEMAIR tip FDR-3G-710
| Oznaka: KFD01.413 | Code: KFD01.413 | kpl | 1 |  | 0
1.20 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo regulacije konstantnega pretoka, s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow regulator, made of galvanised sheet metal with acoustic and thermal insulation, with constant flow control function, with fastening and sealing material type:
| - dimenzije Ø80 | - ø80 dimensions
| - pretok q = 100m3/h | - flow rate q = 100m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOTUS-RI-80-M0 | - SYSTEMAIR tip NOTUS-RI-80-M0
| Oznaka: CAV01.301; CAV01.401 | Code: CAV01.301; CAV01.401 | kpl | 2 |  | 0
1.21 | Volumski regulator pretoka zraka izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with fastening and sealing material type:
| - dimenzije 800x600 | - dimensions 800x600
| - pretok q = 12300 do 3700m3/h | - flow rate q = 12300 to 3700m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-SI-FC-800x600 | - SYSTEMAIR tip OPTIMA-SI-FC-800x600
| Oznaka: VAV01.311 | Code: VAV01.311 | kpl | 1 |  | 0
1.22 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije 750x600 | - dimensions 750x600
| - pretok q = 11700 do 3500m3/h | - flow rate q = 11700 to 3500m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-SI-FC-750x600 | - SYSTEMAIR tip OPTIMA-SI-FC-750x600
| Oznaka: VAV01.411 | Code: VAV01.411 | kpl | 1 |  | 0
1.23 | Elektromotorni pogon z vzmetjo za vstopno žaluzijo klimata, vključno z varnostno funkcijo (NC) in stikali položaja, s pritrdilnim in tesnilnim materialom tipa: | Electric motor actuator with spring for air-conditioning inlet shutter, including safety function (NC) and position switches, with fixing and sealing material type:
| - navor 10Nm | - torque 10Nm
| - električno napajanje 24V AC/DC | - 24V AC/DC power supply
| - ON/OFF regulacija delovanja | - ON/OFF operation control
| - za žaluzije do 2m2 | - for blinds up to 2m2
| - zaščita IP54 | - iP54 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip NF24A-S2 | - BELIMO type NF24A-S2
| Oznaka: KD01.101; KD01.102 | Code: KD01.101; KD01.102 | kpl | 2 |  | 0
1.24 | Elektromotorni pogon z vzmetjo za izstopno žaluzijo klimata, vključno z varnostno funkcijo (NC) in stikali položaja, s pritrdilnim in tesnilnim materialom tipa: | Electric motor drive with spring for climate exit blind, including safety function (NC) and position switches, with fixing and sealing material type:
| - navor 20Nm | - torque 20Nm
| - električno napajanje 24V AC/DC | - 24V AC/DC power supply
| - zvezna regulacija delovanja | - continuous operation control
| - za žaluzije do 4m2 | - for blinds up to 4m2
| - zaščita IP54 | - iP54 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip SF24A-SR-S2 | - BELIMO type SF24A-SR-S2
| Oznaka: KA01.202 | Code: KA01.202 | kpl | 1 |  | 0
1.25 | Elektromotorni pogon za obtok regeneratorja, s stikalom položaja za odprt položaj, s pritrdilnim in tesnilnim materialom tipa: | Electric motor drive for regenerator circulation, with position switch for open position, with fixing and sealing material type:
| - navor 5Nm | - torque 5Nm
| - električno napajanje 24V AC/DC | - 24V AC/DC power supply
| - ON/OFF regulacija delovanja | - ON/OFF operation control
| - za žaluzije do 1m2 | - for blinds up to 1m2
| - zaščita IP54 | - iP54 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip LM24A-S | - BELIMO type LM24A-S
| Oznaka: KD01.104; KD01.203 | Code: KD01.104; KD01.203 | kpl | 2 |  | 0
1.26 | Elektromotorni pogon za mešalno žaluzijo klimata, s pritrdilnim in tesnilnim materialom tipa: | Electric motor drive for air-conditioning mixing louvre, with fixing and sealing material type:
| - navor 5Nm | - torque 5Nm
| - električno napajanje 24V AC/DC | - 24V AC/DC power supply
| - zvezna regulacija delovanja | - continuous operation control
| - za žaluzije do 1m2 | - for blinds up to 1m2
| - zaščita IP54 | - iP54 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip LM24A-SR | - BELIMO type LM24A-SR
| Oznaka: KA01.105 | Code: KA01.105 | kpl | 1 |  | 0
1.27 | Kanalski senzor diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Duct differential pressure sensor, with mounting and sealing material type:
| - območje prikazovanja od 0 do 1500 Pa | - display range 0 to 1500 Pa
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22ADP-184A | - BELIMO type 22ADP-184A
| Oznaka: PICAL01.209; PICAL01.116 | Code: PICAL01.209; PICAL01.116 | kpl | 2 |  | 0
1.28 | Diferenčno tlačno stikalo, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure switch, with type fastening and sealing material:
| - območje prikazovanja od 50 do 500Pa | - display range 50 to 500Pa
| - kontaktni tok maksimalno 1,0A / AC 250V | - contact current max 1.0A / AC 250V
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 01APS-10U | - BELIMO type 01APS-10U
| Oznaka: PDSAH01.100; PDSAH01.113; PDSAH01.203; PDSAH01.207 | Code: PDSAH01.100; PDSAH01.113; PDSAH01.203; PDSAH01.207 | kpl | 4 |  | 0
1.29 | Prikazovalnik diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure indicator, with type fixing and sealing material:
| - območje prikazovanja od 50 do 500Pa | - display range 50 to 500Pa
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DWYER tip Magnahelic | - DWYER tip Magnahelic
| Oznaka: PDI01.100; PDI01.113; PDI01.203; PDI01.207 | Code: PDI01.100; PDI01.113; PDI01.203; PDI01.207 | kpl | 4 |  | 0
1.30 | Tipalo diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure sensor, with mounting and sealing material type:
| - območje prikazovanja od 0 do 1500 Pa | - display range 0 to 1500 Pa
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22ADP-184A | - BELIMO type 22ADP-184A
| Oznaka: PDIC01.110; PDIC01.205 | Code: PDIC01.110; PDIC01.205 | kpl | 2 |  | 0
1.31 | Tipalo diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure sensor, with mounting and sealing material type:
| - območje prikazovanja od 0 do 500 Pa | - display range 0 to 500 Pa
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22ADP-184A | - BELIMO type 22ADP-184A
| Oznaka: PDIC01.103 | Code: PDIC01.103 | kpl | 1 |  | 0
1.32 | Kanalsko tipalo temperature in vlage, s pritrdilnim in tesnilnim materialom tipa: | Duct temperature and humidity sensor, with fixing and sealing material type:
| - območje prikazovanja od 0 do 100%RH | - display range 0 to 100%RH
| - območje prikazovanja od -40 do 60°C | - display range -40 to 60°C
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22DTH-13M | - BELIMO type 22DTH-13M
| Oznaka: TIC/MIC01.114; TIC/MIC01.208 | Code: TIC/MIC01.114; TIC/MIC01.208 | kpl | 2 |  | 0
1.33 | Prostorsko tipalo temperature, vlage in kvalitete zraka CO2, s pritrdilnim in tesnilnim materialom tipa: | Room temperature, humidity and air quality sensor CO2, with fixing and sealing material type:
| - območje merjenja od 0 do 50°C | - measuring range 0 to 50°C
| - območje merjenja od 0 do 100%RH | - measuring range 0 to 100%RH
| - območje CO2 od 0 do 2000ppm | - cO2 range from 0 to 2000ppm
| - izhodni signal 0 do 10V | - output signal 0 to 10V
| - izhodni signal MP-Bus | - mP-Bus output signal
| - zaščita IP30 | - iP30 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22RTM-19-1 | - BELIMO type 22RTM-19-1
| Oznaka: TIC/MIC/QIC01.501 | Code: TIC/MIC/QIC01.501 | kpl | 1 |  | 0
1.34 | Protizmrzovalni termostat, s pritrdilnim in tesnilnim materialom tipa: | Anti-freezing thermostat, with fixing and sealing material type:
| - območje od -10 do 15°C | - range -10 to 15°C
| - dolžina kapilare 6m | - capillary length 6m
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 01ATS-105XC | - BELIMO type 01ATS-105XC
| Oznaka: TSZAL01.107 | Code: TSZAL01.107 | kpl | 1 |  | 0
1.35 | Obtočna črpalka, elektronsko regulirana s frekvenčnim pretvornikom, tipalom diferenčnega tlaka, internimi hidravličnimi, električnimi in komunikacijskimi povezavami, PN10, material jeklena litina, skladnost z ErP, pritrdilnim in tesnilnim materialom tipa: | Circulation pump, electronically controlled with frequency converter, differential pressure sensor, internal hydraulic, electrical and communication connections, PN10, material cast steel, ErP compliant, type fastening and sealing material:
| - za obtok ogrevne vode 50/40°C | - for circulating heating water 50/40°C
| - za pretok V = 1,71m3/h, tlačna višina H = 1.8m | - for flow rate V = 1.71m3/h, pressure head H = 1.8m
| - možnost izbire delovanja črpalke na proporcionalni tlak ter optimizacijo delovne obratovalne točke | - option to select proportional pressure pump operation and optimise the operating point
| - napajanje Pel = 0,050kW, 230V / 50Hz | - power supply Pel = 0,050kW, 230V/50Hz
| - navojni priključek G 1 1/2 | - threaded connection G 1 1/2
| - tlačna stopnja PN10 | - pressure rating PN10
| - temperaturno območje ogrevnega medija od -10 do 110°C | - temperature range of the heating medium from -10 to 110°C
| - komunikacija s CNS RS485 | - communication with CNS RS485
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - GRUNDFOS tip MAGNA3 25-40 | - GRUNDFOS type MAGNA3 25-40
| Oznaka: P01.106 | Code: P01.106 | kpl | 1 |  | 0
1.36 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za ogrevno vodo 50/40°C | - for heating water 50/40°C
| - za pretok V = 1,71m3/h | - for a flow rate of V = 1,71m3/h
| - območje regulacije pretoka do 3200 l/h (3.20 m3/h) | - flow control range up to 3200 l/h (3.20 m3/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - navojni priključek G 1 1/2 po ISO 228/1 | - threaded connection G 1 1/2 according to ISO 228/1
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 20 - 400 kPa, min. dif. tlak 20 kPa | - differential pressure range 20 - 400 kPa, min. differential pressure 20 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM32 | - DANFOS type AB-QM32
| Oznaka: VA01.106 | Code: VA01.106 | kpl | 1 |  | 0
1.37 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za ogrevno vodo 50/40°C | - for heating water 50/40°C
| - za pretok V = 3,11m3/h | - for a flow rate of V = 3,11m3/h
| - območje regulacije pretoka do 3200 l/h (3.20 m3/h) | - flow control range up to 3200 l/h (3.20 m3/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - navojni priključek G 1 1/2 po ISO 228/1 | - threaded connection G 1 1/2 according to ISO 228/1
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 20 - 400 kPa, min. dif. tlak 20 kPa | - differential pressure range 20 - 400 kPa, min. differential pressure 20 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM32 | - DANFOS type AB-QM32
| Oznaka: VA01.111 | Code: VA01.111 | kpl | 1 |  | 0
1.38 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za hladilno vodo 9/14°C | - for cooling water 9/14°C
| - za pretok V = 12,74m3/h | - for a flow rate of V = 12,74m3/h
| - območje regulacije pretoka do 20000 l/h (20 m3/h) | - flow control range up to 20000 l/h (20 m3/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - prirobnični priključek DN65 | - flange connection DN65
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 30 - 400 kPa, min. dif. tlak 30 kPa | - differential pressure range 30 - 400 kPa, min. differential pressure 30 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM65 | - DANFOS type AB-QM65
| Oznaka: VA01.109 | Code: VA01.109 | kpl | 1 |  | 0
1.39 | Sistem reverzne osmoze s predfiltracijo za pripravo demineralizirane vode za potrebe vlažilnika klimatov KS01, KS02, KS15, KS16, s pritrdilnim in tesnilnim materialom, skupaj s/z: | Reverse osmosis system with pre-filtration for the preparation of demineralised water for the humidifier of air-conditioners KS01, KS02, KS15, KS16, with fixing and sealing material, incl:
| - svečnim filtrom s 5 m filternimi vložki | - candle filter with 5 m filter cartridges
| - vstopnim magnetnim ventilom | - inlet solenoid valve
| - vstopnim zaščitnim tlačnim stikalom | - inlet pressure relief switch
| - spiralno navitimi RO moduli v tlačnem ohišju | - spiral wound RO modules in a pressure housing
| - internimi cevnimi povezavami | - internal pipe connections
| - merilcema trenutnega pretoka dobitka in koncentrata | - instantaneous flow meters for the feed and concentrate
| - manometri za kontrolo tlaka vode na vstopu in izstopu koncentrata | - pressure gauges for controlling the water pressure at the inlet and outlet of the concentrate
| - merilcem prevodnosti dobitka | - a conductivity meter
| - mikroprocesorsko krmilno enoto | - microprocessor control unit
| - vzorčevalno pipico | - sampling tap
| - nosilno konstrukcijo iz nerjavnega jekla | - stainless steel load-bearing structure
| - ročno tipko za zaustavitev in zagon RO | - manual key to stop and start the RO
| - plovnim stikalom | - float switch
| - dimenzije naprave 500x1500x500 mm | - dimensions 500x1500x500 mm
| - pretok dobitka 150 l/h | - 150 l/h recharge flow
| - izkoristek naprave 50 - 70 % | - plant efficiency 50 - 70 %
| - zadržani topljenec min 98 % | - solvent retention min 98 %
| - priključki vstop/izstop DN15 | - inlet/outlet connections DN15
| - vstopni tlak min 1,5 bar | - inlet pressure min 1,5 bar
| - delovni tlak 15 bar | - working pressure 15 bar
| - delovna temperatura 10- 35 °C | - operating temperature 10- 35 °C
| - električni priključek 220/50/0,55 V/Hz/kW | - 220/50/0,55 V/Hz/kW electrical connection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - MAKCMC tip MINIRO 15 | - MAKCMC type MINIRO 15
| Oznaka: | Code: | kpl | 1 |  | 0
1.40 | Rezervoar demineralizirane vode in črpalna postaja za potrebe vlažilnika klimatov KS01, KS02, KS15, KS16, s pritrdilnim in tesnilnim materialom, skupaj s/z: | Demineralised water tank and pumping station for the humidifier of air-conditioners KS01, KS02, KS15, KS16, with fixing and sealing material, incl:
| - rezervoarjem iz PE | - pE tank
| - nivojskimi stikali: min/maks, za zaščito črpalke in signalizacijo preliva | - level switches: min/max, for pump protection and overflow signalling
| - hidrostatična sonda za zvezni nivo v rezervoarju | - hydrostatic probe for continuous tank level
| - pripadajočo PVC armaturo | - associated PVC fittings
| - varnostnim prelivom | - safety dressing
| - kontrolnim manometrom | - a check gauge
| - ekspanzijsko posodo iz nerjavnega jekla | - stainless steel expansion tank
| - tlačnim stikalom | - pressure switch
| - centrifugalno črpalko CM 1-6; material nerjavno jeklo AISI 316 | - centrifugal pump CM 1-6; material stainless steel AISI 316
| - volumen rezervoarja 115 l | - tank capacity 115 l
| - dimenzije rezervoarja D460x775 mm | - tank dimensions D460x775 mm
| - kapaciteta črpalke 1,7 m3/h | - pump capacity 1.7 m3/h
| - tlak 3,7bar | - pressure 3,7bar
| - priključki DN 25 | - dN 25 connections
| - el. priključek 400/50/460 V/Hz/W | - 400/50/460 V/Hz/W power connection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - MAKCMC tip RDI 12 C1 | - MAKCMC type RDI 12 C1
| Oznaka: | Code: | kpl | 1 |  | 0
1.41 | Avtomatski dvojni ionski mehčalec vode za potrebe vlažilnika klimatov KS01, KS02, KS15, KS16, s pritrdilnim in tesnilnim materialom, skupaj s/z: | Automatic double ion water softener for the humidifier needs of air conditioners KS01, KS02, KS15, KS16, with fixing and sealing material, incl:
| - elektro-mehanskim krmilnikom | - electro-mechanical controller
| - večpotnim ventilom z dvema distributorjema | - multiport valve with two distributors
| - tlačno posodo iz armiranega polietilena komplet 2 | - pressure vessel of reinforced polyethylene, set of 2
| - solnim ventilom | - salt valve
| - solnikom | - to solnikom
| - smolo močno kislega ionskega izmenjevalca | - strong acid ion-exchange resin
| - čistilnim kosom | - cleaning pieces
| - tabletirano soljo 25kg | - tablet salt 25kg
| - dimenzije naprave 1500x700x1100 mm | - dimensions 1500x700x1100 mm
| - volumen ionske smole 2 x 18 l | - ionic resin volume 2 x 18 l
| - volumen tlačne posode 2 x 20,4 l | - pressure vessel volume 2 x 20.4 l
| - volumen solnika 100 l | - brine tank capacity 100 l
| - poraba tabletirane soli 2,7 – 4,3 kg/reg | - tablet salt consumption 2,7 - 4,3 kg/reg
| - pretok 0,1 – 0,9 m3/h | - flow rate 0,1 - 0,9 m3/h
| - kapaciteta 9,9 –11,2 m3/reg | - capacity 9,9 -11,2 m3/reg
| - priključki vstop/izstop DN20 | - inlet/outlet connections DN20
| - delovni tlak 2,5 – 6 bar | - working pressure 2,5 - 6 bar
| - delovna temperatura do 40°C | - operating temperature up to 40°C
| - el. priključek 220/50/10 V/Hz/W | - 220/50/10 V/Hz/W power connection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - MAKCMC tip MINOM 0DF - 25 | - MAKCMC type MINOM 0DF - 25
| Oznaka: | Code: | kpl | 1 |  | 0
1.42 | Sistem za UV dezinfekcijo vode za potrebe vlažilnika klimatov KS01, KS02, KS15, KS16, s pritrdilnim in tesnilnim materialom, skupaj s/z: | UV water disinfection system for the humidifier of air conditioners KS01, KS02, KS15, KS16, with fixing and sealing material, incl:
| - reaktorjem: material 1.4404, elektopoliran | - reactor: material 1.4404, electropolished
| - nizkotlačnim UV sevalom v zaščitni cevi iz kremenčevega stekla | - low-pressure UV radiation in a protective quartz glass tube
| - mehkim zagonom delovanja sevala | - soft start of the radiator
| - signalizacijo za zamenjavo sevala | - signalling for radiator replacement
| - signalizacijo napak delovanja | - fault signalling
| - upravljalno enoto | - the control unit
| - dimenzije upravljalne enote 168x200x66 mm | - control unit dimensions 168x200x66 mm
| - priključki 3/4 '' | - 3/4'' connections
| - obratovalni tlak PN10 | - operating pressure PN10
| - UV doza 400 J/m2 | - UV dose 400 J/m2
| - hidravlična kapaciteta maks 1,69 m3/h | - hydraulic capacity max 1,69 m3/h
| - temperatura vode 0-35°C | - water temperature 0-35°C
| - temperatura okolice maks 35°C | - ambient temperature max 35°C
| - zaščita reaktor/upravlj. enota IP 65/54 | - reactor/management unit protection IP 65/54
| - el. priključek 220/50/55 V/Hz/W | - 220/50/55 V/Hz/W power connection
| - življenska doba svetil 8.760 h | - lamp life 8.760 h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - MAKCMC tip AQUADA 2 PRO | - MAKCMC tip AQUADA 2 PRO
| Oznaka: | Code: | kpl | 1 |  | 0
| PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS01 | VENTILATION AND AIR CONDITIONING SYSTEM KS01 |  |  |  | 0

## 4.4.2_PrKlim KS02
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.4 | STROJNA DELA | MECHANICAL WORKS
4.4.2 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS02 | VENTILATION AND AIR CONDITIONING SYSTEM KS02 |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
2 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS02 | VENTILATION AND AIR CONDITIONING SYSTEM KS02
2.1 | Klimatska naprava za dovod in odvod zraka KD02/KO02 - glej tudi zavihek Zahteve klimati. | KD02/KO02 supply and extract air conditioner - see also Climate requirements tab.
| Tehnične karakteristike naprave (opis v smeri toka zraka): | Technical characteristics of the appliance (description downstream):
| Dovod: Vdov = 3510 m3/h | Input: Vdov = 3510 m3/h
| - posluževanje dovod: levo v smeri toka zraka! | - inlet: left in the direction of the air flow!
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 10 60% po ISO 16890 (M5 po SIST EN 779), z regulacijsko žaluzijo 923x638x125, s fleksibilnim čelnim priključkom, za pretok zraka 3510m3/h. Maksimalni končni padec tlaka 200Pa. Oznaka: F02.102 | - Filter unit with bag filter cartridge of filtration level ePM 10 60% according to ISO 16890 (M5 according to SIST EN 779), with control shutter 923x638x125, with flexible front connection, for air flow 3510m3/h. Maximum final pressure drop 200Pa. Code: F02.102
| - Rotacijska regeneratorska enota za prenos senzibilne in latentne toplote. Tehnični podatki za zimsko obdobje: - pretok zraka 3510/3320m3/h - stopnja vračanja občutene toplote: 74,7% - stopnja vračanja latentne toplote: 75,7% - vračanje toplotne energije: 37,90kW - stanje dovodnega zr. pred enoto: -13,00°C/90,0% - stanje dovodnega zraka za enoto: 12,40°C/42,3% Tehnični podatki za poletno obdobje: - pretok zraka 3510/3320m3/h - stopnja vračanja občutene toplote: 74,7% - stopnja vračanja latentne toplote: 70,9% - vračanje toplotne energije: 10,10kW - stanje dovodnega zr. pred enoto: 34,50°C/40,0% - stanje dovodnega zraka za enoto: 28,20°C/54,2% Oznaka: RE02.191 | - Rotary regenerative unit for sensible and latent heat transfer. technical data for the winter period: - air flow 3510/3320m3/h - sensible heat recovery rate: 74.7% - latent heat recovery rate: 75.7% - heat energy recovery: 37.90kW - supply air condition upstream of the unit: -13.00°C/90.0% - supply air condition for the unit: 12.40°C/42.3% Technical data for the summer period: - air flow 3510/3320m3/h - sensible heat recovery rate: 74.7% - latent heat recovery rate: 70.9% - heat energy recovery: 10.10kW - supply air condition upstream of the unit: 34.50°C/40.0% - supply air condition for the unit: 28.20°C/54.2% Code: RE02.191
| - Enota pred-grelnika zraka s protizmrzovalno zaščito. - pretok zraka 3510m3/h - grelna moč Qg=20,21kW - temperaturni režim ogrevnega medija 50/40°C - pretok ogrevnega medija 0,488 l/s - padec tlaka na zračni strani 31Pa - temperatura zraka vstop 12,40°C - temperatura zraka izstop 29,50°C - padec tlaka na strani ogr. medija (voda) 10,78kPa - priključka navojna 1" - tlačna stopnja PN16 Oznaka: HE02.103 | - Air preheater unit with anti-freeze protection. - air flow 3510m3/h - heating power Qg=20,21kW - heating medium temperature 50/40°C - heating medium flow rate 0,488 l/s - 31Pa pressure drop on the air side - air temperature inlet 12,40°C - air temperature outlet 29,50°C - pressure drop on the heating medium side (water) 10,78kPa - 1" threaded connectors - pressure rating PN16 Code: HE02.103
| - Vlažilna enota s kontaktnim vlaženjem zraka. Dovod sveže pripravljene demineralizirane vode, z materialom kontaktnega vlažilnika impregniranim srebrom, črpalko, potrebno merilno regulacijsko opremo, ventili na dovodu sveže vode ter ventilom na odvodu vode iz banje, s funkcijo samodejnega praznjenja banje vlažilnika in polnjenja s svežo pripravljeno mehčano vodo glede na prevodnost vode v banji, oziroma glede na čas ko vlažilnik ni v funkciji. Odvod kondenzata s sifonom z vodno in mehansko smardno zaporo. - pretok zraka 3510m3/h - priključna električna moč 0,05kW, 230V, 50Hz - padec tlaka na zračni strani dpz=90Pa - temperatura zraka vstop 29,5°C - relativna vlaga zraka vstop 15% - temperatura zraka izstop 27,27°C - relativna vlaga izstop 21% - izkoristek vlaženja 14,21% - vlaženje 7,2 kg/h - tipalo prevodonsti vode QICCD02.105 - tipalo zgornjega nivoja vode LICH02.105 - tipalo spodnjega nivoja vode LICL02.105 - elektromagnetni ventil za praznenje VD02.105 - elektromagnetni ventil za dovod sveže vode VD02.205 Oznaka: SH02.105 | - Humidification unit with contact humidification. Freshly prepared demineralised water supply, with silver-impregnated contact humidifier material, pump, necessary metering control equipment, valves at the fresh water inlet and at the water outlet of the humidifier tank, with automatic emptying of the humidifier tank and refilling with freshly prepared softened water according to the conductivity of the water in the tank, or according to the time when the humidifier is not in operation. Condensate drainage with siphon with water and mechanical odour trap. - air flow 3510m3/h - connection power 0,05kW, 230V, 50Hz - pressure drop on the air side dpz=90Pa - air temperature 29,5°C - relative humidity 15% - air temperature outlet 27,27°C - relative humidity 21% exit - humidification efficiency 14.21% - humidification 7,2 kg/h - water conductivity sensor QICCD02.105 - upper water level sensor LICH02.105 - lower water level sensor LICL02.105 - solenoid valve for emptying VD02.105 - fresh water inlet solenoid valve VD02.205 Code: SH02.105
| - Enota hladilnika z eliminatorjem kapljic in koritom za odvod kondenzata. - pretok zraka 3510m3/h - hladilna moč Qhtot=15,1kW - temperaturni režim hladilnega medija 9/14°C - pretok hladilnega medija 0.721 l/s - padec tlaka na zračni strani 43/39Pa - temperatura zraka vstop 28,20°C - temperatura zraka izstop 18,80°C - padec tlaka na strani hl. medija (voda) 17,94kPa - priključka navojna 1" - tlačna stopnja PN16 Oznaka: HE02.106 | - Refrigerator unit with drip eliminator and condensate drain. - air flow 3510m3/h - cooling power Qhtot=15,1kW - cooling medium temperature 9/14°C - coolant flow rate 0.721 l/s - air side pressure drop 43/39Pa - air temperature inlet 28,20°C - air temperature outlet 18,80°C - pressure drop on the medium side (water) 17,94kPa - 1" threaded connectors - pressure rating PN16 Code: HE02.106
| - Ventilatorska enota s prostotekočim rotorjem. Elektromotor je EC-motor, s 100% zvezno regulacijo vrtljajev preko potenciometra (0-10V), ki omogoča nastavitev delovanja ventilatorja na ustrezno delovno točko. Enota vsebuje: okence O150 in svetilko s stikalom ter servisno stikalo. - pretok zraka 3510m3/h - eksterni statični padec tlaka dpext=300Pa - priključna električna moč 2,4kW, 3x400V, 50Hz - razred izkoristka elektromotorja IE5/EC - zaščita IP55 Oznaka: FA02.107 | - Fan unit with free-flowing rotor. The electric motor is an EC motor, with 100% continuous speed control via a potentiometer (0-10V), which allows the fan to be set to the appropriate operating point. The unit contains: an O150 window and a lamp with switch and a service switch. - air flow 3510m3/h - external static pressure drop dpext=300Pa - connection power 2,4kW, 3x400V, 50Hz - electric motor efficiency class IE5/EC - iP55 protection Code: FA02.107
| - Dušilna enota. - pretok zraka 3510m3/h - padec tlaka dp=10Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 7 17 18 21 15 11 12 Oznaka: DZ02.108 | - Throttle unit. - air flow 3510m3/h - pressure drop dp=10Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 7 17 18 21 15 11 12 Code: DZ02.108
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 1 75% po ISO 16890 (F8 po SIST EN 779, s fleksibilnim čelnim priključkom, za pretok zraka 3510m3/h. Maksimalni končni padec tlaka 300Pa. Oznaka: F02.109 | - Filter unit with bag filter cartridge of filtration level ePM 1 75% according to ISO 16890 (F8 according to SIST EN 779, with flexible front connection, for air flow of 3510m3/h. Maximum final pressure drop 300Pa. Code: F02.109
| Dolžina: 5,640m | Length: 5,640m
| Širina: 1,060m | Width: 1,060m
| Višina: 0,875m | Height: 0,875m
| Kompletno z dobavo dodatne opreme: | Complete with supply of accessories:
| - odtočni sifoni | - drain traps
| - jadrovinasti nastavki | - sailplane spouts
| - s spojnim, tesnilnim in pritrdilnim materialom in priključki za senzorje, | - with jointing, sealing and fixing materials and sensor connectors,
| Odvod: Vodv = 3320 m3/h | Discharge: waterv = 3320 m3/h
| - posluževanje odvod: desno v smeri toka zraka! | - serving outlet: to the right in the direction of the air flow!
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 10 60% po ISO 16890 (M5 po SIST EN 779), s fleksibilnim čelnim priključkom, za pretok zraka 3320m3/h. Maksimalni končni padec tlaka 200Pa. Oznaka: F02.207 | - Filter unit with bag filter cartridge of filtration level ePM 10 60% according to ISO 16890 (M5 according to SIST EN 779), with flexible front connection, for an air flow of 3320m3/h. Maximum final pressure drop 200Pa. Code: F02.207
| - Dušilna enota. - pretok zraka 3320m3/h - padec tlaka dp=9Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 7 17 18 21 15 11 12 Oznaka: DZ02.206 | - Throttle unit. - air flow 3320m3/h - pressure drop dp=9Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 7 17 18 21 15 11 12 Code: DZ02.206
| - Ventilatorska enota s prostotekočim rotorjem. Elektromotor je EC-motor, s 100% zvezno regulacijo vrtljajev preko potenciometra (0-10V), ki omogoča nastavitev delovanja ventilatorja na ustrezno delovno točko. Enota vsebuje: okence O150 in svetilko s stikalom ter servisno stikalo. - pretok zraka 3320m3/h - eksterni statični padec tlaka dpext=300Pa - priključna električna moč 1.3kW, 3x400V, 50Hz - razred izkoristka elektromotorja IE5/EC - zaščita IP55 Oznaka: FA02.205 | - Fan unit with free-flowing rotor. The electric motor is an EC motor, with 100% continuous speed control via a potentiometer (0-10V), which allows the fan to be set to the appropriate operating point. The unit contains: an O150 window and a lamp with switch and a service switch. - air flow 3320m3/h - external static pressure drop dpext=300Pa - connection power 1.3kW, 3x400V, 50Hz - electric motor efficiency class IE5/EC - iP55 protection Code: FA02.205
| - Dušilna enota. - pretok zraka 3320m3/h - padec tlaka dp=9Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 7 17 18 21 15 11 12 Oznaka: DZ02.204 | - Throttle unit. - air flow 3320m3/h - pressure drop dp=9Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 7 17 18 21 15 11 12 Code: DZ02.204
| - Prazna enota z regulacijsko žaluzijo 923x638x125, fleksibilnim čelnim priključkom, za pretok zraka 3320m3/h. | - Empty unit with control louvre 923x638x125, flexible front connection, for air flow 3320m3/h.
| Dolžina: 4,020m | Length: 4,020m
| Širina: 1,060m | Width: 1,060m
| Višina: 0,750m | Height: 0,750m
| Kompletno z dobavo dodatne opreme: | Complete with supply of accessories:
| - postavitvene noge, gumirane, višine 100-200mm | - rubberised feet, height 100-200mm
| - odtočni sifoni | - drain traps
| - jadrovinasti nastavki | - sailplane spouts
| - postavitev klimata na antivibracijski dušilnik (gumo) za preprečevanje prenosa vibracij in hrupa na konstrukcijo objekta. Dušilniki morajo biti preračunani glede na lastnosti klimata (teža in vrtilna frekvenca ventilatorjev). | - installation of the air conditioner on an anti-vibration damper (rubber) to prevent the transmission of vibrations and noise to the structure of the building. The dampers must be calculated according to the characteristics of the air conditioner (weight and speed of the fans).
| - s spojnim, tesnilnim in pritrdilnim materialom in priključki za senzorje, | - with jointing, sealing and fixing materials and sensor connectors,
| Teža: 1.404kg | Weight: 1.404kg
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR | - SYSTEMAIR | kpl | 1 |  | 0
2.2 | Okrogli prezračevalni kanali izdelani iz pocinkane pločevine po SIST EN 1506, vključno z revizijskimi odprtinami, oblikovnimi kosi, debeline po standardu. V ceni na enoto (m) je potrebno upoštevati ves spojni in pritrdilni material (prirobnice, odrez, spone, vijaki, tesnila, ojačitve, vključno z obešalnim in pritrdilnim materialom sistemskega proizvajalca z lastnostmi odgovarjajoč zahtevam SIST EN 12236: 2002, vključno pleskanje vseh kovinskih korozijsko nezaščitenih delov, po temeljitem predhodnem čiščenju do kovinskega sijaja. Antikorozijska zaščita se izvaja v skladu z EN 12944 za naslednje pogoje: • Življenjska doba več kot 15 let. • Stopnja korozijske atmosfere C4 (visoka). | Round ventilation ducts made of galvanised sheet metal according to SIST EN 1506, including inspection openings, shaped pieces, thickness according to the standard. The unit price (m) must take into account all joining and fixing material (flanges, cut-offs, clamps, bolts, gaskets, reinforcements, including hanging and fixing material of the system manufacturer with properties according to the requirements of SIST EN 12236: 2002, including painting of all metal corrosion-protected parts, after thorough cleaning to a metallic gloss. The corrosion protection shall be carried out in accordance with EN12944, for the following conditions: - Lifetime over 15 years. - Corrosive atmosphere C4 (high).
| - Okrogli prezračevalni kanali Ø180 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø180 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 5 |  | 0
| - Okrogli prezračevalni kanali Ø200 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø200 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 45 |  | 0
| - Okrogli prezračevalni kanali Ø250 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø250 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 55 |  | 0
| - Okrogli prezračevalni kanali Ø280 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø280 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 70 |  | 0
| - Okrogli prezračevalni kanali Ø300 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø300 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 20 |  | 0
| - Okrogli prezračevalni kanali Ø315 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø315 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 5 |  | 0
2.3 | Okrogli pregibni kanali za priključitev stropnih difuzorjev, izdelani iz Al folije ter polnila iz materiala z dušilnim in toplotno-izolativnim efektom. V ceni na enoto (m) je potrebno upoštevati ves spojni material, pritrdilne objemke in tesnilni material, za podatke: | Round folded ducts for the connection of ceiling diffusers, made of Al foil and filling material with damping and thermal insulation effect. The unit price (m) must include all joining material, fixing clamps and sealing material, for details:
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DEC tip: SONODEC - 25 | - DEC tip: SUNDAY - 25
| - Okroglegi pregibni kanali Ø200 | - Ø200 round flexible ducts | m | 17 |  | 0
| - Okroglegi pregibni kanali Ø250 | - Round flexible ducts Ø250 | m | 12 |  | 0
2.4 | Pravokotni prezračevalni kanali izdelani iz pocinkane pločevine po SIST EN 1505:1999, debeline po DIN 24190, klase tesnosti B po SIST EN 1507:2006, vključno z revizijskimi odprtinami, oblikovnimi kosi. V ceni na enoto (m2) je potrebno upoštevati ves spojni in pritrdilni material (prirobnice, odrez, spone, vijaki, tesnila, usmerjevalniki, ojačitve, vključno z obešalnim in pritrdilnim materialom sistemskega proizvajalca z lastnostmi odgovarjajoč zahtevam SIST EN 12236: 2002, vključno pleskanje vseh kovinskih korozijsko nezaščitenih delov, po temeljitem predhodnem čiščenju do kovinskega sijaja. Antikorozijska zaščita se izvaja v skladu z EN 12944 za naslednje pogoje: • Življenjska doba več kot 15 let. • Stopnja korozijske atmosfere C4 (visoka). | Rectangular ventilation ducts made of galvanised sheet metal according to SIST EN 1505:1999, thickness according to DIN 24190, tightness class B according to SIST EN 1507:2006, including inspection openings, shaped pieces. The unit price (m2) must take into account all joining and fixing material (flanges, cut-off, clamps, bolts, gaskets, guides, reinforcements, including hanging and fixing material of the system manufacturer with properties corresponding to the requirements of SIST EN 12236:2002, including the painting of all metal corrosion-protected parts, after thorough preliminary cleaning to a metallic gloss. The anticorrosive protection shall be performed in accordance with EN 12944 for the following conditions: - Lifetime over 15 years. - Corrosive atmosphere C4 (high). | m2 | 300 |  | 0
2.5 | Toplotna izolacija zajemnih, izpušnih ter vtočnih kanalov s parozapornimi ploščami izdelanimi iz sintetičnega kavčuka z zaprto celično strukturo, toplotne prevodnosti manjše ali enake 0,033W/mK pri srednji temperaturi 0 °C, koeficient upora difuziji vodene pare večji ali enak 10000 testirano v skladu z EN 13469 za cevi in EN 12086 za plošče, požarna klasifikacija B/BL-s3,d0 po DIN 4102, oziroma po SIST EN 13501-1. | Thermal insulation of intake, exhaust and inlet ducts with vapour control panels made of synthetic rubber with closed cell structure, thermal conductivity less than or equal to 0,033 W/mK at a mean temperature of 0 °C, resistance coefficient to diffusion of water vapour greater than or equal to 10000 tested in accordance with EN 13469 for pipes and EN 12086 for panels, fire classification B/BL-s3,d0 according to DIN 4102, or according to SIST EN 13501-1.
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - ARMACELL tip: Armaflex AF | - ARMACELL tip: Armaflex AF
| Toplotna izolacija zajemnih kanalov na vtočni strani (ZUZ-ODA), debeline s = 50 mm, + original lepilo | Thermal insulation of the inlet side of the intake ducts (ZUZ-ODA), thickness s = 50 mm, + original adhesive | m2 | 5 |  | 0
| Toplotna izolacija notranjih kanalov na vtočni strani (VTZ-SUP), debeline s = 19 mm, + original lepilo | Thermal insulation of internal ducts on the inlet side (VTZ-SUP), thickness s = 19 mm, + original adhesive | m2 | 195 |  | 0
| Toplotna izolacija izpušnih kanalov (ZAZ-EHA), debeline s = 19 mm, + original lepilo | Exhaust duct thermal insulation (ZAZ-EHA), thickness s = 19 mm, + original adhesive | m2 | 80 |  | 0
2.6 | Požarna izolacija namenjena požarni izolaciji prezračevalnih kanalov, požarne odpornost EI90 po EN 13501, ustrezna za montažo od zunaj ter izdelana na način, da je odporna na zunanje vremenske vplive, vključno z vsem potrebnim pritrdilnim in montažnim materialom. | Fire insulation designed for the fire insulation of ventilation ducts, fire-resistance rating EI90 according to EN 13501, suitable for external installation and manufactured to withstand external weathering, including all necessary fixing and installation materials.
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - PROMAT, KNAUF | - PROMAT, KNAUF
| Požrna izolacija | Fire insulation | m2 | 41 |  | 0
2.7 | Kanalski dušilnik, za preprečevajne prenosa zvoka med prostori, izdelan iz pocinkane pločevine, mineralne volne za dušenje zvoka debeline 100mm, z zaščito pred erozijo iz netkane tkanine, vključno z vsem potrebnim pritrdilnim, povezovalnim, tesnilnim in montažnim materialom, tipa: | Duct silencer, to prevent the transmission of sound between rooms, made of galvanised sheet, 100mm thick mineral wool for sound attenuation, with non-woven fabric erosion protection, including all necessary fixing, connecting, sealing and mounting material, type:
| - dimenzije Ø250/900/100 | - dimensions Ø250/900/100
| - pretok q = 560 m3/h | - flow rate q = 560 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - LINDAB tip SLGU 250 - 900 -100 | - LINDAB type SLGU 250 - 900 -100
| Oznaka: DZ02.321; DZ02.322; DZ02.323 | Code: DZ02.321; DZ02.322; DZ02.323 | kpl | 3 |  | 0
2.8 | Kanalski dušilnik, za preprečevajne prenosa zvoka med prostori, izdelan iz pocinkane pločevine, mineralne volne za dušenje zvoka debeline 100mm, z zaščito pred erozijo iz netkane tkanine, vključno z vsem potrebnim pritrdilnim, povezovalnim, tesnilnim in montažnim materialom, tipa: | Duct silencer, to prevent the transmission of sound between rooms, made of galvanised sheet, 100mm thick mineral wool for sound attenuation, with non-woven fabric erosion protection, including all necessary fixing, connecting, sealing and mounting material, type:
| - dimenzije Ø250/900/100 | - dimensions Ø250/900/100
| - pretok q = 590 m3/h | - flow rate q = 590 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - LINDAB tip SLGU 250 - 900 -100 | - LINDAB type SLGU 250 - 900 -100
| Oznaka: DZ02.311; DZ02.312; DZ02.313 | Code: DZ02.311; DZ02.312; DZ02.313 | kpl | 3 |  | 0
2.9 | Kanalski dušilnik, za preprečevajne prenosa zvoka med prostori, izdelan iz pocinkane pločevine, mineralne volne za dušenje zvoka debeline 100mm, z zaščito pred erozijo iz netkane tkanine, vključno z vsem potrebnim pritrdilnim, povezovalnim, tesnilnim in montažnim materialom, tipa: | Duct silencer, to prevent the transmission of sound between rooms, made of galvanised sheet, 100mm thick mineral wool for sound attenuation, with non-woven fabric erosion protection, including all necessary fixing, connecting, sealing and mounting material, type:
| - dimenzije Ø250/900/100 | - dimensions Ø250/900/100
| - pretok q = 310 m3/h | - flow rate q = 310 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - LINDAB tip SLGU 250 - 900 -100 | - LINDAB type SLGU 250 - 900 -100
| Oznaka: DZ02.314; DZ02.315 | Code: DZ02.314; DZ02.315 | kpl | 2 |  | 0
2.10 | Kanalski dušilnik, za preprečevajne prenosa zvoka med prostori, izdelan iz pocinkane pločevine, mineralne volne za dušenje zvoka debeline 100mm, z zaščito pred erozijo iz netkane tkanine, vključno z vsem potrebnim pritrdilnim, povezovalnim, tesnilnim in montažnim materialom, tipa: | Duct silencer, to prevent the transmission of sound between rooms, made of galvanised sheet, 100mm thick mineral wool for sound attenuation, with non-woven fabric erosion protection, including all necessary fixing, connecting, sealing and mounting material, type:
| - dimenzije Ø250/900/100 | - dimensions Ø250/900/100
| - pretok q = 530 m3/h | - flow rate q = 530 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - LINDAB tip SLGU 250 - 900 -100 | - LINDAB type SLGU 250 - 900 -100
| Oznaka: DZ02.316 | Code: DZ02.316 | kpl | 1 |  | 0
2.11 | Kanalski dušilnik, za preprečevajne prenosa zvoka med prostori, izdelan iz pocinkane pločevine, mineralne volne za dušenje zvoka debeline 100mm, z zaščito pred erozijo iz netkane tkanine, vključno z vsem potrebnim pritrdilnim, povezovalnim, tesnilnim in montažnim materialom, tipa: | Duct silencer, to prevent the transmission of sound between rooms, made of galvanised sheet, 100mm thick mineral wool for sound attenuation, with non-woven fabric erosion protection, including all necessary fixing, connecting, sealing and mounting material, type:
| - dimenzije Ø250/900/100 | - dimensions Ø250/900/100
| - pretok q = 500 m3/h | - flow rate q = 500 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - LINDAB tip SLGU 250 - 900 -100 | - LINDAB type SLGU 250 - 900 -100
| Oznaka: DZ02.326 | Code: DZ02.326 | kpl | 1 |  | 0
2.12 | Kanalski dušilnik, za preprečevajne prenosa zvoka med prostori, izdelan iz pocinkane pločevine, mineralne volne za dušenje zvoka debeline 100mm, z zaščito pred erozijo iz netkane tkanine, vključno z vsem potrebnim pritrdilnim, povezovalnim, tesnilnim in montažnim materialom, tipa: | Duct silencer, to prevent the transmission of sound between rooms, made of galvanised sheet, 100mm thick mineral wool for sound attenuation, with non-woven fabric erosion protection, including all necessary fixing, connecting, sealing and mounting material, type:
| - dimenzije Ø200/900/100 | - dimensions Ø200/900/100
| - pretok q = 290 m3/h | - flow rate q = 290 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - LINDAB tip SLGU 250 - 900 -100 | - LINDAB type SLGU 250 - 900 -100
| Oznaka: DZ02.324; DZ02.325 | Code: DZ02.324; DZ02.325 | kpl | 2 |  | 0
2.13 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, sound and heat insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to the customer's or architect's preference, with connection chamber, with control damper, with connections for air flow measurement, inlet connection of the prepared air is provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø597, H=287, Ø200 | - dimensions Ø597, H=287, Ø200
| - pretok q = 265 m3/h | - flow rate q = 265 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-C-200 | - SYSTEMAIR tip CAP-C-200
| Oznaka: / | Tag: / | kpl | 2 |  | 0
2.14 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, sound and heat insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to the customer's or architect's preference, with connection chamber, with control damper, with connections for air flow measurement, inlet connection of the prepared air is provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø608, H=332, Ø250 | - dimensions Ø608, H=332, Ø250
| - pretok q = 310 m3/h | - flow rate q = 310 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-C-250 | - SYSTEMAIR tip CAP-C-250
| Oznaka: / | Tag: / | kpl | 2 |  | 0
2.15 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, sound and heat insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to the customer's or architect's preference, with connection chamber, with control damper, with connections for air flow measurement, inlet connection of the prepared air is provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø608, H=332, Ø250 | - dimensions Ø608, H=332, Ø250
| - pretok q = 295 m3/h | - flow rate q = 295 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-C-250 | - SYSTEMAIR tip CAP-C-250
| Oznaka: / | Tag: / | kpl | 8 |  | 0
2.16 | Stropni difuzor za odvod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno izolirano, maska je s fiksnimi lamelami, barve (RAL 9010) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, priključek odvoda zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for exhaust air, housing made of galvanised sheet steel, soundproofed, mask with fixed louvres, colour (RAL 9010) or in the colour of the client's or architect's choice, with connection chamber, with control damper, exhaust air connection provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø364, H=290, Ø200 | - dimensions Ø364, H=290, Ø200
| - pretok q = 250 m3/h | - flow rate q = 250 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip VVKN-A-R-400 | - SYSTEMAIR type VVKN-A-R-400
| Oznaka: / | Tag: / | kpl | 2 |  | 0
2.17 | Stropni difuzor za odvod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno izolirano, maska je s fiksnimi lamelami, barve (RAL 9010) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, priključek odvoda zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for exhaust air, housing made of galvanised sheet steel, soundproofed, mask with fixed louvres, colour (RAL 9010) or in the colour of the client's or architect's choice, with connection chamber, with control damper, exhaust air connection provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø364, H=290, Ø200 | - dimensions Ø364, H=290, Ø200
| - pretok q = 280 m3/h | - flow rate q = 280 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip VVKN-A-R-400 | - SYSTEMAIR type VVKN-A-R-400
| Oznaka: / | Tag: / | kpl | 8 |  | 0
2.18 | Stropni difuzor za odvod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno izolirano, maska je s fiksnimi lamelami, barve (RAL 9010) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, priključek odvoda zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for exhaust air, housing made of galvanised sheet steel, soundproofed, mask with fixed louvres, colour (RAL 9010) or in the colour of the client's or architect's choice, with connection chamber, with control damper, exhaust air connection provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø470, H=290, Ø200 | - dimensions Ø470, H=290, Ø200
| - pretok q = 290 m3/h | - flow rate q = 290 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip VVKN-A-R-500 | - SYSTEMAIR type VVKN-A-R-500
| Oznaka: / | Tag: / | kpl | 2 |  | 0
2.19 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije B=550/H=400 | - dimensions B=550/H=400
| - pretok q = 3510 m3/h | - flow rate q = 3510 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-550x400 | - SYSTEMAIR tip FDS-3G-550x400
| Oznaka: KFD02.301 | Code: KFD02.301 | kpl | 1 |  | 0
2.20 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije B=450/H=450 | - dimensions B=450/H=450
| - pretok q = 3320 m3/h | - flow rate q = 3320 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-450x450 | - SYSTEMAIR tip FDS-3G-450x450
| Oznaka: KFD02.401 | Code: KFD02.401 | kpl | 1 |  | 0
2.21 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije B=350/H=300 | - dimensions B=350/H=300
| - pretok q = 1150 m3/h | - flow rate q = 1150 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-350x300 | - SYSTEMAIR tip FDS-3G-350x300
| Oznaka: KFD02.306 | Code: KFD02.306 | kpl | 1 |  | 0
2.22 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije B=350/H=300 | - dimensions B=350/H=300
| - pretok q = 1080 m3/h | - flow rate q = 1080 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-350x300 | - SYSTEMAIR tip FDS-3G-350x300
| Oznaka: KFD02.406 | Code: KFD02.406 | kpl | 1 |  | 0
2.23 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material of type:
| - dimenzije Ø280 | - ø280 dimensions
| - pretok q = 590 m3/h | - flow rate q = 590 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-280 | - SYSTEMAIR tip FDR-3G-280
| Oznaka: KFD02.302; KFD02.303; KFD02.304; KFD02.305 | Code: KFD02.302; KFD02.303; KFD02.304; KFD02.305 | kpl | 4 |  | 0
2.24 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material of type:
| - dimenzije Ø280 | - ø280 dimensions
| - pretok q = 560 m3/h | - flow rate q = 560 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-280 | - SYSTEMAIR tip FDR-3G-280
| Oznaka: KFD02.402; KFD02.403; KFD02.404; KFD02.405 | Code: KFD02.402; KFD02.403; KFD02.404; KFD02.405 | kpl | 4 |  | 0
2.25 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø250 | - dimensions Ø250
| - pretok q = 590 do 200m3/h | - flow rate q = 590 to 200m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-250 | - SYSTEMAIR tip OPTIMA-LV-RI-250
| Oznaka: VAV02.101; VAV02.102; VAV02.103; VAV02.104 | Code: VAV02.101; VAV02.102; VAV02.103; VAV02.104 | kpl | 4 |  | 0
2.26 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø250 | - dimensions Ø250
| - pretok q = 560 do 190m3/h | - flow rate q = 560 to 190m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-250 | - SYSTEMAIR tip OPTIMA-LV-RI-250
| Oznaka: VAV02.201; VAV02.202; VAV02.203; VAV02.204 | Code: VAV02.201; VAV02.202; VAV02.203; VAV02.204 | kpl | 4 |  | 0
2.27 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø180 | - dimensions Ø180
| - pretok q = 310 do 110m3/h | - flow rate q = 310 to 110m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-180 | - SYSTEMAIR tip OPTIMA-LV-RI-180
| Oznaka: VAV02.105; VAV02.106 | Code: VAV02.105; VAV02.106 | kpl | 2 |  | 0
2.28 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø180 | - dimensions Ø180
| - pretok q = 290 do 100m3/h | - flow rate q = 290 to 100m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-180 | - SYSTEMAIR tip OPTIMA-LV-RI-180
| Oznaka: VAV02.205; VAV02.206 | Code: VAV02.205; VAV02.206 | kpl | 2 |  | 0
2.29 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø200 | - ø200 dimensions
| - pretok q = 530 do 170m3/h | - flow rate q = 530 to 170m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-200 | - SYSTEMAIR tip OPTIMA-LV-RI-200
| Oznaka: VAV02.107 | Code: VAV02.107 | kpl | 1 |  | 0
2.30 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø200 | - ø200 dimensions
| - pretok q = 500 do 160m3/h | - flow rate q = 500 to 160m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-200 | - SYSTEMAIR tip OPTIMA-LV-RI-200
| Oznaka: VAV02.207 | Code: VAV02.207 | kpl | 1 |  | 0
2.31 | Elektromotorni pogon z vzmetjo za vstopno/izstopno žaluzijo klimata, vključno z varnostno funkcijo (NC) in stikali položaja, s pritrdilnim in tesnilnim materialom tipa: | Electric motor drive with spring for air-conditioning inlet/outlet blind, including safety function (NC) and position switches, with fixing and sealing material type:
| - navor 10Nm | - torque 10Nm
| - električno napajanje 24V AC/DC | - 24V AC/DC power supply
| - ON/OFF regulacija delovanja | - ON/OFF operation control
| - za žaluzije do 2m2 | - for blinds up to 2m2
| - zaščita IP54 | - iP54 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip NF24A-S2 | - BELIMO type NF24A-S2
| Oznaka: KD02.101; KD02.202 | Code: KD02.101; KD02.202 | kpl | 2 |  | 0
2.32 | Kanalsko tipalo diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Duct differential pressure sensor, with type fastening and sealing material:
| - območje prikazovanja od 0 do 1500 Pa | - display range 0 to 1500 Pa
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22ADP-184A | - BELIMO type 22ADP-184A
| Oznaka: PICAL02.112; PICAL02.212 | Code: PICAL02.112; PICAL02.212 | kpl | 2 |  | 0
2.33 | Tipalo diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure sensor, with mounting and sealing material type:
| - območje prikazovanja od 0 do 1500 Pa | - display range 0 to 1500 Pa
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22ADP-184A | - BELIMO type 22ADP-184A
| Oznaka: PDIC02.107; PDIC02.205 | Code: PDIC02.107; PDIC02.205 | kpl | 2 |  | 0
2.34 | Diferenčno tlačno stikalo, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure switch, with type fastening and sealing material:
| - območje prikazovanja od 50 do 500Pa | - display range 50 to 500Pa
| - kontaktni tok maksimalno 1,0A / AC 250V | - contact current max 1.0A / AC 250V
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 01APS-10U | - BELIMO type 01APS-10U
| Oznaka: PDSAH02.102; PDSAH02.109; PDSAH02.203; PDSAH02.207 | Code: PDSAH02.102; PDSAH02.109; PDSAH02.203; PDSAH02.207 | kpl | 4 |  | 0
2.35 | Prikazovalnik diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure indicator, with type fixing and sealing material:
| - območje prikazovanja od 50 do 500Pa | - display range 50 to 500Pa
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DWYER tip Magnahelic | - DWYER tip Magnahelic
| Oznaka: PDI02.102; PDI02.109; PDI02.203; PDI02.207 | Code: PDI02.102; PDI02.109; PDI02.203; PDI02.207 | kpl | 4 |  | 0
2.36 | Zunanje tipalo temperature in vlage, s pritrdilnim in tesnilnim materialom tipa: | External temperature and humidity sensor, with fixing and sealing material type:
| - območje prikazovanja od 0 do 100%RH | - display range 0 to 100%RH
| - območje prikazovanja od -40 do 60°C | - display range -40 to 60°C
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22UTH-13M | - BELIMO type 22UTH-13M
| Oznaka: TIC/MIC02.100 | Code: TIC/MIC02.100 | kpl | 1 |  | 0
2.37 | Kanalsko tipalo temperature in vlage, s pritrdilnim in tesnilnim materialom tipa: | Duct temperature and humidity sensor, with fixing and sealing material type:
| - območje prikazovanja od 0 do 100%RH | - display range 0 to 100%RH
| - območje prikazovanja od -40 do 60°C | - display range -40 to 60°C
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22DTH-13M | - BELIMO type 22DTH-13M
| Oznaka: TIC/MIC02.110; TIC/MIC02.208 | Code: TIC/MIC02.110; TIC/MIC02.208 | kpl | 2 |  | 0
2.38 | Prostorsko tipalo kvalitete zraka CO2, s pritrdilnim in tesnilnim materialom tipa: | Room air quality sensor CO2, with fixing and sealing material type:
| - območje CO2 od 0 do 2000ppm | - cO2 range 0 to 2000ppm
| - izhodni signal 0 do 10V | - output signal 0 to 10V
| - izhodni signal MP-Bus | - mP-Bus output signal
| - zaščita IP30 | - iP30 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22RTM-19-1 | - BELIMO type 22RTM-19-1
| Oznaka: QIC02.501; QIC02.502; QIC02.503; QIC02.504; QIC02.505; QIC02.506; QIC02.507 | Code: QIC02.501; QIC02.502; QIC02.503; QIC02.504; QIC02.505; QIC02.506; QIC02.507 | kpl | 7 |  | 0
2.39 | Protizmrzovalni termostat, s pritrdilnim in tesnilnim materialom tipa: | Anti-freezing thermostat, with fixing and sealing material type:
| - območje od -10 do 15°C | - range -10 to 15°C
| - dolžina kapilare 6m | - capillary length 6m
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 01ATS-105XC | - BELIMO type 01ATS-105XC
| Oznaka: TSZAL02.104 | Code: TSZAL02.104 | kpl | 1 |  | 0
2.40 | Obtočna črpalka, elektronsko regulirana s frekvenčnim pretvornikom, tipalom diferenčnega tlaka, internimi hidravličnimi, električnimi in komunikacijskimi povezavami, PN10, material jeklena litina, skladnost z ErP, pritrdilnim in tesnilnim materialom tipa: | Circulation pump, electronically controlled with frequency converter, differential pressure sensor, internal hydraulic, electrical and communication connections, PN10, material cast steel, ErP compliant, type fastening and sealing material:
| - za obtok ogrevne vode 50/40°C | - for circulating heating water 50/40°C
| - za pretok V = 1,76m3/h, tlačna višina H = 1.8m | - for flow rate V = 1.76m3/h, pressure head H = 1.8m
| - možnost izbire delovanja črpalke na proporcionalni tlak ter optimizacijo delovne obratovalne točke | - option to select proportional pressure pump operation and optimise the operating point
| - napajanje Pel = 0,050kW, 230V / 50Hz | - power supply Pel = 0,050kW, 230V/50Hz
| - navojni priključek G 1 1/2 | - threaded connection G 1 1/2
| - tlačna stopnja PN10 | - pressure rating PN10
| - temperaturno območje ogrevnega medija od -10 do 110°C | - temperature range of the heating medium from -10 to 110°C
| - komunikacija s CNS RS485 | - communication with CNS RS485
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - GRUNDFOS tip MAGNA3 25-40 | - GRUNDFOS type MAGNA3 25-40
| Oznaka: P02.103 | Code: P02.103 | kpl | 1 |  | 0
2.41 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za ogrevno vodo 50/40°C | - for heating water 50/40°C
| - za pretok V = 1,76m3/h | - for a flow rate of V = 1,76m3/h
| - območje regulacije pretoka do 3200 l/h (3.20 m3/h) | - flow control range up to 3200 l/h (3.20 m3/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - navojni priključek G 1 1/2 po ISO 228/1 | - threaded connection G 1 1/2 according to ISO 228/1
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 20 - 400 kPa, min. dif. tlak 20 kPa | - differential pressure range 20 - 400 kPa, min. differential pressure 20 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM32 | - DANFOS type AB-QM32
| Oznaka: VA02.103 | Code: VA02.103 | kpl | 1 |  | 0
2.42 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za hladilno vodo 9/14°C | - for cooling water 9/14°C
| - za pretok V = 2,59m3/h | - for a flow rate of V = 2,59m3/h
| - območje regulacije pretoka do 3200 l/h (3.20 m3/h) | - flow control range up to 3200 l/h (3.20 m3/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - navojni priključek G 1 1/2 po ISO 228/1 | - threaded connection G 1 1/2 according to ISO 228/1
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 20 - 400 kPa, min. dif. tlak 20 kPa | - differential pressure range 20 - 400 kPa, min. differential pressure 20 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM32 | - DANFOS type AB-QM32
| Oznaka: VA02.106 | Code: VA02.106 | kpl | 1 |  | 0
| PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS02 | VENTILATION AND AIR CONDITIONING SYSTEM KS02 |  |  |  | 0

## 4.4.3_PrKlim KS03
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.4 | STROJNA DELA | MECHANICAL WORKS
4.4.3 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS03 | VENTILATION AND AIR CONDITIONING SYSTEM KS03 |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
3 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS03 | VENTILATION AND AIR CONDITIONING SYSTEM KS03
3.1 | Klimatska naprava za dovod in odvod zraka KD03/KO03 - glej tudi zavihek Zahteve klimati. | KD03/KO03 supply and extract air conditioner - see also Climate requirements tab.
| Tehnične karakteristike naprave (opis v smeri toka zraka): | Technical characteristics of the appliance (description downstream):
| Dovod: Vdov = 11170 m3/h | Input: Vdov = 11170 m3/h
| - posluževanje dovod: desno v smeri toka zraka! | - inlet: right in the direction of the air flow!
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 10 60% po ISO 16890 (M5 po SIST EN 779), s fleksibilnim čelnim priključkom, za pretok zraka 11170m3/h. Maksimalni končni padec tlaka 200Pa. Oznaka: F03.100 | - Filter unit with bag filter cartridge of filtration level ePM 10 60% according to ISO 16890 (M5 according to SIST EN 779), with flexible front connection, for an air flow of 11170m3/h. Maximum final pressure drop 200Pa. Code: F03.100
| - Prazna enota z regulacijskimi žaluzijami 2x 1390x570x125 za pretok zraka 11170m3/h. | - Empty unit with 2x 1390x570x125 control louvres for an air flow of 11170m3/h.
| - Prazna enota z AMS merilno mrežo STRA-R1250X625MM vgrajeno v zgornji del enote, pred rototermom. | - Empty unit with AMS measuring grid STRA-R1250X625MM built into the top of the unit, in front of the rototherm.
| - Rotacijska regeneratorska enota za prenos senzibilne in latentne toplote, z ON/OFF žaluzijami obtoka zraka 2x 1485x210x125. Tehnični podatki za zimsko obdobje: - pretok zraka 4300/3730m3/h - stopnja vračanja občutene toplote: 75,5% - stopnja vračanja latentne toplote: 79% - vračanje toplotne energije: 51,60kW - stanje dovodnega zr. pred enoto: -13,00°C/90,0% - stanje dovodnega zraka za enoto: 13,40°C/49,90% Tehnični podatki za poletno obdobje: - pretok zraka 4300/3730m3/h - stopnja vračanja občutene toplote: 75,5% - stopnja vračanja latentne toplote: 76,8% - vračanje toplotne energije: 20,50kW - stanje dovodnega zr. pred enoto: 34,50°C/40,0% - stanje dovodnega zraka za enoto: 28,10°C/45,3% Oznaka: RE03.191 | - Rotary regenerative unit for sensible and latent heat transfer, with ON/OFF airflow shutters 2x 1485x210x125. technical data for the winter period: - air flow 4300/3730m3/h - sensible heat recovery rate: 75.5% - latent heat recovery rate: 79% - heat energy recovery: 51.60kW - supply air condition upstream of the unit: -13.00°C/90.0% - supply air condition for the unit: 13.40°C/49.90% Technical data for the summer period: - air flow 4300/3730m3/h - sensible heat recovery rate: 75.5% - latent heat recovery rate: 76.8% - heat energy recovery: 20.50kW - supply air condition upstream of the unit: 34.50°C/40.0% - supply air condition for the unit: 28.10°C/45.3% Code: RE03.191
| - Mešalna enota za mešanje zunajnega in prostorskega zraka, z vgrajenimi mešalnimi cevmi za zagotavljanje ustreznega mešanja zraka, z regulacijsko žaluzijo 1390x410x125. | - Mixing unit for mixing outside and indoor air, with integrated mixing pipes to ensure adequate air mixing, with control louvre 1390x410x125.
| - Enota pred-grelnika zraka s protizmrzovalno zaščito. - pretok zraka 11170m3/h - grelna moč Qg=24,9kW - temperaturni režim ogrevnega medija 50/40°C - pretok ogrevnega medija 2,16m3/h - padec tlaka na zračni strani 11Pa - temperatura zraka vstop 17,20°C - temperatura zraka izstop 23,80°C - padec tlaka na strani ogr. medija (voda) 11,22kPa - priključka navojna 1" - tlačna stopnja PN16 Oznaka: HE03.106 | - Air preheater unit with anti-freeze protection. - air flow 11170m3/h - heating power Qg=24,9kW - heating medium temperature 50/40°C - heating medium flow rate 2,16m3/h - air-side pressure drop 11Pa - air temperature inlet 17,20°C - air temperature outlet 23,80°C - pressure drop on the heating medium side (water) 11,22kPa - 1" threaded connectors - pressure rating PN16 Code: HE03.106
| - Vlažilna enota s kontaktnim vlaženjem zraka. Dovod sveže pripravljene demineralizirane vode, z materialom kontaktnega vlažilnika impregniranim srebrom, črpalko, potrebno merilno regulacijsko opremo, ventili na dovodu sveže vode ter ventilom na odvodu vode iz banje, s funkcijo samodejnega praznjenja banje vlažilnika in polnjenja s svežo pripravljeno mehčano vodo glede na prevodnost vode v banji, oziroma glede na čas ko vlažilnik ni v funkciji. Odvod kondenzata s sifonom z vodno in mehansko smardno zaporo. - pretok zraka 11170m3/h - priključna električna moč 0,06kW, 3x400V, 50Hz - padec tlaka na zračni strani dpz=22Pa - temperatura zraka vstop 23,80°C - relativna vlaga zraka vstop 27,9% - temperatura zraka izstop 22,1°C - relativna vlaga izstop 35% - izkoristek vlaženja 15,64% - vlaženje 12,96 kg/h - tipalo prevodonsti vode QICCD03.108 - tipalo zgornjega nivoja vode LICH03.108 - tipalo spodnjega nivoja vode LICL03.108 - elektromagnetni ventil za praznenje VD03.108 - elektromagnetni ventil za dovod sveže vode VD03.208 Oznaka: SH03.108 | - Humidification unit with contact humidification. Freshly prepared demineralised water supply, with silver-impregnated contact humidifier material, pump, necessary metering control equipment, valves at the fresh water inlet and at the water outlet of the humidifier tank, with automatic emptying of the humidifier tank and refilling with freshly prepared softened water according to the conductivity of the water in the tank, or according to the time when the humidifier is not in operation. Condensate drainage with siphon with water and mechanical odour trap. - air flow 11170m3/h - connection power 0,06kW, 3x400V, 50Hz - pressure drop on the air side dpz=22Pa - air temperature inlet 23,80°C - relative humidity 27.9% - air temperature outlet 22,1°C - relative humidity 35% exit - humidification efficiency 15.64% - humidification 12,96 kg/h - water conductivity sensor QICCD03.108 - upper water level sensor LICH03.108 - lower water level sensor LICL03.108 - solenoid valve for emptying VD03.108 - fresh water solenoid valve VD03.208 Code: SH03.108
| - Enota hladilnika z eliminatorjem kapljic in koritom za odvod kondenzata. - pretok zraka 11170m3/h - hladilna moč Qhtot=70,70kW - temperaturni režim hladilnega medija 9/14°C - pretok hladilnega medija 12,14 m3/h - padec tlaka na zračni strani 71/66Pa - temperatura zraka vstop 27,20°C - temperatura zraka izstop 12,50°C - padec tlaka na strani hl. medija (voda) 20,15kPa - priključka navojna 2" - tlačna stopnja PN16 Oznaka: HE03.109 | - Refrigerator unit with drip eliminator and condensate drain. - air flow 11170m3/h - cooling power Qhtot=70,70kW - cooling medium temperature 9/14°C - cooling medium flow rate 12,14 m3/h - pressure drop on the air side 71/66Pa - air temperature inlet 27,20°C - air temperature outlet 12,50°C - pressure drop on the medium side (water) 20,15kPa - 2" threaded connectors - pressure rating PN16 Code: HE03.109
| - Ventilatorska enota s prostotekočim rotorjem. Elektromotor je EC-motor, s 100% zvezno regulacijo vrtljajev preko potenciometra (0-10V), ki omogoča nastavitev delovanja ventilatorja na ustrezno delovno točko. Enota vsebuje: okence O150 in svetilko s stikalom ter servisno stikalo. - pretok zraka 11170m3/h - eksterni statični padec tlaka dpext=450Pa - priključna električna moč 2x2,5kW, 3x400V, 50Hz - razred izkoristka elektromotorja IE5/EC - zaščita IP55 Oznaka: FA03.110 | - Fan unit with free-flowing rotor. The electric motor is an EC motor, with 100% continuous speed control via a potentiometer (0-10V), which allows the fan to be set to the appropriate operating point. The unit contains: an O150 window and a lamp with switch and a service switch. - air flow 11170m3/h - external static pressure drop dpext=450Pa - connection power 2x2,5kW, 3x400V, 50Hz - electric motor efficiency class IE5/EC - iP55 protection Code: FA03.110
| - Dušilna enota. - pretok zraka 11170m3/h - padec tlaka dp=10Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 4 11 26 30 36 33 25 20 Oznaka: DZ03.111 | - Throttle unit. - air flow 11170m3/h - pressure drop dp=10Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 4 11 26 30 36 33 25 20 Code: DZ03.111
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 1 75% po ISO 16890 (F8 po SIST EN 779, s fleksibilnim čelnim priključkom, za pretok zraka 11170m3/h. Maksimalni končni padec tlaka 300Pa. Oznaka: F03.112 | - Filter unit with bag filter cartridge of filtration level ePM 1 75% according to ISO 16890 (F8 according to SIST EN 779, with flexible front connection, for air flow 11170m3/h. Maximum final pressure drop 300Pa. Code: F03.112
| Dolžina: 8,29m | Length: 8,29m
| Širina: 1,665m | Width: 1,665m
| Višina: 1.485m | Height: 1.485m
| Kompletno z dobavo dodatne opreme: | Complete with supply of accessories:
| - odtočni sifoni | - drain traps
| - jadrovinasti nastavki | - sailplane spouts
| - s spojnim, tesnilnim in pritrdilnim materialom in priključki za senzorje, | - with jointing, sealing and fixing materials and sensor connectors,
| Odvod: Vodv = 10600 m3/h | Discharge: waterv = 10600 m3/h
| - posluževanje odvod: levo v smeri toka zraka! | - serving outlet: left in the direction of the air flow!
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 10 60% po ISO 16890 (M5 po SIST EN 779), s fleksibilnim čelnim priključkom, za pretok zraka 10600m3/h. Maksimalni končni padec tlaka 200Pa. Oznaka: F03.207 | - Filter unit with bag filter cartridge of filtration level ePM 10 60% according to ISO 16890 (M5 according to SIST EN 779), with flexible front connection, for an air flow of 10600m3/h. Maximum final pressure drop 200Pa. Code: F03.207
| - Dušilna enota. - pretok zraka 10600m3/h - padec tlaka dp=16Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 9 22 23 27 18 13 14 Oznaka: DZ03.206 | - Throttle unit. - air flow 10600m3/h - pressure drop dp=16Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 9 22 23 27 18 13 14 Code: DZ03.206
| - Ventilatorska enota s prostotekočim rotorjem. Elektromotor je EC-motor, s 100% zvezno regulacijo vrtljajev preko potenciometra (0-10V), ki omogoča nastavitev delovanja ventilatorja na ustrezno delovno točko. Enota vsebuje: okence O150 in svetilko s stikalom ter servisno stikalo. - pretok zraka 10600m3/h - eksterni statični padec tlaka dpext=450Pa - priključna električna moč 2x2,5kW, 3x400V, 50Hz - razred izkoristka elektromotorja IE5/EC - zaščita IP55 Oznaka: FA03.205 | - Fan unit with free-flowing rotor. The electric motor is an EC motor, with 100% continuous speed control via a potentiometer (0-10V), which allows the fan to be set to the appropriate operating point. The unit contains: an O150 window and a lamp with switch and a service switch. - air flow 10600m3/h - external static pressure drop dpext=450Pa - connection power 2x2,5kW, 3x400V, 50Hz - electric motor efficiency class IE5/EC - iP55 protection Code: FA03.205
| - Dušilna enota. - pretok zraka 10600m3/h - padec tlaka dp=16Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 7 17 18 21 15 11 12 Oznaka: DZ03.204 | - Throttle unit. - air flow 10600m3/h - pressure drop dp=16Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 7 17 18 21 15 11 12 Code: DZ03.204
| - Sesalna tlačna enota z regulacijsko žaluzijo 1533x943x125, fleksibilnim čelnim priključkom, za pretok zraka 10600m3/h. | - Suction pressure unit with control shutter 1533x943x125, flexible front connection, for air flow 10600m3/h.
| Dolžina: 4,890m | Length: 4,890m
| Širina: 1,665m | Width: 1,665m
| Višina: 1.055m | Height: 1.055m
| Kompletno z dobavo dodatne opreme: | Complete with supply of accessories:
| - postavitvene noge, gumirane, višine 100-200mm | - rubberised feet, height 100-200mm
| - odtočni sifoni | - drain traps
| - jadrovinasti nastavki | - sailplane spouts
| - postavitev klimata na antivibracijski dušilnik (gumo) za preprečevanje prenosa vibracij in hrupa na konstrukcijo objekta. Dušilniki morajo biti preračunani glede na lastnosti klimata (teža in vrtilna frekvenca ventilatorjev). | - installation of the air conditioner on an anti-vibration damper (rubber) to prevent the transmission of vibrations and noise to the structure of the building. The dampers must be calculated according to the characteristics of the air conditioner (weight and speed of the fans).
| - s spojnim, tesnilnim in pritrdilnim materialom in priključki za senzorje, | - with jointing, sealing and fixing materials and sensor connectors,
| Teža: 3.163kg | Weight: 3.163kg
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR | - SYSTEMAIR | kpl | 1 |  | 0
3.2 | Zunanja zaščitna rešetka za dovod zraka narejene iz jeklene pocinkane pločevine z zaščitno mrežo, z vgrajenim električnim grelnim kablom z zaščitno funkcijo proti zamrzovanju in termostatom za vklop pri +5 °C, pritrditev z vijaki na vzidan okvir iz jeklenega kotnika, barve v skladu z zahtevam načrta arhitekture, s pritrdilnim in tesnilnim materialom tipa: | External air intake grille made of galvanised sheet steel with protective mesh, with built-in electric heating cable with anti-freeze protection function and thermostat for switching on at +5 °C, bolted to a steel angle frame, colour according to architectural design requirements, with fixing and sealing material type:
| - dimenzije B=920/H=2920 | - dimensions B=920/H=2920
| - dimenzija prosta za pretok zraka B=920/H=1820 | - dimension free for air flow B=920/H=1820
| - H=600mm nad terenom zaprta rešetka z betonsko steno | - H=600mm above ground closed grid with concrete wall
| - H=500mm od vrha rešetke zaprta rešetka z betonsko steno | - H=500mm from top of grille closed grille with concrete wall
| - pretok q = 6860 m3/h | - flow rate q = 6860 m3/h
| - padec tlaka Δp = 6 Pa | - pressure drop Δp = 6 Pa
| - prost prerez Aef=1.323 m2 | - free cross-section Aef=1.323 m2
| - električna moč grelca od 1.88 do 3.77 kW, 3x400 V, 50Hz, na preseku za pretok zraka B=920/H=1820 | - heater electrical power from 1.88 to 3.77 kW, 3x400 V, 50Hz, at air flow cross section B=920/H=1820
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - OC IMP KLIMA tip JZR-6 920x2920 | - OC IMP KLIMA tip JZR-6 920x2920
| Oznaka: ZR03.901; ZR03.902 | Code: ZR03.901; ZR03.902 | kpl | 2 |  | 0
3.3 | Zunanja zaščitna rešetka za odvod zraka narejena iz jeklene pocinkane pločevine z zaščitno mrežo, pritrditev z vijaki na vzidan okvir iz jeklenega kotnika, barve v skladu z zahtevam načrta arhitekture, s pritrdilnim in tesnilnim materialom tipa: | External air grille made of galvanised sheet steel with protective mesh, bolted to a steel angle angle frame, colour according to the architectural plan, with fixing and sealing material of the type:
| - dimenzije B=920/H=2920 | - dimensions B=920/H=2920
| - dimenzija prosta za pretok zraka B=920/H=1820 | - dimension free for air flow B=920/H=1820
| - H=600mm nad terenom zaprta rešetka z betonsko steno | - H=600mm above ground closed grid with concrete wall
| - H=500mm od vrha rešetke zaprta rešetka z betonsko steno | - H=500mm from top of grille closed grille with concrete wall
| - pretok q = 13020 m3/h | - flow rate q = 13020 m3/h
| - padec tlaka Δp = 20 Pa | - pressure drop Δp = 20 Pa
| - prost prerez Aef=1.323 m2 | - free cross-section Aef=1.323 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - OC IMP KLIMA tip JZR-6 920x2920 | - OC IMP KLIMA tip JZR-6 920x2920
| Oznaka: ZR03.801 | Code: ZR03.801 | kpl | 1 |  | 0
3.4 | Kanalski dogrelnik zraka izdelan iz vroče pocinkane jeklene pločevine Magnelis ZM200, maksimalne obratovalne temperature 150°C, razreda zrakotesnosti C po EN 15727, s pritrdilnim in tesnilnim materialom tipa: | Duct air heater made of hot-dip galvanized steel sheet Magnelis ZM200, maximum operating temperature 150°C, airtightness class C according to EN 15727, with fastening and sealing material type:
| - pretok q = 6560 m3/h | - flow rate q = 6560 m3/h
| - grelna moč Qg=12,6kW | - heating power Qg=12,6kW
| - temperaturni režim ogrevnega medija 50/40°C | - heating medium temperature 50/40°C
| - pretok ogrevnega medija (voda) 1,10m3/h | - heating medium flow (water) 1,10m3/h
| - padec tlaka na zračni strani 73 Pa | - air side pressure drop 73 Pa
| - temperatura zraka vstop 15°C | - air temperature inlet 15°C
| - temperatura zraka izstopp 21°C | - air temperature outlet 21°C
| - padec tlaka na ogr. medija (voda) 4,54 kPa | - pressure drop across the medium (water) 4,54 kPa
| - priključka navojna 1" | - 1" threaded connectors
| - tlačna stopnja PN10 | - pressure rating PN10
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - VEAB tip PGV 1000x500-2-2,5 | - VEAB type PGV 1000x500-2-2,5
| Oznaka: HE03.311 | Code: HE03.311 | kpl | 1 |  | 0
3.5 | Kanalski dogrelnik zraka izdelan iz jeklene pločevine, prevlečene s cinkom in magnezijem, ZM 310, maksimalne obratovalne temperature 150°C, razreda zrakotesnosti D po EN 15727, s pritrdilnim in tesnilnim materialom tipa: | Ducted air heater made of zinc-magnesium coated steel sheet, ZM 310, maximum operating temperature 150°C, airtightness class D according to EN 15727, with fastening and sealing material type:
| - pretok q = 2210 m3/h | - flow rate q = 2210 m3/h
| - grelna moč Qg=4,3kW | - heating power Qg=4,3kW
| - temperaturni režim ogrevnega medija 50/40°C | - heating medium temperature 50/40°C
| - pretok ogrevnega medija (voda) 0,37m3/h | - heating medium flow (water) 0,37m3/h
| - padec tlaka na zračni strani 53 Pa | - air side pressure drop 53 Pa
| - temperatura zraka vstop 15°C | - air temperature inlet 15°C
| - temperatura zraka izstopp 21°C | - air temperature outlet 21°C
| - padec tlaka na ogr. medija (voda) 5,10 kPa | - pressure drop across the medium (water) 5,10 kPa
| - priključka Ø22mm | - ø22mm connector
| - tlačna stopnja PN10 | - pressure rating PN10
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - VEAB tip CWW 400-2-2,5 | - VEAB type CWW 400-2-2,5
| Oznaka: HE03.312 | Code: HE03.312 | kpl | 1 |  | 0
3.6 | Kanalski dogrelnik zraka izdelan iz jeklene pločevine, prevlečene s cinkom in magnezijem, ZM 310, maksimalne obratovalne temperature 150°C, razreda zrakotesnosti D po EN 15727, s pritrdilnim in tesnilnim materialom tipa: | Duct air heater made of zinc-magnesium coated steel sheet, ZM 310, maximum operating temperature 150°C, airtightness class D according to EN 15727, with fastening and sealing material type:
| - pretok q = 2300 m3/h | - flow rate q = 2300 m3/h
| - grelna moč Qg=4,5kW | - heating power Qg=4,5kW
| - temperaturni režim ogrevnega medija 50/40°C | - heating medium temperature 50/40°C
| - pretok ogrevnega medija (voda) 0,39m3/h | - heating medium flow (water) 0,39m3/h
| - padec tlaka na zračni strani 57 Pa | - pressure drop on the air side 57 Pa
| - temperatura zraka vstop 15°C | - air temperature inlet 15°C
| - temperatura zraka izstopp 21°C | - air temperature outlet 21°C
| - padec tlaka na ogr. medija (voda) 5,30 kPa | - pressure drop across the medium (water) 5,30 kPa
| - priključka Ø22mm | - ø22mm connector
| - tlačna stopnja PN10 | - pressure rating PN10
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - VEAB tip CWW 400-2-2,5 | - VEAB type CWW 400-2-2,5
| Oznaka: HE03.313 | Code: HE03.313 | kpl | 1 |  | 0
3.7 | Okrogli prezračevalni kanali izdelani iz pocinkane pločevine po SIST EN 1506, vključno z revizijskimi odprtinami, oblikovnimi kosi, debeline po standardu. V ceni na enoto (m) je potrebno upoštevati ves spojni in pritrdilni material (prirobnice, odrez, spone, vijaki, tesnila, ojačitve, vključno z obešalnim in pritrdilnim materialom sistemskega proizvajalca z lastnostmi odgovarjajoč zahtevam SIST EN 12236: 2002, vključno pleskanje vseh kovinskih korozijsko nezaščitenih delov, po temeljitem predhodnem čiščenju do kovinskega sijaja. Antikorozijska zaščita se izvaja v skladu z EN 12944 za naslednje pogoje: • Življenjska doba več kot 15 let. • Stopnja korozijske atmosfere C4 (visoka). | Round ventilation ducts made of galvanised sheet metal according to SIST EN 1506, including inspection openings, shaped pieces, thickness according to the standard. The unit price (m) must take into account all joining and fixing material (flanges, cut-offs, clamps, bolts, gaskets, reinforcements, including hanging and fixing material of the system manufacturer with properties according to the requirements of SIST EN 12236: 2002, including painting of all metal corrosion-protected parts, after thorough cleaning to a metallic gloss. The corrosion protection shall be carried out in accordance with EN12944, for the following conditions: - Lifetime over 15 years. - Corrosive atmosphere C4 (high).
| - Okrogli prezračevalni kanali Ø250 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø250 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 10 |  | 0
| - Okrogli prezračevalni kanali Ø315 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø315 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 3 |  | 0
| - Okrogli prezračevalni kanali Ø355 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø355 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 3 |  | 0
| - Okrogli prezračevalni kanali Ø400 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø400 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 20 |  | 0
| - Okrogli prezračevalni kanali Ø450 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø450 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 45 |  | 0
| - Okrogli prezračevalni kanali Ø500 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø500 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 15 |  | 0
| - Okrogli prezračevalni kanali Ø560 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø560 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 12 |  | 0
| - Okrogli prezračevalni kanali Ø710 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø710 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 7 |  | 0
3.8 | Okrogli pregibni kanali za priključitev stropnih difuzorjev, izdelani iz Al folije ter polnila iz materiala z dušilnim in toplotno-izolativnim efektom. V ceni na enoto (m) je potrebno upoštevati ves spojni material, pritrdilne objemke in tesnilni material, za podatke: | Round folded ducts for the connection of ceiling diffusers, made of Al foil and filling material with damping and thermal insulation effect. The unit price (m) must include all joining material, fixing clamps and sealing material, for details:
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DEC tip: SONODEC - 25 | - DEC tip: SUNDAY - 25
| - Okroglegi pregibni kanali Ø250 | - Round flexible ducts Ø250 | m | 12 |  | 0
| - Okroglegi pregibni kanali Ø400 | - Ø400 round flexible ducts | m | 12 |  | 0
3.9 | Pravokotni prezračevalni kanali izdelani iz pocinkane pločevine po SIST EN 1505:1999, debeline po DIN 24190, klase tesnosti B po SIST EN 1507:2006, vključno z revizijskimi odprtinami, oblikovnimi kosi. V ceni na enoto (m2) je potrebno upoštevati ves spojni in pritrdilni material (prirobnice, odrez, spone, vijaki, tesnila, usmerjevalniki, ojačitve, vključno z obešalnim in pritrdilnim materialom sistemskega proizvajalca z lastnostmi odgovarjajoč zahtevam SIST EN 12236: 2002, vključno pleskanje vseh kovinskih korozijsko nezaščitenih delov, po temeljitem predhodnem čiščenju do kovinskega sijaja. Antikorozijska zaščita se izvaja v skladu z EN 12944 za naslednje pogoje: • Življenjska doba več kot 15 let. • Stopnja korozijske atmosfere C4 (visoka). | Rectangular ventilation ducts made of galvanised sheet metal according to SIST EN 1505:1999, thickness according to DIN 24190, tightness class B according to SIST EN 1507:2006, including inspection openings, shaped pieces. The unit price (m2) must take into account all joining and fixing material (flanges, cut-off, clamps, bolts, gaskets, guides, reinforcements, including hanging and fixing material of the system manufacturer with properties according to the requirements of SIST EN 12236:2002, including the painting of all metal corrosion-protected parts, after thorough preliminary cleaning to a metallic gloss. The anticorrosive protection shall be performed in accordance with EN12944 for the following conditions: - Lifetime over 15 years. - Corrosive atmosphere C4 (high). | m2 | 485 |  | 0
3.10 | Toplotna izolacija zajemnih, izpušnih ter vtočnih kanalov s parozapornimi ploščami izdelanimi iz sintetičnega kavčuka z zaprto celično strukturo, toplotne prevodnosti manjše ali enake 0,033W/mK pri srednji temperaturi 0 °C, koeficient upora difuziji vodene pare večji ali enak 10000 testirano v skladu z EN 13469 za cevi in EN 12086 za plošče, požarna klasifikacija B/BL-s3,d0 po DIN 4102, oziroma po SIST EN 13501-1. | Thermal insulation of intake, exhaust and inlet ducts with vapour control panels made of synthetic rubber with closed cell structure, thermal conductivity less than or equal to 0,033 W/mK at a mean temperature of 0 °C, resistance coefficient to diffusion of water vapour greater than or equal to 10000 tested in accordance with EN 13469 for pipes and EN 12086 for panels, fire classification B/BL-s3,d0 according to DIN 4102, or according to SIST EN 13501-1.
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - ARMACELL tip: Armaflex AF | - ARMACELL tip: Armaflex AF
| Toplotna izolacija zajemnih kanalov na vtočni strani (ZUZ-ODA), debeline s = 50 mm, + original lepilo | Thermal insulation of the inlet side of the intake ducts (ZUZ-ODA), thickness s = 50 mm, + original adhesive | m2 | 6 |  | 0
| Toplotna izolacija notranjih kanalov na vtočni strani (VTZ-SUP), debeline s = 19 mm, + original lepilo | Thermal insulation of internal ducts on the inlet side (VTZ-SUP), thickness s = 19 mm, + original adhesive | m2 | 310 |  | 0
| Toplotna izolacija izpušnih kanalov (ZAZ-EHA), debeline s = 19 mm, + original lepilo | Exhaust duct thermal insulation (ZAZ-EHA), thickness s = 19 mm, + original adhesive | m2 | 65 |  | 0
3.11 | Kanalski dušilnik, za preprečevajne prenosa zvoka med prostori, izdelan iz pocinkane pločevine, mineralne volne za dušenje zvoka z zaščito pred erozijo s steklenimi vlakni 70Kf/m3 požarne odpornost M0, vključno z vsem potrebnim pritrdilnim, povezovalnim, tesnilnim in montažnim materialom, tipa: | Duct silencer, to prevent sound transmission between rooms, made of galvanised sheet, mineral wool for sound attenuation with glass fibre erosion protection 70Kf/m3 fire resistance M0, including all necessary fixing, connecting, sealing and mounting material, type:
| - dimenzije Ø560/1120/80 | - dimensions Ø560/1120/80
| - pretok q = 3100 m3/h | - flow rate q = 3100 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip RSA 560/1120/080 (F) | - SYSTEMAIR tip RSA 560/1120/080 (F)
| Oznaka: DZ03.411; DZ03.412 | Code: DZ03.411; DZ03.412 | kpl | 2 |  | 0
3.12 | Kanalski dušilnik, za preprečevajne prenosa zvoka med prostori, izdelan iz pocinkane pločevine, mineralne volne za dušenje zvoka z zaščito pred erozijo s steklenimi vlakni 70Kf/m3 požarne odpornost M0, vključno z vsem potrebnim pritrdilnim, povezovalnim, tesnilnim in montažnim materialom, tipa: | Duct silencer, to prevent sound transmission between rooms, made of galvanised sheet, mineral wool for sound attenuation with glass fibre erosion protection 70Kf/m3 fire resistance M0, including all necessary fixing, connecting, sealing and mounting material, type:
| - dimenzije Ø500/1000/80 | - dimensions Ø500/1000/80
| - pretok q = 2200 m3/h | - flow rate q = 2200 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip RSA 500/1000/080 (F) | - SYSTEMAIR tip RSA 500/1000/080 (F)
| Oznaka: DZ03.413 | Code: DZ03.413 | kpl | 1 |  | 0
3.13 | Kanalski dušilnik, za preprečevajne prenosa zvoka med prostori, izdelan iz pocinkane pločevine, mineralne volne za dušenje zvoka z zaščito pred erozijo s steklenimi vlakni 70Kf/m3 požarne odpornost M0, vključno z vsem potrebnim pritrdilnim, povezovalnim, tesnilnim in montažnim materialom, tipa: | Duct silencer, to prevent sound transmission between rooms, made of galvanised sheet, mineral wool for sound attenuation with glass fibre erosion protection 70Kf/m3 fire resistance M0, including all necessary fixing, connecting, sealing and mounting material, type:
| - dimenzije Ø560/1120/80 | - dimensions Ø560/1120/80
| - pretok q = 2300 m3/h | - flow rate q = 2300 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip RSA 560/1120/080 (F) | - SYSTEMAIR tip RSA 560/1120/080 (F)
| Oznaka: DZ03.313 | Code: DZ03.313 | kpl | 1 |  | 0
3.14 | Talna rešetka za dovod zraka, aluminijasta s fiksnimi vodoravnimi usmerniki pod kotom 0 stopinj, izdelana iz vlečenih Al profilov, pritrjena na vgradni okvir z vidnimi vijaki, nastavni del s protismernimi lamelami za regulacijo količine zraka, skupaj z montažnim materialom, barve v skladu z zahtevam načrta arhitekture, tipa: | Floor air inlet grille, aluminium with fixed horizontal rectifiers at an angle of 0 degrees, made of drawn Al profiles, fixed to the mounting frame with visible screws, adjusting part with anti-air volume control louvres, including mounting material, colour in accordance with the requirements of the architectural plan, type:
| - dimenzije B=500/H=100 | - dimensions B=500/H=100
| - pretok q = 170 m3/h | - flow rate q = 170 m3/h
| - prost prerez Aef=0,017 m2 | - free cross-section Aef=0,017 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - TECNOVENTIL tip BP5/CTX 500x100 | - TECNOVENTIL tip BP5/CTX 500x100
| Oznaka: / | Tag: / | kpl | 5 |  | 0
3.15 | Vrtinčni difutor, primeren za navpično montažo v stopnice, sestavljena iz okrogle vrtinčne difuzorske plošče in pritrdilnega obroča za hitro montažo, z radialno razporejenimi lamelami za usmerjanje zraka in izjemno hitro zmanjšanje hitrosti zraka ter temperaturne razlike, izdelan iz jeklene pločevine, skupaj z montažnim materialom, barve v skladu z zahtevam načrta arhitekture, tipa: | Vortex diffuser suitable for vertical installation in stairs, consisting of a circular vortex diffuser plate and a fastening ring for quick installation, with radially arranged slats to direct the air and reduce air velocity and temperature difference extremely quickly, made of sheet steel, complete with mounting material, colour according to the requirements of the architectural plan, type:
| - dimenzije Ø60/Ø35 | - dimensions Ø60/Ø35
| - pretok q = 7,55 m3/h | - flow rate q = 7,55 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SCHAKO tip SAR-060 | - SCHAKO type SAR-060
| Oznaka: / | Tag: / | kpl | 756 |  | 0
3.16 | Rešetka za dovod zraka, izdelana iz aluminijskih profilov, sestavljena iz nosilnega okvirja z vodoravnim in navpičnim nastavljivim lamelam, dodatkom za nastavitev količine zraka, pritrditev rešetke na prezračevalni kanal, z ugradnim okvirjem, vključno z vsem pritrdilnim in montažnim materialom, barva v skladu z zahtevam načrta arhitekture, tipa: | Air inlet grille made of aluminium profiles, consisting of a support frame with horizontal and vertical adjustable slats, air volume adjustment accessory, grille attachment to the ventilation duct, with mounting frame, including all fixing and mounting material, colour in accordance with the requirements of the architectural plan, type:
| - dimenzije B=800/H=300 | - dimensions B=800/H=300
| - pretok q = 546 m3/h | - flow rate q = 546 m3/h
| - prost prerez Aef=0,143 m2 | - free cross-section Aef=0,143 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-A-2-2-800x300-R1 | - SYSTEMAIR tip NOVA-A-2-2-800x300-R1
| Oznaka: / | Tag: / | kpl | 11 |  | 0
3.17 | Rešetka za dovod zraka, izdelana iz aluminijskih profilov, sestavljena iz nosilnega okvirja z vodoravnim in navpičnim nastavljivim lamelam, dodatkom za nastavitev količine zraka, pritrditev rešetke na prezračevalni kanal, z ugradim okvirjem, vključno z vsem pritrdilnim in montažnim materialom, barva v skladu z zahtevam načrta arhitekture, tipa: | Air inlet grille made of aluminium profiles, consisting of a support frame with horizontal and vertical adjustable slats, air volume adjustment accessory, grille attachment to the ventilation duct, with a framed frame, including all fixing and mounting material, colour in accordance with the requirements of the architectural plan, type:
| - dimenzije B=400/H=300 | - dimensions B=400/H=300
| - pretok q = 277 m3/h | - flow rate q = 277 m3/h
| - prost prerez Aef=0,070 m2 | - free cross-section Aef=0,070 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-A-2-2-400x300-R1 | - SYSTEMAIR tip NOVA-A-2-2-400x300-R1
| Oznaka: / | Tag: / | kpl | 2 |  | 0
3.18 | Rešetka za dovod zraka, izdelana iz aluminijskih profilov, sestavljena iz nosilnega okvirja z vodoravnim in navpičnim fiksnim lamelam, dodatkom za nastavitev količine zraka, pritrditev rešetke na prezračevalni kanal, z ugradim okvirjem, vključno z vsem pritrdilnim in montažnim materialom, barva v skladu z zahtevam načrta arhitekture, tipa: | Air inlet grille made of aluminium profiles, consisting of a support frame with horizontal and vertical fixed slats, air volume adjustment accessory, grille attachment to the ventilation duct, with a framed frame, including all fixing and mounting material, colour in accordance with the requirements of the architectural plan, type:
| - dimenzije B=200/H=100 | - dimensions B=200/H=100
| - pretok q = 100 m3/h | - flow rate q = 100 m3/h
| - prost prerez Aef=0,013 m2 | - free cross-section Aef=0,013 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-E-2-200x100-R1 | - SYSTEMAIR tip NOVA-E-2-200x100-R1
| Oznaka: / | Tag: / | kpl | 1 |  | 0
3.19 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, soundproof and thermally insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to customer's or architect's preference, with connection chamber, with control damper, with connections for air flow measurement, inlet connection of the prepared air to be provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø634, H=508, Ø400 | - dimensions Ø634, H=508, Ø400
| - pretok q = 552/553 m3/h | - flow rate q = 552/553 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-C-400 | - SYSTEMAIR tip CAP-C-400
| Oznaka: / | Tag: / | kpl | 4 |  | 0
3.20 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, soundproof and thermally insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to customer's or architect's preference, with connection chamber, with control damper, with connections for air flow measurement, inlet connection of the prepared air to be provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø634, H=508, Ø400 | - dimensions Ø634, H=508, Ø400
| - pretok q = 575 m3/h | - flow rate q = 575 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-C-400 | - SYSTEMAIR tip CAP-C-400
| Oznaka: / | Tag: / | kpl | 4 |  | 0
3.21 | Rešetka za odvod zraka, izdelana iz jeklene pocinkane pločevine, sestavljena iz nosilnega okvirja z navpičnim nastavljivim lamelam, dodatkom za nastavitev količine zraka, pritrditev rešetke na prezračevalni kanal, z ugradim okvirjem, vključno z vsem pritrdilnim in montažnim materialom, barva v skladu z zahtevam načrta arhitekture, tipa: | Air outlet grille made of galvanised sheet steel, consisting of a support frame with vertical adjustable slats, air volume adjustment accessory, grille attachment to the ventilation duct, with a framed frame, including all fixing and mounting material, colour according to the requirements of the architectural plan, type:
| - dimenzije B=825/H=225 | - dimensions B=825/H=225
| - pretok q = 516/517 m3/h | - flow rate q = 516/517 m3/h
| - prost prerez Aef=0,134 m2 | - free cross-section Aef=0,134 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-C-1-825x225-R1 | - SYSTEMAIR tip NOVA-C-1-825x225-R1
| Oznaka: / | Tag: / | kpl | 12 |  | 0
3.22 | Rešetka za odvod zraka, izdelana iz aluminijskih profilov, sestavljena iz nosilnega okvirja z vodoravnim in navpičnim fiksnim lamelam, dodatkom za nastavitev količine zraka, pritrditev rešetke na prezračevalni kanal, z ugradim okvirjem, vključno z vsem pritrdilnim in montažnim materialom, barva v skladu z zahtevam načrta arhitekture, tipa: | Air outlet grille made of aluminium profiles, consisting of a support frame with horizontal and vertical fixed slats, air volume adjustment accessory, grille attachment to the ventilation duct, with a framed enclosure, including all fixing and mounting material, colour in accordance with the requirements of the architectural plan, type:
| - dimenzije B=200/H=100 | - dimensions B=200/H=100
| - pretok q = 100 m3/h | - flow rate q = 100 m3/h
| - prost prerez Aef=0,013 m2 | - free cross-section Aef=0,013 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-E-2-200x100-R1 | - SYSTEMAIR tip NOVA-E-2-200x100-R1
| Oznaka: / | Tag: / | kpl | 1 |  | 0
3.23 | Stropni difuzor za odvod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno izolirano, maska je s fiksnimi lamelami, barve (RAL 9010) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, priključek odvoda zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for exhaust air, housing made of galvanised sheet steel, soundproofed, mask with fixed louvres, colour (RAL 9010) or in the colour of the client's or architect's choice, with connection chamber, with control damper, exhaust air connection provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø595, H=340, Ø250 | - dimensions Ø595, H=340, Ø250
| - pretok q = 525 m3/h | - flow rate q = 525 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip VVKN-A-R-625 | - SYSTEMAIR tip VVKN-A-R-625
| Oznaka: / | Tag: / | kpl | 4 |  | 0
3.24 | Stropni difuzor za odvod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno izolirano, maska je s fiksnimi lamelami, barve (RAL 9010) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, priključek odvoda zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for exhaust air, housing made of galvanised sheet steel, soundproofed, mask with fixed louvres, colour (RAL 9010) or in the colour of the client's or architect's choice, with connection chamber, with control damper, exhaust air connection provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø595, H=340, Ø250 | - dimensions Ø595, H=340, Ø250
| - pretok q = 550 m3/h | - flow rate q = 550 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip VVKN-A-R-625 | - SYSTEMAIR tip VVKN-A-R-625
| Oznaka: / | Tag: / | kpl | 4 |  | 0
3.25 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material of type:
| - dimenzije B=600/H=750 | - dimensions B=600/H=750
| - pretok q = 6560 m3/h | - flow rate q = 6560 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-600x750 | - SYSTEMAIR tip FDS-3G-600x750
| Oznaka: KFD03.311 | Code: KFD03.311 | kpl | 1 |  | 0
3.26 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material of type:
| - dimenzije B=1000/H=500 | - dimensions B=1000/H=500
| - pretok q = 4510 m3/h | - flow rate q = 4510 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-1000x500 | - SYSTEMAIR tip FDS-3G-1000x500
| Oznaka: KFD03.312 | Code: KFD03.312 | kpl | 1 |  | 0
3.27 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije B=1500/H=500 | - dimensions B=1500/H=500
| - pretok q = 8300 m3/h | - flow rate q = 8300 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-1500x500 | - SYSTEMAIR tip FDS-1500x500
| Oznaka: KFD03.411 | Code: KFD03.411 | kpl | 1 |  | 0
3.28 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material of type:
| - dimenzije Ø500 | - ø500 dimensions
| - pretok q = 2200 m3/h | - flow rate q = 2200 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-500 | - SYSTEMAIR tip FDR-3G-500
| Oznaka: KFD03.412; KFD03.413 | Code: KFD03.412; KFD03.413 | kpl | 2 |  | 0
3.29 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material of type:
| - dimenzije Ø500 | - ø500 dimensions
| - pretok q = 2100 m3/h | - flow rate q = 2100 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-500 | - SYSTEMAIR tip FDR-3G-500
| Oznaka: KFD03.414 | Code: KFD03.414 | kpl | 1 |  | 0
3.30 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije Ø710 | - ø710 dimensions
| - pretok q = 6200 m3/h | - flow rate q = 6200 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-710 | - SYSTEMAIR tip FDR-3G-710
| Oznaka: KFD03.415 | Code: KFD03.415 | kpl | 1 |  | 0
3.31 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije Ø560 | - dimensions Ø560
| - pretok q = 3100 m3/h | - flow rate q = 3100 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-560 | - SYSTEMAIR tip FDR-3G-560
| Oznaka: KFD03.416; KFD03.417 | Code: KFD03.416; KFD03.417 | kpl | 2 |  | 0
3.32 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo regulacije konstantnega pretoka, s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow regulator, made of galvanised sheet metal with acoustic and thermal insulation, with constant flow control function, with fastening and sealing material type:
| - dimenzije Ø80 | - ø80 dimensions
| - pretok q = 100m3/h | - flow rate q = 100m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOTUS-RI-80-M0 | - SYSTEMAIR tip NOTUS-RI-80-M0
| Oznaka: CAV03.301; CAV03.401 | Code: CAV03.301; CAV03.401 | kpl | 2 |  | 0
3.33 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije 800x300 | - dimensions 800x300
| - pretok q = 6560 do 2000m3/h | - flow rate q = 6560 to 2000m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-SI-FC-800x300 | - SYSTEMAIR tip OPTIMA-SI-FC-800x300
| Oznaka: VAV03.311 | Code: VAV03.311 | kpl | 1 |  | 0
3.34 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø400 | - ø400 dimensions
| - pretok q = 2210 do 670m3/h | - flow rate q = 2210 to 670m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-400 | - SYSTEMAIR tip OPTIMA-LV-RI-400
| Oznaka: VAV03.312 | Code: VAV03.312 | kpl | 1 |  | 0
3.35 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø400 | - ø400 dimensions
| - pretok q = 2300 do 700m3/h | - flow rate q = 2300 to 700m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-400 | - SYSTEMAIR tip OPTIMA-LV-RI-400
| Oznaka: VAV03.313 | Code: VAV03.313 | kpl | 1 |  | 0
3.36 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø500 | - ø500 dimensions
| - pretok q = 6200 do 1900m3/h | - flow rate q = 6200 to 1900m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-RI-FC-500 | - SYSTEMAIR tip OPTIMA-RI-FC-500
| Oznaka: VAV03.411 | Code: VAV03.411 | kpl | 1 |  | 0
3.37 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø400 | - ø400 dimensions
| - pretok q = 2100 do 630m3/h | - flow rate q = 2100 to 630m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-400 | - SYSTEMAIR tip OPTIMA-LV-RI-400
| Oznaka: VAV03.412 | Code: VAV03.412 | kpl | 1 |  | 0
3.38 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø400 | - ø400 dimensions
| - pretok q = 2200 do 660m3/h | - flow rate q = 2200 to 660m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-400 | - SYSTEMAIR tip OPTIMA-LV-RI-400
| Oznaka: VAV03.413 | Code: VAV03.413 | kpl | 1 |  | 0
3.39 | Elektromotorni pogon z vzmetjo za vstopno žaluzijo klimata, vključno z varnostno funkcijo (NC) in stikali položaja, s pritrdilnim in tesnilnim materialom tipa: | Electric motor drive with spring for air-conditioning inlet shutter, including safety function (NC) and position switches, with fixing and sealing material type:
| - navor 10Nm | - torque 10Nm
| - električno napajanje 24V AC/DC | - 24V AC/DC power supply
| - ON/OFF regulacija delovanja | - ON/OFF operation control
| - za žaluzije do 2m2 | - for blinds up to 2m2
| - zaščita IP54 | - iP54 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip NF24A-S2 | - BELIMO type NF24A-S2
| Oznaka: KD03.101; KD03.102 | Code: KD03.101; KD03.102 | kpl | 2 |  | 0
3.40 | Elektromotorni pogon z vzmetjo za izstopno žaluzijo klimata, vključno z varnostno funkcijo (NC) in stikali položaja, s pritrdilnim in tesnilnim materialom tipa: | Electric motor drive with spring for climate exit blind, including safety function (NC) and position switches, with fixing and sealing material type:
| - navor 10Nm | - torque 10Nm
| - električno napajanje 24V AC/DC | - 24V AC/DC power supply
| - zvezna regulacija delovanja | - continuous operation control
| - za žaluzije do 2m2 | - for blinds up to 2m2
| - zaščita IP54 | - iP54 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip NF24A-SR-S2 | - BELIMO type NF24A-SR-S2
| Oznaka: KA03.202 | Code: KA03.202 | kpl | 1 |  | 0
3.41 | Elektromotorni pogon za obtok regeneratorja, s stikalom položaja za odprt položaj, s pritrdilnim in tesnilnim materialom tipa: | Electric motor drive for regenerator circulation, with position switch for open position, with fixing and sealing material type:
| - navor 5Nm | - torque 5Nm
| - električno napajanje 24V AC/DC | - 24V AC/DC power supply
| - ON/OFF regulacija delovanja | - ON/OFF operation control
| - za žaluzije do 1m2 | - for blinds up to 1m2
| - zaščita IP54 | - iP54 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip LM24A-S | - BELIMO type LM24A-S
| Oznaka: KD03.104; KD03.203 | Code: KD03.104; KD03.203 | kpl | 2 |  | 0
3.42 | Elektromotorni pogon za mešalno žaluzijo klimata, s pritrdilnim in tesnilnim materialom tipa: | Electric motor drive for air-conditioning mixing louvre, with fixing and sealing material type:
| - navor 5Nm | - torque 5Nm
| - električno napajanje 24V AC/DC | - 24V AC/DC power supply
| - zvezna regulacija delovanja | - continuous operation control
| - za žaluzije do 1m2 | - for blinds up to 1m2
| - zaščita IP54 | - iP54 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip LM24A-SR | - BELIMO type LM24A-SR
| Oznaka: KA03.105 | Code: KA03.105 | kpl | 1 |  | 0
3.43 | Kanalski senzor diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Duct differential pressure sensor, with mounting and sealing material type:
| - območje prikazovanja od 0 do 1500 Pa | - display range 0 to 1500 Pa
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22ADP-184A | - BELIMO type 22ADP-184A
| Oznaka: PICAL03.209; PICAL03.115 | Code: PICAL03.209; PICAL03.115 | kpl | 2 |  | 0
3.44 | Diferenčno tlačno stikalo, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure switch, with type fastening and sealing material:
| - območje prikazovanja od 50 do 500Pa | - display range 50 to 500Pa
| - kontaktni tok maksimalno 1,0A / AC 250V | - contact current max 1.0A / AC 250V
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 01APS-10U | - BELIMO type 01APS-10U
| Oznaka: PDSAH03.100; PDSAH03.112; PDSAH03.203; PDSAH03.207 | Code: PDSAH03.100; PDSAH03.112; PDSAH03.203; PDSAH03.207 | kpl | 4 |  | 0
3.45 | Prikazovalnik diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure indicator, with type fixing and sealing material:
| - območje prikazovanja od 50 do 500Pa | - display range 50 to 500Pa
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DWYER tip Magnahelic | - DWYER tip Magnahelic
| Oznaka: PDI03.100; PDI03.112; PDI03.203; PDI03.207 | Code: PDI03.100; PDI03.112; PDI03.203; PDI03.207 | kpl | 4 |  | 0
3.46 | Tipalo diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure sensor, with mounting and sealing material type:
| - območje prikazovanja od 0 do 1500 Pa | - display range 0 to 1500 Pa
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22ADP-184A | - BELIMO type 22ADP-184A
| Oznaka: PDIC03.110; PDIC03.205 | Code: PDIC03.110; PDIC03.205 | kpl | 2 |  | 0
3.47 | Tipalo diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure sensor, with mounting and sealing material type:
| - območje prikazovanja od 0 do 500 Pa | - display range 0 to 500 Pa
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22ADP-184A | - BELIMO type 22ADP-184A
| Oznaka: PDIC03.103 | Code: PDIC03.103 | kpl | 1 |  | 0
3.48 | Kanalsko tipalo temperature in vlage, s pritrdilnim in tesnilnim materialom tipa: | Duct temperature and humidity sensor, with fixing and sealing material type:
| - območje prikazovanja od 0 do 100%RH | - display range 0 to 100%RH
| - območje prikazovanja od -40 do 60°C | - display range -40 to 60°C
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22DTH-13M | - BELIMO type 22DTH-13M
| Oznaka: TIC/MIC03.113; TIC/MIC03.208 | Code: TIC/MIC03.113; TIC/MIC03.208 | kpl | 2 |  | 0
3.49 | Prostorsko tipalo temperature, vlage in kvalitete zraka CO2, s pritrdilnim in tesnilnim materialom tipa: | Room temperature, humidity and air quality sensor CO2, with fixing and sealing material type:
| - območje merjenja od 0 do 50°C | - measuring range 0 to 50°C
| - območje merjenja od 0 do 100%RH | - measuring range 0 to 100%RH
| - območje CO2 od 0 do 2000ppm | - cO2 range from 0 to 2000ppm
| - izhodni signal 0 do 10V | - output signal 0 to 10V
| - izhodni signal MP-Bus | - mP-Bus output signal
| - zaščita IP30 | - iP30 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22RTM-19-1 | - BELIMO type 22RTM-19-1
| Oznaka: TIC/MIC/QIC03.501; TIC/MIC/QIC03.502; TIC/MIC/QIC03.503 | Code: TIC/MIC/QIC03.501; TIC/MIC/QIC03.502; TIC/MIC/QIC03.503 | kpl | 3 |  | 0
3.50 | Protizmrzovalni termostat, s pritrdilnim in tesnilnim materialom tipa: | Anti-freezing thermostat, with fixing and sealing material type:
| - območje od -10 do 15°C | - range -10 to 15°C
| - dolžina kapilare 6m | - capillary length 6m
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 01ATS-105XC | - BELIMO type 01ATS-105XC
| Oznaka: TSZAL03.107 | Code: TSZAL03.107 | kpl | 1 |  | 0
3.51 | Obtočna črpalka, elektronsko regulirana s frekvenčnim pretvornikom, tipalom diferenčnega tlaka, internimi hidravličnimi, električnimi in komunikacijskimi povezavami, PN10, material jeklena litina, skladnost z ErP, pritrdilnim in tesnilnim materialom tipa: | Circulation pump, electronically controlled with frequency converter, differential pressure sensor, internal hydraulic, electrical and communication connections, PN10, material cast steel, ErP compliant, type fastening and sealing material:
| - za obtok ogrevne vode 50/40°C | - for circulating heating water 50/40°C
| - za pretok V = 2,16m3/h, tlačna višina H = 1,8m | - for flow rate V = 2,16m3/h, pressure head H = 1,8m
| - možnost izbire delovanja črpalke na proporcionalni tlak ter optimizacijo delovne obratovalne točke | - option to select proportional pressure pump operation and optimise the operating point
| - napajanje Pel = 0,050kW, 230V / 50Hz | - power supply Pel = 0,050kW, 230V/50Hz
| - navojni priključek G 1 1/2 | - threaded connection G 1 1/2
| - tlačna stopnja PN10 | - pressure rating PN10
| - temperaturno območje ogrevnega medija od -10 do 110°C | - temperature range of the heating medium from -10 to 110°C
| - komunikacija s CNS RS485 | - communication with CNS RS485
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - GRUNDFOS tip MAGNA3 25-40 | - GRUNDFOS type MAGNA3 25-40
| Oznaka: P03.106 | Code: P03.106 | kpl | 1 |  | 0
3.52 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za ogrevno vodo 50/40°C | - for heating water 50/40°C
| - za pretok V = 2,16m3/h | - for a flow rate of V = 2,16m3/h
| - območje regulacije pretoka do 3200 l/h (3.20 m3/h) | - flow control range up to 3200 l/h (3.20 m3/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - navojni priključek G 1 1/2 po ISO 228/1 | - threaded connection G 1 1/2 according to ISO 228/1
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 20 - 400 kPa, min. dif. tlak 20 kPa | - differential pressure range 20 - 400 kPa, min. differential pressure 20 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM32 | - DANFOS type AB-QM32
| Oznaka: VA03.106 | Code: VA03.106 | kpl | 1 |  | 0
3.53 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za hladilno vodo 9/14°C | - for cooling water 9/14°C
| - za pretok V = 12,14m3/h | - for a flow rate of V = 12,14m3/h
| - območje regulacije pretoka do 20000 l/h (20 m3/h) | - flow control range up to 20000 l/h (20 m3/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - prirobnični priključek DN65 | - flange connection DN65
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 30 - 400 kPa, min. dif. tlak 30 kPa | - differential pressure range 30 - 400 kPa, min. differential pressure 30 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM65 | - DANFOS type AB-QM65
| Oznaka: VA03.109 | Code: VA03.109 | kpl | 1 |  | 0
3.54 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za ogrevno vodo 50/40°C | - for heating water 50/40°C
| - za pretok V = 1,1m3/h | - for a flow rate of V = 1,1m3/h
| - območje regulacije pretoka do 1700 l/h (1,70 m3/h) | - flow control range up to 1700 l/h (1.70 m3/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - navojni priključek G 1 1/4 po ISO 228/1 | - threaded connection G 1 1/4 according to ISO 228/1
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 20 - 400 kPa, min. dif. tlak 20 kPa | - differential pressure range 20 - 400 kPa, min. differential pressure 20 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM25 | - DANFOS type AB-QM25
| Oznaka: VA03.311 | Code: VA03.311 | kpl | 1 |  | 0
3.55 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za ogrevno vodo 50/40°C | - for heating water 50/40°C
| - za pretok V = 0,37m3/h | - for a flow rate of V = 0,37 m3/h
| - območje regulacije pretoka do 450 l/h (0,45 m3/h) | - flow control range up to 450 l/h (0.45 m3/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - navojni priključek G 3/4 po ISO 228/1 | - threaded connection G 3/4 according to ISO 228/1
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 16 - 400 kPa, min. dif. tlak 16 kPa | - differential pressure range 16 - 400 kPa, min. differential pressure 16 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM15 | - DANFOS type AB-QM15
| Oznaka: VA03.312 | Code: VA03.312 | kpl | 1 |  | 0
3.56 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za ogrevno vodo 50/40°C | - for heating water 50/40°C
| - za pretok V = 0,39m3/h | - for a flow rate of V = 0,39m3/h
| - območje regulacije pretoka do 450 l/h (0,45 m3/h) | - flow control range up to 450 l/h (0.45 m3/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - navojni priključek G 3/4 po ISO 228/1 | - threaded connection G 3/4 according to ISO 228/1
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 16 - 400 kPa, min. dif. tlak 16 kPa | - differential pressure range 16 - 400 kPa, min. differential pressure 16 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM15 | - DANFOS type AB-QM15
| Oznaka: VA03.313 | Code: VA03.313 | kpl | 1 |  | 0
3.57 | Sistem reverzne osmoze s predfiltracijo za pripravo demineralizirane vode za potrebe vlažilnika klimatov KS03, KS04, s pritrdilnim in tesnilnim materialom, skupaj s/z: | Reverse osmosis system with pre-filtration for the preparation of demineralised water for the needs of the humidifier of the air conditioners KS03, KS04, with fixing and sealing material, incl:
| - svečnim filtrom s 5 m filternimi vložki | - candle filter with 5 m filter cartridges
| - vstopnim magnetnim ventilom | - inlet solenoid valve
| - vstopnim zaščitnim tlačnim stikalom | - inlet pressure relief switch
| - spiralno navitimi RO moduli v tlačnem ohišju | - spiral wound RO modules in a pressure housing
| - internimi cevnimi povezavami | - internal pipe connections
| - merilcema trenutnega pretoka dobitka in koncentrata | - instantaneous flow meters for the feed and concentrate
| - manometri za kontrolo tlaka vode na vstopu in izstopu koncentrata | - pressure gauges for controlling the water pressure at the inlet and outlet of the concentrate
| - merilcem prevodnosti dobitka | - a conductivity meter
| - mikroprocesorsko krmilno enoto | - microprocessor control unit
| - vzorčevalno pipico | - sampling tap
| - nosilno konstrukcijo iz nerjavnega jekla | - stainless steel load-bearing structure
| - ročno tipko za zaustavitev in zagon RO | - manual key to stop and start the RO
| - plovnim stikalom | - float switch
| - dimenzije naprave 500x1500x500 mm | - dimensions 500x1500x500 mm
| - pretok dobitka 80 l/h | - 80 l/h recharge flow
| - izkoristek naprave 50 - 70 % | - plant efficiency 50 - 70 %
| - zadržani topljenec min 98 % | - solvent retention min 98 %
| - priključki vstop/izstop DN15 | - inlet/outlet connections DN15
| - vstopni tlak min 1,5 bar | - inlet pressure min 1,5 bar
| - delovni tlak 15 bar | - working pressure 15 bar
| - delovna temperatura 10- 35°C | - operating temperature 10- 35°C
| - električni priključek 220/50/0,55 V/Hz/kW | - 220/50/0,55 V/Hz/kW electrical connection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - MAKCMC tip MINIRO 8 | - MAKCMC type MINIRO 8
| Oznaka: | Code: | kpl | 1 |  | 0
3.58 | Rezervoar demineralizirane vode in črpalna postaja za potrebe vlažilnika klimatov KS03, KS04, s pritrdilnim in tesnilnim materialom, skupaj s/z: | Demineralised water tank and pumping station for the needs of the humidifier for air-conditioning KS03, KS04, with fixing and sealing material, incl:
| - rezervoarjem iz PE | - pE tank
| - nivojskimi stikali: min/maks, za zaščito črpalke in signalizacijo preliva | - level switches: min/max, for pump protection and overflow signalling
| - hidrostatična sonda za zvezni nivo v rezervoarju | - hydrostatic probe for continuous tank level
| - pripadajočo PVC armaturo | - associated PVC fittings
| - varnostnim prelivom | - safety dressing
| - kontrolnim manometrom | - a check gauge
| - ekspanzijsko posodo iz nerjavnega jekla | - stainless steel expansion tank
| - tlačnim stikalom | - pressure switch
| - centrifugalno črpalko CM 1-6; material nerjavno jeklo AISI 316 | - centrifugal pump CM 1-6; material stainless steel AISI 316
| - volumen rezervoarja 115 l | - tank capacity 115 l
| - dimenzije rezervoarja D460x775 mm | - tank dimensions D460x775 mm
| - kapaciteta črpalke 1,7 m3/h | - pump capacity 1.7 m3/h
| - tlak 1,3bar | - pressure 1,3bar
| - priključki DN 25 | - dN 25 connections
| - el. priključek 400/50/460 V/Hz/W | - 400/50/460 V/Hz/W power connection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - MAKCMC tip RDI 12 C1 | - MAKCMC type RDI 12 C1
| Oznaka: | Code: | kpl | 1 |  | 0
3.59 | Avtomatski dvojni ionski mehčalec vode za potrebe vlažilnika klimatov KS03, KS04, s pritrdilnim in tesnilnim materialom, skupaj s/z: | Automatic double ion water softener for the humidifier needs of air conditioners KS03, KS04, with fixing and sealing material, incl:
| - elektro-mehanskim krmilnikom | - electro-mechanical controller
| - večpotnim ventilom z dvema distributorjema | - multiport valve with two distributors
| - tlačno posodo iz armiranega polietilena komplet 2 | - pressure vessel of reinforced polyethylene, set of 2
| - solnim ventilom | - salt valve
| - solnikom | - to solnikom
| - smolo močno kislega ionskega izmenjevalca | - strong acid ion-exchange resin
| - čistilnim kosom | - cleaning pieces
| - tabletirano soljo 25kg | - tablet salt 25kg
| - dimenzije naprave 1500x700x1100 mm | - dimensions 1500x700x1100 mm
| - volumen ionske smole 2 x 18 l | - ionic resin volume 2 x 18 l
| - volumen tlačne posode 2 x 20,4 l | - pressure vessel volume 2 x 20.4 l
| - volumen solnika 100 l | - brine tank capacity 100 l
| - poraba tabletirane soli 2,7 – 4,3 kg/reg | - tablet salt consumption 2,7 - 4,3 kg/reg
| - pretok 0,1 – 0,9 m3/h | - flow rate 0,1 - 0,9 m3/h
| - kapaciteta 9,9 –11,2 m3/reg | - capacity 9,9 -11,2 m3/reg
| - priključki vstop/izstop DN20 | - inlet/outlet connections DN20
| - delovni tlak 2,5 – 6 bar | - working pressure 2,5 - 6 bar
| - delovna temperatura do 40°C | - operating temperature up to 40°C
| - el. priključek 220/50/10 V/Hz/W | - 220/50/10 V/Hz/W power connection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - MAKCMC tip MINOM 0DF - 25 | - MAKCMC type MINOM 0DF - 25
| Oznaka: | Code: | kpl | 1 |  | 0
3.60 | Sistem za UV dezinfekcijo vode za potrebe vlažilnika klimatov KS03, KS04 s pritrdilnim in tesnilnim materialom, skupaj s/z: | UV water disinfection system for humidifier needs of air conditioners KS03, KS04 with fixing and sealing material, incl:
| - reaktorjem: material 1.4404, elektopoliran | - reactor: material 1.4404, electropolished
| - nizkotlačnim UV sevalom v zaščitni cevi iz kremenčevega stekla | - low-pressure UV radiation in a protective quartz glass tube
| - mehkim zagonom delovanja sevala | - soft start of the radiator
| - signalizacijo za zamenjavo sevala | - signalling for radiator replacement
| - signalizacijo napak delovanja | - fault signalling
| - upravljalno enoto | - the control unit
| - dimenzije upravljalne enote 168x200x66 mm | - control unit dimensions 168x200x66 mm
| - priključki 3/4 '' | - 3/4'' connections
| - obratovalni tlak PN10 | - operating pressure PN10
| - UV doza 400 J/m2 | - UV dose 400 J/m2
| - hidravlična kapaciteta maks 1,69 m3/h | - hydraulic capacity max 1,69 m3/h
| - temperatura vode 0-35°C | - water temperature 0-35°C
| - temperatura okolice maks 35°C | - ambient temperature max 35°C
| - zaščita reaktor/upravlj. enota IP 65/54 | - reactor/management unit protection IP 65/54
| - el. priključek 220/50/55 V/Hz/W | - 220/50/55 V/Hz/W power connection
| - življenska doba svetil 8.760 h | - lamp life 8.760 h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - MAKCMC tip AQUADA 2 PRO | - MAKCMC tip AQUADA 2 PRO
| Oznaka: | Code: | kpl | 1 |  | 0
| PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS03 | VENTILATION AND AIR CONDITIONING SYSTEM KS03 |  |  |  | 0

## 4.4.4_PrKlim KS04
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.4 | STROJNA DELA | MECHANICAL WORKS
4.4.4 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS04 | VENTILATION AND AIR CONDITIONING SYSTEM KS04 |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
4 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS04 | VENTILATION AND AIR CONDITIONING SYSTEM KS04
4.1 | Klimatska naprava za dovod in odvod zraka KD04/KO04 - glej tudi zavihek Zahteve klimati. | KD04/KO04 supply and extract air conditioner - see also Climate requirements tab.
| Tehnične karakteristike naprave (opis v smeri toka zraka): | Technical characteristics of the appliance (description downstream):
| Dovod: Vdov = 2550 m3/h | Inlet: Vdov = 2550 m3/h
| - posluževanje dovod: levo v smeri toka zraka! | - inlet: left in the direction of the air flow!
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 10 60% po ISO 16890 (M5 po SIST EN 779), z regulacijsko žaluzijo 923x638x125, s fleksibilnim čelnim priključkom, za pretok zraka 2550m3/h. Maksimalni končni padec tlaka 200Pa. Oznaka: F04.102 | - Filter unit with bag filter cartridge of filtration level ePM 10 60% according to ISO 16890 (M5 according to SIST EN 779), with control shutter 923x638x125, with flexible front connection, for air flow 2550m3/h. Maximum final pressure drop 200Pa. Code: F04.102
| - Rotacijska regeneratorska enota za prenos senzibilne in latentne toplote. Tehnični podatki za zimsko obdobje: - pretok zraka 2550/2420m3/h - stopnja vračanja občutene toplote: 75,9% - stopnja vračanja latentne toplote: 77,2% - vračanje toplotne energije: 28kW - stanje dovodnega zr. pred enoto: -13,00°C/90,0% - stanje dovodnega zraka za enoto: 12,80°C/41,7% Tehnični podatki za poletno obdobje: - pretok zraka 2550/2420m3/h - stopnja vračanja občutene toplote: 75,9% - stopnja vračanja latentne toplote: 72,8% - vračanje toplotne energije: 7,40kW - stanje dovodnega zr. pred enoto: 34,50°C/40,0% - stanje dovodnega zraka za enoto: 28°C/54,4% Oznaka: RE04.191 | - Rotary regenerative unit for sensible and latent heat transfer. technical data for the winter period: - air flow 2550/2420m3/h - sensible heat recovery rate: 75.9% - latent heat recovery rate: 77.2% - heat recovery: 28kW - supply air condition upstream of the unit: -13.00°C/90.0% - supply air condition for the unit: 12.80°C/41.7% Technical data for the summer period: - air flow 2550/2420m3/h - sensible heat recovery rate: 75.9% - latent heat recovery rate: 72.8% - heat energy recovery: 7.40kW - supply air condition upstream of the unit: 34.50°C/40.0% - supply air condition for the unit: 28°C/54.4% Code: RE04.191
| - Enota pred-grelnika zraka s protizmrzovalno zaščito. - pretok zraka 2550m3/h - grelna moč Qg=14,4kW - temperaturni režim ogrevnega medija 50/40°C - pretok ogrevnega medija 1,25m3/h - padec tlaka na zračni strani 39Pa - temperatura zraka vstop 12,80°C - temperatura zraka izstop 29,50°C - padec tlaka na strani ogr. medija (voda) 14,24kPa - priključka navojna 3/4" - tlačna stopnja PN16 Oznaka: HE04.103 | - Air preheater unit with anti-freeze protection. - air flow 2550m3/h - heating power Qg=14,4kW - heating medium temperature 50/40°C - heating medium flow rate 1,25m3/h - air side pressure drop 39Pa - air inlet temperature 12,80°C - air temperature outlet 29,50°C - pressure drop on the heating medium side (water) 14,24kPa - 3/4" threaded connectors - pressure rating PN16 Code: HE04.103
| - Vlažilna enota s kontaktnim vlaženjem zraka. Dovod sveže pripravljene demineralizirane vode, z materialom kontaktnega vlažilnika impregniranim srebrom, črpalko, potrebno merilno regulacijsko opremo, ventili na dovodu sveže vode ter ventilom na odvodu vode iz banje, s funkcijo samodejnega praznjenja banje vlažilnika in polnjenja s svežo pripravljeno mehčano vodo glede na prevodnost vode v banji, oziroma glede na čas ko vlažilnik ni v funkciji. Odvod kondenzata s sifonom z vodno in mehansko smardno zaporo. - pretok zraka 2550m3/h - priključna električna moč 0,05kW, 230V, 50Hz - padec tlaka na zračni strani dpz=119Pa - temperatura zraka vstop 29,5°C - relativna vlaga zraka vstop 15,4% - temperatura zraka izstop 27,42°C - relativna vlaga izstop 21% - izkoristek vlaženja 13,19% - vlaženje 6,12 kg/h - tipalo prevodonsti vode QICCD04.105 - tipalo zgornjega nivoja vode LICH04.105 - tipalo spodnjega nivoja vode LICL04.105 - elektromagnetni ventil za praznenje VD04.105 - elektromagnetni ventil za dovod sveže vode VD04.205 Oznaka: SH04.105 | - Humidification unit with contact humidification. Freshly prepared demineralised water supply, with silver-impregnated contact humidifier material, pump, necessary metering control equipment, valves at the fresh water inlet and at the water outlet of the humidifier tank, with automatic emptying of the humidifier tank and refilling with freshly prepared softened water according to the conductivity of the water in the tank, or according to the time when the humidifier is not in operation. Condensate drainage with siphon with water and mechanical odour trap. - air flow 2550m3/h - connection power 0,05kW, 230V, 50Hz - pressure drop on the air side dpz=119Pa - air temperature 29,5°C - relative humidity 15.4% - air temperature outlet 27,42°C - relative humidity 21% exit - humidification efficiency 13.19% - humidification 6,12 kg/h - water conductivity sensor QICCD04.105 - upper water level sensor LICH04.105 - lower water level sensor LICL04.105 - solenoid valve for emptying VD04.105 - fresh water solenoid valve VD04.205 Code: SH04.105
| - Enota hladilnika z eliminatorjem kapljic in koritom za odvod kondenzata. - pretok zraka 2550m3/h - hladilna moč Qhtot=10,7kW - temperaturni režim hladilnega medija 9/14°C - pretok hladilnega medija 1,84m3/h - padec tlaka na zračni strani 69/63Pa - temperatura zraka vstop 28°C - temperatura zraka izstop 18,80°C - padec tlaka na strani hl. medija (voda) 21,17kPa - priključka navojna 3/4" - tlačna stopnja PN16 Oznaka: HE04.106 | - Refrigerator unit with drip eliminator and condensate drain. - air flow 2550m3/h - cooling power Qhtot=10,7kW - cooling medium temperature 9/14°C - coolant flow 1,84m3/h - pressure drop on the air side 69/63Pa - air temperature inlet 28°C - air temperature outlet 18,80°C - pressure drop on the medium side (water) 21.17kPa - 3/4" threaded connectors - pressure rating PN16 Code: HE04.106
| - Ventilatorska enota s prostotekočim rotorjem. Elektromotor je EC-motor, s 100% zvezno regulacijo vrtljajev preko potenciometra (0-10V), ki omogoča nastavitev delovanja ventilatorja na ustrezno delovno točko. Enota vsebuje: okence O150 in svetilko s stikalom ter servisno stikalo. - pretok zraka 2550m3/h - eksterni statični padec tlaka dpext=300Pa - priključna električna moč 2,4kW, 3x400V, 50Hz - razred izkoristka elektromotorja IE5/EC - zaščita IP55 Oznaka: FA04.107 | - Fan unit with free-flowing rotor. The electric motor is an EC motor, with 100% continuous speed control via a potentiometer (0-10V), which allows the fan to be set to the appropriate operating point. The unit contains: an O150 window and a lamp with switch and a service switch. - air flow 2550m3/h - external static pressure drop dpext=300Pa - connection power 2,4kW, 3x400V, 50Hz - electric motor efficiency class IE5/EC - iP55 protection Code: FA04.107
| - Dušilna enota. - pretok zraka 2550m3/h - padec tlaka dp=12Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 4 11 27 28 32 21 15 16 Oznaka: DZ04.108 | - Throttle unit. - air flow 2550m3/h - pressure drop dp=12Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 4 11 27 28 32 21 15 16 Code: DZ04.108
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 1 75% po ISO 16890 (F8 po SIST EN 779, s fleksibilnim čelnim priključkom, za pretok zraka 2550m3/h. Maksimalni končni padec tlaka 300Pa. Oznaka: F04.109 | - Filter unit with bag filter cartridge of filtration level ePM 1 75% according to ISO 16890 (F8 according to SIST EN 779, with flexible front connection, for air flow 2550m3/h. Maximum final pressure drop 300Pa. Code: F04.109
| Dolžina: 5,550m | Length: 5,550m
| Širina: 0.960m | Width: 0.960m
| Višina: 0,875m | Height: 0,875m
| Kompletno z dobavo dodatne opreme: | Complete with supply of accessories:
| - odtočni sifoni | - drain traps
| - jadrovinasti nastavki | - sailplane spouts
| - s spojnim, tesnilnim in pritrdilnim materialom in priključki za senzorje, | - with jointing, sealing and fixing materials and sensor connectors,
| Odvod: Vodv = 2420 m3/h | Discharge: waterv = 2420 m3/h
| - posluževanje odvod: desno v smeri toka zraka! | - serving outlet: right in the direction of the air flow!
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 10 60% po ISO 16890 (M5 po SIST EN 779), s fleksibilnim čelnim priključkom, za pretok zraka 2420m3/h. Maksimalni končni padec tlaka 200Pa. Oznaka: F04.207 | - Filter unit with bag filter cartridge of filtration level ePM 10 60% according to ISO 16890 (M5 according to SIST EN 779), with flexible front connection, for an air flow of 2420m3/h. Maximum final pressure drop 200Pa. Code: F04.207
| - Dušilna enota. - pretok zraka 2420m3/h - padec tlaka dp=16Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 7 17 18 21 15 11 12 Oznaka: DZ04.206 | - Throttle unit. - air flow 2420m3/h - pressure drop dp=16Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 7 17 18 21 15 11 12 Code: DZ04.206
| - Ventilatorska enota s prostotekočim rotorjem. Elektromotor je EC-motor, s 100% zvezno regulacijo vrtljajev preko potenciometra (0-10V), ki omogoča nastavitev delovanja ventilatorja na ustrezno delovno točko. Enota vsebuje: okence O150 in svetilko s stikalom ter servisno stikalo. - pretok zraka 2420m3/h - eksterni statični padec tlaka dpext=300Pa - priključna električna moč 0.78kW, 230V, 50Hz - razred izkoristka elektromotorja IE4/EC - zaščita IP55 Oznaka: FA04.205 | - Fan unit with free-flowing rotor. The electric motor is an EC motor, with 100% continuous speed control via a potentiometer (0-10V), which allows the fan to be set to the appropriate operating point. The unit contains: an O150 window and a lamp with switch and a service switch. - air flow 2420m3/h - external static pressure drop dpext=300Pa - connection power 0.78kW, 230V, 50Hz - electric motor efficiency class IE4/EC - iP55 protection Code: FA04.205
| - Dušilna enota. - pretok zraka 2420m3/h - padec tlaka dp=16Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 7 17 18 21 15 11 12 Oznaka: DZ04.204 | - Throttle unit. - air flow 2420m3/h - pressure drop dp=16Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 7 17 18 21 15 11 12 Code: DZ04.204
| - Prazna enota z regulacijsko žaluzijo 618x538x125, fleksibilnim čelnim priključkom, za pretok zraka 2420m3/h. | - Empty unit with 618x538x125 control louvre, flexible front connection, for air flow 2420m3/h.
| Dolžina: 4,140m | Length: 4,140m
| Širina: 0,750m | Width: 0.750m
| Višina: 0,650m | Height: 0,650m
| Kompletno z dobavo dodatne opreme: | Complete with supply of accessories:
| - postavitvene noge, gumirane, višine 100-200mm | - rubberised feet, height 100-200mm
| - odtočni sifoni | - drain traps
| - jadrovinasti nastavki | - sailplane spigots
| - postavitev klimata na antivibracijski dušilnik (gumo) za preprečevanje prenosa vibracij in hrupa na konstrukcijo objekta. Dušilniki morajo biti preračunani glede na lastnosti klimata (teža in vrtilna frekvenca ventilatorjev). | - installation of the air conditioner on an anti-vibration damper (rubber) to prevent the transmission of vibrations and noise to the structure of the building. The dampers must be calculated according to the characteristics of the air conditioner (weight and speed of the fans).
| - s spojnim, tesnilnim in pritrdilnim materialom in priključki za senzorje, | - with jointing, sealing and fixing materials and sensor connectors,
| Teža: 1.167kg | Weight: 1.167kg
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR | - SYSTEMAIR | kpl | 1 |  | 0
4.2 | Okrogli prezračevalni kanali izdelani iz pocinkane pločevine po SIST EN 1506, vključno z revizijskimi odprtinami, oblikovnimi kosi, debeline po standardu. V ceni na enoto (m) je potrebno upoštevati ves spojni in pritrdilni material (prirobnice, odrez, spone, vijaki, tesnila, ojačitve, vključno z obešalnim in pritrdilnim materialom sistemskega proizvajalca z lastnostmi odgovarjajoč zahtevam SIST EN 12236: 2002, vključno pleskanje vseh kovinskih korozijsko nezaščitenih delov, po temeljitem predhodnem čiščenju do kovinskega sijaja. Antikorozijska zaščita se izvaja v skladu z EN 12944 za naslednje pogoje: • Življenjska doba več kot 15 let. • Stopnja korozijske atmosfere C4 (visoka). | Round ventilation ducts made of galvanised sheet metal according to SIST EN 1506, including inspection openings, shaped pieces, thickness according to the standard. The unit price (m) must take into account all joining and fixing material (flanges, cut-offs, clamps, bolts, gaskets, reinforcements, including hanging and fixing material of the system manufacturer with properties according to the requirements of SIST EN 12236: 2002, including painting of all metal corrosion-protected parts, after thorough cleaning to a metallic gloss. The corrosion protection shall be carried out in accordance with EN12944, for the following conditions: - Lifetime over 15 years. - Corrosive atmosphere C4 (high).
| - Okrogli prezračevalni kanali Ø160 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø160 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 3 |  | 0
| - Okrogli prezračevalni kanali Ø180 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø180 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 8 |  | 0
| - Okrogli prezračevalni kanali Ø200 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø200 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 30 |  | 0
| - Okrogli prezračevalni kanali Ø225 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø225 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 85 |  | 0
| - Okrogli prezračevalni kanali Ø250 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø250 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 10 |  | 0
| - Okrogli prezračevalni kanali Ø315 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø315 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 8 |  | 0
| - Okrogli prezračevalni kanali Ø355 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø355 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 7 |  | 0
| - Okrogli prezračevalni kanali Ø400 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø400 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 10 |  | 0
4.3 | Okrogli pregibni kanali za priključitev stropnih difuzorjev, izdelani iz Al folije ter polnila iz materiala z dušilnim in toplotno-izolativnim efektom. V ceni na enoto (m) je potrebno upoštevati ves spojni material, pritrdilne objemke in tesnilni material, za podatke: | Round folded ducts for the connection of ceiling diffusers, made of Al foil and filling material with damping and thermal insulation effect. The unit price (m) must include all joining material, fixing clamps and sealing material, for details:
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DEC tip: SONODEC - 25 | - DEC tip: SUNDAY - 25
| - Okroglegi pregibni kanali Ø200 | - Ø200 round flexible ducts | m | 20 |  | 0
| - Okroglegi pregibni kanali Ø250 | - Round flexible ducts Ø250 | m | 8 |  | 0
4.4 | Pravokotni prezračevalni kanali izdelani iz pocinkane pločevine po SIST EN 1505:1999, debeline po DIN 24190, klase tesnosti B po SIST EN 1507:2006, vključno z revizijskimi odprtinami, oblikovnimi kosi. V ceni na enoto (m2) je potrebno upoštevati ves spojni in pritrdilni material (prirobnice, odrez, spone, vijaki, tesnila, usmerjevalniki, ojačitve, vključno z obešalnim in pritrdilnim materialom sistemskega proizvajalca z lastnostmi odgovarjajoč zahtevam SIST EN 12236: 2002, vključno pleskanje vseh kovinskih korozijsko nezaščitenih delov, po temeljitem predhodnem čiščenju do kovinskega sijaja. Antikorozijska zaščita se izvaja v skladu z EN 12944 za naslednje pogoje: • Življenjska doba več kot 15 let. • Stopnja korozijske atmosfere C4 (visoka). | Rectangular ventilation ducts made of galvanised sheet metal according to SIST EN 1505:1999, thickness according to DIN 24190, tightness class B according to SIST EN 1507:2006, including inspection openings, shaped pieces. The unit price (m2) must take into account all joining and fixing material (flanges, cut-off, clamps, bolts, gaskets, guides, reinforcements, including hanging and fixing material of the system manufacturer with properties according to the requirements of SIST EN 12236:2002, including the painting of all metal corrosion-protected parts, after thorough preliminary cleaning to a metallic gloss. The anticorrosive protection shall be performed in accordance with EN12944 for the following conditions: - Lifetime over 15 years. - Corrosive atmosphere C4 (high). | m2 | 190 |  | 0
4.5 | Toplotna izolacija zajemnih, izpušnih ter vtočnih kanalov s parozapornimi ploščami izdelanimi iz sintetičnega kavčuka z zaprto celično strukturo, toplotne prevodnosti manjše ali enake 0,033W/mK pri srednji temperaturi 0 °C, koeficient upora difuziji vodene pare večji ali enak 10000 testirano v skladu z EN 13469 za cevi in EN 12086 za plošče, požarna klasifikacija B/BL-s3,d0 po DIN 4102, oziroma po SIST EN 13501-1. | Thermal insulation of intake, exhaust and inlet ducts with vapour control panels made of synthetic rubber with closed cell structure, thermal conductivity less than or equal to 0,033 W/mK at a mean temperature of 0 °C, resistance coefficient to diffusion of water vapour greater than or equal to 10000 tested in accordance with EN 13469 for pipes and EN 12086 for panels, fire classification B/BL-s3,d0 according to DIN 4102, or according to SIST EN 13501-1.
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - ARMACELL tip: Armaflex AF | - ARMACELL tip: Armaflex AF
| Toplotna izolacija zajemnih kanalov na vtočni strani (ZUZ-ODA), debeline s = 50 mm, + original lepilo | Thermal insulation of the inlet side of the intake ducts (ZUZ-ODA), thickness s = 50 mm, + original adhesive | m2 | 5 |  | 0
| Toplotna izolacija notranjih kanalov na vtočni strani (VTZ-SUP), debeline s = 19 mm, + original lepilo | Thermal insulation of internal ducts on the inlet side (VTZ-SUP), thickness s = 19 mm, + original adhesive | m2 | 135 |  | 0
| Toplotna izolacija izpušnih kanalov (ZAZ-EHA), debeline s = 19 mm, + original lepilo | Exhaust duct insulation (ZAZ-EHA), thickness s = 19 mm, + original adhesive | m2 | 55 |  | 0
4.6 | Kanalski dušilnik, za preprečevajne prenosa zvoka med prostori, izdelan iz pocinkane pločevine, mineralne volne za dušenje zvoka debeline 100mm, z zaščito pred erozijo iz netkane tkanine, vključno z vsem potrebnim pritrdilnim, povezovalnim, tesnilnim in montažnim materialom, tipa: | Duct silencer, to prevent the transmission of sound between rooms, made of galvanised sheet, 100mm thick mineral wool for sound attenuation, with non-woven fabric erosion protection, including all necessary fixing, connecting, sealing and mounting material, type:
| - dimenzije Ø250/900/100 | - dimensions Ø250/900/100
| - pretok q = 320 m3/h | - flow rate q = 320 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - LINDAB tip SLGU 250 - 900 -100 | - LINDAB type SLGU 250 - 900 -100
| Oznaka: DZ04.311 | Code: DZ04.311 | kpl | 1 |  | 0
4.7 | Kanalski dušilnik, za preprečevajne prenosa zvoka med prostori, izdelan iz pocinkane pločevine, mineralne volne za dušenje zvoka debeline 100mm, z zaščito pred erozijo iz netkane tkanine, vključno z vsem potrebnim pritrdilnim, povezovalnim, tesnilnim in montažnim materialom, tipa: | Duct silencer, to prevent the transmission of sound between rooms, made of galvanised sheet, 100mm thick mineral wool for sound attenuation, with non-woven fabric erosion protection, including all necessary fixing, connecting, sealing and mounting material, type:
| - dimenzije Ø250/900/100 | - dimensions Ø250/900/100
| - pretok q = 410 m3/h | - flow rate q = 410 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - LINDAB tip SLGU 250 - 900 -100 | - LINDAB type SLGU 250 - 900 -100
| Oznaka: DZ04.312; DZ04.313; DZ04.314 | Code: DZ04.312; DZ04.313; DZ04.314 | kpl | 3 |  | 0
4.8 | Kanalski dušilnik, za preprečevajne prenosa zvoka med prostori, izdelan iz pocinkane pločevine, mineralne volne za dušenje zvoka debeline 100mm, z zaščito pred erozijo iz netkane tkanine, vključno z vsem potrebnim pritrdilnim, povezovalnim, tesnilnim in montažnim materialom, tipa: | Duct silencer, to prevent the transmission of sound between rooms, made of galvanised sheet, 100mm thick mineral wool for sound attenuation, with non-woven fabric erosion protection, including all necessary fixing, connecting, sealing and mounting material, type:
| - dimenzije Ø250/900/100 | - dimensions Ø250/900/100
| - pretok q = 300 m3/h | - flow rate q = 300 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - LINDAB tip SLGU 250 - 900 -100 | - LINDAB type SLGU 250 - 900 -100
| Oznaka: DZ04.321 | Code: DZ04.321 | kpl | 1 |  | 0
4.9 | Kanalski dušilnik, za preprečevajne prenosa zvoka med prostori, izdelan iz pocinkane pločevine, mineralne volne za dušenje zvoka debeline 100mm, z zaščito pred erozijo iz netkane tkanine, vključno z vsem potrebnim pritrdilnim, povezovalnim, tesnilnim in montažnim materialom, tipa: | Duct silencer, to prevent the transmission of sound between rooms, made of galvanised sheet, 100mm thick mineral wool for sound attenuation, with non-woven fabric erosion protection, including all necessary fixing, connecting, sealing and mounting material, type:
| - dimenzije Ø250/900/100 | - dimensions Ø250/900/100
| - pretok q = 390 m3/h | - flow rate q = 390 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - LINDAB tip SLGU 250 - 900 -100 | - LINDAB type SLGU 250 - 900 -100
| Oznaka: DZ04.322; DZ04.323; DZ04.324 | Code: DZ04.322; DZ04.323; DZ04.324 | kpl | 3 |  | 0
4.10 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden z vrha, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, acoustically and thermally insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to the client's or architect's preference, with connection chamber, with control damper, with connections for air flow measurement, inlet connection of the prepared air is provided from the top, including all fixing and mounting material, type:
| - dimenzije Ø597, H=200, Ø200 | - dimensions Ø597, H=200, Ø200
| - pretok q = 160 m3/h | - flow rate q = 160 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-CT-200 | - SYSTEMAIR tip CAP-CT-200
| Oznaka: / | Tag: / | kpl | 2 |  | 0
4.11 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, sound and heat insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to customer's or architect's preference, with connection chamber, with control damper, with connections for air flow measurement, inlet connection of the prepared air is provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø597, H=287, Ø200 | - dimensions Ø597, H=287, Ø200
| - pretok q = 205 m3/h | - flow rate q = 205 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-C-200 | - SYSTEMAIR tip CAP-C-200
| Oznaka: / | Tag: / | kpl | 6 |  | 0
4.12 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, sound and heat insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to customer's or architect's preference, with connection chamber, with control damper, with connections for air flow measurement, inlet connection of the prepared air is provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø608, H=332, Ø250 | - dimensions Ø608, H=332, Ø250
| - pretok q = 330/335 m3/h | - flow rate q = 330/335 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-C-250 | - SYSTEMAIR tip CAP-C-250
| Oznaka: / | Tag: / | kpl | 3 |  | 0
4.13 | Stropni difuzor za odvod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno izolirano, maska je s fiksnimi lamelami, barve (RAL 9010) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, priključek odvoda zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for exhaust air, housing made of galvanised sheet steel, soundproofed, mask with fixed louvres, colour (RAL 9010) or in the colour of the client's or architect's choice, with connection chamber, with control damper, exhaust air connection provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø364, H=290, Ø200 | - dimensions Ø364, H=290, Ø200
| - pretok q = 195 m3/h | - flow rate q = 195 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip VVKN-A-R-400 | - SYSTEMAIR type VVKN-A-R-400
| Oznaka: / | Tag: / | kpl | 6 |  | 0
4.14 | Stropni difuzor za odvod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno izolirano, maska je s fiksnimi lamelami, barve (RAL 9010) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, priključek odvoda zraka je predviden z vrha, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for exhaust air, housing made of galvanised sheet steel, soundproofed, mask with fixed louvres, colour (RAL 9010) or in the colour of the client's or architect's choice, with connection chamber, with control damper, exhaust air connection from the top, including all fixing and mounting material, type:
| - dimenzije Ø364, H=200, Ø200 | - dimensions Ø364, H=200, Ø200
| - pretok q = 150 m3/h | - flow rate q = 150 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip VVKN-A-R-400 | - SYSTEMAIR type VVKN-A-R-400
| Oznaka: / | Tag: / | kpl | 2 |  | 0
4.15 | Stropni difuzor za odvod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno izolirano, maska je s fiksnimi lamelami, barve (RAL 9010) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, priključek odvoda zraka je predviden z vrha, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for exhaust air, housing made of galvanised sheet steel, soundproofed, mask with fixed louvres, colour (RAL 9010) or in the colour of the client's or architect's choice, with connection chamber, with control damper, exhaust air connection from the top, including all fixing and mounting material, type:
| - dimenzije Ø595, H=300, Ø250 | - dimensions Ø595, H=300, Ø250
| - pretok q = 320/315 m3/h | - flow rate q = 320/315 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip VVKN-A-R-625 | - SYSTEMAIR tip VVKN-A-R-625
| Oznaka: / | Tag: / | kpl | 3 |  | 0
4.16 | Protipožarna loputa, za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper, for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, resistant to fire and cold smoke, fire-resistance rating EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG-certificated, with galvanised sheet metal housing, complying with the requirements of the fire safety study with type fastening and sealing material:
| - dimenzije B=450/H=450 | - dimensions B=450/H=450
| - pretok q = 2550 m3/h | - flow rate q = 2550 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-450x450 | - SYSTEMAIR tip FDS-3G-450x450
| Oznaka: KFD04.301 | Code: KFD04.301 | kpl | 1 |  | 0
4.17 | Protipožarna loputa, za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper, for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, resistant to fire and cold smoke, fire-resistance rating EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG-certificated, with galvanised sheet metal housing, complying with the requirements of the fire safety study with type fastening and sealing material:
| - dimenzije B=450/H=450 | - dimensions B=450/H=450
| - pretok q = 2420 m3/h | - flow rate q = 2420 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-450x450 | - SYSTEMAIR tip FDS-3G-450x450
| Oznaka: KFD04.401 | Code: KFD04.401 | kpl | 1 |  | 0
4.18 | Protipožarna loputa, za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper, for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, resistant to fire and cold smoke, fire-resistance rating EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG-certificated, with galvanised sheet metal housing, complying with the requirements of the fire safety study with type fastening and sealing material:
| - dimenzije Ø225 | - dimensions Ø225
| - pretok q = 320 m3/h | - flow rate q = 320 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-225 | - SYSTEMAIR tip FDR-3G-225
| Oznaka: KFD04.302 | Code: KFD04.302 | kpl | 1 |  | 0
4.19 | Protipožarna loputa, za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper, for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, resistant to fire and cold smoke, fire-resistance rating EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG-certificated, with galvanised sheet metal housing, complying with the requirements of the fire safety study with type fastening and sealing material:
| - dimenzije Ø355 | - dimensions Ø355
| - pretok q = 1000 m3/h | - flow rate q = 1000 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-355 | - SYSTEMAIR tip FDR-3G-355
| Oznaka: KFD04.303 | Code: KFD04.303 | kpl | 1 |  | 0
4.20 | Protipožarna loputa, za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper, for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, resistant to fire and cold smoke, fire-resistance rating EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG-certificated, with galvanised sheet metal housing, complying with the requirements of the fire safety study with type fastening and sealing material:
| - dimenzije Ø225 | - dimensions Ø225
| - pretok q = 410 m3/h | - flow rate q = 410 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-225 | - SYSTEMAIR tip FDR-3G-225
| Oznaka: KFD04.304; KFD04.305; KFD04.306 | Code: KFD04.304; KFD04.305; KFD04.306 | kpl | 3 |  | 0
4.21 | Protipožarna loputa, za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper, for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, resistant to fire and cold smoke, fire-resistance rating EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG-certificated, with galvanised sheet metal housing, complying with the requirements of the fire safety study with type fastening and sealing material:
| - dimenzije Ø225 | - dimensions Ø225
| - pretok q = 300 m3/h | - flow rate q = 300 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-225 | - SYSTEMAIR tip FDR-3G-225
| Oznaka: KFD04.402 | Code: KFD04.402 | kpl | 1 |  | 0
4.22 | Protipožarna loputa, za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper, for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, resistant to fire and cold smoke, fire-resistance rating EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG-certificated, with galvanised sheet metal housing, complying with the requirements of the fire safety study with type fastening and sealing material:
| - dimenzije Ø355 | - dimensions Ø355
| - pretok q = 950 m3/h | - flow rate q = 950 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-355 | - SYSTEMAIR tip FDR-3G-355
| Oznaka: KFD04.403 | Code: KFD04.403 | kpl | 1 |  | 0
4.23 | Protipožarna loputa, za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper, for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, resistant to fire and cold smoke, fire-resistance rating EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG-certificated, with galvanised sheet metal housing, complying with the requirements of the fire safety study with type fastening and sealing material:
| - dimenzije Ø225 | - dimensions Ø225
| - pretok q = 390 m3/h | - flow rate q = 390 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-225 | - SYSTEMAIR tip FDR-3G-225
| Oznaka: KFD04.404; KFD04.405; KFD04.406 | Code: KFD04.404; KFD04.405; KFD04.406 | kpl | 3 |  | 0
4.24 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø160 | - ø160 dimensions
| - pretok q = 320 do 110m3/h | - flow rate q = 320 to 110m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-160 | - SYSTEMAIR tip OPTIMA-LV-RI-160
| Oznaka: VAV04.101 | Code: VAV04.101 | kpl | 1 |  | 0
4.25 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø250 | - dimensions Ø250
| - pretok q = 1000 do 320m3/h | - flow rate q = 1000 to 320m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-250 | - SYSTEMAIR tip OPTIMA-LV-RI-250
| Oznaka: VAV04.102 | Code: VAV04.102 | kpl | 1 |  | 0
4.26 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø180 | - dimensions Ø180
| - pretok q = 410 do 140m3/h | - flow rate q = 410 to 140m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-180 | - SYSTEMAIR tip OPTIMA-LV-RI-180
| Oznaka: VAV04.103; VAV04.104; VAV04.105 | Code: VAV04.103; VAV04.104; VAV04.105 | kpl | 3 |  | 0
4.27 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø160 | - ø160 dimensions
| - pretok q = 300 do 100m3/h | - flow rate q = 300 to 100m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-160 | - SYSTEMAIR tip OPTIMA-LV-RI-160
| Oznaka: VAV04.201 | Code: VAV04.201 | kpl | 1 |  | 0
4.28 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø250 | - dimensions Ø250
| - pretok q = 950 do 300m3/h | - flow rate q = 950 to 300m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-250 | - SYSTEMAIR tip OPTIMA-LV-RI-250
| Oznaka: VAV04.202 | Code: VAV04.202 | kpl | 1 |  | 0
4.29 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø180 | - dimensions Ø180
| - pretok q = 390 do 130m3/h | - flow rate q = 390 to 130m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-180 | - SYSTEMAIR tip OPTIMA-LV-RI-180
| Oznaka: VAV04.203; VAV04.204; VAV04.205 | Code: VAV04.203; VAV04.204; VAV04.205 | kpl | 3 |  | 0
4.30 | Elektromotorni pogon z vzmetjo za vstopno/izstopno žaluzijo klimata, vključno z varnostno funkcijo (NC) in stikali položaja, s pritrdilnim in tesnilnim materialom tipa: | Electric motor drive with spring for air-conditioning entry/exit blind, including safety function (NC) and position switches, with fixing and sealing material type:
| - navor 10Nm | - torque 10Nm
| - električno napajanje 24V AC/DC | - 24V AC/DC power supply
| - ON/OFF regulacija delovanja | - ON/OFF operation control
| - za žaluzije do 2m2 | - for blinds up to 2m2
| - zaščita IP54 | - iP54 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip NF24A-S2 | - BELIMO type NF24A-S2
| Oznaka: KD04.101; KD04.202 | Code: KD04.101; KD04.202 | kpl | 2 |  | 0
4.31 | Kanalsko tipalo diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Duct differential pressure sensor, with type fastening and sealing material:
| - območje prikazovanja od 0 do 1500 Pa | - display range 0 to 1500 Pa
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22ADP-184A | - BELIMO type 22ADP-184A
| Oznaka: PICAL04.112; PICAL04.212 | Code: PICAL04.112; PICAL04.212 | kpl | 2 |  | 0
4.32 | Tipalo diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure sensor, with mounting and sealing material type:
| - območje prikazovanja od 0 do 1500 Pa | - display range 0 to 1500 Pa
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22ADP-184A | - BELIMO type 22ADP-184A
| Oznaka: PDIC04.107; PDIC04.205 | Code: PDIC04.107; PDIC04.205 | kpl | 2 |  | 0
4.33 | Diferenčno tlačno stikalo, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure switch, with type fastening and sealing material:
| - območje prikazovanja od 50 do 500Pa | - display range 50 to 500Pa
| - kontaktni tok maksimalno 1,0A / AC 250V | - contact current max 1.0A / AC 250V
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 01APS-10U | - BELIMO type 01APS-10U
| Oznaka: PDSAH04.102; PDSAH04.109; PDSAH04.203; PDSAH04.207 | Code: PDSAH04.102; PDSAH04.109; PDSAH04.203; PDSAH04.207 | kpl | 4 |  | 0
4.34 | Prikazovalnik diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure indicator, with type fixing and sealing material:
| - območje prikazovanja od 50 do 500Pa | - display range 50 to 500Pa
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DWYER tip Magnahelic | - DWYER tip Magnahelic
| Oznaka: PDI04.102; PDI04.109; PDI04.203; PDI04.207 | Code: PDI04.102; PDI04.109; PDI04.203; PDI04.207 | kpl | 4 |  | 0
4.35 | Zunanje tipalo temperature in vlage, s pritrdilnim in tesnilnim materialom tipa: | External temperature and humidity sensor, with fixing and sealing material type:
| - območje prikazovanja od 0 do 100%RH | - display range 0 to 100%RH
| - območje prikazovanja od -40 do 60°C | - display range -40 to 60°C
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22UTH-13M | - BELIMO type 22UTH-13M
| Oznaka: TIC/MIC04.100 | Code: TIC/MIC04.100 | kpl | 1 |  | 0
4.36 | Kanalsko tipalo temperature in vlage, s pritrdilnim in tesnilnim materialom tipa: | Duct temperature and humidity sensor, with fixing and sealing material type:
| - območje prikazovanja od 0 do 100%RH | - display range 0 to 100%RH
| - območje prikazovanja od -40 do 60°C | - display range -40 to 60°C
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22DTH-13M | - BELIMO type 22DTH-13M
| Oznaka: TIC/MIC04.110; TIC/MIC04.208 | Code: TIC/MIC04.110; TIC/MIC04.208 | kpl | 2 |  | 0
4.37 | Prostorsko tipalo kvalitete zraka CO2, s pritrdilnim in tesnilnim materialom tipa: | Room air quality sensor CO2, with fixing and sealing material type:
| - območje CO2 od 0 do 2000ppm | - cO2 range 0 to 2000ppm
| - izhodni signal 0 do 10V | - output signal 0 to 10V
| - izhodni signal MP-Bus | - mP-Bus output signal
| - zaščita IP30 | - iP30 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22RTM-19-1 | - BELIMO type 22RTM-19-1
| Oznaka: QIC04.501; QIC04.502; QIC04.503; QIC04.504; QIC04.505 | Code: QIC04.501; QIC04.502; QIC04.503; QIC04.504; QIC04.505 | kpl | 5 |  | 0
4.38 | Protizmrzovalni termostat, s pritrdilnim in tesnilnim materialom tipa: | Anti-freezing thermostat, with fixing and sealing material type:
| - območje od -10 do 15°C | - range -10 to 15°C
| - dolžina kapilare 6m | - capillary length 6m
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 01ATS-105XC | - BELIMO type 01ATS-105XC
| Oznaka: TSZAL04.104 | Code: TSZAL04.104 | kpl | 1 |  | 0
4.39 | Obtočna črpalka, elektronsko regulirana s frekvenčnim pretvornikom, tipalom diferenčnega tlaka, internimi hidravličnimi, električnimi in komunikacijskimi povezavami, PN10, material jeklena litina, skladnost z ErP, pritrdilnim in tesnilnim materialom tipa: | Circulation pump, electronically controlled with frequency converter, differential pressure sensor, internal hydraulic, electrical and communication connections, PN10, material cast steel, ErP compliant, type fastening and sealing material:
| - za obtok ogrevne vode 50/40°C | - for circulating heating water 50/40°C
| - za pretok V = 1,25m3/h, tlačna višina H = 2m | - for flow rate V = 1,25m3/h, pressure head H = 2m
| - možnost izbire delovanja črpalke na proporcionalni tlak ter optimizacijo delovne obratovalne točke | - option to select proportional pressure pump operation and optimise the operating point
| - napajanje Pel = 0,050kW, 230V / 50Hz | - power supply Pel = 0,050kW, 230V/50Hz
| - navojni priključek G 1 1/2 | - threaded connection G 1 1/2
| - tlačna stopnja PN10 | - pressure rating PN10
| - temperaturno območje ogrevnega medija od -10 do 110°C | - temperature range of the heating medium from -10 to 110°C
| - komunikacija s CNS RS485 | - communication with CNS RS485
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - GRUNDFOS tip MAGNA3 25-40 | - GRUNDFOS type MAGNA3 25-40
| Oznaka: P04.103 | Code: P04.103 | kpl | 1 |  | 0
4.40 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za ogrevno vodo 50/40°C | - for heating water 50/40°C
| - za pretok V = 1,25m3/h | - for a flow rate of V = 1,25m3/h
| - območje regulacije pretoka do 1700 l/h (1,70 m3/h) | - flow control range up to 1700 l/h (1.70 m3/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - navojni priključek G 1 1/4 po ISO 228/1 | - threaded connection G 1 1/4 according to ISO 228/1
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 20 - 400 kPa, min. dif. tlak 20 kPa | - differential pressure range 20 - 400 kPa, min. differential pressure 20 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM25 | - DANFOS tip AB-QM25
| Oznaka: VA04.103 | Code: VA04.103 | kpl | 1 |  | 0
4.41 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za hladilno vodo 9/14°C | - for cooling water 9/14°C
| - za pretok V = 1,84m3/h | - for a flow rate of V = 1,84 m3/h
| - območje regulacije pretoka do 3200 l/h (3,20 m3/h) | - flow control range up to 3200 l/h (3.20 m3/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - navojni priključek G 1 1/2 po ISO 228/1 | - threaded connection G 1 1/2 according to ISO 228/1
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 20 - 400 kPa, min. dif. tlak 20 kPa | - differential pressure range 20 - 400 kPa, min. differential pressure 20 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM32 | - DANFOS type AB-QM32
| Oznaka: VA04.106 | Code: VA04.106 | kpl | 1 |  | 0
| PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS04 | VENTILATION AND AIR CONDITIONING SYSTEM KS04 |  |  |  | 0

## 4.4.5_PrKlim KS05
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.4 | STROJNA DELA | MECHANICAL WORKS
4.4.5 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS05 | VENTILATION AND AIR CONDITIONING SYSTEM KS05 |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
5 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS05 | VENTILATION AND AIR CONDITIONING SYSTEM KS05
5.1 | Klimatska naprava za dovod in odvod zraka KD05/KO05 - glej tudi zavihek Zahteve klimati. | KD05/KO05 supply and extract air conditioner - see also Climate requirements tab.
| Tehnične karakteristike naprave (opis v smeri toka zraka): | Technical characteristics of the appliance (description downstream):
| Dovod: Vdov = 16900 m3/h | Input: Vdov = 16900 m3/h
| - posluževanje dovod: levo v smeri toka zraka! | - inlet: left in the direction of the air flow!
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 10 60% po ISO 16890 (M5 po SIST EN 779), s fleksibilnim čelnim priključkom, za pretok zraka 16900m3/h. Maksimalni končni padec tlaka 200Pa. Oznaka: F05.100 | - Filter unit with bag filter cartridge of filtration level ePM 10 60% according to ISO 16890 (M5 according to SIST EN 779), with flexible front connection, for an air flow of 16900m3/h. Maximum final pressure drop 200Pa. Code: F05.100
| - Prazna enota z regulacijskimi žaluzijami 2x 1695x570x125 za pretok zraka 16900m3/h. | - Empty unit with 2x 1695x570x125 control louvers for 16900m3/h airflow.
| - Prazna enota z AMS merilno mrežo STRA-R1250X650MM vgrajeno v zgornji del enote, pred rototermom. | - Empty unit with AMS measuring grid STRA-R1250X650MM built into the top of the unit, in front of the rototherm.
| - Rotacijska regeneratorska enota za prenos senzibilne in latentne toplote, z ON/OFF žaluzijami obtoka zraka 2x 1790x210x125. Tehnični podatki za zimsko obdobje: - pretok zraka 7870/7040m3/h - stopnja vračanja občutene toplote: 77,2% - stopnja vračanja latentne toplote: 77,3% - vračanje toplotne energije: 95,50kW - stanje dovodnega zr. pred enoto: -13,00°C/90,0% - stanje dovodnega zraka za enoto: 14,00°C/47,30% Tehnični podatki za poletno obdobje: - pretok zraka 7870/7040m3/h - stopnja vračanja občutene toplote: 77,2% - stopnja vračanja latentne toplote: 73,9% - vračanje toplotne energije: 37,00kW - stanje dovodnega zr. pred enoto: 34,50°C/40,0% - stanje dovodnega zraka za enoto: 27,90°C/46,2% Oznaka: RE05.191 | - Rotary regenerative unit for sensible and latent heat transfer, with ON/OFF airflow shutters 2x 1790x210x125. technical data for the winter period: - air flow 7870/7040m3/h - sensible heat recovery rate: 77.2% - latent heat recovery rate: 77.3% - heat energy recovery: 95.50kW - supply air condition upstream of the unit: -13.00°C/90.0% - supply air condition for the unit: 14.00°C/47.30% Technical data for the summer period: - air flow 7870/7040m3/h - sensible heat recovery rate: 77.2% - latent heat recovery rate: 73.9% - heat energy recovery: 37.00kW - supply air condition upstream of the unit: 34.50°C/40.0% - supply air condition for the unit: 27.90°C/46.2% Code: RE05.191
| - Mešalna enota za mešanje zunajnega in prostorskega zraka, z vgrajenimi mešalnimi cevmi za zagotavljanje ustreznega mešanja zraka, z regulacijsko žaluzijo 1695x510x125. | - Mixing unit for mixing outdoor and indoor air, with integrated mixing pipes to ensure adequate air mixing, with control louvre 1695x510x125.
| - Enota pred-grelnika zraka s protizmrzovalno zaščito. - pretok zraka 16900m3/h - grelna moč Qg=41,7kW - temperaturni režim ogrevnega medija 50/40°C - pretok ogrevnega medija 3,63m3/h - padec tlaka na zračni strani 16Pa - temperatura zraka vstop 16,40°C - temperatura zraka izstop 23,70°C - padec tlaka na strani ogr. medija (voda) 11,67kPa - priključka navojna 1 1/4" - tlačna stopnja PN16 Oznaka: HE05.106 | - Air preheater unit with anti-freeze protection. - air flow 16900m3/h - heating power Qg=41,7kW - heating medium temperature 50/40°C - heating medium flow 3,63m3/h - 16Pa pressure drop on the air side - air temperature inlet 16,40°C - air temperature outlet 23,70°C - pressure drop on the heating medium side (water) 11,67kPa - 1 1/4" threaded connectors - pressure rating PN16 Code: HE05.106
| - Vlažilna enota s kontaktnim vlaženjem zraka. Dovod sveže pripravljene demineralizirane vode, z materialom kontaktnega vlažilnika impregniranim srebrom, črpalko, potrebno merilno regulacijsko opremo, ventili na dovodu sveže vode ter ventilom na odvodu vode iz banje, s funkcijo samodejnega praznjenja banje vlažilnika in polnjenja s svežo pripravljeno mehčano vodo glede na prevodnost vode v banji, oziroma glede na čas ko vlažilnik ni v funkciji. Odvod kondenzata s sifonom z vodno in mehansko smardno zaporo. - pretok zraka 16900m3/h - priključna električna moč 0,06kW, 3x400V, 50Hz - padec tlaka na zračni strani dpz=33Pa - temperatura zraka vstop 23,70°C - relativna vlaga zraka vstop 28,1% - temperatura zraka izstop 22,05°C - relativna vlaga izstop 35% - izkoristek vlaženja 15,29% - vlaženje 17,28 kg/h - tipalo prevodonsti vode QICCD05.108 - tipalo zgornjega nivoja vode LICH05.108 - tipalo spodnjega nivoja vode LICL05.108 - elektromagnetni ventil za praznenje VD05.108 - elektromagnetni ventil za dovod sveže vode VD05.208 Oznaka: SH05.108 | - Humidification unit with contact humidification. Freshly prepared demineralised water supply, with silver-impregnated contact humidifier material, pump, necessary metering control equipment, valves at the fresh water inlet and at the water outlet of the humidifier tank, with automatic emptying of the humidifier tank and refilling with freshly prepared softened water according to the conductivity of the water in the tank, or according to the time when the humidifier is not in operation. Condensate drainage with siphon with water and mechanical odour trap. - air flow 16900m3/h - connection power 0,06kW, 3x400V, 50Hz - pressure drop on the air side dpz=33Pa - air temperature inlet 23,70°C - relative humidity 28.1% - air temperature outlet 22,05°C - relative humidity 35% exit - humidification efficiency 15.29% - humidification 17,28 kg/h - water conductivity sensor QICCD05.108 - upper water level sensor LICH05.108 - lower water level sensor LICL05.108 - solenoid valve for emptying VD05.108 - fresh water inlet solenoid valve VD05.208 Code: SH05.108
| - Enota hladilnika z eliminatorjem kapljic in koritom za odvod kondenzata. - pretok zraka 16900m3/h - hladilna moč Qhtot=110,60kW - temperaturni režim hladilnega medija 9/14°C - pretok hladilnega medija 18,99 m3/h - padec tlaka na zračni strani 241/221Pa - temperatura zraka vstop 27,20°C - temperatura zraka izstop 12,30°C - padec tlaka na strani hl. medija (voda) 20,82kPa - priključka navojna 2 1/2" - tlačna stopnja PN16 Oznaka: HE05.109 | - Refrigerator unit with drip eliminator and condensate drain. - air flow 16900m3/h - cooling power Qhtot=110,60kW - cooling medium temperature 9/14°C - coolant flow 18,99 m3/h - pressure drop on the air side 241/221Pa - air temperature inlet 27,20°C - air temperature outlet 12,30°C - pressure drop on the medium side (water) 20,82kPa - 2 1/2" threaded connectors - pressure rating PN16 Code: HE05.109
| - Ventilatorska enota s prostotekočim rotorjem. Elektromotor je EC-motor, s 100% zvezno regulacijo vrtljajev preko potenciometra (0-10V), ki omogoča nastavitev delovanja ventilatorja na ustrezno delovno točko. Enota vsebuje: okence O150 in svetilko s stikalom ter servisno stikalo. - pretok zraka 16900m3/h - eksterni statični padec tlaka dpext=450Pa - priključna električna moč 2x5kW, 3x400V, 50Hz - razred izkoristka elektromotorja IE5/EC - zaščita IP55 Oznaka: FA05.110 | - Fan unit with free-flowing rotor. The electric motor is an EC motor, with 100% continuous speed control via a potentiometer (0-10V), which allows the fan to be set to the appropriate operating point. The unit contains: an O150 window and a lamp with switch and a service switch. - air flow 16900m3/h - external static pressure drop dpext=450Pa - connection power 2x5kW, 3x400V, 50Hz - electric motor efficiency class IE5/EC - iP55 protection Code: FA05.110
| - Dušilna enota. - pretok zraka 16900m3/h - padec tlaka dp=50Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 9 22 23 27 18 13 14 Oznaka: DZ05.111 | - Throttle unit. - air flow 16900m3/h - pressure drop dp=50Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 9 22 23 27 18 13 14 Code: DZ05.111
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 1 75% po ISO 16890 (F8 po SIST EN 779, s fleksibilnim čelnim priključkom, za pretok zraka 16900m3/h. Maksimalni končni padec tlaka 300Pa. Oznaka: F05.112 | - Filter unit with bag filter cartridge of filtration level ePM 1 75% according to ISO 16890 (F8 according to SIST EN 779, with flexible front connection, for air flow 16900m3/h. Maximum final pressure drop 300Pa. Code: F05.112
| Dolžina: 8,270m | Length: 8,270m
| Širina: 1,970m | Width: 1,970m
| Višina: 1,485m | Height: 1,485m
| Kompletno z dobavo dodatne opreme: | Complete with supply of accessories:
| - odtočni sifoni | - drain traps
| - jadrovinasti nastavki | - sailplane spouts
| - s spojnim, tesnilnim in pritrdilnim materialom in priključki za senzorje, | - with jointing, sealing and fixing materials and sensor connectors,
| Odvod: Vodv = 16070 m3/h | Discharge: waterv = 16070 m3/h
| - posluževanje odvod: desno v smeri toka zraka! | - serving outlet: right in the direction of the air flow!
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 10 60% po ISO 16890 (M5 po SIST EN 779), s fleksibilnim čelnim priključkom, za pretok zraka 16070m3/h. Maksimalni končni padec tlaka 200Pa. Oznaka: F05.207 | - Filter unit with bag filter cartridge of filtration level ePM 10 60% according to ISO 16890 (M5 according to SIST EN 779), with flexible front connection, for an air flow of 16070m3/h. Maximum final pressure drop 200Pa. Code: F05.207
| - Dušilna enota. - pretok zraka 16070m3/h - padec tlaka dp=45Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 4 10 25 29 34 31 23 19 Oznaka: DZ05.206 | - Throttle unit. - air flow 16070m3/h - pressure drop dp=45Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 4 10 25 29 34 31 23 19 Code: DZ05.206
| - Ventilatorska enota s prostotekočim rotorjem. Elektromotor je EC-motor, s 100% zvezno regulacijo vrtljajev preko potenciometra (0-10V), ki omogoča nastavitev delovanja ventilatorja na ustrezno delovno točko. Enota vsebuje: okence O150 in svetilko s stikalom ter servisno stikalo. - pretok zraka 16070m3/h - eksterni statični padec tlaka dpext=450Pa - priključna električna moč 2x3,4kW, 3x400V, 50Hz - razred izkoristka elektromotorja IE5/EC - zaščita IP55 Oznaka: FA05.205 | - Fan unit with free-flowing rotor. The electric motor is an EC motor, with 100% continuous speed control via a potentiometer (0-10V), which allows the fan to be set to the appropriate operating point. The unit contains: an O150 window and a lamp with switch and a service switch. - air flow 16070m3/h - external static pressure drop dpext=450Pa - connection power 2x3,4kW, 3x400V, 50Hz - electric motor efficiency class IE5/EC - iP55 protection Code: FA05.205
| - Dušilna enota. - pretok zraka 16070m3/h - padec tlaka dp=45Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 7 16 19 22 20 15 12 Oznaka: DZ05.204 | - Throttle unit. - air flow 16070m3/h - pressure drop dp=45Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 7 16 19 22 20 15 12 Code: DZ05.204
| - Sesalna tlačna enota z regulacijsko žaluzijo 1838x1248x125, fleksibilnim čelnim priključkom, za pretok zraka 16070m3/h. | - Suction pressure unit with control shutter 1838x1248x125, flexible front connection, for air flow 16070m3/h.
| Dolžina: 4,640m | Length: 4,640m
| Širina: 1,970m | Width: 1,970m
| Višina: 1.360m | Height: 1.360m
| Kompletno z dobavo dodatne opreme: | Complete with supply of accessories:
| - postavitvene noge, gumirane, višine 100-200mm | - rubberised feet, height 100-200mm
| - odtočni sifoni | - drain traps
| - jadrovinasti nastavki | - sailplane spouts
| - postavitev klimata na antivibracijski dušilnik (gumo) za preprečevanje prenosa vibracij in hrupa na konstrukcijo objekta. Dušilniki morajo biti preračunani glede na lastnosti klimata (teža in vrtilna frekvenca ventilatorjev). | - installation of the air conditioner on an anti-vibration damper (rubber) to prevent the transmission of vibrations and noise to the structure of the building. The dampers must be calculated according to the characteristics of the air conditioner (weight and speed of the fans).
| - s spojnim, tesnilnim in pritrdilnim materialom in priključki za senzorje, | - with jointing, sealing and fixing materials and sensor connections,
| Teža: 3.822kg | Weight: 3.822kg
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR | - SYSTEMAIR | kpl | 1 |  | 0
5.2 | Zunanja zaščitna rešetka za dovod zraka narejene iz jeklene pocinkane pločevine z zaščitno mrežo, z vgrajenim električnim grelnim kablom z zaščitno funkcijo proti zamrzovanju in termostatom za vklop pri +5 °C, pritrditev z vijaki na vzidan okvir iz jeklenega kotnika, barve v skladu z zahtevam načrta arhitekture, s pritrdilnim in tesnilnim materialom tipa: | External air intake grille made of galvanised sheet steel with protective mesh, with built-in electric heating cable with anti-freeze protection function and thermostat for switching on at +5 °C, bolted to a steel angle frame, colour according to architectural design requirements, with fixing and sealing material type:
| - dimenzije B=920/H=2920 | - dimensions B=920/H=2920
| - dimenzija prosta za pretok zraka B=920/H=1820 | - dimension free for air flow B=920/H=1820
| - H=600mm nad terenom zaprta rešetka z betonsko steno | - H=600mm above ground closed grid with concrete wall
| - H=500mm od vrha rešetke zaprta rešetka z betonsko steno | - H=500mm from top of grille closed grille with concrete wall
| - pretok q = 6804/6803 m3/h | - flow rate q = 6804/6803 m3/h
| - padec tlaka Δp = 6 Pa | - pressure drop Δp = 6 Pa
| - prost prerez Aef=1.323 m2 | - free cross-section Aef=1.323 m2
| - električna moč grelca od 1.88 do 3.77 kW, 3x400 V, 50Hz, na preseku za pretok zraka B=920/H=1820 | - heater electrical power from 1.88 to 3.77 kW, 3x400 V, 50Hz, at air flow cross section B=920/H=1820
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - OC IMP KLIMA tip JZR-6 920x2920 | - OC IMP KLIMA tip JZR-6 920x2920
| Oznaka: ZR05.901; ZR05.902; ZR05.903 | Code: ZR05.901; ZR05.902; ZR05.903 | kpl | 3 |  | 0
5.3 | Zunanja zaščitna rešetka za odvod zraka narejena iz jeklene pocinkane pločevine z zaščitno mrežo, pritrditev z vijaki na vzidan okvir iz jeklenega kotnika, barve v skladu z zahtevam načrta arhitekture, s pritrdilnim in tesnilnim materialom tipa: | External air grille made of galvanised sheet steel with protective mesh, bolted to a steel angle angle frame, colour according to the architectural plan, with fixing and sealing material of the type:
| - dimenzije B=920/H=2920 | - dimensions B=920/H=2920
| - dimenzija prosta za pretok zraka B=920/H=1820 | - dimension free for air flow B=920/H=1820
| - H=600mm nad terenom zaprta rešetka z betonsko steno | - H=600mm above ground closed grid with concrete wall
| - H=500mm od vrha rešetke zaprta rešetka z betonsko steno | - H=500mm from top of grille closed grille with concrete wall
| - pretok q = 9705 m3/h | - flow rate q = 9705 m3/h
| - padec tlaka Δp = 11 Pa | - pressure drop Δp = 11 Pa
| - prost prerez Aef=1.323 m2 | - free cross-section Aef=1.323 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - OC IMP KLIMA tip JZR-6 920x2920 | - OC IMP KLIMA tip JZR-6 920x2920
| Oznaka: ZR05.801; ZR05.802 | Code: ZR05.801; ZR05.802 | kpl | 2 |  | 0
5.4 | Kanalski dogrelnik zraka izdelan iz vroče pocinkane jeklene pločevine Magnelis ZM200, maksimalne obratovalne temperature 150°C, razreda zrakotesnosti C po EN 15727, s pritrdilnim in tesnilnim materialom tipa: | Duct air heater made of hot-dip galvanized steel sheet Magnelis ZM200, maximum operating temperature 150°C, airtightness class C according to EN 15727, with fastening and sealing material type:
| - pretok q = 8300 m3/h | - flow rate q = 8300 m3/h
| - grelna moč Qg=15,9kW | - heating power Qg=15,9kW
| - temperaturni režim ogrevnega medija 50/40°C | - heating medium temperature 50/40°C
| - pretok ogrevnega medija (voda) 1,38m3/h | - heating medium flow (water) 1,38m3/h
| - padec tlaka na zračni strani 58 Pa | - air side pressure drop 58 Pa
| - temperatura zraka vstop 15°C | - air temperature inlet 15°C
| - temperatura zraka vstop 21°C | - air temperature inlet 21°C
| - padec tlaka na ogr. medija (voda) 6,60 kPa | - pressure drop across the medium (water) 6,60 kPa
| - priključka navojna 1" | - 1" threaded connectors
| - tlačna stopnja PN10 | - pressure rating PN10
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - VEAB tip PGV 1200x600-2-2,5 | - VEAB type PGV 1200x600-2-2,5
| Oznaka: HE05.311 | Code: HE05.311 | kpl | 1 |  | 0
5.5 | Kanalski dogrelnik zraka izdelan iz vroče pocinkane jeklene pločevine Magnelis ZM200, maksimalne obratovalne temperature 150°C, razreda zrakotesnosti C po EN 15727, s pritrdilnim in tesnilnim materialom tipa: | Duct air heater made of hot-dip galvanized steel sheet Magnelis ZM200, maximum operating temperature 150°C, airtightness class C according to EN 15727, with fastening and sealing material type:
| - pretok q = 8450 m3/h | - flow rate q = 8450 m3/h
| - grelna moč Qg=16,2kW | - heating power Qg=16,2kW
| - temperaturni režim ogrevnega medija 50/40°C | - heating medium temperature 50/40°C
| - pretok ogrevnega medija (voda) 1,41m3/h | - heating medium flow (water) 1,41m3/h
| - padec tlaka na zračni strani 60 Pa | - pressure drop on the air side 60 Pa
| - temperatura zraka vstop 15°C | - air temperature inlet 15°C
| - temperatura zraka vstop 21°C | - air temperature inlet 21°C
| - padec tlaka na ogr. medija (voda) 6,70 kPa | - pressure drop across the medium (water) 6,70 kPa
| - priključka navojna 1" | - 1" threaded connectors
| - tlačna stopnja PN10 | - pressure rating PN10
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - VEAB tip PGV 1200x600-2-2,5 | - VEAB type PGV 1200x600-2-2,5
| Oznaka: HE05.312 | Code: HE05.312 | kpl | 1 |  | 0
5.6 | Okrogli prezračevalni kanali izdelani iz pocinkane pločevine po SIST EN 1506, vključno z revizijskimi odprtinami, oblikovnimi kosi, debeline po standardu. V ceni na enoto (m) je potrebno upoštevati ves spojni in pritrdilni material (prirobnice, odrez, spone, vijaki, tesnila, ojačitve, vključno z obešalnim in pritrdilnim materialom sistemskega proizvajalca z lastnostmi odgovarjajoč zahtevam SIST EN 12236: 2002, vključno pleskanje vseh kovinskih korozijsko nezaščitenih delov, po temeljitem predhodnem čiščenju do kovinskega sijaja. Antikorozijska zaščita se izvaja v skladu z EN 12944 za naslednje pogoje: • Življenjska doba več kot 15 let. • Stopnja korozijske atmosfere C4 (visoka). | Round ventilation ducts made of galvanised sheet metal according to SIST EN 1506, including inspection openings, shaped pieces, thickness according to the standard. The unit price (m) must take into account all joining and fixing material (flanges, cut-offs, clamps, bolts, gaskets, reinforcements, including hanging and fixing material of the system manufacturer with properties according to the requirements of SIST EN 12236: 2002, including painting of all metal corrosion-protected parts, after thorough cleaning to a metallic gloss. The corrosion protection shall be carried out in accordance with EN12944, for the following conditions: - Lifetime over 15 years. - Corrosive atmosphere C4 (high).
| - Okrogli prezračevalni kanali Ø450 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø450 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 120 |  | 0
5.7 | Pravokotni prezračevalni kanali izdelani iz pocinkane pločevine po SIST EN 1505:1999, debeline po DIN 24190, klase tesnosti B po SIST EN 1507:2006, vključno z revizijskimi odprtinami, oblikovnimi kosi. V ceni na enoto (m2) je potrebno upoštevati ves spojni in pritrdilni material (prirobnice, odrez, spone, vijaki, tesnila, usmerjevalniki, ojačitve, vključno z obešalnim in pritrdilnim materialom sistemskega proizvajalca z lastnostmi odgovarjajoč zahtevam SIST EN 12236: 2002, vključno pleskanje vseh kovinskih korozijsko nezaščitenih delov, po temeljitem predhodnem čiščenju do kovinskega sijaja. Antikorozijska zaščita se izvaja v skladu z EN 12944 za naslednje pogoje: • Življenjska doba več kot 15 let. • Stopnja korozijske atmosfere C4 (visoka). | Rectangular ventilation ducts made of galvanised sheet metal according to SIST EN 1505:1999, thickness according to DIN 24190, tightness class B according to SIST EN 1507:2006, including inspection openings, shaped pieces. The unit price (m2) must take into account all joining and fixing material (flanges, cut-off, clamps, bolts, gaskets, guides, reinforcements, including hanging and fixing material of the system manufacturer with properties according to the requirements of SIST EN 12236:2002, including the painting of all metal corrosion-protected parts, after thorough preliminary cleaning to a metallic gloss. The anticorrosive protection shall be performed in accordance with EN12944 for the following conditions: - Lifetime over 15 years. - Corrosive atmosphere C4 (high). | m2 | 695 |  | 0
5.8 | Toplotna izolacija zajemnih, izpušnih ter vtočnih kanalov s parozapornimi ploščami izdelanimi iz sintetičnega kavčuka z zaprto celično strukturo, toplotne prevodnosti manjše ali enake 0,033W/mK pri srednji temperaturi 0 °C, koeficient upora difuziji vodene pare večji ali enak 10000 testirano v skladu z EN 13469 za cevi in EN 12086 za plošče, požarna klasifikacija B/BL-s3,d0 po DIN 4102, oziroma po SIST EN 13501-1. | Thermal insulation of intake, exhaust and inlet ducts with vapour control panels made of synthetic rubber with closed cell structure, thermal conductivity less than or equal to 0,033 W/mK at a mean temperature of 0 °C, resistance coefficient to diffusion of water vapour greater than or equal to 10000 tested in accordance with EN 13469 for pipes and EN 12086 for panels, fire classification B/BL-s3,d0 according to DIN 4102, or according to SIST EN 13501-1.
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - ARMACELL tip: Armaflex AF | - ARMACELL tip: Armaflex AF
| Toplotna izolacija zajemnih kanalov na vtočni strani (ZUZ-ODA), debeline s = 50 mm, + original lepilo | Thermal insulation of the inlet side of the intake ducts (ZUZ-ODA), thickness s = 50 mm, + original adhesive | m2 | 5 |  | 0
| Toplotna izolacija notranjih kanalov na vtočni strani (VTZ-SUP), debeline s = 19 mm, + original lepilo | Thermal insulation of internal ducts on the inlet side (VTZ-SUP), thickness s = 19 mm, + original adhesive | m2 | 295 |  | 0
| Toplotna izolacija izpušnih kanalov (ZAZ-EHA), debeline s = 19 mm, + original lepilo | Exhaust duct insulation (ZAZ-EHA), thickness s = 19 mm, + original adhesive | m2 | 130 |  | 0
5.9 | Kanalski dušilnik, za preprečevajne prenosa zvoka med prostori, izdelan iz pocinkane pločevine, mineralne volne za dušenje zvoka z zaščito pred erozijo s steklenimi vlakni 70Kg/m3 požarne odpornost M0, vključno z vsem potrebnim pritrdilnim, povezovalnim, tesnilnim in montažnim materialom, tipa: | Duct silencer, to prevent sound transmission between rooms, made of galvanised sheet, mineral wool for sound attenuation with glass fibre erosion protection 70Kg/m3 fire resistance M0, including all necessary fixing, connecting, sealing and mounting material, type:
| - dimenzije Ø450/900/80 | - dimensions Ø450/900/80
| - pretok q = 2007/2008 m3/h | - flow q = 2007/2008 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip RSA 450/900/80 (F) | - SYSTEMAIR tip RSA 450/900/80 (F)
| Oznaka: DZ05.411; DZ05.412; DZ05.413; DZ05.414 | Code: DZ05.411; DZ05.412; DZ05.413; DZ05.414 | kpl | 4 |  | 0
5.10 | Talna rešetka za dovod zraka, aluminijasta s fiksnimi vodoravnimi usmerniki pod kotom 0 stopinj, izdelana iz vlečenih Al profilov, pritrjena na vgradni okvir z vidnimi vijaki, nastavni del s protismernimi lamelami za regulacijo količine zraka, skupaj z montažnim materialom, barve v skladu z zahtevam načrta arhitekture, tipa: | Floor air inlet grille, aluminium with fixed horizontal rectifiers at an angle of 0 degrees, made of drawn Al profiles, fixed to the mounting frame with visible screws, adjusting part with anti-air volume control louvres, including mounting material, colour according to the requirements of the architectural plan, type:
| - dimenzije B=500/H=100 | - dimensions B=500/H=100
| - pretok q = 170 m3/h | - flow rate q = 170 m3/h
| - prost prerez Aef=0,017 m2 | - free cross-section Aef=0,017 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - TECNOVENTIL tip BP5/CTX 500x100 | - TECNOVENTIL tip BP5/CTX 500x100
| Oznaka: / | Tag: / | kpl | 10 |  | 0
5.11 | Vrtinčni difutor, primeren za navpično montažo v stopnice, sestavljena iz okrogle vrtinčne difuzorske plošče in pritrdilnega obroča za hitro montažo, z radialno razporejenimi lamelami za usmerjanje zraka in izjemno hitro zmanjšanje hitrosti zraka ter temperaturne razlike, izdelan iz jeklene pločevine, skupaj z montažnim materialom, barve v skladu z zahtevam načrta arhitekture, tipa: | Vortex diffuser, suitable for vertical installation in stairs, consisting of a circular vortex diffuser plate and a fastening ring for quick installation, with radially arranged slats to direct the air and reduce air velocity and temperature difference extremely quickly, made of sheet steel, complete with mounting material, colour according to the requirements of the architectural plan, type:
| - dimenzije Ø60/Ø35 | - dimensions Ø60/Ø35
| - pretok q = 7,4 m3/h | - flow rate q = 7,4 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SCHAKO tip SAR-060 | - SCHAKO type SAR-060
| Oznaka: / | Tag: / | kpl | 1008 |  | 0
5.12 | Vrtinčni difutor, primeren za navpično montažo v stopnice, sestavljena iz okrogle vrtinčne difuzorske plošče in pritrdilnega obroča za hitro montažo, z radialno razporejenimi lamelami za usmerjanje zraka in izjemno hitro zmanjšanje hitrosti zraka ter temperaturne razlike, izdelan iz jeklene pločevine, skupaj z montažnim materialom, barve v skladu z zahtevam načrta arhitekture, tipa: | Vortex diffuser, suitable for vertical installation in stairs, consisting of a circular vortex diffuser plate and a fastening ring for quick installation, with radially arranged slats to direct the air and reduce air velocity and temperature difference extremely quickly, made of sheet steel, complete with mounting material, colour according to the requirements of the architectural plan, type:
| - dimenzije Ø60/Ø35 | - dimensions Ø60/Ø35
| - pretok q = 7,54 m3/h | - flow rate q = 7,54 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SCHAKO tip SAR-060 | - SCHAKO type SAR-060
| Oznaka: / | Tag: / | kpl | 1008 |  | 0
5.13 | Rešetka za dovod zraka, izdelana iz aluminijskih profilov, sestavljena iz nosilnega okvirja z vodoravnim in navpičnim nastavljivim lamelam, dodatkom za nastavitev količine zraka, pritrditev rešetke na prezračevalni kanal, z ugradnim okvirjem, vključno z vsem pritrdilnim in montažnim materialom, barva v skladu z zahtevam načrta arhitekture, tipa: | Air inlet grille made of aluminium profiles, consisting of a support frame with horizontal and vertical adjustable slats, air volume adjustment accessory, grille attachment to the ventilation duct, with mounting frame, including all fixing and mounting material, colour in accordance with the requirements of the architectural plan, type:
| - dimenzije B=500/H=400 | - dimensions B=500/H=400
| - pretok q = 704 m3/h | - flow rate q = 704 m3/h
| - prost prerez Aef=0,120 m2 | - free cross-section Aef=0,120 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-A-2-2-500x400-R1 | - SYSTEMAIR tip NOVA-A-2-2-500x400-R1
| Oznaka: / | Tag: / | kpl | 12 |  | 0
5.14 | Rešetka za dovod zraka, izdelana iz aluminijskih profilov, sestavljena iz nosilnega okvirja z vodoravnim in navpičnim nastavljivim lamelam, dodatkom za nastavitev količine zraka, pritrditev rešetke na prezračevalni kanal, z ugradnim okvirjem, vključno z vsem pritrdilnim in montažnim materialom, barva v skladu z zahtevam načrta arhitekture, tipa: | Air inlet grille made of aluminium profiles, consisting of a support frame with horizontal and vertical adjustable slats, air volume adjustment accessory, grille attachment to the ventilation duct, with mounting frame, including all fixing and mounting material, colour in accordance with the requirements of the architectural plan, type:
| - dimenzije B=500/H=400 | - dimensions B=500/H=400
| - pretok q = 691 m3/h | - flow rate q = 691 m3/h
| - prost prerez Aef=0,120 m2 | - free cross-section Aef=0,120 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-A-2-2-500x400-R1 | - SYSTEMAIR tip NOVA-A-2-2-500x400-R1
| Oznaka: / | Tag: / | kpl | 12 |  | 0
5.15 | Rešetka za dovod zraka, izdelana iz aluminijskih profilov, sestavljena iz nosilnega okvirja z vodoravnim in navpičnim fiksnim lamelam, dodatkom za nastavitev količine zraka, pritrditev rešetke na prezračevalni kanal, z ugradim okvirjem, vključno z vsem pritrdilnim in montažnim materialom, barva v skladu z zahtevam načrta arhitekture, tipa: | Air inlet grille made of aluminium profiles, consisting of a support frame with horizontal and vertical fixed slats, air volume adjustment accessory, grille attachment to the ventilation duct, with a framed frame, including all fixing and mounting material, colour in accordance with the requirements of the architectural plan, type:
| - dimenzije B=200/H=100 | - dimensions B=200/H=100
| - pretok q = 150 m3/h | - flow rate q = 150 m3/h
| - prost prerez Aef=0,013 m2 | - free cross-section Aef=0,013 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-E-2-200x100-R1 | - SYSTEMAIR tip NOVA-E-2-200x100-R1
| Oznaka: / | Tag: / | kpl | 1 |  | 0
5.16 | Rešetka za odvod zraka, izdelana iz jeklene pocinkane pločevine, sestavljena iz nosilnega okvirja z navpičnim nastavljivim lamelam, dodatkom za nastavitev količine zraka, pritrditev rešetke na prezračevalni kanal, z ugradim okvirjem, vključno z vsem pritrdilnim in montažnim materialom, barva v skladu z zahtevam načrta arhitekture, tipa: | Air outlet grille made of galvanised sheet steel, consisting of a support frame with vertical adjustable slats, air volume adjustment accessory, grille attachment to the ventilation duct, with a framed frame, including all fixing and mounting material, colour according to the requirements of the architectural plan, type:
| - dimenzije B=625/H=225 | - dimensions B=625/H=225
| - pretok q = 986/987 m3/h | - flow rate q = 986/987 m3/h
| - prost prerez Aef=0,068 m2 | - free cross-section Aef=0,068 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-C-1-625x225-R1 | - SYSTEMAIR tip NOVA-C-1-625x225-R1
| Oznaka: / | Tag: / | kpl | 8 |  | 0
5.17 | Rešetka za odvod zraka, izdelana iz jeklene pocinkane pločevine, sestavljena iz nosilnega okvirja z navpičnim nastavljivim lamelam, dodatkom za nastavitev količine zraka, pritrditev rešetke na prezračevalni kanal, z ugradim okvirjem, vključno z vsem pritrdilnim in montažnim materialom, barva v skladu z zahtevam načrta arhitekture, tipa: | Air outlet grille made of galvanised sheet steel, consisting of a support frame with vertical adjustable slats, air volume adjustment accessory, grille attachment to the ventilation duct, with a framed frame, including all fixing and mounting material, colour in accordance with the requirements of the architectural plan, type:
| - dimenzije B=625/H=225 | - dimensions B=625/H=225
| - pretok q = 1003/1004 m3/h | - flow rate q = 1003/1004 m3/h
| - prost prerez Aef=0,068 m2 | - free cross-section Aef=0,068 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-C-1-625x225-R1 | - SYSTEMAIR tip NOVA-C-1-625x225-R1
| Oznaka: / | Tag: / | kpl | 8 |  | 0
5.18 | Rešetka za odvod zraka, izdelana iz aluminijskih profilov, sestavljena iz nosilnega okvirja z vodoravnim in navpičnim fiksnim lamelam, dodatkom za nastavitev količine zraka, pritrditev rešetke na prezračevalni kanal, z ugradim okvirjem, vključno z vsem pritrdilnim in montažnim materialom, barva v skladu z zahtevam načrta arhitekture, tipa: | Air outlet grille made of aluminium profiles, consisting of a support frame with horizontal and vertical fixed slats, air volume adjustment accessory, grille attachment to the ventilation duct, with a framed frame, including all fixing and mounting material, colour in accordance with the requirements of the architectural plan, type:
| - dimenzije B=200/H=100 | - dimensions B=200/H=100
| - pretok q = 150 m3/h | - flow rate q = 150 m3/h
| - prost prerez Aef=0,013 m2 | - free cross-section Aef=0,013 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-E-2-200x100-R1 | - SYSTEMAIR tip NOVA-E-2-200x100-R1
| Oznaka: / | Tag: / | kpl | 1 |  | 0
5.19 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material of type:
| - dimenzije B=1000/H=600 | - dimensions B=1000/H=600
| - pretok q = 8300 m3/h | - flow rate q = 8300 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-1000x600 | - SYSTEMAIR tip FDS-3G-1000x600
| Oznaka: KFD05.311 | Code: KFD05.311 | kpl | 1 |  | 0
5.20 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material of type:
| - dimenzije B=1000/H=600 | - dimensions B=1000/H=600
| - pretok q = 8450 m3/h | - flow rate q = 8450 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-1000x600 | - SYSTEMAIR tip FDS-3G-1000x600
| Oznaka: KFD05.312 | Code: KFD05.312 | kpl | 1 |  | 0
5.21 | Protipožarna loputa, za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper, for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, resistant to fire and cold smoke, fire-resistance rating EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG-certificated, with galvanised sheet steel housing, complying with the requirements of the fire safety study with type-approved fixing and sealing material:
| - dimenzije B=600/H=450 | - dimensions B=600/H=450
| - pretok q = 4015 m3/h | - flow rate q = 4015 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-600x450 | - SYSTEMAIR tip FDS-600x450
| Oznaka: KFD05.411; KFD05.414; KFD05.415 | Code: KFD05.411; KFD05.414; KFD05.415 | kpl | 3 |  | 0
5.22 | Protipožarna loputa, za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper, for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, resistant to fire and cold smoke, fire-resistance rating EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG-certificated, with galvanised sheet steel housing, complying with the requirements of the fire safety study with type-approved fixing and sealing material:
| - dimenzije B=1200/H=450 | - dimensions B=1200/H=450
| - pretok q = 7890 m3/h | - flow rate q = 7890 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-1200x450 | - SYSTEMAIR tip FDS-1200x450
| Oznaka: KFD05.412; KFD05.416 | Code: KFD05.412; KFD05.416 | kpl | 2 |  | 0
5.23 | Protipožarna loputa, za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper, for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, resistant to fire and cold smoke, fire-resistance rating EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG-certificated, with galvanised sheet steel housing, complying with the requirements of the fire safety study with type-approved fixing and sealing material:
| - dimenzije Ø450 | - ø450 dimensions
| - pretok q = 2007/2008 m3/h | - flow q = 2007/2008 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-450 | - SYSTEMAIR tip FDR-3G-450
| Oznaka: KFD05.417; KFD05.418; KFD05.419; KFD05.420 | Code: KFD05.417; KFD05.418; KFD05.419; KFD05.420 | kpl | 4 |  | 0
5.24 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo regulacije konstantnega pretoka, s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow regulator, made of galvanised sheet metal with acoustic and thermal insulation, with constant flow control function, with fastening and sealing material type:
| - dimenzije Ø100 | - ø100 dimensions
| - pretok q = 150m3/h | - flow rate q = 150m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOTUS-RI-100-M0 | - SYSTEMAIR tip NOTUS-RI-100-M0
| Oznaka: CAV05.301; CAV05.401 | Code: CAV05.301; CAV05.401 | kpl | 2 |  | 0
5.25 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function and type fastening and sealing material:
| - dimenzije 800x400 | - dimensions 800x400
| - pretok q = 8300 do 2550m3/h | - flow rate q = 8300 to 2550m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-SI-FC-800x400 | - SYSTEMAIR tip OPTIMA-SI-FC-800x400
| Oznaka: VAV05.311 | Code: VAV05.311 | kpl | 1 |  | 0
5.26 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function and type fastening and sealing material:
| - dimenzije 800x400 | - dimensions 800x400
| - pretok q = 8450 do 2600m3/h | - flow rate q = 8450 to 2600m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-SI-FC-800x400 | - SYSTEMAIR tip OPTIMA-SI-FC-800x400
| Oznaka: VAV05.312 | Code: VAV05.312 | kpl | 1 |  | 0
5.27 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function and type fastening and sealing material:
| - dimenzije 550x300 | - dimensions 550x300
| - pretok q = 4015 do 1235m3/h | - flow rate q = 4015 to 1235m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-SI-FC-550x300 | - SYSTEMAIR tip OPTIMA-SI-FC-550x300
| Oznaka: VAV05.411; VAV05.412 | Code: VAV05.411; VAV05.412 | kpl | 2 |  | 0
5.28 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function and type fastening and sealing material:
| - dimenzije 750x400 | - dimensions 750x400
| - pretok q = 7890 do 2420m3/h | - flow rate q = 7890 to 2420m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-SI-FC-750x400 | - SYSTEMAIR tip OPTIMA-SI-FC-750x400
| Oznaka: VAV05.413 | Code: VAV05.413 | kpl | 1 |  | 0
5.29 | Elektromotorni pogon z vzmetjo za vstopno žaluzijo klimata, vključno z varnostno funkcijo (NC) in stikali položaja, s pritrdilnim in tesnilnim materialom tipa: | Electric motor drive with spring for air-conditioning inlet shutter, including safety function (NC) and position switches, with fixing and sealing material type:
| - navor 10Nm | - torque 10Nm
| - električno napajanje 24V AC/DC | - 24V AC/DC power supply
| - ON/OFF regulacija delovanja | - ON/OFF operation control
| - za žaluzije do 2m2 | - for blinds up to 2m2
| - zaščita IP54 | - iP54 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip NF24A-S2 | - BELIMO type NF24A-S2
| Oznaka: KD05.101; KD05.102 | Code: KD05.101; KD05.102 | kpl | 2 |  | 0
5.30 | Elektromotorni pogon z vzmetjo za izstopno žaluzijo klimata, vključno z varnostno funkcijo (NC) in stikali položaja, s pritrdilnim in tesnilnim materialom tipa: | Electric motor drive with spring for climate exit blind, including safety function (NC) and position switches, with fixing and sealing material type:
| - navor 10Nm | - torque 10Nm
| - električno napajanje 24V AC/DC | - 24V AC/DC power supply
| - zvezna regulacija delovanja | - continuous operation control
| - za žaluzije do 2m2 | - for blinds up to 2m2
| - zaščita IP54 | - iP54 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip NF24A-SR-S2 | - BELIMO type NF24A-SR-S2
| Oznaka: KA05.202 | Code: KA05.202 | kpl | 1 |  | 0
5.31 | Elektromotorni pogon za obtok regeneratorja, s stikalom položaja za odprt položaj, s pritrdilnim in tesnilnim materialom tipa: | Electric motor drive for regenerator circulation, with position switch for open position, with fixing and sealing material type:
| - navor 5Nm | - torque 5Nm
| - električno napajanje 24V AC/DC | - 24V AC/DC power supply
| - ON/OFF regulacija delovanja | - ON/OFF operation control
| - za žaluzije do 1m2 | - for blinds up to 1m2
| - zaščita IP54 | - iP54 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip LM24A-S | - BELIMO type LM24A-S
| Oznaka: KD05.104; KD05.203 | Code: KD05.104; KD05.203 | kpl | 2 |  | 0
5.32 | Elektromotorni pogon za mešalno žaluzijo klimata, s pritrdilnim in tesnilnim materialom tipa: | Electric motor drive for air-conditioning mixing louvre, with fixing and sealing material type:
| - navor 5Nm | - torque 5Nm
| - električno napajanje 24V AC/DC | - 24V AC/DC power supply
| - zvezna regulacija delovanja | - continuous operation control
| - za žaluzije do 1m2 | - for blinds up to 1m2
| - zaščita IP54 | - iP54 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip LM24A-SR | - BELIMO type LM24A-SR
| Oznaka: KA05.105 | Code: KA05.105 | kpl | 1 |  | 0
5.33 | Kanalski senzor diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Duct differential pressure sensor, with mounting and sealing material type:
| - območje prikazovanja od 0 do 1500 Pa | - display range 0 to 1500 Pa
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22ADP-184A | - BELIMO type 22ADP-184A
| Oznaka: PICAL05.209; PICAL05.115 | Code: PICAL05.209; PICAL05.115 | kpl | 2 |  | 0
5.34 | Diferenčno tlačno stikalo, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure switch, with type fastening and sealing material:
| - območje prikazovanja od 50 do 500Pa | - display range 50 to 500Pa
| - kontaktni tok maksimalno 1,0A / AC 250V | - contact current max 1.0A / AC 250V
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 01APS-10U | - BELIMO type 01APS-10U
| Oznaka: PDSAH05.100; PDSAH05.112; PDSAH05.203; PDSAH05.207 | Code: PDSAH05.100; PDSAH05.112; PDSAH05.203; PDSAH05.207 | kpl | 4 |  | 0
5.35 | Prikazovalnik diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure indicator, with type fixing and sealing material:
| - območje prikazovanja od 50 do 500Pa | - display range 50 to 500Pa
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DWYER tip Magnahelic | - DWYER tip Magnahelic
| Oznaka: PDI05.100; PDI05.112; PDI05.203; PDI05.207 | Code: PDI05.100; PDI05.112; PDI05.203; PDI05.207 | kpl | 4 |  | 0
5.36 | Tipalo diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure sensor, with mounting and sealing material type:
| - območje prikazovanja od 0 do 1500 Pa | - display range 0 to 1500 Pa
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22ADP-184A | - BELIMO type 22ADP-184A
| Oznaka: PDIC05.110; PDIC05.205 | Code: PDIC05.110; PDIC05.205 | kpl | 2 |  | 0
5.37 | Tipalo diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure sensor, with mounting and sealing material type:
| - območje prikazovanja od 0 do 500 Pa | - display range 0 to 500 Pa
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22ADP-184A | - BELIMO type 22ADP-184A
| Oznaka: PDIC05.103 | Code: PDIC05.103 | kpl | 1 |  | 0
5.38 | Kanalsko tipalo temperature in vlage, s pritrdilnim in tesnilnim materialom tipa: | Duct temperature and humidity sensor, with fixing and sealing material type:
| - območje prikazovanja od 0 do 100%RH | - display range 0 to 100%RH
| - območje prikazovanja od -40 do 60°C | - display range -40 to 60°C
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22DTH-13M | - BELIMO type 22DTH-13M
| Oznaka: TIC/MIC05.113; TIC/MIC05.208 | Code: TIC/MIC05.113; TIC/MIC05.208 | kpl | 2 |  | 0
5.39 | Prostorsko tipalo temperature, vlage in kvalitete zraka CO2, s pritrdilnim in tesnilnim materialom tipa: | Room temperature, humidity and air quality sensor CO2, with fixing and sealing material type:
| - območje merjenja od 0 do 50°C | - measuring range 0 to 50°C
| - območje merjenja od 0 do 100%RH | - measuring range 0 to 100%RH
| - območje CO2 od 0 do 2000ppm | - cO2 range from 0 to 2000ppm
| - izhodni signal 0 do 10V | - output signal 0 to 10V
| - izhodni signal MP-Bus | - mP-Bus output signal
| - zaščita IP30 | - iP30 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22RTM-19-1 | - BELIMO type 22RTM-19-1
| Oznaka: TIC/MIC/QIC05.501; TIC/MIC/QIC05.502 | Code: TIC/MIC/QIC05.501; TIC/MIC/QIC05.502 | kpl | 2 |  | 0
5.40 | Protizmrzovalni termostat, s pritrdilnim in tesnilnim materialom tipa: | Anti-freezing thermostat, with fixing and sealing material type:
| - območje od -10 do 15°C | - range -10 to 15°C
| - dolžina kapilare 6m | - capillary length 6m
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 01ATS-105XC | - BELIMO type 01ATS-105XC
| Oznaka: TSZAL05.107 | Code: TSZAL05.107 | kpl | 1 |  | 0
5.41 | Obtočna črpalka, elektronsko regulirana s frekvenčnim pretvornikom, tipalom diferenčnega tlaka, internimi hidravličnimi, električnimi in komunikacijskimi povezavami, PN10, material jeklena litina, skladnost z ErP, pritrdilnim in tesnilnim materialom tipa: | Circulation pump, electronically controlled with frequency converter, differential pressure sensor, internal hydraulic, electrical and communication connections, PN10, material cast steel, ErP compliant, type fastening and sealing material:
| - za obtok ogrevne vode 50/40°C | - for circulating heating water 50/40°C
| - za pretok V = 3,63m3/h, tlačna višina H = 1,8m | - for flow rate V = 3,63m3/h, pressure head H = 1,8m
| - možnost izbire delovanja črpalke na proporcionalni tlak ter optimizacijo delovne obratovalne točke | - option to select proportional pressure pump operation and optimise the operating point
| - napajanje Pel = 0,050kW, 230V / 50Hz | - power supply Pel = 0,050kW, 230V/50Hz
| - navojni priključek G 1 1/2 | - threaded connection G 1 1/2
| - tlačna stopnja PN10 | - pressure rating PN10
| - temperaturno območje ogrevnega medija od -10 do 110°C | - temperature range of the heating medium from -10 to 110°C
| - komunikacija s CNS RS485 | - communication with CNS RS485
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - GRUNDFOS tip MAGNA3 25-40 | - GRUNDFOS type MAGNA3 25-40
| Oznaka: P05.106 | Code: P05.106 | kpl | 1 |  | 0
5.42 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za ogrevno vodo 50/40°C | - for heating water 50/40°C
| - za pretok V = 3,63m3/h | - for a flow rate of V = 3,63m3/h
| - območje regulacije pretoka do 7500 l/h (7,50 m3/h) | - flow control range up to 7500 l/h (7.50 m3/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - navojni priključek G 2 po ISO 228/1 | - threaded connection G 2 according to ISO 228/1
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 30 - 400 kPa, min. dif. tlak 30 kPa | - differential pressure range 30 - 400 kPa, min. differential pressure 30 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM40 | - DANFOS tip AB-QM40
| Oznaka: VA05.106 | Code: VA05.106 | kpl | 1 |  | 0
5.43 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za hladilno vodo 9/14°C | - for cooling water 9/14°C
| - za pretok V = 18,99m3/h | - for a flow rate of V = 18,99m3/h
| - območje regulacije pretoka do 20000 l/h (20 m3/h) | - flow control range up to 20000 l/h (20 m3/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - prirobnični priključek DN65 | - flange connection DN65
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 30 - 400 kPa, min. dif. tlak 30 kPa | - differential pressure range 30 - 400 kPa, min. differential pressure 30 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM65 | - DANFOS type AB-QM65
| Oznaka: VA05.109 | Code: VA05.109 | kpl | 1 |  | 0
5.44 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za ogrevno vodo 50/40°C | - for heating water 50/40°C
| - za pretok V = 1,38m3/h | - for a flow rate of V = 1,38 m3/h
| - območje regulacije pretoka do 1700 l/h (1,70 m3/h) | - flow control range up to 1700 l/h (1.70 m3/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - navojni priključek G 1 1/4 po ISO 228/1 | - threaded connection G 1 1/4 according to ISO 228/1
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 20 - 400 kPa, min. dif. tlak 20 kPa | - differential pressure range 20 - 400 kPa, min. differential pressure 20 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM25 | - DANFOS type AB-QM25
| Oznaka: VA05.311 | Code: VA05.311 | kpl | 1 |  | 0
5.45 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za ogrevno vodo 50/40°C | - for heating water 50/40°C
| - za pretok V = 1,41m3/h | - for a flow rate of V = 1,41m3/h
| - območje regulacije pretoka do 1700 l/h (1,70 m3/h) | - flow control range up to 1700 l/h (1.70 m3/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - navojni priključek G 1 1/4 po ISO 228/1 | - threaded connection G 1 1/4 according to ISO 228/1
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 20 - 400 kPa, min. dif. tlak 20 kPa | - differential pressure range 20 - 400 kPa, min. differential pressure 20 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM25 | - DANFOS tip AB-QM25
| Oznaka: VA05.312 | Code: VA05.312 | kpl | 1 |  | 0
5.46 | Sistem reverzne osmoze s predfiltracijo za pripravo demineralizirane vode za potrebe vlažilnika klimatov KS05, KS06, KS17, KS18, s pritrdilnim in tesnilnim materialom, skupaj s/z: | Reverse osmosis system with pre-filtration for the preparation of demineralised water for the humidifier of air-conditioners KS05, KS06, KS17, KS18, with fixing and sealing material, incl:
| - svečnim filtrom s 5 m filternimi vložki | - candle filter with 5 m filter cartridges
| - vstopnim magnetnim ventilom | - inlet solenoid valve
| - vstopnim zaščitnim tlačnim stikalom | - inlet pressure relief switch
| - spiralno navitimi RO moduli v tlačnem ohišju | - spiral wound RO modules in a pressure housing
| - internimi cevnimi povezavami | - internal pipe connections
| - merilcema trenutnega pretoka dobitka in koncentrata | - instantaneous flow meters for the feed and concentrate
| - manometri za kontrolo tlaka vode na vstopu in izstopu koncentrata | - pressure gauges for controlling the water pressure at the inlet and outlet of the concentrate
| - merilcem prevodnosti dobitka | - a conductivity meter
| - mikroprocesorsko krmilno enoto | - microprocessor control unit
| - vzorčevalno pipico | - sampling tap
| - nosilno konstrukcijo iz nerjavnega jekla | - stainless steel load-bearing structure
| - ročno tipko za zaustavitev in zagon RO | - manual key to stop and start the RO
| - plovnim stikalom | - float switch
| - dimenzije naprave 500x1500x500 mm | - dimensions 500x1500x500 mm
| - pretok dobitka 150 l/h | - 150 l/h recharge flow
| - izkoristek naprave 50 - 70 % | - plant efficiency 50 - 70 %
| - zadržani topljenec min 98 % | - solvent retention min 98 %
| - priključki vstop/izstop DN15 | - inlet/outlet connections DN15
| - vstopni tlak min 1,5 bar | - inlet pressure min 1,5 bar
| - delovni tlak 15 bar | - working pressure 15 bar
| - delovna temperatura 10-35 °C | - operating temperature 10-35 °C
| - električni priključek 220/50/0,55 V/Hz/kW | - 220/50/0,55 V/Hz/kW electrical connection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - MAKCMC tip MINIRO 15 | - MAKCMC type MINIRO 15
| Oznaka: | Code: | kpl | 1 |  | 0
5.47 | Rezervoar demineralizirane vode in črpalna postaja za potrebe vlažilnika klimatov KS05, KS06, KS17, KS18, s pritrdilnim in tesnilnim materialom, skupaj s/z: | Demineralised water tank and pumping station for the humidifier of air-conditioners KS05, KS06, KS17, KS18, with fixing and sealing material, incl:
| - rezervoarjem iz PE | - pE tank
| - nivojskimi stikali: min/maks, za zaščito črpalke in signalizacijo preliva | - level switches: min/max, for pump protection and overflow signalling
| - hidrostatična sonda za zvezni nivo v rezervoarju | - hydrostatic probe for continuous tank level
| - pripadajočo PVC armaturo | - associated PVC fittings
| - varnostnim prelivom | - safety dressing
| - kontrolnim manometrom | - a check gauge
| - ekspanzijsko posodo iz nerjavnega jekla | - stainless steel expansion tank
| - tlačnim stikalom | - pressure switch
| - centrifugalno črpalko CM 1-6; material nerjavno jeklo AISI 316 | - centrifugal pump CM 1-6; material stainless steel AISI 316
| - volumen rezervoarja 115 l | - tank capacity 115 l
| - dimenzije rezervoarja D460x775 mm | - tank dimensions D460x775 mm
| - kapaciteta črpalke 1,7 m3/h | - pump capacity 1.7 m3/h
| - tlak 3,7bar | - pressure 3,7bar
| - priključki DN 25 | - dN 25 connections
| - el. priključek 400/50/460 V/Hz/W | - 400/50/460 V/Hz/W power connection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - MAKCMC tip RDI 12 C1 | - MAKCMC type RDI 12 C1
| Oznaka: | Code: | kpl | 1 |  | 0
5.48 | Avtomatski dvojni ionski mehčalec vode za potrebe vlažilnika klimatov KS05, KS06, KS17, KS18, s pritrdilnim in tesnilnim materialom, skupaj s/z: | Automatic double ion water softener for the humidifier needs of air conditioners KS05, KS06, KS17, KS18, with fixing and sealing material, incl:
| - elektro-mehanskim krmilnikom | - electro-mechanical controller
| - večpotnim ventilom z dvema distributorjema | - multiport valve with two distributors
| - tlačno posodo iz armiranega polietilena komplet 2 | - pressure vessel of reinforced polyethylene, set of 2
| - solnim ventilom | - salt valve
| - solnikom | - to solnikom
| - smolo močno kislega ionskega izmenjevalca | - strong acid ion-exchange resin
| - čistilnim kosom | - cleaning pieces
| - tabletirano soljo 25kg | - tablet salt 25kg
| - dimenzije naprave 1500x700x1100 mm | - dimensions 1500x700x1100 mm
| - volumen ionske smole 2 x 18 l | - ionic resin volume 2 x 18 l
| - volumen tlačne posode 2 x 20,4 l | - pressure vessel volume 2 x 20.4 l
| - volumen solnika 100 l | - brine tank capacity 100 l
| - poraba tabletirane soli 2,7 – 4,3 kg/reg | - tablet salt consumption 2,7 - 4,3 kg/reg
| - pretok 0,1 – 0,9 m3/h | - flow rate 0,1 - 0,9 m3/h
| - kapaciteta 9,9 –11,2 m3/reg | - capacity 9,9 -11,2 m3/reg
| - priključki vstop/izstop DN20 | - inlet/outlet connections DN20
| - delovni tlak 2,5 – 6 bar | - working pressure 2,5 - 6 bar
| - delovna temperatura do 40°C | - operating temperature up to 40°C
| - el. priključek 220/50/10 V/Hz/W | - 220/50/10 V/Hz/W power connection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - MAKCMC tip MINOM 0DF - 25 | - MAKCMC type MINOM 0DF - 25
| Oznaka: | Code: | kpl | 1 |  | 0
5.49 | Sistem za UV dezinfekcijo vode za potrebe vlažilnika klimatov KS05, KS06, KS17, KS18, s pritrdilnim in tesnilnim materialom, skupaj s/z: | UV water disinfection system for the humidifier of air conditioners KS05, KS06, KS17, KS18, with fixing and sealing material, incl:
| - reaktorjem: material 1.4404, elektopoliran | - reactor: material 1.4404, electropolished
| - nizkotlačnim UV sevalom v zaščitni cevi iz kremenčevega stekla | - low-pressure UV radiation in a protective quartz glass tube
| - mehkim zagonom delovanja sevala | - soft start of the radiator
| - signalizacijo za zamenjavo sevala | - signalling for radiator replacement
| - signalizacijo napak delovanja | - fault signalling
| - upravljalno enoto | - the control unit
| - dimenzije upravljalne enote 168x200x66 mm | - control unit dimensions 168x200x66 mm
| - priključki 3/4 '' | - 3/4'' connections
| - obratovalni tlak PN10 | - operating pressure PN10
| - UV doza 400 J/m2 | - UV dose 400 J/m2
| - hidravlična kapaciteta maks 1,69 m3/h | - hydraulic capacity max 1,69 m3/h
| - temperatura vode 0-35°C | - water temperature 0-35°C
| - temperatura okolice maks 35°C | - ambient temperature max 35°C
| - zaščita reaktor/upravlj. enota IP 65/54 | - reactor/management unit protection IP 65/54
| - el. priključek 220/50/55 V/Hz/W | - 220/50/55 V/Hz/W power connection
| - življenska doba svetil 8.760 h | - lamp life 8.760 h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - MAKCMC tip AQUADA 2 PRO | - MAKCMC tip AQUADA 2 PRO
| Oznaka: | Code: | kpl | 1 |  | 0
| PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS05 | VENTILATION AND AIR CONDITIONING SYSTEM KS05 |  |  |  | 0

## 4.4.6_PrKlim KS06
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.4 | STROJNA DELA | MECHANICAL WORKS
4.4.6 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS06 | VENTILATION AND AIR CONDITIONING SYSTEM KS06 |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
6 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS06 | VENTILATION AND AIR CONDITIONING SYSTEM KS06
6.1 | Klimatska naprava za dovod in odvod zraka KD06/KO06 - glej tudi zavihek Zahteve klimati. | KD06/KO06 supply and extract air conditioner - see also Climate requirements tab.
| Tehnične karakteristike naprave (opis v smeri toka zraka): | Technical characteristics of the appliance (description downstream):
| Dovod: Vdov = 3510 m3/h | Input: Vdov = 3510 m3/h
| - posluževanje dovod: desno v smeri toka zraka! | - inlet: right in the direction of the air flow!
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 10 60% po ISO 16890 (M5 po SIST EN 779), z regulacijsko žaluzijo 923x638x125, s fleksibilnim čelnim priključkom, za pretok zraka 3510m3/h. Maksimalni končni padec tlaka 200Pa. Oznaka: F06.102 | - Filter unit with bag filter cartridge of filtration level ePM 10 60% according to ISO 16890 (M5 according to SIST EN 779), with control shutter 923x638x125, with flexible front connection, for air flow 3510m3/h. Maximum final pressure drop 200Pa. Code: F06.102
| - Rotacijska regeneratorska enota za prenos senzibilne in latentne toplote. Tehnični podatki za zimsko obdobje: - pretok zraka 3510/3340m3/h - stopnja vračanja občutene toplote: 74,9% - stopnja vračanja latentne toplote: 75,9% - vračanje toplotne energije: 38kW - stanje dovodnega zr. pred enoto: -13,00°C/90,0% - stanje dovodnega zraka za enoto: 12,50°C/42,2% Tehnični podatki za poletno obdobje: - pretok zraka 3510/3340m3/h - stopnja vračanja občutene toplote: 74,9% - stopnja vračanja latentne toplote: 71,1% - vračanje toplotne energije: 10,10kW - stanje dovodnega zr. pred enoto: 34,50°C/40,0% - stanje dovodnega zraka za enoto: 28,10°C/54,4% Oznaka: RE06.191 | - Rotary regenerative unit for sensible and latent heat transfer. technical data for the winter period: - air flow 3510/3340m3/h - sensible heat recovery rate: 74.9% - latent heat recovery rate: 75.9% - heat energy recovery: 38kW - supply air condition upstream of the unit: -13.00°C/90.0% - supply air condition for the unit: 12.50°C/42.2% Technical data for the summer period: - air flow 3510/3340m3/h - sensible heat recovery rate: 74.9% - latent heat recovery rate: 71.1% - heat energy recovery: 10.10kW - supply air condition upstream of the unit: 34.50°C/40.0% - supply air condition for the unit: 28.10°C/54.4% Code: RE06.191
| - Enota pred-grelnika zraka s protizmrzovalno zaščito. - pretok zraka 3510m3/h - grelna moč Qg=20,1kW - temperaturni režim ogrevnega medija 50/40°C - pretok ogrevnega medija 1,75m3/h - padec tlaka na zračni strani 31Pa - temperatura zraka vstop 12,50°C - temperatura zraka izstop 29,50°C - padec tlaka na strani ogr. medija (voda) 10,67kPa - priključka navojna 1" - tlačna stopnja PN16 Oznaka: HE06.103 | - Air preheater unit with anti-freeze protection. - air flow 3510m3/h - heating power Qg=20,1kW - heating medium temperature 50/40°C - heating medium flow 1,75m3/h - 31Pa pressure drop on the air side - air temperature inlet 12,50°C - air temperature outlet 29,50°C - pressure drop on the heating medium side (water) 10,67kPa - 1" threaded connectors - pressure rating PN16 Code: HE06.103
| - Vlažilna enota s kontaktnim vlaženjem zraka. Dovod sveže pripravljene demineralizirane vode, z materialom kontaktnega vlažilnika impregniranim srebrom, črpalko, potrebno merilno regulacijsko opremo, ventili na dovodu sveže vode ter ventilom na odvodu vode iz banje, s funkcijo samodejnega praznjenja banje vlažilnika in polnjenja s svežo pripravljeno mehčano vodo glede na prevodnost vode v banji, oziroma glede na čas ko vlažilnik ni v funkciji. Odvod kondenzata s sifonom z vodno in mehansko smardno zaporo. - pretok zraka 3510m3/h - priključna električna moč 0,05kW, 230V, 50Hz - padec tlaka na zračni strani dpz=90Pa - temperatura zraka vstop 29,5°C - relativna vlaga zraka vstop 15% - temperatura zraka izstop 27,27°C - relativna vlaga izstop 21% - izkoristek vlaženja 14,21% - vlaženje 7,2 kg/h - tipalo prevodonsti vode QICCD06.105 - tipalo zgornjega nivoja vode LICH06.105 - tipalo spodnjega nivoja vode LICL06.105 - elektromagnetni ventil za praznenje VD06.105 - elektromagnetni ventil za dovod sveže vode VD06.205 Oznaka: SH06.105 | - Humidification unit with contact humidification. Freshly prepared demineralised water supply, with silver-impregnated contact humidifier material, pump, necessary metering control equipment, valves at the fresh water inlet and at the water outlet of the humidifier tank, with automatic emptying of the humidifier tank and refilling with freshly prepared softened water according to the conductivity of the water in the tank, or according to the time when the humidifier is not in operation. Condensate drainage with siphon with water and mechanical odour trap. - air flow 3510m3/h - connection power 0,05kW, 230V, 50Hz - pressure drop on the air side dpz=90Pa - air temperature 29,5°C - relative humidity 15% - air temperature outlet 27,27°C - relative humidity 21% exit - humidification efficiency 14.21% - humidification 7,2 kg/h - water conductivity sensor QICCD06.105 - upper water level sensor LICH06.105 - lower water level sensor LICL06.105 - solenoid valve for emptying VD06.105 - fresh water solenoid valve VD06.205 Code: SH06.105
| - Enota hladilnika z eliminatorjem kapljic in koritom za odvod kondenzata. - pretok zraka 3510m3/h - hladilna moč Qhtot=15,1kW - temperaturni režim hladilnega medija 9/14°C - pretok hladilnega medija 2,59m3/h - padec tlaka na zračni strani 43/39Pa - temperatura zraka vstop 28,10°C - temperatura zraka izstop 18,80°C - padec tlaka na strani hl. medija (voda) 22,29kPa - priključka navojna 1" - tlačna stopnja PN16 Oznaka: HE06.106 | - Refrigerator unit with drip eliminator and condensate drain. - air flow 3510m3/h - cooling power Qhtot=15,1kW - cooling medium temperature 9/14°C - coolant flow rate 2,59m3/h - air side pressure drop 43/39Pa - air temperature inlet 28,10°C - air temperature outlet 18,80°C - pressure drop on the medium side (water) 22,29kPa - 1" threaded connectors - pressure rating PN16 Code: HE06.106
| - Ventilatorska enota s prostotekočim rotorjem. Elektromotor je EC-motor, s 100% zvezno regulacijo vrtljajev preko potenciometra (0-10V), ki omogoča nastavitev delovanja ventilatorja na ustrezno delovno točko. Enota vsebuje: okence O150 in svetilko s stikalom ter servisno stikalo. - pretok zraka 3510m3/h - eksterni statični padec tlaka dpext=300Pa - priključna električna moč 2,4kW, 3x400V, 50Hz - razred izkoristka elektromotorja IE5/EC - zaščita IP55 Oznaka: FA06.107 | - Fan unit with free-flowing rotor. The electric motor is an EC motor, with 100% continuous speed control via a potentiometer (0-10V), which allows the fan to be set to the appropriate operating point. The unit contains: an O150 window and a lamp with switch and a service switch. - air flow 3510m3/h - external static pressure drop dpext=300Pa - connection power 2,4kW, 3x400V, 50Hz - electric motor efficiency class IE5/EC - iP55 protection Code: FA06.107
| - Dušilna enota. - pretok zraka 3510m3/h - padec tlaka dp=10Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 7 17 18 21 15 11 12 Oznaka: DZ06.108 | - Throttle unit. - air flow 3510m3/h - pressure drop dp=10Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 7 17 18 21 15 11 12 Code: DZ06.108
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 1 75% po ISO 16890 (F8 po SIST EN 779, s fleksibilnim čelnim priključkom, za pretok zraka 3510m3/h. Maksimalni končni padec tlaka 300Pa. Oznaka: F06.109 | - Filter unit with bag filter cartridge of filtration level ePM 1 75% according to ISO 16890 (F8 according to SIST EN 779, with flexible front connection, for air flow of 3510m3/h. Maximum final pressure drop 300Pa. Code: F06.109
| Dolžina: 5,640m | Length: 5,640m
| Širina: 1,060m | Width: 1,060m
| Višina: 0,875m | Height: 0,875m
| Kompletno z dobavo dodatne opreme: | Complete with supply of accessories:
| - odtočni sifoni | - drain traps
| - jadrovinasti nastavki | - sailplane spouts
| - s spojnim, tesnilnim in pritrdilnim materialom in priključki za senzorje, | - with jointing, sealing and fixing materials and sensor connectors,
| Odvod: Vodv = 3340 m3/h | Discharge: waterv = 3340 m3/h
| - posluževanje odvod: levo v smeri toka zraka! | - serving outlet: left in the direction of the air flow!
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 10 60% po ISO 16890 (M5 po SIST EN 779), s fleksibilnim čelnim priključkom, za pretok zraka 3340m3/h. Maksimalni končni padec tlaka 200Pa. Oznaka: F06.207 | - Filter unit with bag filter cartridge of filtration level ePM 10 60% according to ISO 16890 (M5 according to SIST EN 779), with flexible front connection, for an air flow of 3340m3/h. Maximum final pressure drop 200Pa. Code: F06.207
| - Dušilna enota. - pretok zraka 3340m3/h - padec tlaka dp=10Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 7 17 18 21 15 11 12 Oznaka: DZ06.206 | - Throttle unit. - air flow 3340m3/h - pressure drop dp=10Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 7 17 18 21 15 11 12 Code: DZ06.206
| - Ventilatorska enota s prostotekočim rotorjem. Elektromotor je EC-motor, s 100% zvezno regulacijo vrtljajev preko potenciometra (0-10V), ki omogoča nastavitev delovanja ventilatorja na ustrezno delovno točko. Enota vsebuje: okence O150 in svetilko s stikalom ter servisno stikalo. - pretok zraka 3340m3/h - eksterni statični padec tlaka dpext=300Pa - priključna električna moč 1.3kW, 230V, 50Hz - razred izkoristka elektromotorja IE5/EC - zaščita IP55 Oznaka: FA06.205 | - Fan unit with free-flowing rotor. The electric motor is an EC motor, with 100% continuous speed control via a potentiometer (0-10V), which allows the fan to be set to the appropriate operating point. The unit contains: an O150 window and a lamp with switch and a service switch. - air flow 3340m3/h - external static pressure drop dpext=300Pa - connection power 1.3kW, 230V, 50Hz - electric motor efficiency class IE5/EC - iP55 protection Code: FA06.205
| - Dušilna enota. - pretok zraka 3340m3/h - padec tlaka dp=16Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 7 17 18 21 15 11 12 Oznaka: DZ06.204 | - Throttle unit. - air flow 3340m3/h - pressure drop dp=16Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 7 17 18 21 15 11 12 Code: DZ06.204
| - Prazna enota z regulacijsko žaluzijo 923x638x125, fleksibilnim čelnim priključkom, za pretok zraka 3340m3/h. | - Empty unit with control louvre 923x638x125, flexible front connection, for air flow 3340m3/h.
| Dolžina: 4,020m | Length: 4,020m
| Širina: 1,060m | Width: 1,060m
| Višina: 0,750m | Height: 0,750m
| Kompletno z dobavo dodatne opreme: | Complete with supply of accessories:
| - postavitvene noge, gumirane, višine 100-200mm | - rubberised feet, height 100-200mm
| - odtočni sifoni | - drain traps
| - jadrovinasti nastavki | - sailplane spouts
| - postavitev klimata na antivibracijski dušilnik (gumo) za preprečevanje prenosa vibracij in hrupa na konstrukcijo objekta. Dušilniki morajo biti preračunani glede na lastnosti klimata (teža in vrtilna frekvenca ventilatorjev). | - installation of the air conditioner on an anti-vibration damper (rubber) to prevent the transmission of vibrations and noise to the structure of the building. The dampers must be calculated according to the characteristics of the air conditioner (weight and speed of the fans).
| - s spojnim, tesnilnim in pritrdilnim materialom in priključki za senzorje, | - with jointing, sealing and fixing materials and sensor connectors,
| Teža: 1.404kg | Weight: 1.404kg
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR | - SYSTEMAIR | kpl | 1 |  | 0
6.2 | Okrogli prezračevalni kanali izdelani iz pocinkane pločevine po SIST EN 1506, vključno z revizijskimi odprtinami, oblikovnimi kosi, debeline po standardu. V ceni na enoto (m) je potrebno upoštevati ves spojni in pritrdilni material (prirobnice, odrez, spone, vijaki, tesnila, ojačitve, vključno z obešalnim in pritrdilnim materialom sistemskega proizvajalca z lastnostmi odgovarjajoč zahtevam SIST EN 12236: 2002, vključno pleskanje vseh kovinskih korozijsko nezaščitenih delov, po temeljitem predhodnem čiščenju do kovinskega sijaja. Antikorozijska zaščita se izvaja v skladu z EN 12944 za naslednje pogoje: • Življenjska doba več kot 15 let. • Stopnja korozijske atmosfere C4 (visoka). | Round ventilation ducts made of galvanised sheet metal according to SIST EN 1506, including inspection openings, shaped pieces, thickness according to the standard. The unit price (m) must take into account all joining and fixing material (flanges, cut-offs, clamps, bolts, gaskets, reinforcements, including hanging and fixing material of the system manufacturer with properties according to the requirements of SIST EN 12236: 2002, including painting of all metal corrosion-protected parts, after thorough cleaning to a metallic gloss. The corrosion protection shall be carried out in accordance with EN12944, for the following conditions: - Lifetime over 15 years. - Corrosive atmosphere C4 (high).
| - Okrogli prezračevalni kanali Ø200 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø200 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 35 |  | 0
| - Okrogli prezračevalni kanali Ø250 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø250 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 30 |  | 0
| - Okrogli prezračevalni kanali Ø280 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø280 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 20 |  | 0
| - Okrogli prezračevalni kanali Ø300 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø300 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 8 |  | 0
| - Okrogli prezračevalni kanali Ø355 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø355 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 55 |  | 0
| - Okrogli prezračevalni kanali Ø400 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø400 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 12 |  | 0
6.3 | Okrogli pregibni kanali za priključitev stropnih difuzorjev, izdelani iz Al folije ter polnila iz materiala z dušilnim in toplotno-izolativnim efektom. V ceni na enoto (m) je potrebno upoštevati ves spojni material, pritrdilne objemke in tesnilni material, za podatke: | Round folded ducts for the connection of ceiling diffusers, made of Al foil and filling material with damping and thermal insulation effect. The unit price (m) must include all joining material, fixing clamps and sealing material, for details:
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DEC tip: SONODEC - 25 | - DEC tip: SUNDAY - 25
| - Okroglegi pregibni kanali Ø200 | - Ø200 round flexible ducts | m | 15 |  | 0
| - Okroglegi pregibni kanali Ø250 | - Round flexible ducts Ø250 | m | 15 |  | 0
6.4 | Pravokotni prezračevalni kanali izdelani iz pocinkane pločevine po SIST EN 1505:1999, debeline po DIN 24190, klase tesnosti B po SIST EN 1507:2006, vključno z revizijskimi odprtinami, oblikovnimi kosi. V ceni na enoto (m2) je potrebno upoštevati ves spojni in pritrdilni material (prirobnice, odrez, spone, vijaki, tesnila, usmerjevalniki, ojačitve, vključno z obešalnim in pritrdilnim materialom sistemskega proizvajalca z lastnostmi odgovarjajoč zahtevam SIST EN 12236: 2002, vključno pleskanje vseh kovinskih korozijsko nezaščitenih delov, po temeljitem predhodnem čiščenju do kovinskega sijaja. Antikorozijska zaščita se izvaja v skladu z EN 12944 za naslednje pogoje: • Življenjska doba več kot 15 let. • Stopnja korozijske atmosfere C4 (visoka). | Rectangular ventilation ducts made of galvanised sheet metal according to SIST EN 1505:1999, thickness according to DIN 24190, tightness class B according to SIST EN 1507:2006, including inspection openings, shaped pieces. The unit price (m2) must take into account all joining and fixing material (flanges, cut-off, clamps, bolts, gaskets, guides, reinforcements, including hanging and fixing material of the system manufacturer with properties according to the requirements of SIST EN 12236:2002, including the painting of all metal corrosion-protected parts, after thorough preliminary cleaning to a metallic gloss. The anticorrosive protection shall be performed in accordance with EN12944 for the following conditions: - Lifetime over 15 years. - Corrosive atmosphere C4 (high). | m2 | 205 |  | 0
6.5 | Toplotna izolacija zajemnih, izpušnih ter vtočnih kanalov s parozapornimi ploščami izdelanimi iz sintetičnega kavčuka z zaprto celično strukturo, toplotne prevodnosti manjše ali enake 0,033W/mK pri srednji temperaturi 0 °C, koeficient upora difuziji vodene pare večji ali enak 10000 testirano v skladu z EN 13469 za cevi in EN 12086 za plošče, požarna klasifikacija B/BL-s3,d0 po DIN 4102, oziroma po SIST EN 13501-1. | Thermal insulation of intake, exhaust and inlet ducts with vapour control panels made of synthetic rubber with closed cell structure, thermal conductivity less than or equal to 0,033 W/mK at a mean temperature of 0 °C, resistance coefficient to diffusion of water vapour greater than or equal to 10000 tested in accordance with EN 13469 for pipes and EN 12086 for panels, fire classification B/BL-s3,d0 according to DIN 4102, or according to SIST EN 13501-1.
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - ARMACELL tip: Armaflex AF | - ARMACELL tip: Armaflex AF
| Toplotna izolacija zajemnih kanalov na vtočni strani (ZUZ-ODA), debeline s = 50 mm, + original lepilo | Thermal insulation of the inlet side of the intake ducts (ZUZ-ODA), thickness s = 50 mm, + original adhesive | m2 | 5 |  | 0
| Toplotna izolacija notranjih kanalov na vtočni strani (VTZ-SUP), debeline s = 19 mm, + original lepilo | Thermal insulation of internal ducts on the inlet side (VTZ-SUP), thickness s = 19 mm, + original adhesive | m2 | 220 |  | 0
| Toplotna izolacija izpušnih kanalov (ZAZ-EHA), debeline s = 19 mm, + original lepilo | Exhaust duct thermal insulation (ZAZ-EHA), thickness s = 19 mm, + original adhesive | m2 | 55 |  | 0
6.6 | Kanalski dušilnik, za preprečevajne prenosa zvoka med prostori, izdelan iz pocinkane pločevine, mineralne volne za dušenje zvoka z zaščito pred erozijo s steklenimi vlakni 70Kg/m3 požarne odpornost M0, vključno z vsem potrebnim pritrdilnim, povezovalnim, tesnilnim in montažnim materialom, tipa: | Duct silencer, to prevent sound transmission between rooms, made of galvanised sheet, mineral wool for sound attenuation with glass fibre erosion protection 70Kg/m3 fire resistance M0, including all necessary fixing, connecting, sealing and mounting material, type:
| - dimenzije Ø355/710/70 | - dimensions Ø355/710/70
| - pretok q = 870 m3/h | - flow rate q = 870 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip RSA Ø355/710/70 (F) | - SYSTEMAIR tip RSA Ø355/710/70 (F)
| Oznaka: DZ06.311 | Code: DZ06.311 | kpl | 1 |  | 0
6.7 | Kanalski dušilnik, za preprečevajne prenosa zvoka med prostori, izdelan iz pocinkane pločevine, mineralne volne za dušenje zvoka z zaščito pred erozijo s steklenimi vlakni 70Kg/m3 požarne odpornost M0, vključno z vsem potrebnim pritrdilnim, povezovalnim, tesnilnim in montažnim materialom, tipa: | Duct silencer, to prevent sound transmission between rooms, made of galvanised sheet, mineral wool for sound attenuation with glass fibre erosion protection 70Kg/m3 fire resistance M0, including all necessary fixing, connecting, sealing and mounting material, type:
| - dimenzije Ø355/710/70 | - dimensions Ø355/710/70
| - pretok q = 830 m3/h | - flow rate q = 830 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip RSA Ø355/710/70 (F) | - SYSTEMAIR tip RSA Ø355/710/70 (F)
| Oznaka: DZ06.321 | Code: DZ06.321 | kpl | 1 |  | 0
6.8 | Kanalski dušilnik, za preprečevajne prenosa zvoka med prostori, izdelan iz pocinkane pločevine, mineralne volne za dušenje zvoka debeline 100mm, z zaščito pred erozijo iz netkane tkanine, vključno z vsem potrebnim pritrdilnim, povezovalnim, tesnilnim in montažnim materialom, tipa: | Duct silencer, to prevent the transmission of sound between rooms, made of galvanised sheet, 100mm thick mineral wool for sound attenuation, with non-woven fabric erosion protection, including all necessary fixing, connecting, sealing and mounting material, type:
| - dimenzije Ø250/900/100 | - dimensions Ø250/900/100
| - pretok q = 590 m3/h | - flow rate q = 590 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - LINDAB tip SLGU 250 - 900 -100 | - LINDAB type SLGU 250 - 900 -100
| Oznaka: DZ06.312; DZ06.314 | Code: DZ06.312; DZ06.314 | kpl | 2 |  | 0
6.9 | Kanalski dušilnik, za preprečevajne prenosa zvoka med prostori, izdelan iz pocinkane pločevine, mineralne volne za dušenje zvoka debeline 100mm, z zaščito pred erozijo iz netkane tkanine, vključno z vsem potrebnim pritrdilnim, povezovalnim, tesnilnim in montažnim materialom, tipa: | Duct silencer, to prevent the transmission of sound between rooms, made of galvanised sheet, 100mm thick mineral wool for sound attenuation, with non-woven fabric erosion protection, including all necessary fixing, connecting, sealing and mounting material, type:
| - dimenzije Ø250/900/100 | - dimensions Ø250/900/100
| - pretok q = 560 m3/h | - flow rate q = 560 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - LINDAB tip SLGU 250 - 900 -100 | - LINDAB type SLGU 250 - 900 -100
| Oznaka: DZ06.322; DZ06.324 | Code: DZ06.322; DZ06.324 | kpl | 2 |  | 0
6.10 | Kanalski dušilnik, za preprečevajne prenosa zvoka med prostori, izdelan iz pocinkane pločevine, mineralne volne za dušenje zvoka z zaščito pred erozijo s steklenimi vlakni 70Kf/m3 požarne odpornost M0, vključno z vsem potrebnim pritrdilnim, povezovalnim, tesnilnim in montažnim materialom, tipa: | Duct silencer, to prevent the transmission of sound between rooms, made of galvanised sheet, mineral wool for sound attenuation with glass fibre erosion protection 70Kf/m3 fire resistance M0, including all necessary fixing, connecting, sealing and mounting material, type:
| - dimenzije Ø355/710/70 | - dimensions Ø355/710/70
| - pretok q = 1180 m3/h | - flow rate q = 1180 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip RSA Ø355/710/70 (F) | - SYSTEMAIR tip RSA Ø355/710/70 (F)
| Oznaka: DZ06.313 | Code: DZ06.313 | kpl | 1 |  | 0
6.11 | Kanalski dušilnik, za preprečevajne prenosa zvoka med prostori, izdelan iz pocinkane pločevine, mineralne volne za dušenje zvoka z zaščito pred erozijo s steklenimi vlakni 70Kf/m3 požarne odpornost M0, vključno z vsem potrebnim pritrdilnim, povezovalnim, tesnilnim in montažnim materialom, tipa: | Duct silencer, to prevent the transmission of sound between rooms, made of galvanised sheet, mineral wool for sound attenuation with glass fibre erosion protection 70Kf/m3 fire resistance M0, including all necessary fixing, connecting, sealing and mounting material, type:
| - dimenzije Ø355/710/70 | - dimensions Ø355/710/70
| - pretok q = 1120 m3/h | - flow rate q = 1120 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip RSA Ø355/710/70 (F) | - SYSTEMAIR tip RSA Ø355/710/70 (F)
| Oznaka: DZ06.323 | Code: DZ06.323 | kpl | 1 |  | 0
6.12 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, sound and heat insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to customer's or architect's preference, with connection chamber, with control damper, with connections for air flow measurement, inlet connection of the prepared air is provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø608, H=332, Ø250 | - dimensions Ø608, H=332, Ø250
| - pretok q = 290 m3/h | - flow rate q = 290 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-C-250 | - SYSTEMAIR tip CAP-C-250
| Oznaka: / | Tag: / | kpl | 6 |  | 0
6.13 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, sound and heat insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to customer's or architect's preference, with connection chamber, with control damper, with connections for air flow measurement, inlet connection of the prepared air is provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø608, H=332, Ø250 | - dimensions Ø608, H=332, Ø250
| - pretok q = 295 m3/h | - flow rate q = 295 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-C-250 | - SYSTEMAIR tip CAP-C-250
| Oznaka: / | Tag: / | kpl | 6 |  | 0
6.14 | Stropni difuzor za odvod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno izolirano, maska je s fiksnimi lamelami, barve (RAL 9010) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, priključek odvoda zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for exhaust air, housing made of galvanised sheet steel, soundproofed, mask with fixed louvres, colour (RAL 9010) or in the colour of the client's or architect's choice, with connection chamber, with control damper, exhaust air connection provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø470, H=290, Ø200 | - dimensions Ø470, H=290, Ø200
| - pretok q = 280/275 m3/h | - flow rate q = 280/275 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip VVKN-A-R-500 | - SYSTEMAIR type VVKN-A-R-500
| Oznaka: / | Tag: / | kpl | 12 |  | 0
6.15 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study with fastening and sealing material type:
| - dimenzije B=450/H=450 | - dimensions B=450/H=450
| - pretok q = 3510 m3/h | - flow rate q = 3510 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-450x450 | - SYSTEMAIR tip FDS-3G-450x450
| Oznaka: KFD06.301 | Code: KFD06.301 | kpl | 1 |  | 0
6.16 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study with fastening and sealing material type:
| - dimenzije Ø355 | - dimensions Ø355
| - pretok q = 870 m3/h | - flow rate q = 870 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-355 | - SYSTEMAIR tip FDR-3G-355
| Oznaka: KFD06.302; KFD06.303 | Code: KFD06.302; KFD06.303 | kpl | 2 |  | 0
6.17 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study with fastening and sealing material type:
| - dimenzije Ø280 | - ø280 dimensions
| - pretok q = 590 m3/h | - flow rate q = 590 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-280 | - SYSTEMAIR tip FDR-3G-280
| Oznaka: KFD06.304 | Code: KFD06.304 | kpl | 1 |  | 0
6.18 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study with fastening and sealing material type:
| - dimenzije Ø355 | - dimensions Ø355
| - pretok q = 1180 m3/h | - flow rate q = 1180 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-355 | - SYSTEMAIR tip FDR-3G-355
| Oznaka: KFD06.305 | Code: KFD06.305 | kpl | 1 |  | 0
6.19 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study with fastening and sealing material type:
| - dimenzije B=450/H=450 | - dimensions B=450/H=450
| - pretok q = 3340 m3/h | - flow rate q = 3340 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-450x450 | - SYSTEMAIR tip FDS-3G-450x450
| Oznaka: KFD06.401 | Code: KFD06.401 | kpl | 1 |  | 0
6.20 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study with fastening and sealing material type:
| - dimenzije Ø355 | - dimensions Ø355
| - pretok q = 830 m3/h | - flow rate q = 830 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-355 | - SYSTEMAIR tip FDR-3G-355
| Oznaka: KFD06.402; KFD06.403 | Code: KFD06.402; KFD06.403 | kpl | 2 |  | 0
6.21 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije Ø280 | - ø280 dimensions
| - pretok q = 560 m3/h | - flow rate q = 560 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-280 | - SYSTEMAIR tip FDR-3G-280
| Oznaka: KFD06.404 | Code: KFD06.404 | kpl | 1 |  | 0
6.22 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study with fastening and sealing material type:
| - dimenzije Ø355 | - dimensions Ø355
| - pretok q = 1120 m3/h | - flow rate q = 1120 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-355 | - SYSTEMAIR tip FDR-3G-355
| Oznaka: KFD06.405 | Code: KFD06.405 | kpl | 1 |  | 0
6.23 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø250 | - dimensions Ø250
| - pretok q = 870 do 300m3/h | - flow rate q = 870 to 300m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-250 | - SYSTEMAIR tip OPTIMA-LV-RI-250
| Oznaka: VAV06.101; VAV06.102 | Code: VAV06.101; VAV06.102 | kpl | 2 |  | 0
6.24 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø200 | - ø200 dimensions
| - pretok q = 590 do 200m3/h | - flow rate q = 590 to 200m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-200 | - SYSTEMAIR tip OPTIMA-LV-RI-200
| Oznaka: VAV06.103; VAV06.104; VAV06.105 | Code: VAV06.103; VAV06.104; VAV06.105 | kpl | 3 |  | 0
6.25 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø225 | - dimensions Ø225
| - pretok q = 830 do 290m3/h | - flow rate q = 830 to 290m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-RI-FC-225 | - SYSTEMAIR tip OPTIMA-RI-FC-225
| Oznaka: VAV06.201; VAV06.202 | Code: VAV06.201; VAV06.202 | kpl | 2 |  | 0
6.26 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø200 | - ø200 dimensions
| - pretok q = 560 do 190m3/h | - flow rate q = 560 to 190m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-200 | - SYSTEMAIR tip OPTIMA-LV-RI-200
| Oznaka: VAV06.203; VAV06.204; VAV06.205 | Code: VAV06.203; VAV06.204; VAV06.205 | kpl | 3 |  | 0
6.27 | Elektromotorni pogon z vzmetjo za vstopno/izstopno žaluzijo klimata, vključno z varnostno funkcijo (NC) in stikali položaja, s pritrdilnim in tesnilnim materialom tipa: | Electric motor drive with spring for air-conditioning entry/exit blind, including safety function (NC) and position switches, with fixing and sealing material type:
| - navor 10Nm | - torque 10Nm
| - električno napajanje 24V AC/DC | - 24V AC/DC power supply
| - ON/OFF regulacija delovanja | - ON/OFF operation control
| - za žaluzije do 2m2 | - for blinds up to 2m2
| - zaščita IP54 | - iP54 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip NF24A-S2 | - BELIMO type NF24A-S2
| Oznaka: KD06.101; KD06.202 | Code: KD06.101; KD06.202 | kpl | 2 |  | 0
6.28 | Kanalsko tipalo diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Duct differential pressure sensor, with type fastening and sealing material:
| - območje prikazovanja od 0 do 1500 Pa | - display range 0 to 1500 Pa
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22ADP-184A | - BELIMO type 22ADP-184A
| Oznaka: PICAL06.112; PICAL06.212 | Code: PICAL06.112; PICAL06.212 | kpl | 2 |  | 0
6.29 | Tipalo diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure sensor, with mounting and sealing material type:
| - območje prikazovanja od 0 do 1500 Pa | - display range 0 to 1500 Pa
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22ADP-184A | - BELIMO type 22ADP-184A
| Oznaka: PDIC06.107; PDIC06.205 | Code: PDIC06.107; PDIC06.205 | kpl | 2 |  | 0
6.30 | Diferenčno tlačno stikalo, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure switch, with type fastening and sealing material:
| - območje prikazovanja od 50 do 500Pa | - display range 50 to 500Pa
| - kontaktni tok maksimalno 1,0A / AC 250V | - contact current max 1.0A / AC 250V
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 01APS-10U | - BELIMO type 01APS-10U
| Oznaka: PDSAH06.102; PDSAH06.109; PDSAH06.203; PDSAH06.207 | Code: PDSAH06.102; PDSAH06.109; PDSAH06.203; PDSAH06.207 | kpl | 4 |  | 0
6.31 | Prikazovalnik diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure indicator, with type fixing and sealing material:
| - območje prikazovanja od 50 do 500Pa | - display range 50 to 500Pa
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DWYER tip Magnahelic | - DWYER tip Magnahelic
| Oznaka: PDI06.102; PDI06.109; PDI06.203; PDI06.207 | Code: PDI06.102; PDI06.109; PDI06.203; PDI06.207 | kpl | 4 |  | 0
6.32 | Zunanje tipalo temperature in vlage, s pritrdilnim in tesnilnim materialom tipa: | External temperature and humidity sensor, with fixing and sealing material type:
| - območje prikazovanja od 0 do 100%RH | - display range 0 to 100%RH
| - območje prikazovanja od -40 do 60°C | - display range -40 to 60°C
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22UTH-13M | - BELIMO type 22UTH-13M
| Oznaka: TIC/MIC06.100 | Code: TIC/MIC06.100 | kpl | 1 |  | 0
6.33 | Kanalsko tipalo temperature in vlage, s pritrdilnim in tesnilnim materialom tipa: | Duct temperature and humidity sensor, with fixing and sealing material type:
| - območje prikazovanja od 0 do 100%RH | - display range 0 to 100%RH
| - območje prikazovanja od -40 do 60°C | - display range -40 to 60°C
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22DTH-13M | - BELIMO type 22DTH-13M
| Oznaka: TIC/MIC06.110; TIC/MIC06.208 | Code: TIC/MIC06.110; TIC/MIC06.208 | kpl | 2 |  | 0
6.34 | Prostorsko tipalo kvalitete zraka CO2, s pritrdilnim in tesnilnim materialom tipa: | Room air quality sensor CO2, with fixing and sealing material type:
| - območje CO2 od 0 do 2000ppm | - cO2 range 0 to 2000ppm
| - izhodni signal 0 do 10V | - output signal 0 to 10V
| - izhodni signal MP-Bus | - mP-Bus output signal
| - zaščita IP30 | - iP30 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22RTM-19-1 | - BELIMO type 22RTM-19-1
| Oznaka: QIC06.501; QIC06.502; QIC06.503; QIC06.504; QIC06.505 | Code: QIC06.501; QIC06.502; QIC06.503; QIC06.504; QIC06.505 | kpl | 5 |  | 0
6.35 | Protizmrzovalni termostat, s pritrdilnim in tesnilnim materialom tipa: | Anti-freezing thermostat, with fixing and sealing material type:
| - območje od -10 do 15°C | - range -10 to 15°C
| - dolžina kapilare 6m | - capillary length 6m
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 01ATS-105XC | - BELIMO type 01ATS-105XC
| Oznaka: TSZAL06.104 | Code: TSZAL06.104 | kpl | 1 |  | 0
6.36 | Obtočna črpalka, elektronsko regulirana s frekvenčnim pretvornikom, tipalom diferenčnega tlaka, internimi hidravličnimi, električnimi in komunikacijskimi povezavami, PN10, material jeklena litina, skladnost z ErP, pritrdilnim in tesnilnim materialom tipa: | Circulation pump, electronically controlled with frequency converter, differential pressure sensor, internal hydraulic, electrical and communication connections, PN10, material cast steel, ErP compliant, type fastening and sealing material:
| - za obtok ogrevne vode 50/40°C | - for circulating heating water 50/40°C
| - za pretok V = 1,75m3/h, tlačna višina H = 1,8m | - for flow rate V = 1,75m3/h, pressure head H = 1,8m
| - možnost izbire delovanja črpalke na proporcionalni tlak ter optimizacijo delovne obratovalne točke | - option to select proportional pressure pump operation and optimise the operating point
| - napajanje Pel = 0,050kW, 230V / 50Hz | - power supply Pel = 0,050kW, 230V/50Hz
| - navojni priključek G 1 1/2 | - threaded connection G 1 1/2
| - tlačna stopnja PN10 | - pressure rating PN10
| - temperaturno območje ogrevnega medija od -10 do 110°C | - temperature range of the heating medium from -10 to 110°C
| - komunikacija s CNS RS485 | - communication with CNS RS485
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - GRUNDFOS tip MAGNA3 25-40 | - GRUNDFOS type MAGNA3 25-40
| Oznaka: P06.103 | Code: P06.103 | kpl | 1 |  | 0
6.37 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za ogrevno vodo 50/40°C | - for heating water 50/40°C
| - za pretok V = 1,75m3/h | - for a flow rate of V = 1,75m3/h
| - območje regulacije pretoka do 3200 l/h (3,20 m3/h) | - flow control range up to 3200 l/h (3.20 m3/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - navojni priključek G 1 1/2 po ISO 228/1 | - threaded connection G 1 1/2 according to ISO 228/1
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 20 - 400 kPa, min. dif. tlak 20 kPa | - differential pressure range 20 - 400 kPa, min. differential pressure 20 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM32 | - DANFOS type AB-QM32
| Oznaka: VA06.103 | Code: VA06.103 | kpl | 1 |  | 0
6.38 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za hladilno vodo 9/14°C | - for cooling water 9/14°C
| - za pretok V = 2,59m3/h | - for a flow rate of V = 2,59m3/h
| - območje regulacije pretoka do 3200 l/h (3,20 m3/h) | - flow control range up to 3200 l/h (3.20 m3/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - navojni priključek G 1 1/2 po ISO 228/1 | - threaded connection G 1 1/2 according to ISO 228/1
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 20 - 400 kPa, min. dif. tlak 20 kPa | - differential pressure range 20 - 400 kPa, min. differential pressure 20 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM32 | - DANFOS type AB-QM32
| Oznaka: VA06.106 | Code: VA06.106 | kpl | 1 |  | 0
| PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS06 | VENTILATION AND AIR CONDITIONING SYSTEM KS06 |  |  |  | 0

## 4.4.7_PrKlim KS07
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.4 | STROJNA DELA | MECHANICAL WORKS
4.4.7 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS07 | VENTILATION AND AIR CONDITIONING SYSTEM KS07 |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
7 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS07 | VENTILATION AND AIR CONDITIONING SYSTEM KS07
7.1 | Klimatska naprava za dovod in odvod zraka KD07/KO07 - glej tudi zavihek Zahteve klimati. | KD07/KO07 supply and extract air conditioner - see also Climate requirements tab.
| Tehnične karakteristike naprave (opis v smeri toka zraka): | Technical characteristics of the device (description downstream):
| Dovod: Vdov = 4400 m3/h | Inlet: Vdov = 4400 m3/h
| - posluževanje dovod: levo v smeri toka zraka! | - inlet: left in the direction of the air flow!
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 10 60% po ISO 16890 (M5 po SIST EN 779), s fleksibilnim čelnim priključkom, za pretok zraka 4400m3/h. Maksimalni končni padec tlaka 200Pa. Oznaka: F07.100 | - Filter unit with bag filter cartridge of filtration level ePM 10 60% according to ISO 16890 (M5 according to SIST EN 779), with flexible front connection, for an air flow of 4400m3/h. Maximum final pressure drop 200Pa. Code: F07.100
| - Prazna enota z regulacijskimi žaluzijami 2x 1085x422,5x125 za pretok zraka 4400m3/h. | - Empty unit with 2x 1085x422,5x125 control louvers for air flow 4400m3/h.
| - Prazna enota z AMS merilno mrežo STRA-R950X450MM vgrajeno v zgornji del enote, pred rototermom. | - Empty unit with STRA-R950X450MM AMS measuring grid mounted in the upper part of the unit, in front of the rototherm.
| - Rotacijska regeneratorska enota za prenos senzibilne in latentne toplote, z ON/OFF žaluzijami obtoka zraka 2x 1180x210x125. Tehnični podatki za zimsko obdobje: - pretok zraka 4400/4190m3/h - stopnja vračanja občutene toplote: 74,2% - stopnja vračanja latentne toplote: 75,1% - vračanje toplotne energije: 51,90kW - stanje dovodnega zr. pred enoto: -13,00°C/90,0% - stanje dovodnega zraka za enoto: 13,00°C/49,50% Tehnični podatki za poletno obdobje: - pretok zraka 4400/4190m3/h - stopnja vračanja občutene toplote: 74,2% - stopnja vračanja latentne toplote: 71,2% - vračanje toplotne energije: 20,10kW - stanje dovodnega zr. pred enoto: 34,50°C/40,0% - stanje dovodnega zraka za enoto: 28,20°C/45,9% Oznaka: RE07.191 | - Rotary regenerative unit for sensible and latent heat transfer, with ON/OFF airflow shutters 2x 1180x210x125. technical data for the winter period: - air flow 4400/4190m3/h - sensible heat recovery rate: 74.2% - latent heat recovery rate: 75.1% - heat energy recovery: 51.90kW - supply air condition upstream of the unit: -13.00°C/90.0% - supply air condition for the unit: 13.00°C/49.50% Technical data for the summer period: - air flow 4400/4190m3/h - sensible heat recovery rate: 74.2% - latent heat recovery rate: 71.2% - heat energy recovery: 20.10kW - supply air condition upstream of the unit: 34.50°C/40.0% - supply air condition for the unit: 28.20°C/45.9% Code: RE07.191
| - Mešalna enota za mešanje zunajnega in prostorskega zraka, z vgrajenimi mešalnimi cevmi za zagotavljanje ustreznega mešanja zraka, z regulacijsko žaluzijo 1085x210x125. | - Mixing unit for mixing outside and indoor air, with integrated mixing pipes to ensure adequate air mixing, with control louvre 1085x210x125.
| - Enota pred-grelnika zraka s protizmrzovalno zaščito. - pretok zraka 4400m3/h - grelna moč Qg=8,3kW - temperaturni režim ogrevnega medija 50/40°C - pretok ogrevnega medija 0,72m3/h - padec tlaka na zračni strani 3Pa - temperatura zraka vstop 16,60°C - temperatura zraka izstop 22,10°C - padec tlaka na strani ogr. medija (voda) 4,53kPa - priključka navojna 3/4" - tlačna stopnja PN16 Oznaka: HE07.106 | - Air preheater unit with anti-freeze protection. - air flow 4400m3/h - heating power Qg=8,3kW - heating medium temperature 50/40°C - heating medium flow rate 0,72m3/h - air side pressure drop 3Pa - air inlet temperature 16,60°C - air temperature outlet 22,10°C - pressure drop on the heating medium side (water) 4.53kPa - 3/4" threaded connectors - pressure rating PN16 Code: HE07.106
| - Vlažilna enota s kontaktnim vlaženjem zraka. Dovod sveže pripravljene demineralizirane vode, z materialom kontaktnega vlažilnika impregniranim srebrom, črpalko, potrebno merilno regulacijsko opremo, ventili na dovodu sveže vode ter ventilom na odvodu vode iz banje, s funkcijo samodejnega praznjenja banje vlažilnika in polnjenja s svežo pripravljeno mehčano vodo glede na prevodnost vode v banji, oziroma glede na čas ko vlažilnik ni v funkciji. Odvod kondenzata s sifonom z vodno in mehansko smardno zaporo. - pretok zraka 4400m3/h - priključna električna moč 0,06kW, 3x400V, 50Hz - padec tlaka na zračni strani dpz=11Pa - temperatura zraka vstop 22,1°C - relativna vlaga zraka vstop 27,9% - temperatura zraka izstop 21,6°C - relativna vlaga izstop 30% - izkoristek vlaženja 4,84% - vlaženje 2,16 kg/h - tipalo prevodonsti vode QICCD07.108 - tipalo zgornjega nivoja vode LICH07.108 - tipalo spodnjega nivoja vode LICL07.108 - elektromagnetni ventil za praznenje VD07.108 - elektromagnetni ventil za dovod sveže vode VD07.208 Oznaka: SH07.108 | - Humidification unit with contact humidification. Freshly prepared demineralised water supply, with silver-impregnated contact humidifier material, pump, necessary metering control equipment, valves at the fresh water inlet and at the water outlet of the humidifier tank, with automatic emptying of the humidifier tank and refilling with freshly prepared softened water according to the conductivity of the water in the tank, or according to the time when the humidifier is not in operation. Condensate drainage with siphon with water and mechanical odour trap. - air flow 4400m3/h - connection power 0,06kW, 3x400V, 50Hz - pressure drop on the air side dpz=11Pa - air temperature 22,1°C - relative humidity 27.9% - air temperature outlet 21,6°C - relative humidity 30% outlet - humidification efficiency 4.84% - humidification 2,16 kg/h - water conductivity sensor QICCD07.108 - upper water level sensor LICH07.108 - lower water level sensor LICL07.108 - solenoid valve for emptying VD07.108 - fresh water solenoid valve VD07.208 Code: SH07.108
| - Enota hladilnika z eliminatorjem kapljic in koritom za odvod kondenzata. - pretok zraka 4400m3/h - hladilna moč Qhtot=28,2kW - temperaturni režim hladilnega medija 9/14°C - pretok hladilnega medija 4,84 m3/h - padec tlaka na zračni strani 45/40Pa - temperatura zraka vstop 26,80°C - temperatura zraka izstop 14,10°C - padec tlaka na strani hl. medija (voda) 20,02kPa - priključka navojna 1 1/4" - tlačna stopnja PN16 Oznaka: HE07.109 | - Refrigerator unit with drip eliminator and condensate drain. - air flow 4400m3/h - cooling power Qhtot=28,2kW - cooling medium temperature 9/14°C - cooling medium flow rate 4,84 m3/h - 45/40Pa pressure drop on the air side - air temperature inlet 26,80°C - air temperature outlet 14,10°C - pressure drop on the medium side (water) 20,02kPa - 1 1/4" threaded connectors - pressure rating PN16 Code: HE07.109
| - Ventilatorska enota s prostotekočim rotorjem. Elektromotor je EC-motor, s 100% zvezno regulacijo vrtljajev preko potenciometra (0-10V), ki omogoča nastavitev delovanja ventilatorja na ustrezno delovno točko. Enota vsebuje: okence O150 in svetilko s stikalom ter servisno stikalo. - pretok zraka 4400m3/h - eksterni statični padec tlaka dpext=450Pa - priključna električna moč 2,5kW, 3x400V, 50Hz - razred izkoristka elektromotorja IE5/EC - zaščita IP55 Oznaka: FA07.110 | - Fan unit with free-flowing rotor. The electric motor is an EC motor, with 100% continuous speed control via a potentiometer (0-10V), which allows the fan to be set to the appropriate operating point. The unit contains: an O150 window and a lamp with switch and a service switch. - air flow 4400m3/h - external static pressure drop dpext=450Pa - connection power 2,5kW, 3x400V, 50Hz - electric motor efficiency class IE5/EC - iP55 protection Code: FA07.110
| - Enota do-grelnika zraka. - pretok zraka 4400m3/h - grelna moč Qg=10,4kW - temperaturni režim ogrevnega medija 50/40°C - pretok ogrevnega medija 0,90 m3/h - padec tlaka na zračni strani 3Pa - temperatura zraka vstop 14,10°C - temperatura zraka izstop 21°C - padec tlaka na strani ogr. medija (voda) 7,02kPa - priključka navojna 3/4" - tlačna stopnja PN16 Oznaka: HE07.111 | - Do-it-yourself air heater unit. - air flow 4400m3/h - heating power Qg=10,4kW - heating medium temperature 50/40°C - heating medium flow rate 0,90 m3/h - pressure drop on the air side 3Pa - air temperature 14,10°C - air temperature outlet 21°C - pressure drop on the heating medium side (water) 7,02kPa - 3/4" threaded connectors - pressure rating PN16 Code: HE07.111
| - Dušilna enota. - pretok zraka 4400m3/h - padec tlaka dp=1Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 2 6 13 13 13 10 8 8 Oznaka: DZ07.112 | - Throttle unit. - air flow 4400m3/h - pressure drop dp=1Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 2 6 13 13 13 13 10 8 8 8 Code: DZ07.112
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 1 75% po ISO 16890 (F8 po SIST EN 779, s fleksibilnim čelnim priključkom, za pretok zraka 4400m3/h. Maksimalni končni padec tlaka 300Pa. Oznaka: F07.113 | - Filter unit with bag filter cartridge of filtration level ePM 1 75% according to ISO 16890 (F8 according to SIST EN 779, with flexible front connection, for air flow of 4400m3/h. Maximum final pressure drop 300Pa. Code: F07.113
| Dolžina: 8,300m | Length: 8,300m
| Širina: 1,360m | Width: 1,360m
| Višina: 1,180m | Height: 1,180m
| Kompletno z dobavo dodatne opreme: | Complete with supply of accessories:
| - odtočni sifoni | - drain traps
| - jadrovinasti nastavki | - sailplane spouts
| - s spojnim, tesnilnim in pritrdilnim materialom in priključki za senzorje, | - with jointing, sealing and fixing materials and sensor connectors,
| Odvod: Vodv = 4190 m3/h | Discharge: waterv = 4190 m3/h
| - posluževanje odvod: desno v smeri toka zraka! | - serving outlet: right in the direction of the air flow!
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 10 60% po ISO 16890 (M5 po SIST EN 779), s fleksibilnim čelnim priključkom, za pretok zraka 4190m3/h. Maksimalni končni padec tlaka 200Pa. Oznaka: F07.207 | - Filter unit with bag filter cartridge of filtration level ePM 10 60% according to ISO 16890 (M5 according to SIST EN 779), with flexible front connection, for an air flow of 4190m3/h. Maximum final pressure drop 200Pa. Code: F07.207
| - Dušilna enota. - pretok zraka 4190m3/h - padec tlaka dp=1Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 2 6 13 13 13 10 8 8 Oznaka: DZ07.206 | - Throttle unit. - air flow 4190m3/h - pressure drop dp=1Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 2 6 13 13 13 13 10 8 8 8 Code: DZ07.206
| - Ventilatorska enota s prostotekočim rotorjem. Elektromotor je EC-motor, s 100% zvezno regulacijo vrtljajev preko potenciometra (0-10V), ki omogoča nastavitev delovanja ventilatorja na ustrezno delovno točko. Enota vsebuje: okence O150 in svetilko s stikalom ter servisno stikalo. - pretok zraka 4190m3/h - eksterni statični padec tlaka dpext=450Pa - priključna električna moč 2,5kW, 3x400V, 50Hz - razred izkoristka elektromotorja IE5/EC - zaščita IP55 Oznaka: FA07.205 | - Fan unit with free-flowing rotor. The electric motor is an EC motor, with 100% continuous speed control via a potentiometer (0-10V), which allows the fan to be set to the appropriate operating point. The unit contains: an O150 window and a lamp with switch and a service switch. - air flow 4190m3/h - external static pressure drop dpext=450Pa - connection power 2,5kW, 3x400V, 50Hz - electric motor efficiency class IE5/EC - iP55 protection Code: FA07.205
| - Dušilna enota. - pretok zraka 4190m3/h - padec tlaka dp=1Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 2 6 13 13 13 10 8 8 Oznaka: DZ07.204 | - Throttle unit. - air flow 4190m3/h - pressure drop dp=1Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 2 6 13 13 13 13 10 8 8 8 Code: DZ07.204
| - Sesalna tlačna enota z regulacijsko žaluzijo 1228x943x125, fleksibilnim čelnim priključkom, za pretok zraka 4190m3/h. | - Suction pressure unit with control louvre 1228x943x125, flexible front connection, for air flow 4190m3/h.
| Dolžina: 5,220m | Length: 5,220m
| Širina: 1,360m | Width: 1,360m
| Višina: 1,055m | Height: 1,055m
| Kompletno z dobavo dodatne opreme: | Complete with supply of accessories:
| - postavitvene noge, gumirane, višine 100-200mm | - rubberised feet, height 100-200mm
| - odtočni sifoni | - drain traps
| - jadrovinasti nastavki | - sailplane spigots
| - postavitev klimata na antivibracijski dušilnik (gumo) za preprečevanje prenosa vibracij in hrupa na konstrukcijo objekta. Dušilniki morajo biti preračunani glede na lastnosti klimata (teža in vrtilna frekvenca ventilatorjev). | - installation of the air conditioner on an anti-vibration damper (rubber) to prevent the transmission of vibrations and noise to the structure of the building. The dampers must be calculated according to the characteristics of the air conditioner (weight and speed of the fans).
| - s spojnim, tesnilnim in pritrdilnim materialom in priključki za senzorje, | - with jointing, sealing and fixing materials and sensor connectors,
| Teža: 2.465kg | Weight: 2.465kg
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR | - SYSTEMAIR | kpl | 1 |  | 0
7.2 | Zunanja zaščitna rešetka za dovod zraka narejene iz jeklene pocinkane pločevine z zaščitno mrežo, z vgrajenim električnim grelnim kablom z zaščitno funkcijo proti zamrzovanju in termostatom za vklop pri +5 °C, pritrditev z vijaki na vzidan okvir iz jeklenega kotnika, barve v skladu z zahtevam načrta arhitekture, s pritrdilnim in tesnilnim materialom tipa: | External air intake grille made of galvanised sheet steel with protective mesh, with built-in electric heating cable with anti-freeze protection function and thermostat for switching on at +5 °C, bolted to a steel angle frame, colour according to architectural design requirements, with fixing and sealing material type:
| - dimenzije B=920/H=2920 | - dimensions B=920/H=2920
| - dimenzija prosta za pretok zraka B=920/H=1820 | - dimension free for air flow B=920/H=1820
| - H=600mm nad terenom zaprta rešetka z betonsko steno | - H=600mm above ground closed grid with concrete wall
| - H=500mm od vrha rešetke zaprta rešetka z betonsko steno | - H=500mm from top of grille closed grille with concrete wall
| - pretok q = 5390 m3/h | - flow rate q = 5390 m3/h
| - padec tlaka Δp = 3 Pa | - pressure drop Δp = 3 Pa
| - prost prerez Aef=1.323 m2 | - free cross-section Aef=1.323 m2
| - električna moč grelca od 1.88 do 3.77 kW, 3x400 V, 50Hz, na preseku za pretok zraka B=920/H=1820 | - heater electrical power from 1.88 to 3.77 kW, 3x400 V, 50Hz, at air flow cross section B=920/H=1820
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - OC IMP KLIMA tip JZR-6 920x2920 | - OC IMP KLIMA tip JZR-6 920x2920
| Oznaka: ZR07.901 | Code: ZR07.901 | kpl | 1 |  | 0
7.3 | Zunanja zaščitna rešetka za odvod zraka narejena iz jeklene pocinkane pločevine z zaščitno mrežo, pritrditev z vijaki na vzidan okvir iz jeklenega kotnika, barve v skladu z zahtevam načrta arhitekture, s pritrdilnim in tesnilnim materialom tipa: | External air grille made of galvanised sheet steel with protective mesh, bolted to a steel angle angle frame, colour according to the architectural plan, with fixing and sealing material of the type:
| - dimenzije B=920/H=2920 | - dimensions B=920/H=2920
| - dimenzija prosta za pretok zraka B=920/H=1820 | - dimension free for air flow B=920/H=1820
| - H=600mm nad terenom zaprta rešetka z betonsko steno | - H=600mm above ground closed grid with concrete wall
| - H=500mm od vrha rešetke zaprta rešetka z betonsko steno | - H=500mm from top of grille closed grille with concrete wall
| - pretok q = 5125 m3/h | - flow rate q = 5125 m3/h
| - padec tlaka Δp = 3 Pa | - pressure drop Δp = 3 Pa
| - prost prerez Aef=1.323 m2 | - free cross-section Aef=1.323 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - OC IMP KLIMA tip JZR-6 920x2920 | - OC IMP KLIMA tip JZR-6 920x2920
| Oznaka: ZR07.801 | Code: ZR07.801 | kpl | 1 |  | 0
7.4 | Okrogli prezračevalni kanali izdelani iz pocinkane pločevine po SIST EN 1506, vključno z revizijskimi odprtinami, oblikovnimi kosi, debeline po standardu. V ceni na enoto (m) je potrebno upoštevati ves spojni in pritrdilni material (prirobnice, odrez, spone, vijaki, tesnila, ojačitve, vključno z obešalnim in pritrdilnim materialom sistemskega proizvajalca z lastnostmi odgovarjajoč zahtevam SIST EN 12236: 2002, vključno pleskanje vseh kovinskih korozijsko nezaščitenih delov, po temeljitem predhodnem čiščenju do kovinskega sijaja. Antikorozijska zaščita se izvaja v skladu z EN 12944 za naslednje pogoje: • Življenjska doba več kot 15 let. • Stopnja korozijske atmosfere C4 (visoka). | Round ventilation ducts made of galvanised sheet metal according to SIST EN 1506, including inspection openings, shaped pieces, thickness according to the standard. The unit price (m) must take into account all joining and fixing material (flanges, cut-offs, clamps, bolts, gaskets, reinforcements, including hanging and fixing material of the system manufacturer with properties according to the requirements of SIST EN 12236: 2002, including painting of all metal corrosion-protected parts, after thorough cleaning to a metallic gloss. The corrosion protection shall be carried out in accordance with EN12944, for the following conditions: - Lifetime over 15 years. - Corrosive atmosphere C4 (high).
| - Okrogli prezračevalni kanali Ø250 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø250 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 6 |  | 0
| - Okrogli prezračevalni kanali Ø355 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø355 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 3 |  | 0
| - Okrogli prezračevalni kanali Ø400 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø400 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 11 |  | 0
| - Okrogli prezračevalni kanali Ø500 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø500 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 8 |  | 0
7.5 | Okrogli pregibni kanali za priključitev stropnih difuzorjev, izdelani iz Al folije ter polnila iz materiala z dušilnim in toplotno-izolativnim efektom. V ceni na enoto (m) je potrebno upoštevati ves spojni material, pritrdilne objemke in tesnilni material, za podatke: | Round folded ducts for the connection of ceiling diffusers, made of Al foil and filling material with damping and thermal insulation effect. The unit price (m) must include all joining material, fixing clamps and sealing material, for details:
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DEC tip: SONODEC - 25 | - DEC tip: SUNDAY - 25
| - Okroglegi pregibni kanali Ø250 | - Round flexible ducts Ø250 | m | 10 |  | 0
| - Okroglegi pregibni kanali Ø400 | - Ø400 round flexible ducts | m | 10 |  | 0
7.6 | Pravokotni prezračevalni kanali izdelani iz pocinkane pločevine po SIST EN 1505:1999, debeline po DIN 24190, klase tesnosti B po SIST EN 1507:2006, vključno z revizijskimi odprtinami, oblikovnimi kosi. V ceni na enoto (m2) je potrebno upoštevati ves spojni in pritrdilni material (prirobnice, odrez, spone, vijaki, tesnila, usmerjevalniki, ojačitve, vključno z obešalnim in pritrdilnim materialom sistemskega proizvajalca z lastnostmi odgovarjajoč zahtevam SIST EN 12236: 2002, vključno pleskanje vseh kovinskih korozijsko nezaščitenih delov, po temeljitem predhodnem čiščenju do kovinskega sijaja. Antikorozijska zaščita se izvaja v skladu z EN 12944 za naslednje pogoje: • Življenjska doba več kot 15 let. • Stopnja korozijske atmosfere C4 (visoka). | Rectangular ventilation ducts made of galvanised sheet metal according to SIST EN 1505:1999, thickness according to DIN 24190, tightness class B according to SIST EN 1507:2006, including inspection openings, shaped pieces. The unit price (m2) must take into account all joining and fixing material (flanges, cut-off, clamps, bolts, gaskets, guides, reinforcements, including hanging and fixing material from the system manufacturer with properties according to SIST EN 12236:2002, including painting of all metal parts not protected by corrosion, after thorough pre-cleaning to a metallic shine. The anticorrosive protection shall be carried out in accordance with EN12944 for the following conditions: - Lifetime over 15 years. - Corrosive atmosphere C4 (high). | m2 | 190 |  | 0
7.7 | Toplotna izolacija zajemnih, izpušnih ter vtočnih kanalov s parozapornimi ploščami izdelanimi iz sintetičnega kavčuka z zaprto celično strukturo, toplotne prevodnosti manjše ali enake 0,033W/mK pri srednji temperaturi 0 °C, koeficient upora difuziji vodene pare večji ali enak 10000 testirano v skladu z EN 13469 za cevi in EN 12086 za plošče, požarna klasifikacija B/BL-s3,d0 po DIN 4102, oziroma po SIST EN 13501-1. | Thermal insulation of intake, exhaust and inlet ducts with vapour control panels made of synthetic rubber with closed cell structure, thermal conductivity less than or equal to 0,033 W/mK at a mean temperature of 0 °C, resistance coefficient to diffusion of water vapour greater than or equal to 10000 tested in accordance with EN 13469 for pipes and EN 12086 for panels, fire classification B/BL-s3,d0 according to DIN 4102, or according to SIST EN 13501-1.
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - ARMACELL tip: Armaflex AF | - ARMACELL tip: Armaflex AF
| Toplotna izolacija zajemnih kanalov na vtočni strani (ZUZ-ODA), debeline s = 50 mm, + original lepilo | Thermal insulation of the inlet side of the intake ducts (ZUZ-ODA), thickness s = 50 mm, + original adhesive | m2 | 5 |  | 0
| Toplotna izolacija notranjih kanalov na vtočni strani (VTZ-SUP), debeline s = 19 mm, + original lepilo | Thermal insulation of internal ducts on the inlet side (VTZ-SUP), thickness s = 19 mm, + original adhesive | m2 | 80 |  | 0
| Toplotna izolacija izpušnih kanalov (ZAZ-EHA), debeline s = 19 mm, + original lepilo | Exhaust duct insulation (ZAZ-EHA), thickness s = 19 mm, + original adhesive | m2 | 80 |  | 0
7.8 | Rešetka za dovod zraka, izdelana iz aluminijskih profilov, sestavljena iz nosilnega okvirja z vodoravnim in navpičnim fiksnim lamelam, dodatkom za nastavitev količine zraka, pritrditev rešetke na prezračevalni kanal, z ugradim okvirjem, vključno z vsem pritrdilnim in montažnim materialom, barva v skladu z zahtevam načrta arhitekture, tipa: | Air inlet grille made of aluminium profiles, consisting of a support frame with horizontal and vertical fixed slats, air volume adjustment accessory, grille attachment to the ventilation duct, with a framed frame, including all fixing and mounting material, colour in accordance with the requirements of the architectural plan, type:
| - dimenzije B=200/H=100 | - dimensions B=200/H=100
| - pretok q = 150 m3/h | - flow rate q = 150 m3/h
| - prost prerez Aef=0,013 m2 | - free cross-section Aef=0,013 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-E-2-200x100-R1 | - SYSTEMAIR tip NOVA-E-2-200x100-R1
| Oznaka: / | Tag: / | kpl | 1 |  | 0
7.9 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, soundproofed, hood made of panel with polymer nozzles, colour (RAL 9003) or in the colour of the customer's or architect's choice, with connection chamber, with control damper, with connections for air flow measurement, inlet connection of the prepared air is provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø634, H=508, Ø400 | - dimensions Ø634, H=508, Ø400
| - pretok q = 708/709 m3/h | - flow rate q = 708/709 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-C-400 | - SYSTEMAIR tip CAP-C-400
| Oznaka: / | Tag: / | kpl | 6 |  | 0
7.10 | Rešetka za odvod zraka, izdelana iz aluminijskih profilov, sestavljena iz nosilnega okvirja z vodoravnim in navpičnim fiksnim lamelam, dodatkom za nastavitev količine zraka, pritrditev rešetke na prezračevalni kanal, z ugradim okvirjem, vključno z vsem pritrdilnim in montažnim materialom, barva v skladu z zahtevam načrta arhitekture, tipa: | Air outlet grille made of aluminium profiles, consisting of a support frame with horizontal and vertical fixed slats, air volume adjustment accessory, grille attachment to the ventilation duct, with a framed enclosure, including all fixing and mounting material, colour in accordance with the requirements of the architectural plan, type:
| - dimenzije B=200/H=100 | - dimensions B=200/H=100
| - pretok q = 150 m3/h | - flow rate q = 150 m3/h
| - prost prerez Aef=0,013 m2 | - free cross-section Aef=0,013 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-E-2-200x100-R1 | - SYSTEMAIR tip NOVA-E-2-200x100-R1
| Oznaka: / | Tag: / | kpl | 1 |  | 0
7.11 | Stropni difuzor za odvod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno izolirano, maska je s fiksnimi lamelami, barve (RAL 9010) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, priključek odvoda zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for exhaust air, housing made of galvanised sheet steel, soundproofed, mask with fixed louvres, colour (RAL 9010) or in the colour of the client's or architect's choice, with connection chamber, with control damper, exhaust air connection provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø595, H=340, Ø250 | - dimensions Ø595, H=340, Ø250
| - pretok q = 673/674 m3/h | - flow rate q = 673/674 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip VVKN-A-R-625 | - SYSTEMAIR tip VVKN-A-R-625
| Oznaka: / | Tag: / | kpl | 6 |  | 0
7.12 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije B=700/H=500 | - dimensions B=700/H=500
| - pretok q = 4250 m3/h | - flow rate q = 4250 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-700x500 | - SYSTEMAIR tip FDS-3G-700x500
| Oznaka: KFD07.311 | Code: KFD07.311 | kpl | 1 |  | 0
7.13 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije Ø500 | - ø500 dimensions
| - pretok q = 2125 m3/h | - flow rate q = 2125 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-500 | - SYSTEMAIR tip FDR-3G-500
| Oznaka: KFD07.312; KFD07.313 | Code: KFD07.312; KFD07.313 | kpl | 2 |  | 0
7.14 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije B=650/H=400 | - dimensions B=650/H=400
| - pretok q = 4040 m3/h | - flow rate q = 4040 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-650x400 | - SYSTEMAIR tip FDS-650x400
| Oznaka: KFD07.411 | Code: KFD07.411 | kpl | 1 |  | 0
7.15 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo regulacije konstantnega pretoka, s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow regulator, made of galvanised sheet metal with acoustic and thermal insulation, with constant flow control function, with fastening and sealing material type:
| - dimenzije Ø100 | - ø100 dimensions
| - pretok q = 150m3/h | - flow rate q = 150m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOTUS-RI-100-M0 | - SYSTEMAIR tip NOTUS-RI-100-M0
| Oznaka: CAV07.301; CAV07.401 | Code: CAV07.301; CAV07.401 | kpl | 2 |  | 0
7.16 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije 550x300 | - dimensions 550x300
| - pretok q = 4250 do 1280m3/h | - flow rate q = 4250 to 1280m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-SI-FC-550x300 | - SYSTEMAIR tip OPTIMA-SI-FC-550x300
| Oznaka: VAV07.311 | Code: VAV07.311 | kpl | 1 |  | 0
7.17 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije 550x300 | - dimensions 550x300
| - pretok q = 4040 do 1220m3/h | - flow rate q = 4040 to 1220m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-SI-FC-550x300 | - SYSTEMAIR tip OPTIMA-SI-FC-550x300
| Oznaka: VAV07.411 | Code: VAV07.411 | kpl | 1 |  | 0
7.18 | Elektromotorni pogon z vzmetjo za vstopno žaluzijo klimata, vključno z varnostno funkcijo (NC) in stikali položaja, s pritrdilnim in tesnilnim materialom tipa: | Electric motor actuator with spring for air-conditioning inlet shutter, including safety function (NC) and position switches, with fixing and sealing material type:
| - navor 10Nm | - torque 10Nm
| - električno napajanje 24V AC/DC | - 24V AC/DC power supply
| - ON/OFF regulacija delovanja | - ON/OFF operation control
| - za žaluzije do 2m2 | - for blinds up to 2m2
| - zaščita IP54 | - iP54 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip NF24A-S2 | - BELIMO type NF24A-S2
| Oznaka: KD07.101; KD07.102 | Code: KD07.101; KD07.102 | kpl | 2 |  | 0
7.19 | Elektromotorni pogon z vzmetjo za izstopno žaluzijo klimata, vključno z varnostno funkcijo (NC) in stikali položaja, s pritrdilnim in tesnilnim materialom tipa: | Electric motor drive with spring for climate exit blind, including safety function (NC) and position switches, with fixing and sealing material type:
| - navor 10Nm | - torque 10Nm
| - električno napajanje 24V AC/DC | - 24V AC/DC power supply
| - zvezna regulacija delovanja | - continuous operation control
| - za žaluzije do 2m2 | - for blinds up to 2m2
| - zaščita IP54 | - iP54 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip NF24A-SR-S2 | - BELIMO type NF24A-SR-S2
| Oznaka: KA07.202 | Code: KA07.202 | kpl | 1 |  | 0
7.20 | Elektromotorni pogon za obtok regeneratorja, s stikalom položaja za odprt položaj, s pritrdilnim in tesnilnim materialom tipa: | Electric motor drive for regenerator circulation, with position switch for open position, with fixing and sealing material type:
| - navor 5Nm | - torque 5Nm
| - električno napajanje 24V AC/DC | - 24V AC/DC power supply
| - ON/OFF regulacija delovanja | - ON/OFF operation control
| - za žaluzije do 1m2 | - for blinds up to 1m2
| - zaščita IP54 | - iP54 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip LM24A-S | - BELIMO type LM24A-S
| Oznaka: KD07.104; KD07.203 | Code: KD07.104; KD07.203 | kpl | 2 |  | 0
7.21 | Elektromotorni pogon za mešalno žaluzijo klimata, s pritrdilnim in tesnilnim materialom tipa: | Electric motor drive for air-conditioning mixing louvre, with fixing and sealing material type:
| - navor 2Nm | - torque 2Nm
| - električno napajanje 24V AC/DC | - 24V AC/DC power supply
| - zvezna regulacija delovanja | - continuous operation control
| - za žaluzije do 0,4m2 | - for blinds up to 0,4m2
| - zaščita IP54 | - iP54 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip CM24-SR-R | - BELIMO type CM24-SR-R
| Oznaka: KA07.105 | Code: KA07.105 | kpl | 1 |  | 0
7.22 | Kanalski senzor diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Duct differential pressure sensor, with mounting and sealing material type:
| - območje prikazovanja od 0 do 1500 Pa | - display range 0 to 1500 Pa
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22ADP-184A | - BELIMO type 22ADP-184A
| Oznaka: PICAL07.209; PICAL07.116 | Code: PICAL07.209; PICAL07.116 | kpl | 2 |  | 0
7.23 | Diferenčno tlačno stikalo, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure switch, with type fastening and sealing material:
| - območje prikazovanja od 50 do 500Pa | - display range 50 to 500Pa
| - kontaktni tok maksimalno 1,0A / AC 250V | - contact current max 1.0A / AC 250V
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 01APS-10U | - BELIMO type 01APS-10U
| Oznaka: PDSAH07.100; PDSAH07.113; PDSAH07.203; PDSAH07.207 | Code: PDSAH07.100; PDSAH07.113; PDSAH07.203; PDSAH07.207 | kpl | 4 |  | 0
7.24 | Prikazovalnik diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure indicator, with type fixing and sealing material:
| - območje prikazovanja od 50 do 500Pa | - display range 50 to 500Pa
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DWYER tip Magnahelic | - DWYER tip Magnahelic
| Oznaka: PDI07.100; PDI07.113; PDI07.203; PDI07.207 | Code: PDI07.100; PDI07.113; PDI07.203; PDI07.207 | kpl | 4 |  | 0
7.25 | Tipalo diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure sensor, with type fastening and sealing material:
| - območje prikazovanja od 0 do 1500 Pa | - display range 0 to 1500 Pa
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22ADP-184A | - BELIMO type 22ADP-184A
| Oznaka: PDIC07.110; PDIC07.205 | Code: PDIC07.110; PDIC07.205 | kpl | 2 |  | 0
7.26 | Tipalo diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure sensor, with type fastening and sealing material:
| - območje prikazovanja od 0 do 500 Pa | - display range 0 to 500 Pa
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22ADP-184A | - BELIMO type 22ADP-184A
| Oznaka: PDIC07.103 | Code: PDIC07.103 | kpl | 1 |  | 0
7.27 | Kanalsko tipalo temperature in vlage, s pritrdilnim in tesnilnim materialom tipa: | Duct temperature and humidity sensor, with fixing and sealing material type:
| - območje prikazovanja od 0 do 100%RH | - display range 0 to 100%RH
| - območje prikazovanja od -40 do 60°C | - display range -40 to 60°C
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22DTH-13M | - BELIMO type 22DTH-13M
| Oznaka: TIC/MIC07.114; TIC/MIC07.208 | Code: TIC/MIC07.114; TIC/MIC07.208 | kpl | 2 |  | 0
7.28 | Prostorsko tipalo temperature, vlage in kvalitete zraka CO2, s pritrdilnim in tesnilnim materialom tipa: | Room temperature, humidity and air quality sensor CO2, with fixing and sealing material type:
| - območje merjenja od 0 do 50°C | - measuring range 0 to 50°C
| - območje merjenja od 0 do 100%RH | - measuring range 0 to 100%RH
| - območje CO2 od 0 do 2000ppm | - cO2 range from 0 to 2000ppm
| - izhodni signal 0 do 10V | - output signal 0 to 10V
| - izhodni signal MP-Bus | - mP-Bus output signal
| - zaščita IP30 | - iP30 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22RTM-19-1 | - BELIMO type 22RTM-19-1
| Oznaka: TIC/MIC/QIC07.501 | Code: TIC/MIC/QIC07.501 | kpl | 1 |  | 0
7.29 | Protizmrzovalni termostat, s pritrdilnim in tesnilnim materialom tipa: | Anti-freezing thermostat, with fixing and sealing material type:
| - območje od -10 do 15°C | - range -10 to 15°C
| - dolžina kapilare 6m | - capillary length 6m
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 01ATS-105XC | - BELIMO type 01ATS-105XC
| Oznaka: TSZAL07.107 | Code: TSZAL07.107 | kpl | 1 |  | 0
7.30 | Obtočna črpalka, elektronsko regulirana s frekvenčnim pretvornikom, tipalom diferenčnega tlaka, internimi hidravličnimi, električnimi in komunikacijskimi povezavami, PN10, material jeklena litina, skladnost z ErP, pritrdilnim in tesnilnim materialom tipa: | Circulation pump, electronically controlled with frequency converter, differential pressure sensor, internal hydraulic, electrical and communication connections, PN10, material cast steel, ErP compliant, type fastening and sealing material:
| - za obtok ogrevne vode 50/40°C | - for circulating heating water 50/40°C
| - za pretok V = 0.72m3/h, tlačna višina H = 1.4m | - for flow rate V = 0.72m3/h, pressure head H = 1.4m
| - možnost izbire delovanja črpalke na proporcionalni tlak ter optimizacijo delovne obratovalne točke | - option to select proportional pressure pump operation and optimise the operating point
| - napajanje Pel = 0,018kW, 230V / 50Hz | - power supply Pel = 0,018kW, 230V/50Hz
| - navojni priključek G 1 1/2 | - threaded connection G 1 1/2
| - tlačna stopnja PN10 | - pressure rating PN10
| - temperaturno območje ogrevnega medija od 2 do 110°C | - heating medium temperature range from 2 to 110°C
| - komunikacija s CNS RS485 | - communication with CNS RS485
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - GRUNDFOS tip ALPHA2 25-40 130 | - GRUNDFOS type ALPHA2 25-40 130
| Oznaka: P07.106 | Code: P07.106 | kpl | 1 |  | 0
7.31 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za ogrevno vodo 50/40°C | - for heating water 50/40°C
| - za pretok V = 0.72m3/h | - for a flow rate of V = 0.72m3/h
| - območje regulacije pretoka do 900 l/h (0.9 m3/h) | - flow control range up to 900 l/h (0.9 m3/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - navojni priključek G 1 po ISO 228/1 | - threaded connection G 1 according to ISO 228/1
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 16 - 400 kPa, min. dif. tlak 16 kPa | - differential pressure range 16 - 400 kPa, min. differential pressure 16 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM20 | - DANFOS type AB-QM20
| Oznaka: VA07.106 | Code: VA07.106 | kpl | 1 |  | 0
7.32 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za hladilno vodo 9/14°C | - for cooling water 9/14°C
| - za pretok V = 4,84m3/h | - for a flow rate of V = 4,84m3/h
| - območje regulacije pretoka do 7500 l/h (7,5 m3/h) | - flow control range up to 7500 l/h (7.5 m3/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - navojni priključek G 2 po ISO 228/1 | - threaded connection G 2 according to ISO 228/1
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 30 - 400 kPa, min. dif. tlak 30 kPa | - differential pressure range 30 - 400 kPa, min. differential pressure 30 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM40 | - DANFOS tip AB-QM40
| Oznaka: VA07.109 | Code: VA07.109 | kpl | 1 |  | 0
7.33 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za ogrevno vodo 50/40°C | - for heating water 50/40°C
| - za pretok V = 0,90m3/h | - for a flow rate of V = 0,90m3/h
| - območje regulacije pretoka do 1700 l/h (1,70 m3/h) | - flow control range up to 1700 l/h (1.70 m3/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - navojni priključek G 1 1/4 po ISO 228/1 | - threaded connection G 1 1/4 according to ISO 228/1
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 20 - 400 kPa, min. dif. tlak 20 kPa | - differential pressure range 20 - 400 kPa, min. differential pressure 20 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM25 | - DANFOS type AB-QM25
| Oznaka: VA07.111 | Code: VA07.111 | kpl | 1 |  | 0
7.34 | Sistem reverzne osmoze s predfiltracijo za pripravo demineralizirane vode za potrebe vlažilnika klimatov KS07, KS08, s pritrdilnim in tesnilnim materialom, skupaj s/z: | Reverse osmosis system with pre-filtration for the preparation of demineralised water for the needs of the humidifier of the air conditioners KS07, KS08, with fixing and sealing material, incl:
| - svečnim filtrom s 5 m filternimi vložki | - candle filter with 5 m filter cartridges
| - vstopnim magnetnim ventilom | - inlet solenoid valve
| - vstopnim zaščitnim tlačnim stikalom | - inlet pressure relief switch
| - spiralno navitimi RO moduli v tlačnem ohišju | - spiral wound RO modules in a pressure housing
| - internimi cevnimi povezavami | - internal pipe connections
| - merilcema trenutnega pretoka dobitka in koncentrata | - instantaneous flow meters for the feed and concentrate
| - manometri za kontrolo tlaka vode na vstopu in izstopu koncentrata | - pressure gauges for controlling the water pressure at the inlet and outlet of the concentrate
| - merilcem prevodnosti dobitka | - a conductivity meter
| - mikroprocesorsko krmilno enoto | - microprocessor control unit
| - vzorčevalno pipico | - sampling tap
| - nosilno konstrukcijo iz nerjavnega jekla | - stainless steel load-bearing structure
| - ročno tipko za zaustavitev in zagon RO | - manual key to stop and start the RO
| - plovnim stikalom | - float switch
| - dimenzije naprave 500x1500x500 mm | - dimensions 500x1500x500 mm
| - pretok dobitka 80 l/h | - 80 l/h recharge flow
| - izkoristek naprave 50 - 70 % | - plant efficiency 50 - 70 %
| - zadržani topljenec min 98 % | - solvent retention min 98 %
| - priključki vstop/izstop DN15 | - inlet/outlet connections DN15
| - vstopni tlak min 1,5 bar | - inlet pressure min 1,5 bar
| - delovni tlak 15 bar | - working pressure 15 bar
| - delovna temperatura 10-35°C | - operating temperature 10-35°C
| - električni priključek 220/50/0,55 V/Hz/kW | - 220/50/0,55 V/Hz/kW electrical connection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - MAKCMC tip MINIRO 8 | - MAKCMC type MINIRO 8
| Oznaka: | Code: | kpl | 1 |  | 0
7.35 | Rezervoar demineralizirane vode in črpalna postaja za potrebe vlažilnika klimatov KS07, KS08, s pritrdilnim in tesnilnim materialom, skupaj s/z: | Demineralised water tank and pumping station for the needs of the humidifier of the air conditioners KS07, KS08, with fixing and sealing material, incl:
| - rezervoarjem iz PE | - pE tank
| - nivojskimi stikali: min/maks, za zaščito črpalke in signalizacijo preliva | - level switches: min/max, for pump protection and overflow signalling
| - hidrostatična sonda za zvezni nivo v rezervoarju | - hydrostatic probe for continuous tank level
| - pripadajočo PVC armaturo | - associated PVC fittings
| - varnostnim prelivom | - safety dressing
| - kontrolnim manometrom | - a check gauge
| - ekspanzijsko posodo iz nerjavnega jekla | - stainless steel expansion tank
| - tlačnim stikalom | - pressure switch
| - centrifugalno črpalko CM 1-6; material nerjavno jeklo AISI 316 | - centrifugal pump CM 1-6; material stainless steel AISI 316
| - volumen rezervoarja 115 l | - tank capacity 115 l
| - dimenzije rezervoarja D460x775 mm | - tank dimensions D460x775 mm
| - kapaciteta črpalke 1,7 m3/h | - pump capacity 1.7 m3/h
| - tlak 1,3bar | - pressure 1,3bar
| - priključki DN 25 | - dN 25 connections
| - el. priključek 400/50/460 V/Hz/W | - 400/50/460 V/Hz/W power connection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - MAKCMC tip RDI 12 C1 | - MAKCMC type RDI 12 C1
| Oznaka: | Code: | kpl | 1 |  | 0
7.36 | Avtomatski dvojni ionski mehčalec vode za potrebe vlažilnika klimatov KS07, KS08, s pritrdilnim in tesnilnim materialom, skupaj s/z: | Automatic double ion water softener for the humidifier needs of air conditioners KS07, KS08, with fixing and sealing material, incl:
| - elektro-mehanskim krmilnikom | - electro-mechanical controller
| - večpotnim ventilom z dvema distributorjema | - multiport valve with two distributors
| - tlačno posodo iz armiranega polietilena komplet 2 | - pressure vessel of reinforced polyethylene, set of 2
| - solnim ventilom | - salt valve
| - solnikom | - to solnikom
| - smolo močno kislega ionskega izmenjevalca | - strong acid ion-exchange resin
| - čistilnim kosom | - cleaning pieces
| - tabletirano soljo 25kg | - tablet salt 25kg
| - dimenzije naprave 1500x700x1100 mm | - dimensions 1500x700x1100 mm
| - volumen ionske smole 2 x 18 l | - ionic resin volume 2 x 18 l
| - volumen tlačne posode 2 x 20,4 l | - pressure vessel volume 2 x 20.4 l
| - volumen solnika 100 l | - brine tank capacity 100 l
| - poraba tabletirane soli 2,7 – 4,3 kg/reg | - tablet salt consumption 2,7 - 4,3 kg/reg
| - pretok 0,1 – 0,9 m3/h | - flow rate 0,1 - 0,9 m3/h
| - kapaciteta 9,9 –11,2 m3/reg | - capacity 9,9 -11,2 m3/reg
| - priključki vstop/izstop DN20 | - inlet/outlet connections DN20
| - delovni tlak 2,5 – 6 bar | - working pressure 2,5 - 6 bar
| - delovna temperatura do 40°C | - operating temperature up to 40°C
| - el. priključek 220/50/10 V/Hz/W | - 220/50/10 V/Hz/W power connection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - MAKCMC tip MINOM 0DF - 25 | - MAKCMC type MINOM 0DF - 25
| Oznaka: | Code: | kpl | 1 |  | 0
7.37 | Sistem za UV dezinfekcijo vode za potrebe vlažilnika klimatov KS07, KS08 s pritrdilnim in tesnilnim materialom, skupaj s/z: | UV water disinfection system for the humidifier of air conditioners KS07, KS08 with fixing and sealing material, incl:
| - reaktorjem: material 1.4404, elektopoliran | - reactor: material 1.4404, electropolished
| - nizkotlačnim UV sevalom v zaščitni cevi iz kremenčevega stekla | - low-pressure UV radiation in a protective quartz glass tube
| - mehkim zagonom delovanja sevala | - soft start of the radiator
| - signalizacijo za zamenjavo sevala | - signalling for radiator replacement
| - signalizacijo napak delovanja | - fault signalling
| - upravljalno enoto | - the control unit
| - dimenzije upravljalne enote 168x200x66 mm | - control unit dimensions 168x200x66 mm
| - priključki 3/4 '' | - 3/4'' connections
| - obratovalni tlak PN10 | - operating pressure PN10
| - UV doza 400 J/m2 | - UV dose 400 J/m2
| - hidravlična kapaciteta maks 1,69 m3/h | - hydraulic capacity max 1,69 m3/h
| - temperatura vode 0-35°C | - water temperature 0-35°C
| - temperatura okolice maks 35°C | - ambient temperature max 35°C
| - zaščita reaktor/upravlj. enota IP 65/54 | - reactor/management unit protection IP 65/54
| - el. priključek 220/50/55 V/Hz/W | - 220/50/55 V/Hz/W power connection
| - življenska doba svetil 8.760 h | - lamp life 8.760 h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - MAKCMC tip AQUADA 2 PRO | - MAKCMC tip AQUADA 2 PRO
| Oznaka: | Code: | kpl | 1 |  | 0
| PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS07 | VENTILATION AND AIR CONDITIONING SYSTEM KS07 |  |  |  | 0

## 4.4.8_PrKlim KS08
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.4 | STROJNA DELA | MECHANICAL WORKS
4.4.8 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS08 | VENTILATION AND AIR CONDITIONING SYSTEM KS08 |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
8 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS08 | VENTILATION AND AIR CONDITIONING SYSTEM KS08
8.1 | Klimatska naprava za dovod in odvod zraka KD08/KO08 - glej tudi zavihek Zahteve klimati. | KD08/KO08 supply and extract air conditioner - see also Climate requirements tab.
| Tehnične karakteristike naprave (opis v smeri toka zraka): | Technical characteristics of the device (description downstream):
| Dovod: Vdov = 990 m3/h | Input: Vdov = 990 m3/h
| - posluževanje dovod: desno v smeri toka zraka! | - inlet: right in the direction of the air flow!
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 10 60% po ISO 16890 (M5 po SIST EN 779), z regulacijsko žaluzijo 618x638x125, s fleksibilnim čelnim priključkom, za pretok zraka 990m3/h. Maksimalni končni padec tlaka 200Pa. Oznaka: F08.102 | - Filter unit with bag filter cartridge of filtration level ePM 10 60% according to ISO 16890 (M5 according to SIST EN 779), with control shutter 618x638x125, with flexible front connection, for air flow 990m3/h. Maximum final pressure drop 200Pa. Code: F08.102
| - Rotacijska regeneratorska enota za prenos senzibilne in latentne toplote. Tehnični podatki za zimsko obdobje: - pretok zraka 990/935m3/h - stopnja vračanja občutene toplote: 75,3% - stopnja vračanja latentne toplote: 75,9% - vračanje toplotne energije: 10,8kW - stanje dovodnega zr. pred enoto: -13,00°C/90,0% - stanje dovodnega zraka za enoto: 12,60°C/41,8% Tehnični podatki za poletno obdobje: - pretok zraka 990/935m3/h - stopnja vračanja občutene toplote: 74,6% - stopnja vračanja latentne toplote: 72,9% - vračanje toplotne energije: 2,80kW - stanje dovodnega zr. pred enoto: 34,50°C/40,0% - stanje dovodnega zraka za enoto: 28,20°C/54,1% Oznaka: RE08.191 | - Rotary regenerative unit for sensible and latent heat transfer. technical data for the winter period: - air flow 990/935m3/h - sensible heat recovery rate: 75.3% - latent heat recovery rate: 75.9% - heat energy recovery: 10.8kW - supply air condition upstream of the unit: -13.00°C/90.0% - supply air condition for the unit: 12.60°C/41.8% Technical data for the summer period: - air flow 990/935m3/h - sensible heat recovery rate: 74.6% - latent heat recovery rate: 72.9% - heat energy recovery: 2.80kW - supply air condition upstream of the unit: 34.50°C/40.0% - supply air condition for the unit: 28.20°C/54.1% Code: RE08.191
| - Enota pred-grelnika zraka s protizmrzovalno zaščito. - pretok zraka 990m3/h - grelna moč Qg=5,63kW - temperaturni režim ogrevnega medija 50/40°C - pretok ogrevnega medija 0,49m3/h - padec tlaka na zračni strani 4Pa - temperatura zraka vstop 12,60°C - temperatura zraka izstop 29,50°C - padec tlaka na strani ogr. medija (voda) 10,44kPa - priključka navojna 1/2" - tlačna stopnja PN16 Oznaka: HE08.103 | - Air preheater unit with anti-freeze protection. - air flow 990m3/h - heating power Qg=5,63kW - heating medium temperature 50/40°C - heating medium flow rate 0,49m3/h - 4Pa pressure drop on the air side - air inlet temperature 12,60°C - air temperature outlet 29,50°C - pressure drop on the heating medium side (water) 10,44kPa - 1/2" threaded connectors - pressure rating PN16 Code: HE08.103
| - Vlažilna enota s kontaktnim vlaženjem zraka. Dovod sveže pripravljene demineralizirane vode, z materialom kontaktnega vlažilnika impregniranim srebrom, črpalko, potrebno merilno regulacijsko opremo, ventili na dovodu sveže vode ter ventilom na odvodu vode iz banje, s funkcijo samodejnega praznjenja banje vlažilnika in polnjenja s svežo pripravljeno mehčano vodo glede na prevodnost vode v banji, oziroma glede na čas ko vlažilnik ni v funkciji. Odvod kondenzata s sifonom z vodno in mehansko smardno zaporo. - pretok zraka 990m3/h - priključna električna moč 0,05kW, 230V, 50Hz - padec tlaka na zračni strani dpz=9Pa - temperatura zraka vstop 29,5°C - relativna vlaga zraka vstop 14,8% - temperatura zraka izstop 27,19°C - relativna vlaga izstop 21% - izkoristek vlaženja 14,65% - vlaženje 4,68 kg/h - tipalo prevodonsti vode QICCD08.105 - tipalo zgornjega nivoja vode LICH08.105 - tipalo spodnjega nivoja vode LICL08.105 - elektromagnetni ventil za praznenje VD08.105 - elektromagnetni ventil za dovod sveže vode VD08.205 Oznaka: SH08.105 | - Humidification unit with contact humidification. Freshly prepared demineralised water supply, with silver-impregnated contact humidifier material, pump, necessary metering control equipment, valves at the fresh water inlet and at the water outlet of the humidifier tank, with automatic emptying of the humidifier tank and refilling with freshly prepared softened water according to the conductivity of the water in the tank, or according to the time when the humidifier is not in operation. Condensate drainage with siphon with water and mechanical odour trap. - air flow 990m3/h - connection power 0,05kW, 230V, 50Hz - pressure drop on the air side dpz=9Pa - air temperature 29,5°C - relative humidity 14.8% - air temperature outlet 27,19°C - relative humidity 21% exit - humidification efficiency 14.65% - humidification 4,68 kg/h - water conductivity sensor QICCD08.105 - upper water level sensor LICH08.105 - lower water level sensor LICL08.105 - solenoid valve for emptying VD08.105 - fresh water solenoid valve VD08.205 Code: SH08.105
| - Enota hladilnika z eliminatorjem kapljic in koritom za odvod kondenzata. - pretok zraka 990m3/h - hladilna moč Qhtot=4,2kW - temperaturni režim hladilnega medija 9/14°C - pretok hladilnega medija 0,72m3/h - padec tlaka na zračni strani 10/9Pa - temperatura zraka vstop 28,20°C - temperatura zraka izstop 18,80°C - padec tlaka na strani hl. medija (voda) 10,06kPa - priključka navojna 3/4" - tlačna stopnja PN16 Oznaka: HE08.106 | - Refrigerator unit with drip eliminator and condensate drain. - air flow 990m3/h - cooling power Qhtot=4,2kW - cooling medium temperature 9/14°C - cooling medium flow rate 0,72m3/h - air side pressure drop 10/9Pa - air temperature inlet 28,20°C - air temperature outlet 18,80°C - pressure drop on the medium side (water) 10,06kPa - 3/4" threaded connectors - pressure rating PN16 Code: HE08.106
| - Ventilatorska enota s prostotekočim rotorjem. Elektromotor je EC-motor, s 100% zvezno regulacijo vrtljajev preko potenciometra (0-10V), ki omogoča nastavitev delovanja ventilatorja na ustrezno delovno točko. Enota vsebuje: okence O150 in svetilko s stikalom ter servisno stikalo. - pretok zraka 990m3/h - eksterni statični padec tlaka dpext=300Pa - priključna električna moč 0,76kW, 230V, 50Hz - razred izkoristka elektromotorja IE4/EC - zaščita IP54 Oznaka: FA08.107 | - Fan unit with free-flowing rotor. The electric motor is an EC motor, with 100% continuous speed control via a potentiometer (0-10V), which allows the fan to be set to the appropriate operating point. The unit contains: an O150 window and a lamp with switch and a service switch. - air flow 990m3/h - external static pressure drop dpext=300Pa - connection power 0,76kW, 230V, 50Hz - electric motor efficiency class IE4/EC - iP54 protection Code: FA08.107
| - Dušilna enota. - pretok zraka 990m3/h - padec tlaka dp=2Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 7 17 18 21 15 11 12 Oznaka: DZ08.108 | - Throttle unit. - air flow 990m3/h - pressure drop dp=2Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 7 17 18 21 15 11 12 Code: DZ08.108
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 1 75% po ISO 16890 (F8 po SIST EN 779, s fleksibilnim čelnim priključkom, za pretok zraka 990m3/h. Maksimalni končni padec tlaka 300Pa. Oznaka: F08.109 | - Filter unit with bag filter cartridge of filtration level ePM 1 75% according to ISO 16890 (F8 according to SIST EN 779, with flexible front connection, for air flow 990m3/h. Maximum final pressure drop 300Pa. Code: F08.109
| Dolžina: 5,250m | Length: 5,250m
| Širina: 0,750m | Width: 0.750m
| Višina: 0,875m | Height: 0,875m
| Kompletno z dobavo dodatne opreme: | Complete with supply of accessories:
| - odtočni sifoni | - drain traps
| - jadrovinasti nastavki | - sailplane spouts
| - s spojnim, tesnilnim in pritrdilnim materialom in priključki za senzorje, | - with jointing, sealing and fixing materials and sensor connections,
| Odvod: Vodv = 935 m3/h | Discharge: waterv = 935 m3/h
| - posluževanje odvod: levo v smeri toka zraka! | - serving outlet: left in the direction of the air flow!
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 10 60% po ISO 16890 (M5 po SIST EN 779), s fleksibilnim čelnim priključkom, za pretok zraka 935m3/h. Maksimalni končni padec tlaka 200Pa. Oznaka: F08.207 | - Filter unit with bag filter cartridge of filtration level ePM 10 60% according to ISO 16890 (M5 according to SIST EN 779), with flexible front connection, for an air flow of 935m3/h. Maximum final pressure drop 200Pa. Code: F08.207
| - Dušilna enota. - pretok zraka 935m3/h - padec tlaka dp=6Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 7 17 18 21 15 11 12 Oznaka: DZ08.206 | - Throttle unit. - air flow 935m3/h - pressure drop dp=6Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 7 17 18 21 15 11 12 Code: DZ08.206
| - Ventilatorska enota s prostotekočim rotorjem. Elektromotor je EC-motor, s 100% zvezno regulacijo vrtljajev preko potenciometra (0-10V), ki omogoča nastavitev delovanja ventilatorja na ustrezno delovno točko. Enota vsebuje: okence O150 in svetilko s stikalom ter servisno stikalo. - pretok zraka 935m3/h - eksterni statični padec tlaka dpext=300Pa - priključna električna moč 0,76kW, 230V, 50Hz - razred izkoristka elektromotorja IE4/EC - zaščita IP54 Oznaka: FA08.205 | - Fan unit with free-flowing rotor. The electric motor is an EC motor, with 100% continuous speed control via a potentiometer (0-10V), which allows the fan to be set to the appropriate operating point. The unit contains: an O150 window and a lamp with switch and a service switch. - air flow 935m3/h - external static pressure drop dpext=300Pa - connection power 0,76kW, 230V, 50Hz - electric motor efficiency class IE4/EC - iP54 protection Code: FA08.205
| - Dušilna enota. - pretok zraka 935m3/h - padec tlaka dp=6Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 7 17 18 21 15 11 12 Oznaka: DZ08.204 | - Throttle unit. - air flow 935m3/h - pressure drop dp=6Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 7 17 18 21 15 11 12 Code: DZ08.204
| - Prazna enota z regulacijsko žaluzijo 618x333x125, fleksibilnim čelnim priključkom, za pretok zraka 935m3/h. | - Empty unit with 618x333x125 control louvre, flexible front connection, for air flow 935m3/h.
| Dolžina: 3,900m | Length: 3,900m
| Širina: 0,750m | Width: 0.750m
| Višina: 0,445m | Height: 0,445m
| Kompletno z dobavo dodatne opreme: | Complete with supply of accessories:
| - postavitvene noge, gumirane, višine 100-200mm | - rubberised feet, height 100-200mm
| - odtočni sifoni | - drain traps
| - jadrovinasti nastavki | - sailplane spouts
| - postavitev klimata na antivibracijski dušilnik (gumo) za preprečevanje prenosa vibracij in hrupa na konstrukcijo objekta. Dušilniki morajo biti preračunani glede na lastnosti klimata (teža in vrtilna frekvenca ventilatorjev). | - installation of the air conditioner on an anti-vibration damper (rubber) to prevent the transmission of vibrations and noise to the structure of the building. The dampers must be calculated according to the characteristics of the air conditioner (weight and speed of the fans).
| - s spojnim, tesnilnim in pritrdilnim materialom in priključki za senzorje, | - with jointing, sealing and fixing materials and sensor connections,
| Teža: 931kg | Weight: 931kg
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR | - SYSTEMAIR | kpl | 1 |  | 0
8.2 | Okrogli prezračevalni kanali izdelani iz pocinkane pločevine po SIST EN 1506, vključno z revizijskimi odprtinami, oblikovnimi kosi, debeline po standardu. V ceni na enoto (m) je potrebno upoštevati ves spojni in pritrdilni material (prirobnice, odrez, spone, vijaki, tesnila, ojačitve, vključno z obešalnim in pritrdilnim materialom sistemskega proizvajalca z lastnostmi odgovarjajoč zahtevam SIST EN 12236: 2002, vključno pleskanje vseh kovinskih korozijsko nezaščitenih delov, po temeljitem predhodnem čiščenju do kovinskega sijaja. Antikorozijska zaščita se izvaja v skladu z EN 12944 za naslednje pogoje: • Življenjska doba več kot 15 let. • Stopnja korozijske atmosfere C4 (visoka). | Round ventilation ducts made of galvanised sheet metal according to SIST EN 1506, including inspection openings, shaped pieces, thickness according to the standard. The unit price (m) must take into account all joining and fixing material (flanges, cut-offs, clamps, bolts, gaskets, reinforcements, including hanging and fixing material of the system manufacturer with properties according to the requirements of SIST EN 12236: 2002, including painting of all metal corrosion-protected parts, after thorough cleaning to a metallic gloss. The corrosion protection shall be carried out in accordance with EN12944, for the following conditions: - Lifetime over 15 years. - Corrosive atmosphere C4 (high).
| - Okrogli prezračevalni kanali Ø100 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø100 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 5 |  | 0
| - Okrogli prezračevalni kanali Ø125 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø125 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 3 |  | 0
| - Okrogli prezračevalni kanali Ø140 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø140 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 3 |  | 0
| - Okrogli prezračevalni kanali Ø160 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø160 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 55 |  | 0
| - Okrogli prezračevalni kanali Ø200 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø200 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 30 |  | 0
| - Okrogli prezračevalni kanali Ø225 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø225 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 50 |  | 0
| - Okrogli prezračevalni kanali Ø250 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø250 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 25 |  | 0
| - Okrogli prezračevalni kanali Ø300 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø300 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 15 |  | 0
8.3 | Okrogli pregibni kanali za priključitev stropnih difuzorjev, izdelani iz Al folije ter polnila iz materiala z dušilnim in toplotno-izolativnim efektom. V ceni na enoto (m) je potrebno upoštevati ves spojni material, pritrdilne objemke in tesnilni material, za podatke: | Round folded ducts for the connection of ceiling diffusers, made of Al foil and filling material with damping and thermal insulation effect. The unit price (m) must include all joining material, fixing clamps and sealing material, for details:
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DEC tip: SONODEC - 25 | - DEC tip: SUNDAY - 25
| - Okroglegi pregibni kanali Ø160 | - Round flexible ducts Ø160 | m | 15 |  | 0
| - Okroglegi pregibni kanali Ø200 | - Ø200 round flexible ducts | m | 8 |  | 0
8.4 | Pravokotni prezračevalni kanali izdelani iz pocinkane pločevine po SIST EN 1505:1999, debeline po DIN 24190, klase tesnosti B po SIST EN 1507:2006, vključno z revizijskimi odprtinami, oblikovnimi kosi. V ceni na enoto (m2) je potrebno upoštevati ves spojni in pritrdilni material (prirobnice, odrez, spone, vijaki, tesnila, usmerjevalniki, ojačitve, vključno z obešalnim in pritrdilnim materialom sistemskega proizvajalca z lastnostmi odgovarjajoč zahtevam SIST EN 12236: 2002, vključno pleskanje vseh kovinskih korozijsko nezaščitenih delov, po temeljitem predhodnem čiščenju do kovinskega sijaja. Antikorozijska zaščita se izvaja v skladu z EN 12944 za naslednje pogoje: • Življenjska doba več kot 15 let. • Stopnja korozijske atmosfere C4 (visoka). | Rectangular ventilation ducts made of galvanised sheet metal according to SIST EN 1505:1999, thickness according to DIN 24190, tightness class B according to SIST EN 1507:2006, including inspection openings, shaped pieces. The unit price (m2) must take into account all joining and fixing material (flanges, cut-off, clamps, bolts, gaskets, guides, reinforcements, including hanging and fixing material of the system manufacturer with properties corresponding to the requirements of SIST EN 12236:2002, including the painting of all metal corrosion-protected parts, after thorough preliminary cleaning to a metallic gloss. The anticorrosive protection shall be performed in accordance with EN 12944 for the following conditions: - Lifetime over 15 years. - Corrosive atmosphere C4 (high). | m2 | 142 |  | 0
8.5 | Toplotna izolacija zajemnih, izpušnih ter vtočnih kanalov s parozapornimi ploščami izdelanimi iz sintetičnega kavčuka z zaprto celično strukturo, toplotne prevodnosti manjše ali enake 0,033W/mK pri srednji temperaturi 0 °C, koeficient upora difuziji vodene pare večji ali enak 10000 testirano v skladu z EN 13469 za cevi in EN 12086 za plošče, požarna klasifikacija B/BL-s3,d0 po DIN 4102, oziroma po SIST EN 13501-1. | Thermal insulation of intake, exhaust and inlet ducts with vapour control panels made of synthetic rubber with closed cell structure, thermal conductivity less than or equal to 0,033 W/mK at a mean temperature of 0 °C, resistance coefficient to diffusion of water vapour greater than or equal to 10000 tested in accordance with EN 13469 for pipes and EN 12086 for panels, fire classification B/BL-s3,d0 according to DIN 4102, or according to SIST EN 13501-1.
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - ARMACELL tip: Armaflex AF | - ARMACELL tip: Armaflex AF
| Toplotna izolacija zajemnih kanalov na vtočni strani (ZUZ-ODA), debeline s = 50 mm, + original lepilo | Thermal insulation of the inlet side of the intake ducts (ZUZ-ODA), thickness s = 50 mm, + original adhesive | m2 | 2 |  | 0
| Toplotna izolacija notranjih kanalov na vtočni strani (VTZ-SUP), debeline s = 19 mm, + original lepilo | Thermal insulation of internal ducts on the inlet side (VTZ-SUP), thickness s = 19 mm, + original adhesive | m2 | 105 |  | 0
| Toplotna izolacija izpušnih kanalov (ZAZ-EHA), debeline s = 19 mm, + original lepilo | Exhaust duct insulation (ZAZ-EHA), thickness s = 19 mm, + original adhesive | m2 | 50 |  | 0
8.6 | Kanalski dušilnik, za preprečevajne prenosa zvoka med prostori, izdelan iz pocinkane pločevine, mineralne volne za dušenje zvoka debeline 100mm, z zaščito pred erozijo iz netkane tkanine, vključno z vsem potrebnim pritrdilnim, povezovalnim, tesnilnim in montažnim materialom, tipa: | Duct silencer, to prevent the transmission of sound between rooms, made of galvanised sheet, 100mm thick mineral wool for sound attenuation, with non-woven fabric erosion protection, including all necessary fixing, connecting, sealing and mounting material, type:
| - dimenzije Ø200/900/100 | - dimensions Ø200/900/100
| - pretok q = 280 m3/h | - flow rate q = 280 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - LINDAB tip SLGU 200 - 900 -100 | - LINDAB type SLGU 200 - 900 -100
| Oznaka: DZ08.311 | Code: DZ08.311 | kpl | 1 |  | 0
8.7 | Kanalski dušilnik, za preprečevajne prenosa zvoka med prostori, izdelan iz pocinkane pločevine, mineralne volne za dušenje zvoka debeline 100mm, z zaščito pred erozijo iz netkane tkanine, vključno z vsem potrebnim pritrdilnim, povezovalnim, tesnilnim in montažnim materialom, tipa: | Duct silencer, to prevent the transmission of sound between rooms, made of galvanised sheet, 100mm thick mineral wool for sound attenuation, with non-woven fabric erosion protection, including all necessary fixing, connecting, sealing and mounting material, type:
| - dimenzije Ø200/900/100 | - dimensions Ø200/900/100
| - pretok q = 140 m3/h | - flow rate q = 140 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - LINDAB tip SLGU 200 - 900 -100 | - LINDAB type SLGU 200 - 900 -100
| Oznaka: DZ08.312; DZ08.313; DZ08.314 | Code: DZ08.312; DZ08.313; DZ08.314 | kpl | 3 |  | 0
8.8 | Kanalski dušilnik, za preprečevajne prenosa zvoka med prostori, izdelan iz pocinkane pločevine, mineralne volne za dušenje zvoka debeline 100mm, z zaščito pred erozijo iz netkane tkanine, vključno z vsem potrebnim pritrdilnim, povezovalnim, tesnilnim in montažnim materialom, tipa: | Duct silencer, to prevent the transmission of sound between rooms, made of galvanised sheet, 100mm thick mineral wool for sound attenuation, with non-woven fabric erosion protection, including all necessary fixing, connecting, sealing and mounting material, type:
| - dimenzije Ø160/900/100 | - dimensions Ø160/900/100
| - pretok q = 80 m3/h | - flow rate q = 80 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - LINDAB tip SLGU 160 - 900 -100 | - LINDAB type SLGU 160 - 900 -100
| Oznaka: DZ08.315 | Code: DZ08.315 | kpl | 1 |  | 0
8.9 | Kanalski dušilnik, za preprečevajne prenosa zvoka med prostori, izdelan iz pocinkane pločevine, mineralne volne za dušenje zvoka debeline 100mm, z zaščito pred erozijo iz netkane tkanine, vključno z vsem potrebnim pritrdilnim, povezovalnim, tesnilnim in montažnim materialom, tipa: | Duct silencer, to prevent the transmission of sound between rooms, made of galvanised sheet, 100mm thick mineral wool for sound attenuation, with non-woven fabric erosion protection, including all necessary fixing, connecting, sealing and mounting material, type:
| - dimenzije Ø200/900/100 | - dimensions Ø200/900/100
| - pretok q = 270 m3/h | - flow rate q = 270 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - LINDAB tip SLGU 200 - 900 -100 | - LINDAB type SLGU 200 - 900 -100
| Oznaka: DZ08.321 | Code: DZ08.321 | kpl | 1 |  | 0
8.10 | Kanalski dušilnik, za preprečevajne prenosa zvoka med prostori, izdelan iz pocinkane pločevine, mineralne volne za dušenje zvoka debeline 100mm, z zaščito pred erozijo iz netkane tkanine, vključno z vsem potrebnim pritrdilnim, povezovalnim, tesnilnim in montažnim materialom, tipa: | Duct silencer, to prevent the transmission of sound between rooms, made of galvanised sheet, 100mm thick mineral wool for sound attenuation, with non-woven fabric erosion protection, including all necessary fixing, connecting, sealing and mounting material, type:
| - dimenzije Ø160/900/100 | - dimensions Ø160/900/100
| - pretok q = 130 m3/h | - flow rate q = 130 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - LINDAB tip SLGU 160 - 900 -100 | - LINDAB type SLGU 160 - 900 -100
| Oznaka: DZ08.322; DZ08.323; DZ08.324 | Code: DZ08.322; DZ08.323; DZ08.324 | kpl | 3 |  | 0
8.11 | Kanalski dušilnik, za preprečevajne prenosa zvoka med prostori, izdelan iz pocinkane pločevine, mineralne volne za dušenje zvoka debeline 100mm, z zaščito pred erozijo iz netkane tkanine, vključno z vsem potrebnim pritrdilnim, povezovalnim, tesnilnim in montažnim materialom, tipa: | Duct silencer, to prevent the transmission of sound between rooms, made of galvanised sheet, 100mm thick mineral wool for sound attenuation, with non-woven fabric erosion protection, including all necessary fixing, connecting, sealing and mounting material, type:
| - dimenzije Ø160/900/100 | - dimensions Ø160/900/100
| - pretok q = 75 m3/h | - flow rate q = 75 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - LINDAB tip SLGU 160 - 900 -100 | - LINDAB type SLGU 160 - 900 -100
| Oznaka: DZ08.325 | Code: DZ08.325 | kpl | 1 |  | 0
8.12 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, sound and heat insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to the customer's or architect's preference, with connection chamber, with control damper, with connections for air flow measurement, inlet connection of the prepared air is provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø497, H=252, Ø160 | - dimensions Ø497, H=252, Ø160
| - pretok q = 80 m3/h | - flow rate q = 80 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-C-160 | - SYSTEMAIR tip CAP-C-160
| Oznaka: / | Tag: / | kpl | 1 |  | 0
8.13 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, sound and heat insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to the customer's or architect's preference, with connection chamber, with control damper, with connections for air flow measurement, inlet connection of the prepared air is provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø497, H=252, Ø160 | - dimensions Ø497, H=252, Ø160
| - pretok q = 105 m3/h | - flow rate q = 105 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-C-160 | - SYSTEMAIR tip CAP-C-160
| Oznaka: / | Tag: / | kpl | 2 |  | 0
8.14 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, sound and heat insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to the customer's or architect's preference, with connection chamber, with control damper, with connections for air flow measurement, inlet connection of the prepared air is provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø597, H=287, Ø200 | - dimensions Ø597, H=287, Ø200
| - pretok q = 140 m3/h | - flow rate q = 140 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-C-200 | - SYSTEMAIR tip CAP-C-200
| Oznaka: / | Tag: / | kpl | 5 |  | 0
8.15 | Stropni difuzor za odvod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno izolirano, maska je s fiksnimi lamelami, barve (RAL 9010) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, priključek odvoda zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for exhaust air, housing made of galvanised sheet steel, soundproofed, mask with fixed louvres, colour (RAL 9010) or in the colour of the client's or architect's choice, with connection chamber, with control damper, exhaust air connection provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø275, H=250, Ø160 | - dimensions Ø275, H=250, Ø160
| - pretok q = 135 m3/h | - flow rate q = 135 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip VVKN-A-R-300 | - SYSTEMAIR type VVKN-A-R-300
| Oznaka: / | Tag: / | kpl | 2 |  | 0
8.16 | Stropni difuzor za odvod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno izolirano, maska je s fiksnimi lamelami, barve (RAL 9010) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, priključek odvoda zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for exhaust air, housing made of galvanised sheet steel, soundproofed, mask with fixed louvres, colour (RAL 9010) or in the colour of the client's or architect's choice, with connection chamber, with control damper, exhaust air connection provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø275, H=250, Ø160 | - dimensions Ø275, H=250, Ø160
| - pretok q = 130 m3/h | - flow rate q = 130 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip VVKN-A-R-300 | - SYSTEMAIR type VVKN-A-R-300
| Oznaka: / | Tag: / | kpl | 3 |  | 0
8.17 | Stropni difuzor za odvod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno izolirano, maska je s fiksnimi lamelami, barve (RAL 9010) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, priključek odvoda zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for exhaust air, housing made of galvanised sheet steel, soundproofed, mask with fixed louvres, colour (RAL 9010) or in the colour of the client's or architect's choice, with connection chamber, with control damper, exhaust air connection provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø275, H=250, Ø160 | - dimensions Ø275, H=250, Ø160
| - pretok q = 100 m3/h | - flow rate q = 100 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip VVKN-A-R-300 | - SYSTEMAIR type VVKN-A-R-300
| Oznaka: / | Tag: / | kpl | 2 |  | 0
8.18 | Stropni difuzor za odvod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno izolirano, maska je s fiksnimi lamelami, barve (RAL 9010) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, priključek odvoda zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for exhaust air, housing made of galvanised sheet steel, soundproofed, mask with fixed louvres, colour (RAL 9010) or in the colour of the client's or architect's choice, with connection chamber, with control damper, exhaust air connection provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø275, H=250, Ø160 | - dimensions Ø275, H=250, Ø160
| - pretok q = 75 m3/h | - flow rate q = 75 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip VVKN-A-R-300 | - SYSTEMAIR type VVKN-A-R-300
| Oznaka: / | Tag: / | kpl | 1 |  | 0
8.19 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije B=300/H=300 | - dimensions B=300/H=300
| - pretok q = 990 m3/h | - flow rate q = 990 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-300x300 | - SYSTEMAIR tip FDS-3G-300x300
| Oznaka: KFD08.301 | Code: KFD08.301 | kpl | 1 |  | 0
8.20 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije Ø225 | - dimensions Ø225
| - pretok q = 280 m3/h | - flow rate q = 280 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-225 | - SYSTEMAIR tip FDR-3G-225
| Oznaka: KFD08.302 | Code: KFD08.302 | kpl | 1 |  | 0
8.21 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije Ø200 | - ø200 dimensions
| - pretok q = 140 m3/h | - flow rate q = 140 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-200 | - SYSTEMAIR tip FDR-3G-200
| Oznaka: KFD08.303; KFD08.304 | Code: KFD08.303; KFD08.304 | kpl | 2 |  | 0
8.22 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije Ø250 | - dimensions Ø250
| - pretok q = 430 m3/h | - flow rate q = 430 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-250 | - SYSTEMAIR tip FDR-3G-250
| Oznaka: KFD08.305 | Code: KFD08.305 | kpl | 1 |  | 0
8.23 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije B=300/H=300 | - dimensions B=300/H=300
| - pretok q = 935 m3/h | - flow rate q = 935 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-300x300 | - SYSTEMAIR tip FDS-3G-300x300
| Oznaka: KFD08.401 | Code: KFD08.401 | kpl | 1 |  | 0
8.24 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije Ø225 | - dimensions Ø225
| - pretok q = 270 m3/h | - flow rate q = 270 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-225 | - SYSTEMAIR tip FDR-3G-225
| Oznaka: KFD08.402 | Code: KFD08.402 | kpl | 1 |  | 0
8.25 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material of type:
| - dimenzije Ø160 | - ø160 dimensions
| - pretok q = 130 m3/h | - flow rate q = 130 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-160 | - SYSTEMAIR tip FDR-3G-160
| Oznaka: KFD08.403; KFD08.404 | Code: KFD08.403; KFD08.404 | kpl | 2 |  | 0
8.26 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material of type:
| - dimenzije Ø250 | - dimensions Ø250
| - pretok q = 405 m3/h | - flow rate q = 405 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-250 | - SYSTEMAIR tip FDR-3G-250
| Oznaka: KFD08.405 | Code: KFD08.405 | kpl | 1 |  | 0
8.27 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø140 | - ø140 dimensions
| - pretok q = 280 do 100m3/h | - flow rate q = 280 to 100m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-140 | - SYSTEMAIR tip OPTIMA-LV-RI-140
| Oznaka: VAV08.101 | Code: VAV08.101 | kpl | 1 |  | 0
8.28 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø100 | - ø100 dimensions
| - pretok q = 140 do 70m3/h | - flow rate q = 140 to 70m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-100 | - SYSTEMAIR tip OPTIMA-LV-RI-100
| Oznaka: VAV08.102; VAV08.103; VAV08.104 | Code: VAV08.102; VAV08.103; VAV08.104 | kpl | 3 |  | 0
8.29 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø125 | - dimensions Ø125
| - pretok q = 210 do 100m3/h | - flow rate q = 210 to 100m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-125 | - SYSTEMAIR tip OPTIMA-LV-RI-125
| Oznaka: VAV08.105 | Code: VAV08.105 | kpl | 1 |  | 0
8.30 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø100 | - ø100 dimensions
| - pretok q = 80 do 45m3/h | - flow rate q = 80 to 45m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-100 | - SYSTEMAIR tip OPTIMA-LV-RI-100
| Oznaka: VAV08.106 | Code: VAV08.106 | kpl | 1 |  | 0
8.31 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø140 | - ø140 dimensions
| - pretok q = 270 do 95m3/h | - flow rate q = 270 to 95m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-140 | - SYSTEMAIR tip OPTIMA-LV-RI-140
| Oznaka: VAV08.201 | Code: VAV08.201 | kpl | 1 |  | 0
8.32 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø100 | - ø100 dimensions
| - pretok q = 130 do 65m3/h | - flow rate q = 130 to 65m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-100 | - SYSTEMAIR tip OPTIMA-LV-RI-100
| Oznaka: VAV08.202; VAV08.203; VAV08.204 | Code: VAV08.202; VAV08.203; VAV08.204 | kpl | 3 |  | 0
8.33 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø125 | - dimensions Ø125
| - pretok q = 200 do 95m3/h | - flow rate q = 200 to 95m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-125 | - SYSTEMAIR tip OPTIMA-LV-RI-125
| Oznaka: VAV08.205 | Code: VAV08.205 | kpl | 1 |  | 0
8.34 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø100 | - ø100 dimensions
| - pretok q = 75 do 40m3/h | - flow rate q = 75 to 40m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-100 | - SYSTEMAIR tip OPTIMA-LV-RI-100
| Oznaka: VAV08.206 | Code: VAV08.206 | kpl | 1 |  | 0
8.35 | Elektromotorni pogon z vzmetjo za vstopno/izstopno žaluzijo klimata, vključno z varnostno funkcijo (NC) in stikali položaja, s pritrdilnim in tesnilnim materialom tipa: | Electric motor drive with spring for air-conditioning entry/exit blind, including safety function (NC) and position switches, with fixing and sealing material type:
| - navor 10Nm | - torque 10Nm
| - električno napajanje 24V AC/DC | - 24V AC/DC power supply
| - ON/OFF regulacija delovanja | - ON/OFF operation control
| - za žaluzije do 2m2 | - for blinds up to 2m2
| - zaščita IP54 | - iP54 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip NF24A-S2 | - BELIMO type NF24A-S2
| Oznaka: KD08.101; KD08.202 | Code: KD08.101; KD08.202 | kpl | 2 |  | 0
8.36 | Kanalsko tipalo diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Duct differential pressure sensor, with type fastening and sealing material:
| - območje prikazovanja od 0 do 1500 Pa | - display range 0 to 1500 Pa
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22ADP-184A | - BELIMO type 22ADP-184A
| Oznaka: PICAL08.112; PICAL08.212 | Code: PICAL08.112; PICAL08.212 | kpl | 2 |  | 0
8.37 | Tipalo diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure sensor, with mounting and sealing material type:
| - območje prikazovanja od 0 do 1500 Pa | - display range 0 to 1500 Pa
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22ADP-184A | - BELIMO type 22ADP-184A
| Oznaka: PDIC08.107; PDIC08.205 | Code: PDIC08.107; PDIC08.205 | kpl | 2 |  | 0
8.38 | Diferenčno tlačno stikalo, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure switch, with type fastening and sealing material:
| - območje prikazovanja od 50 do 500Pa | - display range 50 to 500Pa
| - kontaktni tok maksimalno 1,0A / AC 250V | - contact current max 1.0A / AC 250V
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 01APS-10U | - BELIMO type 01APS-10U
| Oznaka: PDSAH08.102; PDSAH08.109; PDSAH08.203; PDSAH08.207 | Code: PDSAH08.102; PDSAH08.109; PDSAH08.203; PDSAH08.207 | kpl | 4 |  | 0
8.39 | Prikazovalnik diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure indicator, with type fixing and sealing material:
| - območje prikazovanja od 50 do 500Pa | - display range 50 to 500Pa
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DWYER tip Magnahelic | - DWYER tip Magnahelic
| Oznaka: PDI08.102; PDI08.109; PDI08.203; PDI08.207 | Code: PDI08.102; PDI08.109; PDI08.203; PDI08.207 | kpl | 4 |  | 0
8.40 | Zunanje tipalo temperature in vlage, s pritrdilnim in tesnilnim materialom tipa: | External temperature and humidity sensor, with fixing and sealing material type:
| - območje prikazovanja od 0 do 100%RH | - display range 0 to 100%RH
| - območje prikazovanja od -40 do 60°C | - display range -40 to 60°C
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22UTH-13M | - BELIMO type 22UTH-13M
| Oznaka: TIC/MIC08.100 | Code: TIC/MIC08.100 | kpl | 1 |  | 0
8.41 | Kanalsko tipalo temperature in vlage, s pritrdilnim in tesnilnim materialom tipa: | Duct temperature and humidity sensor, with fixing and sealing material type:
| - območje prikazovanja od 0 do 100%RH | - display range 0 to 100%RH
| - območje prikazovanja od -40 do 60°C | - display range -40 to 60°C
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22DTH-13M | - BELIMO type 22DTH-13M
| Oznaka: TIC/MIC08.110; TIC/MIC08.208 | Code: TIC/MIC08.110; TIC/MIC08.208 | kpl | 2 |  | 0
8.42 | Prostorsko tipalo kvalitete zraka CO2, s pritrdilnim in tesnilnim materialom tipa: | Room air quality sensor CO2, with fixing and sealing material type:
| - območje CO2 od 0 do 2000ppm | - cO2 range from 0 to 2000ppm
| - izhodni signal 0 do 10V | - output signal 0 to 10V
| - izhodni signal MP-Bus | - mP-Bus output signal
| - zaščita IP30 | - iP30 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22RTM-19-1 | - BELIMO type 22RTM-19-1
| Oznaka: QIC08.501; QIC08.502; QIC08.503; QIC08.504; QIC08.505; QIC08.506 | Code: QIC08.501; QIC08.502; QIC08.503; QIC08.504; QIC08.505; QIC08.506 | kpl | 6 |  | 0
8.43 | Protizmrzovalni termostat, s pritrdilnim in tesnilnim materialom tipa: | Anti-freezing thermostat, with fixing and sealing material type:
| - območje od -10 do 15°C | - range -10 to 15°C
| - dolžina kapilare 6m | - capillary length 6m
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 01ATS-105XC | - BELIMO type 01ATS-105XC
| Oznaka: TSZAL08.104 | Code: TSZAL08.104 | kpl | 1 |  | 0
8.44 | Obtočna črpalka, elektronsko regulirana s frekvenčnim pretvornikom, tipalom diferenčnega tlaka, internimi hidravličnimi, električnimi in komunikacijskimi povezavami, PN10, material jeklena litina, skladnost z ErP, pritrdilnim in tesnilnim materialom tipa: | Circulation pump, electronically controlled with frequency converter, differential pressure sensor, internal hydraulic, electrical and communication connections, PN10, material cast steel, ErP compliant, type fastening and sealing material:
| - za obtok ogrevne vode 50/40°C | - for circulating heating water 50/40°C
| - za pretok V = 0,49m3/h, tlačna višina H = 1,7m | - for flow rate V = 0,49m3/h, pressure head H = 1,7m
| - možnost izbire delovanja črpalke na proporcionalni tlak ter optimizacijo delovne obratovalne točke | - option to select proportional pressure pump operation and optimise the operating point
| - napajanje Pel = 0,018kW, 230V / 50Hz | - power supply Pel = 0,018kW, 230V/50Hz
| - navojni priključek G 1 1/2 | - threaded connection G 1 1/2
| - tlačna stopnja PN10 | - pressure rating PN10
| - temperaturno območje ogrevnega medija od 2 do 110°C | - heating medium temperature range from 2 to 110°C
| - komunikacija s CNS RS485 | - communication with CNS RS485
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - GRUNDFOS tip ALPHA2 25-40 130 | - GRUNDFOS type ALPHA2 25-40 130
| Oznaka: P08.103 | Code: P08.103 | kpl | 1 |  | 0
8.45 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za ogrevno vodo 50/40°C | - for heating water 50/40°C
| - za pretok V = 0,49m3/h | - for a flow rate of V = 0,49 m3/h
| - območje regulacije pretoka do 900 l/h (0,900 m3/h) | - flow control range up to 900 l/h (0,900 m3/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - navojni priključek G 1 po ISO 228/1 | - threaded connection G 1 according to ISO 228/1
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 16 - 400 kPa, min. dif. tlak 16 kPa | - differential pressure range 16 - 400 kPa, min. differential pressure 16 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM20 | - DANFOS type AB-QM20
| Oznaka: VA08.103 | Code: VA08.103 | kpl | 1 |  | 0
8.46 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za hladilno vodo 9/14°C | - for cooling water 9/14°C
| - za pretok V = 0,72m3/h | - for a flow rate of V = 0,72m3/h
| - območje regulacije pretoka do 900 l/h (0,900 m3/h) | - flow control range up to 900 l/h (0,900 m3/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - navojni priključek G 1 po ISO 228/1 | - threaded connection G 1 according to ISO 228/1
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 16 - 400 kPa, min. dif. tlak 16 kPa | - differential pressure range 16 - 400 kPa, min. differential pressure 16 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM20 | - DANFOS type AB-QM20
| Oznaka: VA08.106 | Code: VA08.106 | kpl | 1 |  | 0
| PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS08 | VENTILATION AND AIR CONDITIONING SYSTEM KS08 |  |  |  | 0

## 4.4.9_PrKlim KS14
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.4 | STROJNA DELA | MECHANICAL WORKS
4.4.9 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS14 | VENTILATION AND AIR CONDITIONING SYSTEM KS14 |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
9 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS14 | VENTILATION AND AIR CONDITIONING SYSTEM KS14
9.1 | Klimatska naprava za dovod in odvod zraka KD14/KO14 - glej tudi zavihek Zahteve klimati. | KD14/KO14 supply and extract air conditioner - see also Climate requirements tab.
| Tehnične karakteristike naprave (opis v smeri toka zraka): | Technical characteristics of the appliance (description downstream):
| Dovod: Vdov = 17160 m3/h | Input: Vdov = 17160 m3/h
| - posluževanje dovod: desno v smeri toka zraka! | - inlet: right in the direction of the air flow!
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 10 60% po ISO 16890 (M5 po SIST EN 779), z regulacijsko žaluzijo 1695x1200x125, s fleksibilnim čelnim priključkom, za pretok zraka 17160m3/h. Maksimalni končni padec tlaka 200Pa. Oznaka: F14.102 | - Filter unit with bag filter cartridge of filtration level ePM 10 60% according to ISO 16890 (M5 according to SIST EN 779), with control shutter 1695x1200x125, with flexible front connection, for air flow 17160m3/h. Maximum final pressure drop 200Pa. Code: F14.102
| - Rotacijska regeneratorska enota za prenos senzibilne in latentne toplote. Tehnični podatki za zimsko obdobje: - pretok zraka 17160/16300m3/h - stopnja vračanja občutene toplote: 76,2% - stopnja vračanja latentne toplote: 77,5% - vračanje toplotne energije: 181,90kW - stanje dovodnega zr. pred enoto: -13,00°C/90,0% - stanje dovodnega zraka za enoto: 12,20°C/41,3% Tehnični podatki za poletno obdobje: - pretok zraka 17160/16300m3/h - stopnja vračanja občutene toplote: 76,2% - stopnja vračanja latentne toplote: 73,2% - vračanje toplotne energije: 50,30kW - stanje dovodnega zr. pred enoto: 34,50°C/40,0% - stanje dovodnega zraka za enoto: 28,00°C/54,5% Oznaka: RE14.191 | - Rotary regenerative unit for sensible and latent heat transfer. technical data for the winter period: - air flow 17160/16300m3/h - sensible heat recovery rate: 76.2% - latent heat recovery rate: 77.5% - heat energy recovery: 181.90kW - supply air condition upstream of the unit: -13.00°C/90.0% - supply air condition for the unit: 12.20°C/41.3% Technical data for the summer period: - air flow 17160/16300m3/h - sensible heat recovery rate: 76.2% - latent heat recovery rate: 73.2% - heat energy recovery: 50.30kW - supply air condition upstream of the unit: 34.50°C/40.0% - supply air condition for the unit: 28.00°C/54.5% Code: RE14.191
| - Enota pred-grelnika zraka s protizmrzovalno zaščito. - pretok zraka 17160m3/h - grelna moč Qg=99,92kW - temperaturni režim ogrevnega medija 50/40°C - pretok ogrevnega medija 8,69m3/h - padec tlaka na zračni strani 35Pa - temperatura zraka vstop 12,20°C - temperatura zraka izstop 29,50°C - padec tlaka na strani ogr. medija (voda) 13,94kPa - priključka navojna 2" - tlačna stopnja PN16 Oznaka: HE14.103 | - Air preheater unit with anti-freeze protection. - air flow 17160m3/h - heating power Qg=99,92kW - heating medium temperature 50/40°C - heating medium flow 8,69m3/h - air side pressure drop 35Pa - air temperature inlet 12,20°C - air temperature outlet 29,50°C - pressure drop on the heating medium side (water) 13,94kPa - 2" threaded connectors - pressure rating PN16 Code: HE14.103
| - Prazna enota. | - Empty unit.
| - Vlažilna enota s kontaktnim vlaženjem zraka. Dovod sveže pripravljene demineralizirane vode, z materialom kontaktnega vlažilnika impregniranim srebrom, črpalko, potrebno merilno regulacijsko opremo, ventili na dovodu sveže vode ter ventilom na odvodu vode iz banje, s funkcijo samodejnega praznjenja banje vlažilnika in polnjenja s svežo pripravljeno mehčano vodo glede na prevodnost vode v banji, oziroma glede na čas ko vlažilnik ni v funkciji. Odvod kondenzata s sifonom z vodno in mehansko smardno zaporo. - pretok zraka 17160m3/h - priključna električna moč 0,06kW, 3x400V, 50Hz - padec tlaka na zračni strani dpz=34Pa - temperatura zraka vstop 29,5°C - relativna vlaga zraka vstop 14,9% - temperatura zraka izstop 27,23°C - relativna vlaga izstop 21% - izkoristek vlaženja 14,36% - vlaženje 22,32 kg/h - tipalo prevodonsti vode QICCD14.105 - tipalo zgornjega nivoja vode LICH14.105 - tipalo spodnjega nivoja vode LICL14.105 - elektromagnetni ventil za praznenje VD14.105 - elektromagnetni ventil za dovod sveže vode VD14.205 Oznaka: SH14.105 | - Humidification unit with contact humidification. Freshly prepared demineralised water supply, with silver-impregnated contact humidifier material, pump, necessary metering control equipment, valves at the fresh water inlet and at the water outlet of the humidifier tank, with automatic emptying of the humidifier tank and refilling with freshly prepared softened water according to the conductivity of the water in the tank, or according to the time when the humidifier is not in operation. Condensate drainage with siphon with water and mechanical odour trap. - air flow 17160m3/h - connection power 0,06kW, 3x400V, 50Hz - pressure drop on the air side dpz=34Pa - air temperature 29,5°C - relative humidity 14.9% - air temperature outlet 27,23°C - relative humidity 21% exit - humidification efficiency 14.36% - humidification 22,32 kg/h - water conductivity sensor QICCD14.105 - lICH14.105 upper water level sensor - lICL14.105 lower water level sensor - solenoid valve for emptying VD14.105 - fresh water solenoid valve VD14.205 Code: SH14.105
| - Prazna enota. | - Empty unit.
| - Enota hladilnika z eliminatorjem kapljic in koritom za odvod kondenzata. - pretok zraka 17160m3/h - hladilna moč Qhtot=72,55kW - temperaturni režim hladilnega medija 9/14°C - pretok hladilnega medija 12,46m3/h - padec tlaka na zračni strani 58/52Pa - temperatura zraka vstop 28,00°C - temperatura zraka izstop 18,80°C - padec tlaka na strani hl. medija (voda) 21,28kPa - priključka navojna 2" - tlačna stopnja PN16 Oznaka: HE14.106 | - Refrigerator unit with drip eliminator and condensate drain. - air flow 17160m3/h - cooling power Qhtot=72,55kW - cooling medium temperature 9/14°C - coolant flow rate 12,46m3/h - pressure drop on the air side 58/52Pa - air temperature inlet 28,00°C - air temperature outlet 18,80°C - pressure drop on the medium side (water) 21,28kPa - 2" threaded connectors - pressure rating PN16 Code: HE14.106
| - Ventilatorska enota s prostotekočim rotorjem. Elektromotor je EC-motor, s 100% zvezno regulacijo vrtljajev preko potenciometra (0-10V), ki omogoča nastavitev delovanja ventilatorja na ustrezno delovno točko. Enota vsebuje: okence O150 in svetilko s stikalom ter servisno stikalo. - pretok zraka 17160m3/h - eksterni statični padec tlaka dpext=300Pa - priključna električna moč 2x4,60kW, 3x400V, 50Hz - razred izkoristka elektromotorja IE5/EC - zaščita IP55 Oznaka: FA14.107 | - Fan unit with free-flowing rotor. The electric motor is an EC motor, with 100% continuous speed control via a potentiometer (0-10V), which allows the fan to be set to the appropriate operating point. The unit contains: an O150 window and a lamp with switch and a service switch. - air flow 17160m3/h - external static pressure drop dpext=300Pa - connection power 2x4,60kW, 3x400V, 50Hz - electric motor efficiency class IE5/EC - iP55 protection Code: FA14.107
| - Dušilna enota. - pretok zraka 17160m3/h - padec tlaka dp=8Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 2 6 13 13 15 11 9 9 Oznaka: DZ14.108 | - Throttle unit. - air flow 17160m3/h - pressure drop dp=8Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 2 6 13 13 15 11 9 9 Code: DZ14.108
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 1 75% po ISO 16890 (F8 po SIST EN 779, s fleksibilnim čelnim priključkom, za pretok zraka 17160m3/h. Maksimalni končni padec tlaka 300Pa. Oznaka: F14.109 | - Filter unit with bag filter cartridge of filtration level ePM 1 75% according to ISO 16890 (F8 according to SIST EN 779, with flexible front connection, for air flow 17160m3/h. Maximum final pressure drop 300Pa. Code: F14.109
| Dolžina: 8,040m | Length: 8,040m
| Širina: 2.260m | Width: 2.260m
| Višina: 1,485m | Height: 1,485m
| Kompletno z dobavo dodatne opreme: | Complete with supply of accessories:
| - odtočni sifoni | - drain traps
| - jadrovinasti nastavki | - sailplane spouts
| - s spojnim, tesnilnim in pritrdilnim materialom in priključki za senzorje, | - with jointing, sealing and fixing materials and sensor connections,
| Odvod: Vodv = 16300 m3/h | Discharge: waterv = 16300 m3/h
| - posluževanje odvod: levo v smeri toka zraka! | - serving outlet: left in the direction of the air flow!
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 10 60% po ISO 16890 (M5 po SIST EN 779), s fleksibilnim čelnim priključkom, za pretok zraka 16300m3/h. Maksimalni končni padec tlaka 200Pa. Oznaka: F14.207 | - Filter unit with bag filter cartridge of filtration level ePM 10 60% according to ISO 16890 (M5 according to SIST EN 779), with flexible front connection, for an air flow of 16300m3/h. Maximum final pressure drop 200Pa. Code: F14.207
| - Dušilna enota. - pretok zraka 16300m3/h - padec tlaka dp=8Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 7 16 19 22 20 15 12 Oznaka: DZ14.206 | - Throttle unit. - air flow 16300m3/h - pressure drop dp=8Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 7 16 19 22 20 15 12 Code: DZ14.206
| - Ventilatorska enota s prostotekočim rotorjem. Elektromotor je EC-motor, s 100% zvezno regulacijo vrtljajev preko potenciometra (0-10V), ki omogoča nastavitev delovanja ventilatorja na ustrezno delovno točko. Enota vsebuje: okence O150 in svetilko s stikalom ter servisno stikalo. - pretok zraka 16300m3/h - eksterni statični padec tlaka dpext=300Pa - priključna električna moč 2x3,5kW, 3x4000V, 50Hz - razred izkoristka elektromotorja IE5/EC - zaščita IP55 Oznaka: FA14.205 | - Fan unit with free-flowing rotor. The electric motor is an EC motor, with 100% continuous speed control via a potentiometer (0-10V), which allows the fan to be set to the appropriate operating point. The unit contains: an O150 window and a lamp with switch and a service switch. - air flow 16300m3/h - external static pressure drop dpext=300Pa - power input 2x3,5kW, 3x4000V, 50Hz - electric motor efficiency class IE5/EC - iP55 protection Code: FA14.205
| - Dušilna enota. - pretok zraka 16300m3/h - padec tlaka dp=9Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 7 16 19 22 20 15 12 Oznaka: DZ14.204 | - Throttle unit. - air flow 16300m3/h - pressure drop dp=9Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 7 16 19 22 20 15 12 Code: DZ14.204
| - Prazna enota z regulacijsko žaluzijo 1205x785x125, fleksibilnim čelnim priključkom, za pretok zraka 16300m3/h. | - Empty unit with control louvre 1205x785x125, flexible front connection, for air flow 16300m3/h.
| Dolžina: 5,210m | Length: 5,210m
| Širina: 2,260m | Width: 2,260m
| Višina: 1,360m | Height: 1,360m
| Kompletno z dobavo dodatne opreme: | Complete with supply of accessories:
| - postavitvene noge, gumirane, višine 100-200mm | - rubberised feet, height 100-200mm
| - odtočni sifoni | - drain traps
| - jadrovinasti nastavki | - sailplane spouts
| - postavitev klimata na antivibracijski dušilnik (gumo) za preprečevanje prenosa vibracij in hrupa na konstrukcijo objekta. Dušilniki morajo biti preračunani glede na lastnosti klimata (teža in vrtilna frekvenca ventilatorjev). | - installation of the air conditioner on an anti-vibration damper (rubber) to prevent the transmission of vibrations and noise to the structure of the building. The dampers must be calculated according to the characteristics of the air conditioner (weight and speed of the fans).
| - s spojnim, tesnilnim in pritrdilnim materialom in priključki za senzorje, | - with jointing, sealing and fixing materials and sensor connections,
| Teža: 4069kg | Weight: 4069kg
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR | - SYSTEMAIR | kpl | 1 |  | 0
9.2 | Okrogli prezračevalni kanali izdelani iz pocinkane pločevine po SIST EN 1506, vključno z revizijskimi odprtinami, oblikovnimi kosi, debeline po standardu. V ceni na enoto (m) je potrebno upoštevati ves spojni in pritrdilni material (prirobnice, odrez, spone, vijaki, tesnila, ojačitve, vključno z obešalnim in pritrdilnim materialom sistemskega proizvajalca z lastnostmi odgovarjajoč zahtevam SIST EN 12236: 2002, vključno pleskanje vseh kovinskih korozijsko nezaščitenih delov, po temeljitem predhodnem čiščenju do kovinskega sijaja. Antikorozijska zaščita se izvaja v skladu z EN 12944 za naslednje pogoje: • Življenjska doba več kot 15 let. • Stopnja korozijske atmosfere C4 (visoka). | Round ventilation ducts made of galvanised sheet metal according to SIST EN 1506, including inspection openings, shaped pieces, thickness according to the standard. The unit price (m) must take into account all joining and fixing material (flanges, cut-offs, clamps, bolts, gaskets, reinforcements, including hanging and fixing material of the system manufacturer with properties according to the requirements of SIST EN 12236: 2002, including painting of all metal corrosion-protected parts, after thorough cleaning to a metallic gloss. The corrosion protection shall be carried out in accordance with EN12944, for the following conditions: - Lifetime over 15 years. - Corrosive atmosphere C4 (high).
| - Okrogli prezračevalni kanali Ø200 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø200 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 70 |  | 0
| - Okrogli prezračevalni kanali Ø225 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø225 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 60 |  | 0
| - Okrogli prezračevalni kanali Ø250 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø250 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 3 |  | 0
| - Okrogli prezračevalni kanali Ø280 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø280 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 30 |  | 0
| - Okrogli prezračevalni kanali Ø300 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø300 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 30 |  | 0
| - Okrogli prezračevalni kanali Ø315 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø315 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 4 |  | 0
| - Okrogli prezračevalni kanali Ø355 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø355 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 85 |  | 0
| - Okrogli prezračevalni kanali Ø400 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø400 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 2 |  | 0
| - Okrogli prezračevalni kanali Ø500 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø500 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 2 |  | 0
9.3 | Okrogli pregibni kanali za priključitev stropnih difuzorjev, izdelani iz Al folije ter polnila iz materiala z dušilnim in toplotno-izolativnim efektom. V ceni na enoto (m) je potrebno upoštevati ves spojni material, pritrdilne objemke in tesnilni material, za podatke: | Round folded ducts for the connection of ceiling diffusers, made of Al foil and filling material with damping and thermal insulation effect. The unit price (m) must include all joining material, fixing clamps and sealing material, for details:
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DEC tip: SONODEC - 25 | - DEC tip: SUNDAY - 25
| - Okroglegi pregibni kanali Ø200 | - Ø200 round flexible ducts | m | 75 |  | 0
9.4 | Pravokotni prezračevalni kanali izdelani iz pocinkane pločevine po SIST EN 1505:1999, debeline po DIN 24190, klase tesnosti B po SIST EN 1507:2006, vključno z revizijskimi odprtinami, oblikovnimi kosi. V ceni na enoto (m2) je potrebno upoštevati ves spojni in pritrdilni material (prirobnice, odrez, spone, vijaki, tesnila, usmerjevalniki, ojačitve, vključno z obešalnim in pritrdilnim materialom sistemskega proizvajalca z lastnostmi odgovarjajoč zahtevam SIST EN 12236: 2002, vključno pleskanje vseh kovinskih korozijsko nezaščitenih delov, po temeljitem predhodnem čiščenju do kovinskega sijaja. Antikorozijska zaščita se izvaja v skladu z EN 12944 za naslednje pogoje: • Življenjska doba več kot 15 let. • Stopnja korozijske atmosfere C4 (visoka). | Rectangular ventilation ducts made of galvanised sheet metal according to SIST EN 1505:1999, thickness according to DIN 24190, tightness class B according to SIST EN 1507:2006, including inspection openings, shaped pieces. The unit price (m2) must take into account all joining and fixing material (flanges, cut-off, clamps, bolts, gaskets, guides, reinforcements, including hanging and fixing material of the system manufacturer with properties according to the requirements of SIST EN 12236:2002, including the painting of all metal corrosion-protected parts, after thorough preliminary cleaning to a metallic gloss. The anticorrosive protection shall be performed in accordance with EN12944 for the following conditions: - Lifetime over 15 years. - Corrosive atmosphere C4 (high). | m2 | 910 |  | 0
9.5 | Toplotna izolacija zajemnih, izpušnih ter vtočnih kanalov s parozapornimi ploščami izdelanimi iz sintetičnega kavčuka z zaprto celično strukturo, toplotne prevodnosti manjše ali enake 0,033W/mK pri srednji temperaturi 0 °C, koeficient upora difuziji vodene pare večji ali enak 10000 testirano v skladu z EN 13469 za cevi in EN 12086 za plošče, požarna klasifikacija B/BL-s3,d0 po DIN 4102, oziroma po SIST EN 13501-1. | Thermal insulation of intake, exhaust and inlet ducts with vapour control panels made of synthetic rubber with closed cell structure, thermal conductivity less than or equal to 0,033 W/mK at a mean temperature of 0 °C, resistance coefficient to diffusion of water vapour greater than or equal to 10000 tested in accordance with EN 13469 for pipes and EN 12086 for panels, fire classification B/BL-s3,d0 according to DIN 4102, or according to SIST EN 13501-1.
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - ARMACELL tip: Armaflex AF | - ARMACELL tip: Armaflex AF
| Toplotna izolacija zunanjih kanalov na vtočni strani (VTZ-SUP), debeline s = 50 mm, + original lepilo, + 0,8mm Al pločevine | Thermal insulation of external ducts on the inlet side (VTZ-SUP), thickness s = 50 mm, + original adhesive, + 0.8 mm Al sheet | m2 | 15 |  | 0
| Toplotna izolacija zunanjih kanalov na odtočni strani (ODZ-ETA), debeline s = 50 mm, + original lepilo, + 0,8mm Al pločevine | Thermal insulation of external ducts on the drain side (ODZ-ETA), thickness s = 50 mm, + original adhesive, + 0.8 mm Al sheet | m2 | 35 |  | 0
| Toplotna izolacija notranjih kanalov na vtočni strani (VTZ-SUP), debeline s = 19 mm, + original lepilo | Thermal insulation of internal ducts on the inlet side (VTZ-SUP), thickness s = 19 mm, + original adhesive | m2 | 1170 |  | 0
9.6 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, sound and heat insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to customer's or architect's preference, with connection chamber, with control damper, with connections for air flow measurement, inlet connection of the prepared air is provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø597, H=287, Ø200 | - dimensions Ø597, H=287, Ø200
| - pretok q = 310 m3/h | - flow rate q = 310 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-C-200 | - SYSTEMAIR tip CAP-C-200
| Oznaka: / | Tag: / | kpl | 20 |  | 0
9.7 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, sound and heat insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to customer's or architect's preference, with connection chamber, with control damper, with connections for air flow measurement, inlet connection of the prepared air is provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø597, H=287, Ø200 | - dimensions Ø597, H=287, Ø200
| - pretok q = 255/250 m3/h | - flow rate q = 255/250 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-C-200 | - SYSTEMAIR tip CAP-C-200
| Oznaka: / | Tag: / | kpl | 18 |  | 0
9.8 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, sound and heat insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to the customer's or architect's preference, with connection chamber, with control damper, with connections for air flow measurement, inlet connection of the prepared air is provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø597, H=287, Ø200 | - dimensions Ø597, H=287, Ø200
| - pretok q = 345/340 m3/h | - flow rate q = 345/340 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-C-200 | - SYSTEMAIR tip CAP-C-200
| Oznaka: / | Tag: / | kpl | 8 |  | 0
9.9 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, soundproof and thermally insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to customer's or architect's preference, with connection chamber, with control damper, with connections for air flow measurement, inlet connection of the prepared air to be provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø597, H=287, Ø200 | - dimensions Ø597, H=287, Ø200
| - pretok q = 410/400 m3/h | - flow rate q = 410/400 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-C-200 | - SYSTEMAIR tip CAP-C-200
| Oznaka: / | Tag: / | kpl | 9 |  | 0
9.10 | Rešetka za odvod zraka, izdelana iz aluminijskih profilov, sestavljena iz nosilnega okvirja z vodoravnim in navpičnim fiksnim lamelam, dodatkom za nastavitev količine zraka, pritrditev rešetke na prezračevalni kanal, z ugradim okvirjem, vključno z vsem pritrdilnim in montažnim materialom, barva v skladu z zahtevam načrta arhitekture, tipa: | Air outlet grille made of aluminium profiles, consisting of a support frame with horizontal and vertical fixed slats, air volume adjustment accessory, grille attachment to the ventilation duct, with a framed frame, including all fixing and mounting material, colour in accordance with the requirements of the architectural plan, type:
| - dimenzije B=1000/H=500 | - dimensions B=1000/H=500
| - pretok q = 1735 m3/h | - flow rate q = 1735 m3/h
| - prost prerez Aef=0,441 m2 | - free cross-section Aef=0,441 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-E-2-1000x500-R1 | - SYSTEMAIR tip NOVA-E-2-1000x500-R1
| Oznaka: / | Tag: / | kpl | 2 |  | 0
9.11 | Rešetka za odvod zraka, izdelana iz aluminijskih profilov, sestavljena iz nosilnega okvirja z vodoravnim in navpičnim fiksnim lamelam, dodatkom za nastavitev količine zraka, pritrditev rešetke na prezračevalni kanal, z ugradim okvirjem, vključno z vsem pritrdilnim in montažnim materialom, barva v skladu z zahtevam načrta arhitekture, tipa: | Air outlet grille made of aluminium profiles, consisting of a support frame with horizontal and vertical fixed slats, air volume adjustment accessory, grille attachment to the ventilation duct, with a framed frame, including all fixing and mounting material, colour in accordance with the requirements of the architectural plan, type:
| - dimenzije B=1200/H=500 | - dimensions B=1200/H=500
| - pretok q = 2630 m3/h | - flow rate q = 2630 m3/h
| - prost prerez Aef=0,531 m2 | - free cross-section Aef=0,531 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-E-2-1200x500-R1 | - SYSTEMAIR tip NOVA-E-2-1200x500-R1
| Oznaka: / | Tag: / | kpl | 1 |  | 0
9.12 | Rešetka za odvod zraka, izdelana iz aluminijskih profilov, sestavljena iz nosilnega okvirja z vodoravnim in navpičnim fiksnim lamelam, dodatkom za nastavitev količine zraka, pritrditev rešetke na prezračevalni kanal, z ugradim okvirjem, vključno z vsem pritrdilnim in montažnim materialom, barva v skladu z zahtevam načrta arhitekture, tipa: | Air outlet grille made of aluminium profiles, consisting of a support frame with horizontal and vertical fixed slats, air volume adjustment accessory, grille attachment to the ventilation duct, with a framed frame, including all fixing and mounting material, colour in accordance with the requirements of the architectural plan, type:
| - dimenzije B=1200/H=500 | - dimensions B=1200/H=500
| - pretok q = 4310 m3/h | - flow rate q = 4310 m3/h
| - prost prerez Aef=0,531 m2 | - free cross-section Aef=0,531 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-E-2-1200x500-R1 | - SYSTEMAIR tip NOVA-E-2-1200x500-R1
| Oznaka: / | Tag: / | kpl | 1 |  | 0
9.13 | Rešetka za odvod zraka, izdelana iz aluminijskih profilov, sestavljena iz nosilnega okvirja z vodoravnim in navpičnim fiksnim lamelam, dodatkom za nastavitev količine zraka, pritrditev rešetke na prezračevalni kanal, z ugradim okvirjem, vključno z vsem pritrdilnim in montažnim materialom, barva v skladu z zahtevam načrta arhitekture, tipa: | Air outlet grille made of aluminium profiles, consisting of a support frame with horizontal and vertical fixed slats, air volume adjustment accessory, grille attachment to the ventilation duct, with a framed frame, including all fixing and mounting material, colour in accordance with the requirements of the architectural plan, type:
| - dimenzije B=1200/H=500 | - dimensions B=1200/H=500
| - pretok q = 2945 m3/h | - flow rate q = 2945 m3/h
| - prost prerez Aef=0,531 m2 | - free cross-section Aef=0,531 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-E-2-1200x500-R1 | - SYSTEMAIR tip NOVA-E-2-1200x500-R1
| Oznaka: / | Tag: / | kpl | 2 |  | 0
9.14 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study with fastening and sealing material type:
| - dimenzije B=1100/H=400 | - dimensions B=1100/H=400
| - pretok q = 6200 m3/h | - flow rate q = 6200 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-1100x400 | - SYSTEMAIR tip FDS-3G-1100x400
| Oznaka: KFD14.071 | Code: KFD14.071 | kpl | 1 |  | 0
9.15 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study with fastening and sealing material type:
| - dimenzije B=1100/H=400 | - dimensions B=1100/H=400
| - pretok q = 5890 m3/h | - flow rate q = 5890 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-1100x400 | - SYSTEMAIR tip FDS-3G-1100x400
| Oznaka: KFD14.081 | Code: KFD14.081 | kpl | 1 |  | 0
9.16 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study with fastening and sealing material type:
| - dimenzije B=800/H=350 | - dimensions B=800/H=350
| - pretok q = 4540 m3/h | - flow rate q = 4540 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-800x350 | - SYSTEMAIR tip FDS-3G-800x350
| Oznaka: KFD14.171 | Code: KFD14.171 | kpl | 1 |  | 0
9.17 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study with fastening and sealing material type:
| - dimenzije B=800/H=350 | - dimensions B=800/H=350
| - pretok q = 4310 m3/h | - flow rate q = 4310 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-800x350 | - SYSTEMAIR tip FDS-3G-800x350
| Oznaka: KFD14.181 | Code: KFD14.181 | kpl | 1 |  | 0
9.18 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study with fastening and sealing material type:
| - dimenzije B=550/H=350 | - dimensions B=550/H=350
| - pretok q = 2770 m3/h | - flow rate q = 2770 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-550x350 | - SYSTEMAIR tip FDS-3G-550x350
| Oznaka: KFD14.271 | Code: KFD14.271 | kpl | 1 |  | 0
9.19 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study with fastening and sealing material type:
| - dimenzije B=500/H=400 | - dimensions B=500/H=400
| - pretok q = 2630 m3/h | - flow rate q = 2630 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-500x400 | - SYSTEMAIR tip FDS-3G-500x400
| Oznaka: KFD14.281 | Code: KFD14.281 | kpl | 1 |  | 0
9.20 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study with fastening and sealing material type:
| - dimenzije B=700/H=350 | - dimensions B=700/H=350
| - pretok q = 3650 m3/h | - flow rate q = 3650 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-700x350 | - SYSTEMAIR tip FDS-3G-700x350
| Oznaka: KFD14.371 | Code: KFD14.371 | kpl | 1 |  | 0
9.21 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije B=650/H=350 | - dimensions B=650/H=350
| - pretok q = 3470 m3/h | - flow rate q = 3470 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-650x350 | - SYSTEMAIR tip FDS-3G-650x350
| Oznaka: KFD14.381 | Code: KFD14.381 | kpl | 1 |  | 0
9.22 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije 500x250 | - dimensions 500x250
| - pretok q = 3100 do 1025m3/h | - flow rate q = 3100 to 1025m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-SI-FC-500x250 | - SYSTEMAIR tip OPTIMA-SI-FC-500x250
| Oznaka: VAV14.001; VAV14.002 | Code: VAV14.001; VAV14.002 | kpl | 2 |  | 0
9.23 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije 550x400 | - dimensions 550x400
| - pretok q = 5890 do 1950m3/h | - flow rate q = 5890 to 1950m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-SI-FC-550x400 | - SYSTEMAIR tip OPTIMA-SI-FC-550x400
| Oznaka: VAV14.021 | Code: VAV14.021 | kpl | 1 |  | 0
9.24 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø250 | - dimensions Ø250
| - pretok q = 1000 do 320m3/h | - flow rate q = 1000 to 320m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-250 | - SYSTEMAIR tip OPTIMA-LV-RI-250
| Oznaka: VAV14.101; VAV14.102 | Code: VAV14.101; VAV14.102 | kpl | 2 |  | 0
9.25 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø315 | - dimensions Ø315
| - pretok q = 1270 do 430m3/h | - flow rate q = 1270 to 430m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-315 | - SYSTEMAIR tip OPTIMA-LV-RI-315
| Oznaka: VAV14.103; VAV14.104 | Code: VAV14.103; VAV14.104 | kpl | 2 |  | 0
9.26 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije 500x350 | - dimensions 500x350
| - pretok q = 4310 do 1430m3/h | - flow rate q = 4310 to 1430m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-SI-FC-500x350 | - SYSTEMAIR tip OPTIMA-SI-FC-500x350
| Oznaka: VAV14.121 | Code: VAV14.121 | kpl | 1 |  | 0
9.27 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije 350x350 | - dimensions 350x350
| - pretok q = 2770 do 920m3/h | - flow rate q = 2770 to 920m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-SI-FC-350x350 | - SYSTEMAIR tip OPTIMA-SI-FC-350x350
| Oznaka: VAV14.201 | Code: VAV14.201 | kpl | 1 |  | 0
9.28 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function and type fastening and sealing material:
| - dimenzije Ø400 | - ø400 dimensions
| - pretok q = 2630 do 870m3/h | - flow rate q = 2630 to 870m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-400 | - SYSTEMAIR tip OPTIMA-LV-RI-400
| Oznaka: VAV14.221 | Code: VAV14.221 | kpl | 1 |  | 0
9.29 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function and type fastening and sealing material:
| - dimenzije 400x350 | - dimensions 400x350
| - pretok q = 3650 do 1210m3/h | - flow rate q = 3650 to 1210m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-SI-FC-400x350 | - SYSTEMAIR tip OPTIMA-SI-FC-400x350
| Oznaka: VAV14.301 | Code: VAV14.301 | kpl | 1 |  | 0
9.30 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function and type fastening and sealing material:
| - dimenzije 400x350 | - dimensions 400x350
| - pretok q = 3470 do 1150m3/h | - flow rate q = 3470 to 1150m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-SI-FC-400x350 | - SYSTEMAIR tip OPTIMA-SI-FC-400x350
| Oznaka: VAV14.321 | Code: VAV14.321 | kpl | 1 |  | 0
9.31 | Elektromotorni pogon z vzmetjo za vstopno/izstopno žaluzijo klimata, vključno z varnostno funkcijo (NC) in stikali položaja, s pritrdilnim in tesnilnim materialom tipa: | Electric motor drive with spring for air-conditioning inlet/outlet blind, including safety function (NC) and position switches, with fixing and sealing material type:
| - navor 10Nm | - torque 10Nm
| - električno napajanje 24V AC/DC | - 24V AC/DC power supply
| - ON/OFF regulacija delovanja | - ON/OFF operation control
| - za žaluzije do 2m2 | - for blinds up to 2m2
| - zaščita IP54 | - iP54 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip NF24A-S2 | - BELIMO type NF24A-S2
| Oznaka: KD14.101; KD14.202 | Code: KD14.101; KD14.202 | kpl | 2 |  | 0
9.32 | Kanalsko tipalo diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Duct differential pressure sensor, with type fastening and sealing material:
| - območje prikazovanja od 0 do 1500 Pa | - display range 0 to 1500 Pa
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22ADP-184A | - BELIMO type 22ADP-184A
| Oznaka: PICAL14.112; PICAL14.212 | Code: PICAL14.112; PICAL14.212 | kpl | 2 |  | 0
9.33 | Tipalo diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure sensor, with type fastening and sealing material:
| - območje prikazovanja od 0 do 1500 Pa | - display range 0 to 1500 Pa
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22ADP-184A | - BELIMO type 22ADP-184A
| Oznaka: PDIC14.107; PDIC14.205 | Code: PDIC14.107; PDIC14.205 | kpl | 2 |  | 0
9.34 | Diferenčno tlačno stikalo, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure switch, with type fastening and sealing material:
| - območje prikazovanja od 50 do 500Pa | - display range 50 to 500Pa
| - kontaktni tok maksimalno 1,0A / AC 250V | - contact current max 1.0A / AC 250V
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 01APS-10U | - BELIMO type 01APS-10U
| Oznaka: PDSAH14.102; PDSAH14.109; PDSAH14.203; PDSAH14.207 | Code: PDSAH14.102; PDSAH14.109; PDSAH14.203; PDSAH14.207 | kpl | 4 |  | 0
9.35 | Prikazovalnik diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure indicator, with type fixing and sealing material:
| - območje prikazovanja od 50 do 500Pa | - display range 50 to 500Pa
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DWYER tip Magnahelic | - DWYER tip Magnahelic
| Oznaka: PDI14.102; PDI14.109; PDI14.203; PDI14.207 | Code: PDI14.102; PDI14.109; PDI14.203; PDI14.207 | kpl | 4 |  | 0
9.36 | Zunanje tipalo temperature in vlage, s pritrdilnim in tesnilnim materialom tipa: | External temperature and humidity sensor, with fixing and sealing material type:
| - območje prikazovanja od 0 do 100%RH | - display range 0 to 100%RH
| - območje prikazovanja od -40 do 60°C | - display range -40 to 60°C
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22UTH-13M | - BELIMO type 22UTH-13M
| Oznaka: TIC/MIC14.100 | Code: TIC/MIC14.100 | kpl | 1 |  | 0
9.37 | Kanalsko tipalo temperature in vlage, s pritrdilnim in tesnilnim materialom tipa: | Duct temperature and humidity sensor, with fixing and sealing material type:
| - območje prikazovanja od 0 do 100%RH | - display range 0 to 100%RH
| - območje prikazovanja od -40 do 60°C | - display range -40 to 60°C
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22DTH-13M | - BELIMO type 22DTH-13M
| Oznaka: TIC/MIC14.110; TIC/MIC14.208 | Code: TIC/MIC14.110; TIC/MIC14.208 | kpl | 2 |  | 0
9.38 | Kanalsko tipalo kvalitete zraka CO2, s pritrdilnim in tesnilnim materialom tipa: | Duct air quality sensor CO2, with fixing and sealing material type:
| - območje CO2 od 0 do 2000ppm | - cO2 range 0 to 2000ppm
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 0 do 10V | - output signal 0 to 10V
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22DC-13 | - BELIMO type 22DC-13
| Oznaka: QIC14.021; QIC14.121; QIC14.221; QIC14.321 | Code: QIC14.021; QIC14.121; QIC14.221; QIC14.321 | kpl | 4 |  | 0
9.39 | Protizmrzovalni termostat, s pritrdilnim in tesnilnim materialom tipa: | Anti-freezing thermostat, with fixing and sealing material type:
| - območje od -10 do 15°C | - range -10 to 15°C
| - dolžina kapilare 6m | - capillary length 6m
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 01ATS-105XC | - BELIMO type 01ATS-105XC
| Oznaka: TSZAL14.104 | Code: TSZAL14.104 | kpl | 1 |  | 0
9.40 | Obtočna črpalka, elektronsko regulirana s frekvenčnim pretvornikom, tipalom diferenčnega tlaka, internimi hidravličnimi, električnimi in komunikacijskimi povezavami, PN10, material jeklena litina, skladnost z ErP, pritrdilnim in tesnilnim materialom tipa: | Circulation pump, electronically controlled with frequency converter, differential pressure sensor, internal hydraulic, electrical and communication connections, PN10, material cast steel, ErP compliant, type fastening and sealing material:
| - za obtok ogrevne vode 50/40°C | - for circulating heating water 50/40°C
| - za pretok V = 8,69m3/h, tlačna višina H = 2,4m | - for flow rate V = 8,69m3/h, pressure head H = 2,4m
| - možnost izbire delovanja črpalke na proporcionalni tlak ter optimizacijo delovne obratovalne točke | - option to select proportional pressure pump operation and optimise the operating point
| - napajanje Pel = 0,185kW, 230V / 50Hz | - power supply Pel = 0,185kW, 230V/50Hz
| - navojni priključek G 1 1/2 | - threaded connection G 1 1/2
| - tlačna stopnja PN10 | - pressure rating PN10
| - temperaturno območje ogrevnega medija od -10 do 110°C | - temperature range of the heating medium from -10 to 110°C
| - komunikacija s CNS RS485 | - communication with CNS RS485
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - GRUNDFOS tip MAGNA3 25-120 | - GRUNDFOS type MAGNA3 25-120
| Oznaka: P14.103 | Code: P14.103 | kpl | 1 |  | 0
9.41 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za ogrevno vodo 50/40°C | - for heating water 50/40°C
| - za pretok V = 8,69m3/h | - for a flow rate of V = 8,69m3/h
| - območje regulacije pretoka do 12500 l/h (12,500 m3/h) | - flow control range up to 12,500 m3/h (12,500 l/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - navojni priključek G 2 1/2" po ISO 228/1 | - threaded connection G 2 1/2" to ISO 228/1
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 30 - 400 kPa, min. dif. tlak 30 kPa | - differential pressure range 30 - 400 kPa, min. differential pressure 30 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM50 | - DANFOS type AB-QM50
| Oznaka: VA14.103 | Code: VA14.103 | kpl | 1 |  | 0
9.42 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za hladilno vodo 9/14°C | - for cooling water 9/14°C
| - za pretok V = 12,46m3/h | - for a flow rate of V = 12,46m3/h
| - območje regulacije pretoka do 2000 l/h (20,000 m3/h) | - flow control range up to 2000 l/h (20,000 m3/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - prirobnični priključek DN65 | - flange connection DN65
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 30 - 400 kPa, min. dif. tlak 30 kPa | - differential pressure range 30 - 400 kPa, min. differential pressure 30 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM65 | - DANFOS type AB-QM65
| Oznaka: VA14.106 | Code: VA14.106 | kpl | 1 |  | 0
| PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS14 | VENTILATION AND AIR CONDITIONING SYSTEM KS14 |  |  |  | 0

## 4.4.10_PrKlim KS15
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.4 | STROJNA DELA | MECHANICAL WORKS
4.4.10 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS15 | VENTILATION AND AIR CONDITIONING SYSTEM KS15 |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
10 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS15 | VENTILATION AND AIR CONDITIONING SYSTEM KS15
10.1 | Klimatska naprava za dovod in odvod zraka KD15/KO15 - glej tudi zavihek Zahteve klimati. | KD15/KO15 supply and extract air conditioner - see also Climate requirements tab.
| Tehnične karakteristike naprave (opis v smeri toka zraka): | Technical characteristics of the appliance (description downstream):
| Dovod: Vdov = 1980 m3/h | Input: Vdov = 1980 m3/h
| - posluževanje dovod: horizontalna izvedba levo in desno v smeri toka zraka! | - inlet: horizontal left and right in the direction of the air flow!
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 10 60% po ISO 16890 (M5 po SIST EN 779), z regulacijsko žaluzijo 475x495x125, s fleksibilnim čelnim priključkom, za pretok zraka 1980m3/h. Maksimalni končni padec tlaka 200Pa. Oznaka: F15.102 | - Filter unit with bag filter cartridge of filtration level ePM 10 60% according to ISO 16890 (M5 according to SIST EN 779), with control shutter 475x495x125, with flexible front connection, for air flow 1980m3/h. Maximum final pressure drop 200Pa. Code: F15.102
| - Dušilna enota. - pretok zraka 1980m3/h - padec tlaka dp=11Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 7 17 18 21 15 11 12 Oznaka: DZ15.103 | - Throttle unit. - air flow 1980m3/h - pressure drop dp=11Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 7 17 18 21 15 11 12 Code: DZ15.103
| - Ventilatorska enota s prostotekočim rotorjem. Elektromotor je EC-motor, s 100% zvezno regulacijo vrtljajev preko potenciometra (0-10V), ki omogoča nastavitev delovanja ventilatorja na ustrezno delovno točko. Enota vsebuje: okence O150 in svetilko s stikalom ter servisno stikalo. - pretok zraka 1980m3/h - eksterni statični padec tlaka dpext=300Pa - priključna električna moč 2.4kW, 3x400V, 50Hz - razred izkoristka elektromotorja IE5/EC - zaščita IP55 Oznaka: FA15.104 | - Fan unit with free-flowing rotor. The electric motor is an EC motor, with 100% continuous speed control via a potentiometer (0-10V), which allows the fan to be set to the appropriate operating point. The unit contains: an O150 window and a lamp with switch and a service switch. - air flow 1980m3/h - external static pressure drop dpext=300Pa - connection power 2.4kW, 3x400V, 50Hz - electric motor efficiency class IE5/EC - iP55 protection Code: FA15.104
| - Ploščni rekuperator za prenos senzibilne toplote z el. motorno regulacijsko žaluzijo za obtok zraka (protizmrzovalna zaščita). Tehnični podatki za zimsko obdobje: - pretok zraka 1980/1980m3/h - stopnja vračanja občutene toplote: 78,8% - vračanje toplotne energije: 18,78kW - stanje dovodnega zr. pred enoto: -13,00°C/90,0% - stanje dovodnega zraka za enoto: 15,30°C/10,0% Tehnični podatki za poletno obdobje: - pretok zraka 1980/1980m3/h - stopnja vračanja občutene toplote: 81,6% - vračanje toplotne energije: 4,61kW - stanje dovodnega zr. pred enoto: 34,50°C/40,0% - stanje dovodnega zraka za enoto: 27,60°C/59% Oznaka: RE15.106 | - Sensible heat transfer plate recuperator with electric motor-controlled air circulation louvre (frost protection). technical data for the winter period: - air flow 1980/1980m3/h - sensible heat recovery rate: 78.8% - heat energy recovery: 18.78kW - supply air condition upstream of the unit: -13.00°C/90.0% - supply air condition for the unit: 15.30°C/10.0% Technical data for the summer period: - air flow 1980/1980m3/h - sensible heat recovery rate: 81.6% - heat energy recovery: 4.61kW - supply air condition upstream of the unit: 34.50°C/40.0% - supply air condition for the unit: 27.60°C/59% Code: RE15.106
| - Enota pred-grelnika zraka s protizmrzovalno zaščito. - pretok zraka 1980m3/h - grelna moč Qg=13,73kW - temperaturni režim ogrevnega medija 50/40°C - pretok ogrevnega medija 1,19m3/h - padec tlaka na zračni strani 98Pa - temperatura zraka vstop 15,30°C - temperatura zraka izstop 36,00°C - padec tlaka na strani ogr. medija (voda) 8,19kPa - priključka navojna 3/4" - tlačna stopnja PN16 Oznaka: HE15.107 | - Air preheater unit with anti-freeze protection. - air flow 1980m3/h - heating power Qg=13,73kW - heating medium temperature 50/40°C - heating medium flow 1,19m3/h - air-side pressure drop 98Pa - air temperature inlet 15,30°C - air temperature outlet 36,00°C - pressure drop on the heating medium side (water) 8,19kPa - 3/4" threaded connectors - pressure rating PN16 Code: HE15.107
| - Prazna enota. | - Empty unit.
| - Vlažilna enota s kontaktnim vlaženjem zraka. Dovod sveže pripravljene demineralizirane vode, z materialom kontaktnega vlažilnika impregniranim srebrom, črpalko, potrebno merilno regulacijsko opremo, ventili na dovodu sveže vode ter ventilom na odvodu vode iz banje, s funkcijo samodejnega praznjenja banje vlažilnika in polnjenja s svežo pripravljeno mehčano vodo glede na prevodnost vode v banji, oziroma glede na čas ko vlažilnik ni v funkciji. Odvod kondenzata s sifonom z vodno in mehansko smardno zaporo. - pretok zraka 1980m3/h - priključna električna moč 0,05kW, 230V, 50Hz - padec tlaka na zračni strani dpz=144Pa - temperatura zraka vstop 36°C - relativna vlaga zraka vstop 2,9% - temperatura zraka izstop 26,98°C - relativna vlaga izstop 21% - izkoristek vlaženja 40% - vlaženje 19,8 kg/h - tipalo prevodonsti vode QICCD15.109 - tipalo zgornjega nivoja vode LICH15.109 - tipalo spodnjega nivoja vode LICL15.109 - elektromagnetni ventil za praznenje VD15.109 - elektromagnetni ventil za dovod sveže vode VD15.209 Oznaka: SH15.109 | - Humidification unit with contact humidification. Freshly prepared demineralised water supply, with silver-impregnated contact humidifier material, pump, necessary metering control equipment, valves at the fresh water inlet and at the water outlet of the humidifier tank, with automatic emptying of the humidifier tank and refilling with freshly prepared softened water according to the conductivity of the water in the tank, or according to the time when the humidifier is not in operation. Condensate drainage with siphon with water and mechanical odour trap. - air flow 1980m3/h - connection power 0,05kW, 230V, 50Hz - pressure drop on the air side dpz=144Pa - air temperature inlet 36°C - relative humidity inlet 2.9% - air temperature outlet 26,98°C - relative humidity 21% exit - humidification efficiency 40% - humidification 19,8 kg/h - water conductivity sensor QICCD15.109 - lICH15.109 upper water level sensor - lICL15.109 lower water level sensor - solenoid valve for emptying VD15.109 - fresh water solenoid valve VD15.209 Code: SH15.109
| - Prazna enota. | - Empty unit.
| - Enota hladilnika z eliminatorjem kapljic in koritom za odvod kondenzata. - pretok zraka 1980m3/h - hladilna moč Qhtot=9,1kW - temperaturni režim hladilnega medija 9/14°C - pretok hladilnega medija 1,56m3/h - padec tlaka na zračni strani 105/92Pa - temperatura zraka vstop 27,60°C - temperatura zraka izstop 18,50°C - padec tlaka na strani hl. medija (voda) 23,54kPa - priključka navojna 3/4" - tlačna stopnja PN16 Oznaka: HE15.110 | - Refrigerator unit with drip eliminator and condensate drain. - air flow 1980m3/h - cooling power Qhtot=9,1kW - cooling medium temperature 9/14°C - coolant flow 1,56m3/h - air side pressure drop 105/92Pa - air temperature inlet 27,60°C - air temperature outlet 18,50°C - pressure drop on the medium side (water) 23,54kPa - 3/4" threaded connectors - pressure rating PN16 Code: HE15.110
| - Dušilna enota. - pretok zraka 1980m3/h - padec tlaka dp=11Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 7 17 18 21 15 11 12 Oznaka: DZ15.111 | - Throttle unit. - air flow 1980m3/h - pressure drop dp=11Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 7 17 18 21 15 11 12 Code: DZ15.111
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 1 75% po ISO 16890 (F8 po SIST EN 779, s fleksibilnim čelnim priključkom, za pretok zraka 1980m3/h. Maksimalni končni padec tlaka 300Pa. Oznaka: F15.112 | - Filter unit with bag filter cartridge of filtration level ePM 1 75% according to ISO 16890 (F8 according to SIST EN 779, with flexible front connection, for air flow 1980m3/h. Maximum final pressure drop 300Pa. Code: F15.112
| Dolžina: 9,070m | Length: 9,070m
| Širina: 0,750m | Width: 0.750m
| Višina: 0,775m | Height: 0,775m
| Kompletno z dobavo dodatne opreme: | Complete with supply of accessories:
| - odtočni sifoni | - drain traps
| - jadrovinasti nastavki | - sailplane spouts
| - s spojnim, tesnilnim in pritrdilnim materialom in priključki za senzorje, | - with jointing, sealing and fixing materials and sensor connectors,
| Odvod: Vodv = 1980 m3/h | Discharge: waterv = 1980 m3/h
| - posluževanje odvod: horizontalna izvedba desno in levo v smeri toka zraka! | - venting: horizontal right and left in the direction of the air flow!
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 10 60% po ISO 16890 (M5 po SIST EN 779), s fleksibilnim čelnim priključkom, za pretok zraka 1980m3/h. Maksimalni končni padec tlaka 200Pa. Oznaka: F15.207 | - Filter unit with bag filter cartridge of filtration level ePM 10 60% according to ISO 16890 (M5 according to SIST EN 779), with flexible front connection, for an air flow of 1980m3/h. Maximum final pressure drop 200Pa. Code: F15.207
| - Dušilna enota. - pretok zraka 1980m3/h - padec tlaka dp=11Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 7 17 18 21 15 11 12 Oznaka: DZ15.206 | - Throttle unit. - air flow 1980m3/h - pressure drop dp=11Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 7 17 18 21 15 11 12 Code: DZ15.206
| - Ventilatorska enota s prostotekočim rotorjem. Elektromotor je EC-motor, s 100% zvezno regulacijo vrtljajev preko potenciometra (0-10V), ki omogoča nastavitev delovanja ventilatorja na ustrezno delovno točko. Enota vsebuje: okence O150 in svetilko s stikalom ter servisno stikalo. - pretok zraka 1980m3/h - eksterni statični padec tlaka dpext=300Pa - priključna električna moč 0,76kW, 230V, 50Hz - razred izkoristka elektromotorja IE4/EC - zaščita IP54 Oznaka: FA15.204 | - Fan unit with free-flowing rotor. The electric motor is an EC motor, with 100% continuous speed control via a potentiometer (0-10V), which allows the fan to be set to the appropriate operating point. The unit contains: an O150 window and a lamp with switch and a service switch. - air flow 1980m3/h - external static pressure drop dpext=300Pa - connection power 0,76kW, 230V, 50Hz - electric motor efficiency class IE4/EC - iP54 protection Code: FA15.204
| - Dušilna enota. - pretok zraka 1980m3/h - padec tlaka dp=11Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 7 17 18 21 15 11 12 Oznaka: DZ15.203 | - Throttle unit. - air flow 1980m3/h - pressure drop dp=11Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 7 17 18 21 15 11 12 Code: DZ15.203
| - Prazna enota z regulacijsko žaluzijo 495x145x125, fleksibilnim čelnim priključkom, za pretok zraka 1980m3/h. | - Empty unit with control louvre 495x145x125, flexible front connection, for air flow 1980m3/h.
| Dolžina: 5,410m | Length: 5,410m
| Širina: 0,750m | Width: 0,750m
| Višina: 0,775m | Height: 0,775m
| Kompletno z dobavo dodatne opreme: | Complete with supply of accessories:
| - postavitvene noge, gumirane, višine 100-200mm | - rubberised feet, height 100-200mm
| - odtočni sifoni | - drain traps
| - jadrovinasti nastavki | - sailplane spouts
| - postavitev klimata na antivibracijski dušilnik (gumo) za preprečevanje prenosa vibracij in hrupa na konstrukcijo objekta. Dušilniki morajo biti preračunani glede na lastnosti klimata (teža in vrtilna frekvenca ventilatorjev). | - installation of the air conditioner on an anti-vibration damper (rubber) to prevent the transmission of vibrations and noise to the structure of the building. The dampers must be calculated according to the characteristics of the air conditioner (weight and speed of the fans).
| - s spojnim, tesnilnim in pritrdilnim materialom in priključki za senzorje, | - with jointing, sealing and fixing materials and sensor connectors,
| Teža: 1592kg | Weight: 1592kg
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR | - SYSTEMAIR | kpl | 1 |  | 0
10.2 | Okrogli prezračevalni kanali izdelani iz pocinkane pločevine po SIST EN 1506, vključno z revizijskimi odprtinami, oblikovnimi kosi, debeline po standardu. V ceni na enoto (m) je potrebno upoštevati ves spojni in pritrdilni material (prirobnice, odrez, spone, vijaki, tesnila, ojačitve, vključno z obešalnim in pritrdilnim materialom sistemskega proizvajalca z lastnostmi odgovarjajoč zahtevam SIST EN 12236: 2002, vključno pleskanje vseh kovinskih korozijsko nezaščitenih delov, po temeljitem predhodnem čiščenju do kovinskega sijaja. Antikorozijska zaščita se izvaja v skladu z EN 12944 za naslednje pogoje: • Življenjska doba več kot 15 let. • Stopnja korozijske atmosfere C4 (visoka). | Round ventilation ducts made of galvanised sheet metal according to SIST EN 1506, including inspection openings, shaped pieces, thickness according to the standard. The unit price (m) must take into account all joining and fixing material (flanges, cut-offs, clamps, bolts, gaskets, reinforcements, including hanging and fixing material of the system manufacturer with properties according to the requirements of SIST EN 12236: 2002, including painting of all metal corrosion-protected parts, after thorough cleaning to a metallic gloss. The corrosion protection shall be carried out in accordance with EN12944, for the following conditions: - Lifetime over 15 years. - Corrosive atmosphere C4 (high).
| - Okrogli prezračevalni kanali Ø80 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø80 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 5 |  | 0
| - Okrogli prezračevalni kanali Ø100 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø100 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 120 |  | 0
| - Okrogli prezračevalni kanali Ø125 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø125 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 45 |  | 0
| - Okrogli prezračevalni kanali Ø140 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø140 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 3 |  | 0
| - Okrogli prezračevalni kanali Ø150 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø150 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 55 |  | 0
| - Okrogli prezračevalni kanali Ø160 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø160 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 16 |  | 0
| - Okrogli prezračevalni kanali Ø180 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø180 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 25 |  | 0
| - Okrogli prezračevalni kanali Ø200 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø200 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 25 |  | 0
| - Okrogli prezračevalni kanali Ø225 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø225 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 10 |  | 0
| - Okrogli prezračevalni kanali Ø250 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø250 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 3 |  | 0
| - Okrogli prezračevalni kanali Ø300 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø300 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 25 |  | 0
| - Okrogli prezračevalni kanali Ø315 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø315 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 25 |  | 0
10.3 | Okrogli pregibni kanali za priključitev stropnih difuzorjev, izdelani iz Al folije ter polnila iz materiala z dušilnim in toplotno-izolativnim efektom. V ceni na enoto (m) je potrebno upoštevati ves spojni material, pritrdilne objemke in tesnilni material, za podatke: | Round folded ducts for the connection of ceiling diffusers, made of Al foil and filling material with damping and thermal insulation effect. The unit price (m) must include all joining material, fixing clamps and sealing material, for details:
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DEC tip: SONODEC - 25 | - DEC tip: SUNDAY - 25
| - Okroglegi pregibni kanali Ø125 | - Ø125 round flexible ducts | m | 20 |  | 0
| - Okroglegi pregibni kanali Ø160 | - Round flexible ducts Ø160 | m | 5 |  | 0
| - Okroglegi pregibni kanali Ø200 | - Ø200 round flexible ducts | m | 15 |  | 0
| - Okroglegi pregibni kanali Ø315 | - Round flexible ducts Ø315 | m | 2 |  | 0
10.4 | Pravokotni prezračevalni kanali izdelani iz pocinkane pločevine po SIST EN 1505:1999, debeline po DIN 24190, klase tesnosti B po SIST EN 1507:2006, vključno z revizijskimi odprtinami, oblikovnimi kosi. V ceni na enoto (m2) je potrebno upoštevati ves spojni in pritrdilni material (prirobnice, odrez, spone, vijaki, tesnila, usmerjevalniki, ojačitve, vključno z obešalnim in pritrdilnim materialom sistemskega proizvajalca z lastnostmi odgovarjajoč zahtevam SIST EN 12236: 2002, vključno pleskanje vseh kovinskih korozijsko nezaščitenih delov, po temeljitem predhodnem čiščenju do kovinskega sijaja. Antikorozijska zaščita se izvaja v skladu z EN 12944 za naslednje pogoje: • Življenjska doba več kot 15 let. • Stopnja korozijske atmosfere C4 (visoka). | Rectangular ventilation ducts made of galvanised sheet metal according to SIST EN 1505:1999, thickness according to DIN 24190, tightness class B according to SIST EN 1507:2006, including inspection openings, shaped pieces. The unit price (m2) must take into account all joining and fixing material (flanges, cut-off, clamps, bolts, gaskets, guides, reinforcements, including hanging and fixing material of the system manufacturer with properties according to the requirements of SIST EN 12236:2002, including the painting of all metal corrosion-protected parts, after thorough preliminary cleaning to a metallic gloss. The anticorrosive protection shall be performed in accordance with EN12944 for the following conditions: - Lifetime over 15 years. - Corrosive atmosphere C4 (high). | m2 | 210 |  | 0
10.5 | Toplotna izolacija zajemnih, izpušnih ter vtočnih kanalov s parozapornimi ploščami izdelanimi iz sintetičnega kavčuka z zaprto celično strukturo, toplotne prevodnosti manjše ali enake 0,033W/mK pri srednji temperaturi 0 °C, koeficient upora difuziji vodene pare večji ali enak 10000 testirano v skladu z EN 13469 za cevi in EN 12086 za plošče, požarna klasifikacija B/BL-s3,d0 po DIN 4102, oziroma po SIST EN 13501-1. | Thermal insulation of intake, exhaust and inlet ducts with vapour control panels made of synthetic rubber with closed cell structure, thermal conductivity less than or equal to 0,033 W/mK at a mean temperature of 0 °C, resistance coefficient to diffusion of water vapour greater than or equal to 10000 tested in accordance with EN 13469 for pipes and EN 12086 for panels, fire classification B/BL-s3,d0 according to DIN 4102, or according to SIST EN 13501-1.
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - ARMACELL tip: Armaflex AF | - ARMACELL tip: Armaflex AF
| Toplotna izolacija zunanjih kanalov na vtočni strani (VTZ-SUP), debeline s = 50 mm, + original lepilo, + 0,8mm Al pločevine | Thermal insulation of external ducts on the inlet side (VTZ-SUP), thickness s = 50 mm, + original adhesive, + 0.8 mm Al sheet | m2 | 33 |  | 0
| Toplotna izolacija zunanjih kanalov na odtočni strani (ODZ-ETA), debeline s = 50 mm, + original lepilo, + 0,8mm Al pločevine | Thermal insulation of external ducts on the drain side (ODZ-ETA), thickness s = 50 mm, + original adhesive, + 0,8 mm Al sheet | m2 | 52 |  | 0
| Toplotna izolacija notranjih kanalov na vtočni strani (VTZ-SUP), debeline s = 19 mm, + original lepilo | Thermal insulation of internal ducts on the inlet side (VTZ-SUP), thickness s = 19 mm, + original adhesive | m2 | 215 |  | 0
10.6 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z ragulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, soundproof and thermally insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to the client's or architect's preference, with connection chamber, with regulating flap, with air flow measurement connections, ready-air inlet connection to be provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø597, H=287, Ø200 | - dimensions Ø597, H=287, Ø200
| - pretok q = 285 m3/h | - flow rate q = 285 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-C-200 | - SYSTEMAIR tip CAP-C-200
| Oznaka: / | Tag: / | kpl | 4 |  | 0
10.7 | Linijski difuzor za dovod zraka, izdelan iz aluminijastih profilov, belo prašnato obarvane v RAL9003 ali po izboru arhitekta in komore iz pocinkane pločevine, toplotno izolirane na zunanji strani, kompletno s priključki iz strani in regulacijsko loputo za nastavitev volumskega pretoka zraka, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Linear air inlet diffuser made of aluminium profiles, powder-coated white RAL9003 or architect's choice, and chamber of galvanised sheet metal, thermally insulated on the outside, complete with side connections and control damper for volume flow adjustment, including all fixing and mounting material, type:
| - dimenzije L=500, H=250, Ø125 | - dimensions L=500, H=250, Ø125
| - pretok q = 50 m3/h | - flow rate q = 50 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip HELLA-2-500 | - SYSTEMAIR tip HELLA-2-500
| Oznaka: / | Tag: / | kpl | 3 |  | 0
10.8 | Linijski difuzor za dovod zraka, izdelan iz aluminijastih profilov, belo prašnato obarvane v RAL9003 ali po izboru arhitekta in komore iz pocinkane pločevine, kompletno s priključki iz strani in regulacijsko loputo za nastavitev volumskega pretoka zraka, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Linear air inlet diffuser made of aluminium profiles, powder-coated white RAL9003 or architect's choice, and galvanised sheet metal chamber, complete with side connections and volume flow control damper, including all fixing and mounting material, type:
| - dimenzije L=1500, H=250, Ø160 | - dimensions L=1500, H=250, Ø160
| - pretok q = 200/210 m3/h | - flow rate q = 200/210 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip HELLA-2-1500 | - SYSTEMAIR tip HELLA-2-1500
| Oznaka: / | Tag: / | kpl | 3 |  | 0
10.9 | Linijski difuzor za dovod zraka, izdelan iz aluminijastih profilov, belo prašnato obarvane v RAL9003 ali po izboru arhitekta in komore iz pocinkane pločevine, kompletno s priključki iz strani in regulacijsko loputo za nastavitev volumskega pretoka zraka, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Linear air inlet diffuser made of aluminium profiles, powder-coated white RAL9003 or architect's choice, and galvanised sheet metal chamber, complete with side connections and volume flow control damper, including all fixing and mounting material, type:
| - dimenzije L=500, H=250, Ø125 | - dimensions L=500, H=250, Ø125
| - pretok q = 40 m3/h | - flow rate q = 40 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip HELLA-2-500 | - SYSTEMAIR tip HELLA-2-500
| Oznaka: / | Tag: / | kpl | 2 |  | 0
10.10 | Stropni difuzor za odvod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno izolirano, maska je s fiksnimi lamelami, barve (RAL 9010) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z ragulacijsko loputo, priključek odvoda zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for exhaust air, housing made of galvanised sheet steel, soundproofed, mask with fixed louvres, colour (RAL 9010) or in the colour of the client's or architect's choice, with connection chamber, with air control damper, exhaust air connection provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø364, H=290, Ø200 | - dimensions Ø364, H=290, Ø200
| - pretok q = 285 m3/h | - flow rate q = 285 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip VVKN-A-R-400 | - SYSTEMAIR type VVKN-A-R-400
| Oznaka: / | Tag: / | kpl | 4 |  | 0
10.11 | Linijski difuzor za odvod zraka, izdelan iz aluminijastih profilov, belo prašnato obarvane v RAL9003 ali po izboru arhitekta in komore iz pocinkane pločevine, kompletno s priključki iz strani in regulacijsko loputo za nastavitev volumskega pretoka zraka, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Linear diffuser for exhaust air, made of aluminium profiles, powder-coated white RAL9003 or architect's choice, and chamber of galvanised sheet metal, complete with side connections and control flap for volume flow adjustment, including all fixing and mounting material, type:
| - dimenzije L=500, H=250, Ø125 | - dimensions L=500, H=250, Ø125
| - pretok q = 50 m3/h | - flow rate q = 50 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip HELLA-2-500 | - SYSTEMAIR tip HELLA-2-500
| Oznaka: / | Tag: / | kpl | 3 |  | 0
10.12 | Linijski difuzor za odvod zraka, izdelan iz aluminijastih profilov, belo prašnato obarvane v RAL9003 ali po izboru arhitekta in komore iz pocinkane pločevine, kompletno s priključki iz strani in regulacijsko loputo za nastavitev volumskega pretoka zraka, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Linear diffuser for exhaust air, made of aluminium profiles, powder-coated white RAL9003 or architect's choice, and chamber of galvanised sheet metal, complete with side connections and control flap for volume flow adjustment, including all fixing and mounting material, type:
| - dimenzije L=500, H=250, Ø125 | - dimensions L=500, H=250, Ø125
| - pretok q = 40 m3/h | - flow rate q = 40 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip HELLA-2-500 | - SYSTEMAIR tip HELLA-2-500
| Oznaka: / | Tag: / | kpl | 2 |  | 0
10.13 | Prezračevalni ventil za odvod zraka, izdelan iz jeklene pločevine, belo prašnato obarvane v RAL9016-90 ali po izboru arhitekta, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Air vent valve for exhaust air, made of sheet steel, powder-coated white in RAL9016-90 or architect's choice, including all fixing and mounting material, type:
| - dimenzije Ø100 | - ø100 dimensions
| - pretok q = 90 m3/h | - flow rate q = 90 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip EFF-100 | - SYSTEMAIR tip EFF-100
| Oznaka: / | Tag: / | kpl | 6 |  | 0
10.14 | Prezračevalni ventil za odvod zraka, izdelan iz jeklene pločevine, belo prašnato obarvane v RAL9016-90 ali po izboru arhitekta, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Air vent valve for exhaust air, made of sheet steel, powder-coated white in RAL9016-90 or architect's choice, including all fixing and mounting material, type:
| - dimenzije Ø100 | - ø100 dimensions
| - pretok q = 70 m3/h | - flow rate q = 70 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip EFF-100 | - SYSTEMAIR tip EFF-100
| Oznaka: / | Tag: / | kpl | 1 |  | 0
10.15 | Prezračevalna rešetka za vgradnjo v vrata, izdelana iz aluminijastih profilov s fiksnimi lamelami, prašnato obarvane v barvi RAL9003 ali po izboru arhitekta, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ventilation grille for installation in doors, made of aluminium profiles with fixed slats, powder-coated RAL9003 or architect's choice, including all fixing and mounting materials, type:
| - dimenzije 400x300 | - dimensions 400x300
| - pretok q = 270 m3/h | - flow rate q = 270 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-D-1-400x300 | - SYSTEMAIR tip NOVA-D-1-400x300
| Oznaka: / | Tag: / | kpl | 2 |  | 0
10.16 | Prezračevalna rešetka za vgradnjo v vrata, izdelana iz aluminijastih profilov s fiksnimi lamelami, prašnato obarvane v barvi RAL9003 ali po izboru arhitekta, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ventilation grille for installation in doors, made of aluminium profiles with fixed slats, powder-coated RAL9003 or architect's choice, including all fixing and mounting materials, type:
| - dimenzije 300x150 | - dimensions 300x150
| - pretok q = 70 m3/h | - flow rate q = 70 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-D-1-300x150 | - SYSTEMAIR tip NOVA-D-1-300x150
| Oznaka: / | Tag: / | kpl | 1 |  | 0
10.17 | Protipožarna loputa, za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper, for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, resistant to fire and cold smoke, fire-resistance rating EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG-certificated, with galvanised sheet metal housing, complying with the requirements of the fire safety study with type fastening and sealing material:
| - dimenzije B=400/H=300 | - dimensions B=400/H=300
| - pretok q = 1980 m3/h | - flow rate q = 1980 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-400x300 | - SYSTEMAIR tip FDS-3G-400x300
| Oznaka: KFD15.301; KFD15.401 | Code: KFD15.301; KFD15.401 | kpl | 2 |  | 0
10.18 | Volumski regulator pretoka zraka, izdelan iz polimernega materiala, s funkcijo regulacije konstantnega pretoka, s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow regulator, made of polymer material, with constant flow control function, with fastening and sealing material type:
| - dimenzije Ø80 | - ø80 dimensions
| - pretok q = 50m3/h | - flow rate q = 50m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip RDR-80/15-50 | - SYSTEMAIR tip RDR-80/15-50
| Oznaka: CAV15.101; CAV15.201 | Code: CAV15.101; CAV15.201 | kpl | 2 |  | 0
10.19 | Volumski regulator pretoka zraka, izdelan iz polimernega materiala, s funkcijo regulacije konstantnega pretoka, s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow regulator, made of polymer material, with constant flow control function, with fastening and sealing material type:
| - dimenzije Ø100 | - ø100 dimensions
| - pretok q = 50m3/h | - flow rate q = 50m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip RDR-100/15-50 | - SYSTEMAIR tip RDR-100/15-50
| Oznaka: CAV15.103; CAV15.204; CAV15.104; CAV15.205 | Code: CAV15.103; CAV15.204; CAV15.104; CAV15.205 | kpl | 4 |  | 0
10.20 | Volumski regulator pretoka zraka, izdelan iz polimernega materiala, s funkcijo regulacije konstantnega pretoka, s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow regulator, made of polymer material, with constant flow control function, with fastening and sealing material type:
| - dimenzije Ø100 | - ø100 dimensions
| - pretok q = 40m3/h | - flow rate q = 40m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip RDR-100/15-50 | - SYSTEMAIR tip RDR-100/15-50
| Oznaka: CAV15.102; CAV15.203; CAV15.105; CAV15.206 | Code: CAV15.102; CAV15.203; CAV15.105; CAV15.206 | kpl | 4 |  | 0
10.21 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo regulacije konstantnega pretoka, s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow regulator, made of galvanised sheet metal with acoustic and thermal insulation, with constant flow control function, with fastening and sealing material type:
| - dimenzije Ø80 | - ø80 dimensions
| - pretok q = 70m3/h | - flow rate q = 70m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOTUS-RI-80-M0 | - SYSTEMAIR tip NOTUS-RI-80-M0
| Oznaka: CAV15.202 | Code: CAV15.202 | kpl | 1 |  | 0
10.22 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø140 | - ø140 dimensions
| - pretok q = 270 do 90m3/h | - flow rate q = 270 to 90m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-140 | - SYSTEMAIR tip OPTIMA-LV-RI-140
| Oznaka: VAV15.201; VAV15.202 | Code: VAV15.201; VAV15.202 | kpl | 2 |  | 0
10.23 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø125 | - dimensions Ø125
| - pretok q = 205/200 do 85/80m3/h | - flow rate q = 205/200 to 85/80m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-125 | - SYSTEMAIR tip OPTIMA-LV-RI-125
| Oznaka: VAV15.101; VAV15.102; VAV15.103 | Code: VAV15.101; VAV15.102; VAV15.103 | kpl | 3 |  | 0
10.24 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø315 | - dimensions Ø315
| - pretok q = 1140 do 640m3/h | - flow rate q = 1140 to 640m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-315 | - SYSTEMAIR tip OPTIMA-LV-RI-315
| Oznaka: VAV15.104; VAV15.203 | Code: VAV15.104; VAV15.203 | kpl | 2 |  | 0
10.25 | Elektromotorni pogon z vzmetjo za vstopno/izstopno žaluzijo klimata, vključno z varnostno funkcijo (NC) in stikali položaja, s pritrdilnim in tesnilnim materialom tipa: | Electric motor drive with spring for air-conditioning inlet/outlet blind, including safety function (NC) and position switches, with fixing and sealing material type:
| - navor 10Nm | - torque 10Nm
| - električno napajanje 24V AC/DC | - 24V AC/DC power supply
| - ON/OFF regulacija delovanja | - ON/OFF operation control
| - za žaluzije do 2m2 | - for blinds up to 2m2
| - zaščita IP54 | - iP54 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip NF24A-S2 | - BELIMO type NF24A-S2
| Oznaka: KD15.101; KD15.202 | Code: KD15.101; KD15.202 | kpl | 2 |  | 0
10.26 | Elektromotorni pogon za žaluzijo obtoka rekuperatorja, vključno s stikali položaja, s pritrdilnim in tesnilnim materialom tipa: | Electric motor drive for the recuperator circulation shutter, including position switches, with fixing and sealing material type:
| - navor 5Nm | - torque 5Nm
| - električno napajanje 24V AC/DC | - 24V AC/DC power supply
| - zvezna regulacija delovanja DC (0)2...10V | - dC continuous operation control (0)2...10V
| - za žaluzije do 1m2 | - for blinds up to 1m2
| - zaščita IP54 | - iP54 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip LM24A-SR | - BELIMO type LM24A-SR
| Oznaka: DY15.105 | Code: DY15.105 | kpl | 1 |  | 0
10.27 | Kanalsko tipalo diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Duct differential pressure sensor, with type fastening and sealing material:
| - območje prikazovanja od 0 do 1500 Pa | - display range 0 to 1500 Pa
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22ADP-184A | - BELIMO type 22ADP-184A
| Oznaka: PICAL15.115; PICAL15.215 | Code: PICAL15.115; PICAL15.215 | kpl | 2 |  | 0
10.28 | Tipalo diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure sensor, with mounting and sealing material type:
| - območje prikazovanja od 0 do 1500 Pa | - display range 0 to 1500 Pa
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22ADP-184A | - BELIMO type 22ADP-184A
| Oznaka: PDIC15.104; PDIC15.204 | Code: PDIC15.104; PDIC15.204 | kpl | 2 |  | 0
10.29 | Diferenčno tlačno stikalo, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure switch, with type fastening and sealing material:
| - območje prikazovanja od 50 do 500Pa | - display range 50 to 500Pa
| - kontaktni tok maksimalno 1,0A / AC 250V | - contact current max 1.0A / AC 250V
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 01APS-10U | - BELIMO type 01APS-10U
| Oznaka: PDSAH15.102; PDSAH15.112; PDSAH15.205; PDSAH15.207 | Code: PDSAH15.102; PDSAH15.112; PDSAH15.205; PDSAH15.207 | kpl | 4 |  | 0
10.30 | Prikazovalnik diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure indicator, with type fixing and sealing material:
| - območje prikazovanja od 50 do 500Pa | - display range 50 to 500Pa
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DWYER tip Magnahelic | - DWYER tip Magnahelic
| Oznaka: PDI15.102; PDI15.112; PDI15.205; PDI15.207 | Code: PDI15.102; PDI15.112; PDI15.205; PDI15.207 | kpl | 4 |  | 0
10.31 | Zunanje tipalo temperature in vlage, s pritrdilnim in tesnilnim materialom tipa: | External temperature and humidity sensor, with fixing and sealing material type:
| - območje prikazovanja od 0 do 100%RH | - display range 0 to 100%RH
| - območje prikazovanja od -40 do 60°C | - display range -40 to 60°C
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22UTH-13M | - BELIMO type 22UTH-13M
| Oznaka: TIC/MIC15.100 | Code: TIC/MIC15.100 | kpl | 1 |  | 0
10.32 | Kanalsko tipalo temperature in vlage, s pritrdilnim in tesnilnim materialom tipa: | Duct temperature and humidity sensor, with fixing and sealing material type:
| - območje prikazovanja od 0 do 100%RH | - display range 0 to 100%RH
| - območje prikazovanja od -40 do 60°C | - display range -40 to 60°C
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22DTH-13M | - BELIMO type 22DTH-13M
| Oznaka: TIC/MIC15.113; TIC/MIC15.208 | Code: TIC/MIC15.113; TIC/MIC15.208 | kpl | 2 |  | 0
10.33 | Prostorsko tipalo kvalitete zraka CO2, s pritrdilnim in tesnilnim materialom tipa: | Room air quality sensor CO2, with fixing and sealing material type:
| - območje CO2 od 0 do 2000ppm | - cO2 range from 0 to 2000ppm
| - izhodni signal 0 do 10V | - output signal 0 to 10V
| - izhodni signal MP-Bus | - mP-Bus output signal
| - zaščita IP30 | - iP30 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22RTM-19-1 | - BELIMO type 22RTM-19-1
| Oznaka: QIC15.501 | Code: QIC15.501 | kpl | 1 |  | 0
10.34 | Protizmrzovalni termostat, s pritrdilnim in tesnilnim materialom tipa: | Anti-freezing thermostat, with fixing and sealing material type:
| - območje od -10 do 15°C | - range -10 to 15°C
| - dolžina kapilare 6m | - capillary length 6m
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 01ATS-105XC | - BELIMO type 01ATS-105XC
| Oznaka: TSZAL15.108 | Code: TSZAL15.108 | kpl | 1 |  | 0
10.35 | Obtočna črpalka, elektronsko regulirana s frekvenčnim pretvornikom, tipalom diferenčnega tlaka, internimi hidravličnimi, električnimi in komunikacijskimi povezavami, PN10, material jeklena litina, skladnost z ErP, pritrdilnim in tesnilnim materialom tipa: | Circulation pump, electronically controlled with frequency converter, differential pressure sensor, internal hydraulic, electrical and communication connections, PN10, material cast steel, ErP compliant, type fastening and sealing material:
| - za obtok ogrevne vode 50/40°C | - for circulating heating water 50/40°C
| - za pretok V = 1,19m3/h, tlačna višina H = 1,8m | - for flow rate V = 1,19m3/h, pressure head H = 1,8m
| - možnost izbire delovanja črpalke na proporcionalni tlak ter optimizacijo delovne obratovalne točke | - option to select proportional pressure pump operation and optimise the operating point
| - napajanje Pel = 0,050kW, 230V / 50Hz | - power supply Pel = 0,050kW, 230V/50Hz
| - navojni priključek G 1 1/2 | - threaded connection G 1 1/2
| - tlačna stopnja PN10 | - pressure rating PN10
| - temperaturno območje ogrevnega medija od -10 do 110°C | - temperature range of the heating medium from -10 to 110°C
| - komunikacija s CNS RS485 | - communication with CNS RS485
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - GRUNDFOS tip MAGNA3 25-40 | - GRUNDFOS type MAGNA3 25-40
| Oznaka: P15.107 | Code: P15.107 | kpl | 1 |  | 0
10.36 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za ogrevno vodo 50/40°C | - for heating water 50/40°C
| - za pretok V = 1,19m3/h | - for a flow rate of V = 1,19m3/h
| - območje regulacije pretoka do 1700 l/h (1,700 m3/h) | - flow control range up to 1,700 m3/h (1,700 l/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - navojni priključek G 1 1/4" po ISO 228/1 | - threaded connection G 1 1/4" to ISO 228/1
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 20 - 400 kPa, min. dif. tlak 20 kPa | - differential pressure range 20 - 400 kPa, min. differential pressure 20 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM25 | - DANFOS type AB-QM25
| Oznaka: VA15.107 | Code: VA15.107 | kpl | 1 |  | 0
10.37 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za hladilno vodo 9/14°C | - for cooling water 9/14°C
| - za pretok V = 1,56m3/h | - for a flow rate of V = 1,56 m3/h
| - območje regulacije pretoka do 1700 l/h (1,700 m3/h) | - flow control range up to 1,700 m3/h (1,700 l/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - navojni priključek G 1 1/4" po ISO 228/1 | - threaded connection G 1 1/4" to ISO 228/1
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 20 - 400 kPa, min. dif. tlak 20 kPa | - differential pressure range 20 - 400 kPa, min. differential pressure 20 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM25 | - DANFOS type AB-QM25
| Oznaka: VA15.110 | Code: VA15.110 | kpl | 1 |  | 0
| PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS15 | VENTILATION AND AIR CONDITIONING SYSTEM KS15 |  |  |  | 0

## 4.4.11_PrKlim KS17
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.4 | STROJNA DELA | MECHANICAL WORKS
4.4.11 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS17 | VENTILATION AND AIR CONDITIONING SYSTEM KS17 |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
11 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS17 | VENTILATION AND AIR CONDITIONING SYSTEM KS17
11.1 | Klimatska naprava za dovod in odvod zraka KD17/KO17 - glej tudi zavihek Zahteve klimati. | KD17/KO17 supply and extract air conditioner - see also Climate requirements tab.
| Tehnične karakteristike naprave (opis v smeri toka zraka): | Technical characteristics of the appliance (description downstream):
| Dovod: Vdov = 4670 m3/h | Input: Vdov = 4670 m3/h
| - posluževanje dovod: horizontalna izvedba desno in levo v smeri toka zraka! | - inlet: horizontal right and left in the direction of the air flow!
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 10 60% po ISO 16890 (M5 po SIST EN 779), z regulacijsko žaluzijo 780x900x125, s fleksibilnim čelnim priključkom, za pretok zraka 4670m3/h. Maksimalni končni padec tlaka 200Pa. Oznaka: F17.102 | - Filter unit with bag filter cartridge of filtration level ePM 10 60% according to ISO 16890 (M5 according to SIST EN 779), with control shutter 780x900x125, with flexible front connection, for air flow 4670m3/h. Maximum final pressure drop 200Pa. Code: F17.102
| - Dušilna enota. - pretok zraka 4670m3/h - padec tlaka dp=9Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 7 17 18 21 15 11 12 Oznaka: DZ17.103 | - Throttle unit. - air flow 4670m3/h - pressure drop dp=9Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 7 17 18 21 15 11 12 Code: DZ17.103
| - Ventilatorska enota s prostotekočim rotorjem. Elektromotor je EC-motor, s 100% zvezno regulacijo vrtljajev preko potenciometra (0-10V), ki omogoča nastavitev delovanja ventilatorja na ustrezno delovno točko. Enota vsebuje: okence O150 in svetilko s stikalom ter servisno stikalo. - pretok zraka 4670m3/h - eksterni statični padec tlaka dpext=300Pa - priključna električna moč 2.4kW, 3x400V, 50Hz - razred izkoristka elektromotorja IE5/EC - zaščita IP55 Oznaka: FA17.104 | - Fan unit with free-flowing rotor. The electric motor is an EC motor, with 100% continuous speed control via a potentiometer (0-10V), which allows the fan to be set to the appropriate operating point. The unit contains: an O150 window and a lamp with switch and a service switch. - air flow 4670m3/h - external static pressure drop dpext=300Pa - connection power 2.4kW, 3x400V, 50Hz - electric motor efficiency class IE5/EC - iP55 protection Code: FA17.104
| - Ploščni rekuperator za prenos senzibilne toplote z el. motorno regulacijsko žaluzijo za obtok zraka (protizmrzovalna zaščita). Tehnični podatki za zimsko obdobje: - pretok zraka 4670/4160m3/h - stopnja vračanja občutene toplote: 72,1% - vračanje toplotne energije: 40,37kW - stanje dovodnega zr. pred enoto: -13,00°C/90,0% - stanje dovodnega zraka za enoto: 12,70°C/14,0% Tehnični podatki za poletno obdobje: - pretok zraka 4670/4160m3/h - stopnja vračanja občutene toplote: 70,1% - vračanje toplotne energije: 9,66kW - stanje dovodnega zr. pred enoto: 34,50°C/40,0% - stanje dovodnega zraka za enoto: 28,50°C/56% Oznaka: RE17.106 | - Sensible heat transfer plate recuperator with electric motor-controlled air circulation louvre (frost protection). technical data for the winter period: - air flow 4670/4160m3/h - sensible heat recovery rate: 72.1% - heat energy recovery: 40.37kW - supply air condition upstream of the unit: -13.00°C/90.0% - supply air condition for the unit: 12.70°C/14.0% Technical data for the summer period: - air flow 4670/4160m3/h - sensible heat recovery rate: 70.1% - heat energy recovery: 9.66kW - supply air condition upstream of the unit: 34.50°C/40.0% - supply air condition for the unit: 28.50°C/56% Code: RE17.106
| - Enota pred-grelnika zraka s protizmrzovalno zaščito. - pretok zraka 4670m3/h - grelna moč Qg=36,94kW - temperaturni režim ogrevnega medija 50/40°C - pretok ogrevnega medija 3,21m3/h - padec tlaka na zračni strani 51Pa - temperatura zraka vstop 12,40°C - temperatura zraka izstop 36,00°C - padec tlaka na strani ogr. medija (voda) 12,02kPa - priključka navojna 1 1/4" - tlačna stopnja PN16 Oznaka: HE17.107 | - Air preheater unit with anti-freeze protection. - air flow 4670m3/h - heating power Qg=36,94kW - heating medium temperature 50/40°C - heating medium flow 3,21m3/h - air side pressure drop 51Pa - air temperature inlet 12,40°C - air temperature outlet 36,00°C - pressure drop on the heating medium side (water) 12,02kPa - 1 1/4" threaded connectors - pressure rating PN16 Code: HE17.107
| - Prazna enota. | - Empty unit.
| - Vlažilna enota s kontaktnim vlaženjem zraka. Dovod sveže pripravljene demineralizirane vode, z materialom kontaktnega vlažilnika impregniranim srebrom, črpalko, potrebno merilno regulacijsko opremo, ventili na dovodu sveže vode ter ventilom na odvodu vode iz banje, s funkcijo samodejnega praznjenja banje vlažilnika in polnjenja s svežo pripravljeno mehčano vodo glede na prevodnost vode v banji, oziroma glede na čas ko vlažilnik ni v funkciji. Odvod kondenzata s sifonom z vodno in mehansko smardno zaporo. - pretok zraka 4670m3/h - priključna električna moč 0,06kW, 3x400V, 50Hz - padec tlaka na zračni strani dpz=144Pa - temperatura zraka vstop 36°C - relativna vlaga zraka vstop 3,4% - temperatura zraka izstop 27,00°C - relativna vlaga izstop 21,8% - izkoristek vlaženja 40,17% - vlaženje 29,88 kg/h - tipalo prevodonsti vode QICCD17.109 - tipalo zgornjega nivoja vode LICH17.109 - tipalo spodnjega nivoja vode LICL17.109 - elektromagnetni ventil za praznenje VD17.109 - elektromagnetni ventil za dovod sveže vode VD17.209 Oznaka: SH17.109 | - Humidification unit with contact humidification. Freshly prepared demineralised water supply, with silver-impregnated contact humidifier material, pump, necessary metering control equipment, valves at the fresh water inlet and at the water outlet of the humidifier tank, with automatic emptying of the humidifier tank and refilling with freshly prepared softened water according to the conductivity of the water in the tank, or according to the time when the humidifier is not in operation. Condensate drainage with siphon with water and mechanical odour trap. - air flow 4670m3/h - connection power 0,06kW, 3x400V, 50Hz - pressure drop on the air side dpz=144Pa - air temperature inlet 36°C - relative humidity inlet 3.4% - air temperature outlet 27,00°C - relative humidity 21.8% - humidification efficiency 40.17% - humidification 29,88 kg/h - water conductivity sensor QICCD17.109 - upper water level sensor LICH17.109 - lICL17.109 lower water level sensor - solenoid valve for emptying VD17.109 - fresh water solenoid valve VD17.209 Code: SH17.109
| - Prazna enota. | - Empty unit.
| - Enota hladilnika z eliminatorjem kapljic in koritom za odvod kondenzata. - pretok zraka 4670m3/h - hladilna moč Qhtot=25,42kW - temperaturni režim hladilnega medija 9/14°C - pretok hladilnega medija 4,36m3/h - padec tlaka na zračni strani 53/46Pa - temperatura zraka vstop 28,50°C - temperatura zraka izstop 18,00°C - padec tlaka na strani hl. medija (voda) 27,26kPa - priključka navojna 1 1/4" - tlačna stopnja PN16 Oznaka: HE17.110 | - Refrigerator unit with drip eliminator and condensate drain. - air flow 4670m3/h - cooling power Qhtot=25,42kW - cooling medium temperature 9/14°C - cooling medium flow rate 4,36m3/h - air side pressure drop 53/46Pa - air temperature inlet 28,50°C - air temperature outlet 18,00°C - pressure drop on the medium side (water) 27,26kPa - 1 1/4" threaded connectors - pressure rating PN16 Code: HE17.110
| - Dušilna enota. - pretok zraka 4670mm3/h - padec tlaka dp=11Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 7 17 18 21 15 11 12 Oznaka: DZ17.111 | - Throttle unit. - air flow 4670mm3/h - pressure drop dp=11Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 7 17 18 21 15 11 12 Code: DZ17.111
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 1 75% po ISO 16890 (F8 po SIST EN 779, s fleksibilnim čelnim priključkom, za pretok zraka 4670m3/h. Maksimalni končni padec tlaka 300Pa. Oznaka: F17.112 | - Filter unit with bag filter cartridge of filtration level ePM 1 75% according to ISO 16890 (F8 according to SIST EN 779, with flexible front connection, for air flow 4670m3/h. Maximum final pressure drop 300Pa. Code: F17.112
| Dolžina: 9,150m | Length: 9,150m
| Širina: 1,055m | Width: 1,055m
| Višina: 1,180m | Height: 1,180m
| Kompletno z dobavo dodatne opreme: | Complete with supply of accessories:
| - odtočni sifoni | - drain traps
| - jadrovinasti nastavki | - sailplane spigots
| - s spojnim, tesnilnim in pritrdilnim materialom in priključki za senzorje, | - with jointing, sealing and fixing materials and sensor connectors,
| Odvod: Vodv = 4160 m3/h | Discharge: waterv = 4160 m3/h
| - posluževanje odvod: horizontalna izvedba levo in desno v smeri toka zraka! | - venting: horizontal left and right in the direction of the air flow!
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 10 60% po ISO 16890 (M5 po SIST EN 779), s fleksibilnim čelnim priključkom, za pretok zraka 4160m3/h. Maksimalni končni padec tlaka 200Pa. Oznaka: F17.207 | - Filter unit with bag filter cartridge of filtration level ePM 10 60% according to ISO 16890 (M5 according to SIST EN 779), with flexible front connection, for an air flow of 4160m3/h. Maximum final pressure drop 200Pa. Code: F17.207
| - Dušilna enota. - pretok zraka 4160m3/h - padec tlaka dp=7Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 7 17 18 21 15 11 12 Oznaka: DZ17.206 | - Throttle unit. - air flow 4160m3/h - pressure drop dp=7Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 7 17 18 21 15 11 12 Code: DZ17.206
| - Ventilatorska enota s prostotekočim rotorjem. Elektromotor je EC-motor, s 100% zvezno regulacijo vrtljajev preko potenciometra (0-10V), ki omogoča nastavitev delovanja ventilatorja na ustrezno delovno točko. Enota vsebuje: okence O150 in svetilko s stikalom ter servisno stikalo. - pretok zraka 4160m3/h - eksterni statični padec tlaka dpext=300Pa - priključna električna moč 2,40kW, 3x400V, 50Hz - razred izkoristka elektromotorja IE5/EC - zaščita IP54 Oznaka: FA17.204 | - Fan unit with free-flowing rotor. The electric motor is an EC motor, with 100% continuous speed control via a potentiometer (0-10V), which allows the fan to be set to the appropriate operating point. The unit contains: an O150 window and a lamp with switch and a service switch. - air flow 4160m3/h - external static pressure drop dpext=300Pa - connection power 2,40kW, 3x400V, 50Hz - electric motor efficiency class IE5/EC - iP54 protection Code: FA17.204
| - Dušilna enota. - pretok zraka 4160m3/h - padec tlaka dp=11Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 7 17 18 21 15 11 12 Oznaka: DZ17.203 | - Throttle unit. - air flow 4160m3/h - pressure drop dp=11Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 7 17 18 21 15 11 12 Code: DZ17.203
| - Prazna enota z regulacijsko žaluzijo 900x465x125, fleksibilnim čelnim priključkom, za pretok zraka 4160m3/h. | - Empty unit with 900x465x125 control louvre, flexible front connection, for air flow of 4160m3/h.
| Dolžina: 5,830m | Length: 5,830m
| Širina: 1,055m | Width: 1,055m
| Višina: 1,180m | Height: 1,180m
| Kompletno z dobavo dodatne opreme: | Complete with supply of accessories:
| - postavitvene noge, gumirane, višine 100-200mm | - rubberised feet, height 100-200mm
| - odtočni sifoni | - drain traps
| - jadrovinasti nastavki | - sailplane spouts
| - postavitev klimata na antivibracijski dušilnik (gumo) za preprečevanje prenosa vibracij in hrupa na konstrukcijo objekta. Dušilniki morajo biti preračunani glede na lastnosti klimata (teža in vrtilna frekvenca ventilatorjev). | - installation of the air conditioner on an anti-vibration damper (rubber) to prevent the transmission of vibrations and noise to the structure of the building. The dampers must be calculated according to the characteristics of the air conditioner (weight and speed of the fans).
| - s spojnim, tesnilnim in pritrdilnim materialom in priključki za senzorje, | - with jointing, sealing and fixing materials and sensor connectors,
| Teža: 2564kg | Weight: 2564kg
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR | - SYSTEMAIR | kpl | 1 |  | 0
11.2 | Okrogli prezračevalni kanali izdelani iz pocinkane pločevine po SIST EN 1506, vključno z revizijskimi odprtinami, oblikovnimi kosi, debeline po standardu. V ceni na enoto (m) je potrebno upoštevati ves spojni in pritrdilni material (prirobnice, odrez, spone, vijaki, tesnila, ojačitve, vključno z obešalnim in pritrdilnim materialom sistemskega proizvajalca z lastnostmi odgovarjajoč zahtevam SIST EN 12236: 2002, vključno pleskanje vseh kovinskih korozijsko nezaščitenih delov, po temeljitem predhodnem čiščenju do kovinskega sijaja. Antikorozijska zaščita se izvaja v skladu z EN 12944 za naslednje pogoje: • Življenjska doba več kot 15 let. • Stopnja korozijske atmosfere C4 (visoka). | Round ventilation ducts made of galvanised sheet metal according to SIST EN 1506, including inspection openings, shaped pieces, thickness according to the standard. The unit price (m) must take into account all joining and fixing material (flanges, cut-offs, clamps, bolts, gaskets, reinforcements, including hanging and fixing material of the system manufacturer with properties according to the requirements of SIST EN 12236: 2002, including painting of all metal corrosion-protected parts, after thorough cleaning to a metallic gloss. The corrosion protection shall be carried out in accordance with EN12944, for the following conditions: - Lifetime over 15 years. - Corrosive atmosphere C4 (high).
| - Okrogli prezračevalni kanali Ø80 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø80 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 60 |  | 0
| - Okrogli prezračevalni kanali Ø100 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø100 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 60 |  | 0
| - Okrogli prezračevalni kanali Ø125 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø125 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 85 |  | 0
| - Okrogli prezračevalni kanali Ø140 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø140 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 3 |  | 0
| - Okrogli prezračevalni kanali Ø150 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø150 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 8 |  | 0
| - Okrogli prezračevalni kanali Ø160 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø160 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 55 |  | 0
| - Okrogli prezračevalni kanali Ø180 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø180 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 25 |  | 0
| - Okrogli prezračevalni kanali Ø200 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø200 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 40 |  | 0
| - Okrogli prezračevalni kanali Ø225 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø225 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 8 |  | 0
| - Okrogli prezračevalni kanali Ø250 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø250 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 6 |  | 0
| - Okrogli prezračevalni kanali Ø280 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø280 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 10 |  | 0
| - Okrogli prezračevalni kanali Ø315 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø315 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 12 |  | 0
11.3 | Okrogli pregibni kanali za priključitev stropnih difuzorjev, izdelani iz Al folije ter polnila iz materiala z dušilnim in toplotno-izolativnim efektom. V ceni na enoto (m) je potrebno upoštevati ves spojni material, pritrdilne objemke in tesnilni material, za podatke: | Round folded ducts for the connection of ceiling diffusers, made of Al foil and filling material with damping and thermal insulation effect. The unit price (m) must include all joining material, fixing clamps and sealing material, for details:
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DEC tip: SONODEC - 25 | - DEC tip: SUNDAY - 25
| - Okroglegi pregibni kanali Ø125 | - Ø125 round flexible ducts | m | 30 |  | 0
| - Okroglegi pregibni kanali Ø160 | - Round flexible ducts Ø160 | m | 15 |  | 0
| - Okroglegi pregibni kanali Ø200 | - Ø200 round flexible ducts | m | 12 |  | 0
| - Okroglegi pregibni kanali Ø250 | - Round flexible ducts Ø250 | m | 3 |  | 0
| - Okroglegi pregibni kanali Ø315 | - Round flexible ducts Ø315 | m | 2 |  | 0
11.4 | Pravokotni prezračevalni kanali izdelani iz pocinkane pločevine po SIST EN 1505:1999, debeline po DIN 24190, klase tesnosti B po SIST EN 1507:2006, vključno z revizijskimi odprtinami, oblikovnimi kosi. V ceni na enoto (m2) je potrebno upoštevati ves spojni in pritrdilni material (prirobnice, odrez, spone, vijaki, tesnila, usmerjevalniki, ojačitve, vključno z obešalnim in pritrdilnim materialom sistemskega proizvajalca z lastnostmi odgovarjajoč zahtevam SIST EN 12236: 2002, vključno pleskanje vseh kovinskih korozijsko nezaščitenih delov, po temeljitem predhodnem čiščenju do kovinskega sijaja. Antikorozijska zaščita se izvaja v skladu z EN 12944 za naslednje pogoje: • Življenjska doba več kot 15 let. • Stopnja korozijske atmosfere C4 (visoka). | Rectangular ventilation ducts made of galvanised sheet metal according to SIST EN 1505:1999, thickness according to DIN 24190, tightness class B according to SIST EN 1507:2006, including inspection openings, shaped pieces. The unit price (m2) must take into account all joining and fixing material (flanges, cut-off, clamps, bolts, gaskets, guides, reinforcements, including hanging and fixing material of the system manufacturer with properties corresponding to the requirements of SIST EN 12236:2002, including the painting of all metal corrosion-protected parts, after thorough preliminary cleaning to a metallic gloss. The anticorrosive protection shall be performed in accordance with EN 12944 for the following conditions: - Lifetime over 15 years. - Corrosive atmosphere C4 (high). | m2 | 325 |  | 0
11.5 | Toplotna izolacija zajemnih, izpušnih ter vtočnih kanalov s parozapornimi ploščami izdelanimi iz sintetičnega kavčuka z zaprto celično strukturo, toplotne prevodnosti manjše ali enake 0,033W/mK pri srednji temperaturi 0 °C, koeficient upora difuziji vodene pare večji ali enak 10000 testirano v skladu z EN 13469 za cevi in EN 12086 za plošče, požarna klasifikacija B/BL-s3,d0 po DIN 4102, oziroma po SIST EN 13501-1. | Thermal insulation of intake, exhaust and inlet ducts with vapour control panels made of synthetic rubber with closed cell structure, thermal conductivity less than or equal to 0,033 W/mK at a mean temperature of 0 °C, resistance coefficient to diffusion of water vapour greater than or equal to 10000 tested in accordance with EN 13469 for pipes and EN 12086 for panels, fire classification B/BL-s3,d0 according to DIN 4102, or according to SIST EN 13501-1.
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - ARMACELL tip: Armaflex AF | - ARMACELL tip: Armaflex AF
| Toplotna izolacija zunanjih kanalov na vtočni strani (VTZ-SUP), debeline s = 50 mm, + original lepilo, + 0,8mm Al pločevine | Thermal insulation of external ducts on the inlet side (VTZ-SUP), thickness s = 50 mm, + original adhesive, + 0.8 mm Al sheet | m2 | 26 |  | 0
| Toplotna izolacija zunanjih kanalov na odtočni strani (ODZ-ETA), debeline s = 50 mm, + original lepilo, + 0,8mm Al pločevine | Thermal insulation of external ducts on the drain side (ODZ-ETA), thickness s = 50 mm, + original adhesive, + 0,8 mm Al sheet | m2 | 32 |  | 0
| Toplotna izolacija notranjih kanalov na vtočni strani (VTZ-SUP), debeline s = 19 mm, + original lepilo | Thermal insulation of internal ducts on the inlet side (VTZ-SUP), thickness s = 19 mm, + original adhesive | m2 | 235 |  | 0
11.6 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z ragulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, soundproof and thermally insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to the client's or architect's preference, with connection chamber, with regulating flap, with air flow measurement connections, ready-air inlet connection to be provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø497, H=252, Ø160 | - dimensions Ø497, H=252, Ø160
| - pretok q = 125 m3/h | - flow rate q = 125 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-C-160 | - SYSTEMAIR tip CAP-C-160
| Oznaka: / | Tag: / | kpl | 2 |  | 0
11.7 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z ragulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, soundproof and thermally insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to the client's or architect's preference, with connection chamber, with regulating flap, with connections for air flow measurement, inlet connection of the prepared air to be provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø497, H=252, Ø160 | - dimensions Ø497, H=252, Ø160
| - pretok q = 200 m3/h | - flow rate q = 200 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-C-160 | - SYSTEMAIR tip CAP-C-160
| Oznaka: / | Tag: / | kpl | 1 |  | 0
11.8 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden z vrha, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, acoustically and thermally insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to the client's or architect's preference, with connection chamber, with control damper, with connections for air flow measurement, inlet connection of the prepared air is provided from the top, including all fixing and mounting material, type:
| - dimenzije Ø497, H=409, Ø160 | - dimensions Ø497, H=409, Ø160
| - pretok q = 150 m3/h | - flow rate q = 150 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-CT-160 | - SYSTEMAIR tip CAP-CT-160
| Oznaka: / | Tag: / | kpl | 1 |  | 0
11.9 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden z vrha, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, acoustically and thermally insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to the client's or architect's preference, with connection chamber, with control damper, with connections for air flow measurement, inlet connection of the prepared air is provided from the top, including all fixing and mounting material, type:
| - dimenzije Ø497, H=409, Ø160 | - dimensions Ø497, H=409, Ø160
| - pretok q = 310 m3/h | - flow rate q = 310 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-CT-160 | - SYSTEMAIR tip CAP-CT-160
| Oznaka: / | Tag: / | kpl | 2 |  | 0
11.10 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, s ragulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, acoustically and thermally insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to the client's or architect's preference, with connection chamber, with regulating flap, with air flow measurement connections, ready-air inlet connection provided on the side, including all fixing and mounting material, type:
| - dimenzije Ø597, H=287, Ø200 | - dimensions Ø597, H=287, Ø200
| - pretok q = 250 m3/h | - flow rate q = 250 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-C-200 | - SYSTEMAIR tip CAP-C-200
| Oznaka: / | Tag: / | kpl | 1 |  | 0
11.11 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden z vrha, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, acoustically and thermally insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to customer's or architect's preference, with connection chamber, with control damper, with connections for air flow measurement, inlet connection of the prepared air is provided from the top, including all fixing and mounting material, type:
| - dimenzije Ø597, H=469, Ø200 | - dimensions Ø597, H=469, Ø200
| - pretok q = 300 m3/h | - flow rate q = 300 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-CT-200 | - SYSTEMAIR tip CAP-CT-200
| Oznaka: / | Tag: / | kpl | 1 |  | 0
11.12 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden z vrha, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, acoustically and thermally insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to customer's or architect's preference, with connection chamber, with control damper, with connections for air flow measurement, inlet connection of the prepared air is provided from the top, including all fixing and mounting material, type:
| - dimenzije Ø597, H=469, Ø200 | - dimensions Ø597, H=469, Ø200
| - pretok q = 310 m3/h | - flow rate q = 310 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-CT-200 | - SYSTEMAIR tip CAP-CT-200
| Oznaka: / | Tag: / | kpl | 2 |  | 0
11.13 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, s ragulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, acoustically and thermally insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to the client's or architect's preference, with connection chamber, with regulating flap, with air flow measurement connections, ready-air inlet connection provided on the side, including all fixing and mounting material, type:
| - dimenzije Ø608, H=332, Ø250 | - dimensions Ø608, H=332, Ø250
| - pretok q = 360 m3/h | - flow rate q = 360 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-C-250 | - SYSTEMAIR tip CAP-C-250
| Oznaka: / | Tag: / | kpl | 1 |  | 0
11.14 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, s ragulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, acoustically and thermally insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to the client's or architect's preference, with connection chamber, with regulating flap, with air flow measurement connections, ready-air inlet connection provided on the side, including all fixing and mounting material, type:
| - dimenzije Ø608, H=332, Ø250 | - dimensions Ø608, H=332, Ø250
| - pretok q = 370 m3/h | - flow rate q = 370 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-C-250 | - SYSTEMAIR tip CAP-C-250
| Oznaka: / | Tag: / | kpl | 1 |  | 0
11.15 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden z vrha, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, acoustically and thermally insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to customer's or architect's preference, with connection chamber, with control damper, with connections for air flow measurement, inlet connection of the prepared air is provided from the top, including all fixing and mounting material, type:
| - dimenzije Ø632, H=634, Ø315 | - dimensions Ø632, H=634, Ø315
| - pretok q = 630 m3/h | - flow rate q = 630 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-CT-315 | - SYSTEMAIR tip CAP-CT-315
| Oznaka: / | Tag: / | kpl | 1 |  | 0
11.16 | Linijski difuzor za dovod zraka, izdelan iz aluminijastih profilov, belo prašnato obarvane v RAL9003 ali po izboru arhitekta in komore iz pocinkane pločevine, kompletno s priključki iz strani in regulacijsko loputo za nastavitev volumskega pretoka zraka, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Linear air inlet diffuser made of aluminium profiles, powder-coated white RAL9003 or architect's choice, and galvanised sheet metal chamber, complete with side connections and volume flow control damper, including all fixing and mounting material, type:
| - dimenzije L=500, H=250, Ø125 | - dimensions L=500, H=250, Ø125
| - pretok q = 20 m3/h | - flow rate q = 20 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip HELLA-2-500 | - SYSTEMAIR tip HELLA-2-500
| Oznaka: / | Tag: / | kpl | 1 |  | 0
11.17 | Linijski difuzor za dovod zraka, izdelan iz aluminijastih profilov, belo prašnato obarvane v RAL9003 ali po izboru arhitekta in komore iz pocinkane pločevine, kompletno s priključki iz strani in regulacijsko loputo za nastavitev volumskega pretoka zraka, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Linear air inlet diffuser made of aluminium profiles, powder-coated white RAL9003 or architect's choice, and galvanised sheet metal chamber, complete with side connections and volume flow control damper, including all fixing and mounting material, type:
| - dimenzije L=500, H=250, Ø125 | - dimensions L=500, H=250, Ø125
| - pretok q = 40 m3/h | - flow rate q = 40 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip HELLA-2-500 | - SYSTEMAIR tip HELLA-2-500
| Oznaka: / | Tag: / | kpl | 6 |  | 0
11.18 | Linijski difuzor za dovod zraka, izdelan iz aluminijastih profilov, belo prašnato obarvane v RAL9003 ali po izboru arhitekta in komore iz pocinkane pločevine, kompletno s priključki iz strani in regulacijsko loputo za nastavitev volumskega pretoka zraka, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Linear air inlet diffuser made of aluminium profiles, powder-coated white RAL9003 or architect's choice, and galvanised sheet metal chamber, complete with side connections and volume flow control damper, including all fixing and mounting material, type:
| - dimenzije L=500, H=250, Ø125 | - dimensions L=500, H=250, Ø125
| - pretok q = 50 m3/h | - flow rate q = 50 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip HELLA-2-500 | - SYSTEMAIR tip HELLA-2-500
| Oznaka: / | Tag: / | kpl | 1 |  | 0
11.19 | Linijski difuzor za dovod zraka, izdelan iz aluminijastih profilov, belo prašnato obarvane v RAL9003 ali po izboru arhitekta in komore iz pocinkane pločevine, kompletno s priključki iz strani in regulacijsko loputo za nastavitev volumskega pretoka zraka, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Linear air inlet diffuser made of aluminium profiles, powder-coated white RAL9003 or architect's choice, and galvanised sheet metal chamber, complete with side connections and volume flow control damper, including all fixing and mounting material, type:
| - dimenzije L=900, H=250, Ø125 | - dimensions L=900, H=250, Ø125
| - pretok q = 70 m3/h | - flow rate q = 70 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip HELLA-2-900 | - SYSTEMAIR tip HELLA-2-900
| Oznaka: / | Tag: / | kpl | 1 |  | 0
11.20 | Linijski difuzor za dovod zraka, izdelan iz aluminijastih profilov, belo prašnato obarvane v RAL9003 ali po izboru arhitekta in komore iz pocinkane pločevine, kompletno s priključki iz strani in regulacijsko loputo za nastavitev volumskega pretoka zraka, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Linear air inlet diffuser made of aluminium profiles, powder-coated white RAL9003 or architect's choice, and galvanised sheet metal chamber, complete with side connections and volume flow control damper, including all fixing and mounting material, type:
| - dimenzije L=900, H=250, Ø125 | - dimensions L=900, H=250, Ø125
| - pretok q = 90 m3/h | - flow rate q = 90 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip HELLA-2-900 | - SYSTEMAIR tip HELLA-2-900
| Oznaka: / | Tag: / | kpl | 1 |  | 0
11.21 | Linijski difuzor za dovod zraka, izdelan iz aluminijastih profilov, belo prašnato obarvane v RAL9003 ali po izboru arhitekta in komore iz pocinkane pločevine, kompletno s priključki iz strani in regulacijsko loputo za nastavitev volumskega pretoka zraka, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Linear air inlet diffuser made of aluminium profiles, powder-coated white RAL9003 or architect's choice, and galvanised sheet metal chamber, complete with side connections and volume flow control damper, including all fixing and mounting material, type:
| - dimenzije L=900, H=250, Ø125 | - dimensions L=900, H=250, Ø125
| - pretok q = 100 m3/h | - flow rate q = 100 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip HELLA-2-900 | - SYSTEMAIR tip HELLA-2-900
| Oznaka: / | Tag: / | kpl | 2 |  | 0
11.22 | Linijski difuzor za dovod zraka, izdelan iz aluminijastih profilov, belo prašnato obarvane v RAL9003 ali po izboru arhitekta in komore iz pocinkane pločevine, kompletno s priključki iz strani in regulacijsko loputo za nastavitev volumskega pretoka zraka, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Linear air inlet diffuser made of aluminium profiles, powder-coated white RAL9003 or architect's choice, and galvanised sheet metal chamber, complete with side connections and volume flow control damper, including all fixing and mounting material, type:
| - dimenzije L=1000, H=250, Ø160 | - dimensions L=1000, H=250, Ø160
| - pretok q = 130 m3/h | - flow rate q = 130 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip HELLA-2-1000 | - SYSTEMAIR tip HELLA-2-1000
| Oznaka: / | Tag: / | kpl | 1 |  | 0
11.23 | Prezračevalni ventil za dovod zraka, izdelan iz jeklene pločevine, belo prašnato obarvane v RAL9016-90 ali po izboru arhitekta, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Air inlet ventilation valve made of sheet steel, powder-coated white in RAL9016-90 or architect's choice, including all fixing and mounting material, type:
| - dimenzije Ø80 | - ø80 dimensions
| - pretok q = 30 m3/h | - flow rate q = 30 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip TFF-80 | - SYSTEMAIR tip TFF-80
| Oznaka: / | Tag: / | kpl | 4 |  | 0
11.24 | Stropni difuzor za odvod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno izolirano, maska je s fiksnimi lamelami, barve (RAL 9010) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, priključek odvoda zraka je predviden z vrha, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for exhaust air, housing made of galvanised sheet steel, soundproofed, mask with fixed louvres, colour (RAL 9010) or in the colour of the client's or architect's choice, with connection chamber, with control damper, exhaust air connection from the top, including all fixing and mounting material, type:
| - dimenzije Ø275, H=200, Ø160 | - dimensions Ø275, H=200, Ø160
| - pretok q = 170 m3/h | - flow rate q = 170 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip VVKN-A-R-300 | - SYSTEMAIR type VVKN-A-R-300
| Oznaka: / | Tag: / | kpl | 2 |  | 0
11.25 | Stropni difuzor za odvod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno izolirano, maska je s fiksnimi lamelami, barve (RAL 9010) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, priključek odvoda zraka je predviden z vrha, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for exhaust air, housing made of galvanised sheet steel, soundproofed, mask with fixed louvres, colour (RAL 9010) or in the colour of the client's or architect's choice, with connection chamber, with control damper, exhaust air connection from the top, including all fixing and mounting material, type:
| - dimenzije Ø470, H=290, Ø200 | - dimensions Ø470, H=290, Ø200
| - pretok q = 330 m3/h | - flow rate q = 330 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip VVKN-A-R-500 | - SYSTEMAIR type VVKN-A-R-500
| Oznaka: / | Tag: / | kpl | 1 |  | 0
11.26 | Stropni difuzor za odvod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno izolirano, maska je s fiksnimi lamelami, barve (RAL 9010) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, priključek odvoda zraka je predviden z vrha, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for exhaust air, housing made of galvanised sheet steel, soundproofed, mask with fixed louvres, colour (RAL 9010) or in the colour of the client's or architect's choice, with connection chamber, with control damper, exhaust air connection from the top, including all fixing and mounting material, type:
| - dimenzije Ø470, H=290, Ø200 | - dimensions Ø470, H=290, Ø200
| - pretok q = 340 m3/h | - flow rate q = 340 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip VVKN-A-R-500 | - SYSTEMAIR type VVKN-A-R-500
| Oznaka: / | Tag: / | kpl | 2 |  | 0
11.27 | Stropni difuzor za odvod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno izolirano, maska je s fiksnimi lamelami, barve (RAL 9010) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, priključek odvoda zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for exhaust air, housing made of galvanised sheet steel, soundproofed, mask with fixed louvres, colour (RAL 9010) or in the colour of the client's or architect's choice, with connection chamber, with control damper, exhaust air connection provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø470, H=290, Ø200 | - dimensions Ø470, H=290, Ø200
| - pretok q = 400 m3/h | - flow rate q = 400 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip VVKN-A-R-500 | - SYSTEMAIR type VVKN-A-R-500
| Oznaka: / | Tag: / | kpl | 1 |  | 0
11.28 | Stropni difuzor za odvod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno izolirano, maska je s fiksnimi lamelami, barve (RAL 9010) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, priključek odvoda zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for exhaust air, housing made of galvanised sheet steel, soundproofed, mask with fixed louvres, colour (RAL 9010) or in the colour of the client's or architect's choice, with connection chamber, with control damper, exhaust air connection provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø470, H=290, Ø200 | - dimensions Ø470, H=290, Ø200
| - pretok q = 410 m3/h | - flow rate q = 410 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip VVKN-A-R-500 | - SYSTEMAIR type VVKN-A-R-500
| Oznaka: / | Tag: / | kpl | 1 |  | 0
11.29 | Prezračevalni ventil za odvod zraka, izdelan iz jeklene pločevine, belo prašnato obarvane v RAL9016-90 ali po izboru arhitekta, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Air vent valve for exhaust air, made of sheet steel, powder-coated white in RAL9016-90 or architect's choice, including all fixing and mounting material, type:
| - dimenzije Ø80 | - ø80 dimensions
| - pretok q = 30 m3/h | - flow rate q = 30 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip EFF-80 | - SYSTEMAIR tip EFF-80
| Oznaka: / | Tag: / | kpl | 4 |  | 0
11.30 | Prezračevalni ventil za odvod zraka, izdelan iz jeklene pločevine, belo prašnato obarvane v RAL9016-90 ali po izboru arhitekta, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Air vent valve for exhaust air, made of sheet steel, powder-coated white in RAL9016-90 or architect's choice, including all fixing and mounting material, type:
| - dimenzije Ø125 | - dimensions Ø125
| - pretok q = 90 m3/h | - flow rate q = 90 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip EFF-125 | - SYSTEMAIR tip EFF-125
| Oznaka: / | Tag: / | kpl | 12 |  | 0
11.31 | Linijski difuzor za odvod zraka, izdelan iz aluminijastih profilov, belo prašnato obarvane v RAL9003 ali po izboru arhitekta in komore iz pocinkane pločevine, kompletno s priključki iz strani in regulacijsko loputo za nastavitev volumskega pretoka zraka, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Linear diffuser for exhaust air, made of aluminium profiles, powder-coated white RAL9003 or architect's choice, and chamber of galvanised sheet metal, complete with side connections and control flap for volume flow adjustment, including all fixing and mounting material, type:
| - dimenzije L=500, H=250, Ø125 | - dimensions L=500, H=250, Ø125
| - pretok q = 20 m3/h | - flow rate q = 20 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip HELLA-2-500 | - SYSTEMAIR tip HELLA-2-500
| Oznaka: / | Tag: / | kpl | 1 |  | 0
11.32 | Linijski difuzor za odvod zraka, izdelan iz aluminijastih profilov, belo prašnato obarvane v RAL9003 ali po izboru arhitekta in komore iz pocinkane pločevine, kompletno s priključki iz strani in regulacijsko loputo za nastavitev volumskega pretoka zraka, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Linear diffuser for exhaust air, made of aluminium profiles, powder-coated white RAL9003 or architect's choice, and chamber of galvanised sheet metal, complete with side connections and control flap for volume flow adjustment, including all fixing and mounting material, type:
| - dimenzije L=500, H=250, Ø125 | - dimensions L=500, H=250, Ø125
| - pretok q = 40 m3/h | - flow rate q = 40 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip HELLA-2-500 | - SYSTEMAIR tip HELLA-2-500
| Oznaka: / | Tag: / | kpl | 6 |  | 0
11.33 | Linijski difuzor za odvod zraka, izdelan iz aluminijastih profilov, belo prašnato obarvane v RAL9003 ali po izboru arhitekta in komore iz pocinkane pločevine, kompletno s priključki iz strani in regulacijsko loputo za nastavitev volumskega pretoka zraka, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Linear diffuser for exhaust air, made of aluminium profiles, powder-coated white RAL9003 or architect's choice, and chamber of galvanised sheet metal, complete with side connections and control flap for volume flow adjustment, including all fixing and mounting material, type:
| - dimenzije L=500, H=250, Ø125 | - dimensions L=500, H=250, Ø125
| - pretok q = 50 m3/h | - flow rate q = 50 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip HELLA-2-500 | - SYSTEMAIR tip HELLA-2-500
| Oznaka: / | Tag: / | kpl | 1 |  | 0
11.34 | Linijski difuzor za odvod zraka, izdelan iz aluminijastih profilov, belo prašnato obarvane v RAL9003 ali po izboru arhitekta in komore iz pocinkane pločevine, kompletno s priključki iz strani in regulacijsko loputo za nastavitev volumskega pretoka zraka, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Linear diffuser for exhaust air, made of aluminium profiles powder-coated white RAL9003 or architect's choice and chamber of galvanised sheet metal, complete with side connections and control flap for volume flow adjustment, including all fixing and mounting material, type:
| - dimenzije L=900, H=250, Ø125 | - dimensions L=900, H=250, Ø125
| - pretok q = 70 m3/h | - flow rate q = 70 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip HELLA-2-900 | - SYSTEMAIR tip HELLA-2-900
| Oznaka: / | Tag: / | kpl | 1 |  | 0
11.35 | Linijski difuzor za odvod zraka, izdelan iz aluminijastih profilov, belo prašnato obarvane v RAL9003 ali po izboru arhitekta in komore iz pocinkane pločevine, kompletno s priključki iz strani in regulacijsko loputo za nastavitev volumskega pretoka zraka, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Linear diffuser for exhaust air, made of aluminium profiles powder-coated white RAL9003 or architect's choice and chamber of galvanised sheet metal, complete with side connections and control flap for volume flow adjustment, including all fixing and mounting material, type:
| - dimenzije L=900, H=250, Ø125 | - dimensions L=900, H=250, Ø125
| - pretok q = 90 m3/h | - flow rate q = 90 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip HELLA-2-900 | - SYSTEMAIR tip HELLA-2-900
| Oznaka: / | Tag: / | kpl | 1 |  | 0
11.36 | Linijski difuzor za odvod zraka, izdelan iz aluminijastih profilov, belo prašnato obarvane v RAL9003 ali po izboru arhitekta in komore iz pocinkane pločevine, kompletno s priključki iz strani in regulacijsko loputo za nastavitev volumskega pretoka zraka, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Linear diffuser for exhaust air, made of aluminium profiles powder-coated white RAL9003 or architect's choice and chamber of galvanised sheet metal, complete with side connections and control flap for volume flow adjustment, including all fixing and mounting material, type:
| - dimenzije L=900, H=250, Ø125 | - dimensions L=900, H=250, Ø125
| - pretok q = 100 m3/h | - flow rate q = 100 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip HELLA-2-900 | - SYSTEMAIR tip HELLA-2-900
| Oznaka: / | Tag: / | kpl | 2 |  | 0
11.37 | Linijski difuzor za odvod zraka, izdelan iz aluminijastih profilov, belo prašnato obarvane v RAL9003 ali po izboru arhitekta in komore iz pocinkane pločevine, kompletno s priključki iz strani in regulacijsko loputo za nastavitev volumskega pretoka zraka, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Linear diffuser for exhaust air, made of aluminium profiles powder-coated white RAL9003 or architect's choice and chamber of galvanised sheet metal, complete with side connections and control flap for volume flow adjustment, including all fixing and mounting material, type:
| - dimenzije L=1000, H=250, Ø160 | - dimensions L=1000, H=250, Ø160
| - pretok q = 130 m3/h | - flow rate q = 130 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip HELLA-2-1000 | - SYSTEMAIR tip HELLA-2-1000
| Oznaka: / | Tag: / | kpl | 1 |  | 0
11.38 | Prezračevalna rešetka za vgradnjo v vrata, izdelana iz aluminijastih profilov s fiksnimi lamelami, prašnato obarvane v barvi RAL9003 ali po izboru arhitekta, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ventilation grille for installation in doors, made of aluminium profiles with fixed slats, powder-coated RAL9003 or architect's choice, including all fixing and mounting materials, type:
| - dimenzije 400x300 | - dimensions 400x300
| - pretok q = 360 m3/h | - flow rate q = 360 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-D-1-400x300 | - SYSTEMAIR tip NOVA-D-1-400x300
| Oznaka: / | Tag: / | kpl | 2 |  | 0
11.39 | Prezračevalna rešetka za vgradnjo v vrata, izdelana iz aluminijastih profilov s fiksnimi lamelami, prašnato obarvane v barvi RAL9003 ali po izboru arhitekta, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ventilation grille for installation in doors, made of aluminium profiles with fixed slats, powder-coated RAL9003 or architect's choice, including all fixing and mounting materials, type:
| - dimenzije 400x300 | - dimensions 400x300
| - pretok q = 270 m3/h | - flow rate q = 270 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-D-1-400x300 | - SYSTEMAIR tip NOVA-D-1-400x300
| Oznaka: / | Tag: / | kpl | 1 |  | 0
11.40 | Prezračevalna rešetka za vgradnjo v vrata, izdelana iz aluminijastih profilov s fiksnimi lamelami, prašnato obarvane v barvi RAL9003 ali po izboru arhitekta, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ventilation grille for installation in doors, made of aluminium profiles with fixed slats, powder-coated RAL9003 or architect's choice, including all fixing and mounting materials, type:
| - dimenzije 300x150 | - dimensions 300x150
| - pretok q = 90 m3/h | - flow rate q = 90 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-D-1-300x150 | - SYSTEMAIR tip NOVA-D-1-300x150
| Oznaka: / | Tag: / | kpl | 1 |  | 0
11.41 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material of type:
| - dimenzije B=500/H=300 | - dimensions B=500/H=300
| - pretok q = 2315 m3/h | - flow rate q = 2315 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-500x300 | - SYSTEMAIR tip FDS-3G-500x300
| Oznaka: KFD17.371; KFD17.372 | Code: KFD17.371; KFD17.372 | kpl | 2 |  | 0
11.42 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material of type:
| - dimenzije B=400/H=250 | - dimensions B=400/H=250
| - pretok q = 1435 m3/h | - flow rate q = 1435 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-400x250 | - SYSTEMAIR tip FDS-3G-400x250
| Oznaka: KFD17.273 | Code: KFD17.273 | kpl | 1 |  | 0
11.43 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije B=400/H=200 | - dimensions B=400/H=200
| - pretok q = 880 m3/h | - flow rate q = 880 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-400x200 | - SYSTEMAIR tip FDS-3G-400x200
| Oznaka: KFD17.283; KFD17.381; KFD17.382 | Code: KFD17.283; KFD17.381; KFD17.382 | kpl | 3 |  | 0
11.44 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije B=500/H=300 | - dimensions B=500/H=300
| - pretok q = 2155 m3/h | - flow rate q = 2155 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-500x300 | - SYSTEMAIR tip FDS-3G-500x300
| Oznaka: KFD17.274 | Code: KFD17.274 | kpl | 1 |  | 0
11.45 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije B=500/H=300 | - dimensions B=500/H=300
| - pretok q = 2200 m3/h | - flow rate q = 2200 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-500x300 | - SYSTEMAIR tip FDS-3G-500x300
| Oznaka: KFD17.284 | Code: KFD17.284 | kpl | 1 |  | 0
11.46 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije Ø100 | - ø100 dimensions
| - pretok q = 30 m3/h | - flow rate q = 30 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-100 | - SYSTEMAIR tip FDR-3G-100
| Oznaka: KFD17.271; KFD17.272; KFD17.281; KFD17.282 | Code: KFD17.271; KFD17.272; KFD17.281; KFD17.282 | kpl | 4 |  | 0
11.47 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije Ø200 | - ø200 dimensions
| - pretok q = 250 m3/h | - flow rate q = 250 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-200 | - SYSTEMAIR tip FDR-3G-200
| Oznaka: KFD17.171 | Code: KFD17.171 | kpl | 1 |  | 0
11.48 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije Ø160 | - ø160 dimensions
| - pretok q = 200 m3/h | - flow rate q = 200 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-160 | - SYSTEMAIR tip FDR-3G-160
| Oznaka: KFD17.172 | Code: KFD17.172 | kpl | 1 |  | 0
11.49 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije Ø225 | - dimensions Ø225
| - pretok q = 450 m3/h | - flow rate q = 450 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-225 | - SYSTEMAIR tip FDR-3G-225
| Oznaka: KFD17.181 | Code: KFD17.181 | kpl | 1 |  | 0
11.50 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije B=250/H=300 | - dimensions B=250/H=300
| - pretok q = 1080 m3/h | - flow rate q = 1080 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-250x300 | - SYSTEMAIR tip FDS-3G-250x300
| Oznaka: KFD17.182 | Code: KFD17.182 | kpl | 1 |  | 0
11.51 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije Ø315 | - dimensions Ø315
| - pretok q = 630 m3/h | - flow rate q = 630 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-315 | - SYSTEMAIR tip FDR-3G-315
| Oznaka: KFD17.071 | Code: KFD17.071 | kpl | 1 |  | 0
11.52 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije Ø250 | - dimensions Ø250
| - pretok q = 630 m3/h | - flow rate q = 630 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-250 | - SYSTEMAIR tip FDR-3G-250
| Oznaka: KFD17.081 | Code: KFD17.081 | kpl | 1 |  | 0
11.53 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo regulacije konstantnega pretoka, s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow regulator, made of galvanised sheet metal with acoustic and thermal insulation, with constant flow control function, with fastening and sealing material type:
| - dimenzije Ø180 | - dimensions Ø180
| - pretok q = 630m3/h | - flow rate q = 630m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOTUS-RI-180-M0 | - SYSTEMAIR tip NOTUS-RI-180-M0
| Oznaka: CAV17.101 | Code: CAV17.101 | kpl | 1 |  | 0
11.54 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo regulacije konstantnega pretoka, s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow regulator, made of galvanised sheet metal with acoustic and thermal insulation, with constant flow control function, with fastening and sealing material type:
| - dimenzije Ø140 | - ø140 dimensions
| - pretok q = 360m3/h | - flow rate q = 360m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOTUS-RI-140-M0 | - SYSTEMAIR tip NOTUS-RI-140-M0
| Oznaka: CAV17.151 | Code: CAV17.151 | kpl | 1 |  | 0
11.55 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo regulacije konstantnega pretoka, s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow regulator, made of galvanised sheet metal with acoustic and thermal insulation, with constant flow control function, with fastening and sealing material type:
| - dimenzije Ø125 | - dimensions Ø125
| - pretok q = 270m3/h | - flow rate q = 270m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOTUS-RI-125-M0 | - SYSTEMAIR tip NOTUS-RI-125-M0
| Oznaka: CAV17.152 | Code: CAV17.152 | kpl | 1 |  | 0
11.56 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo regulacije konstantnega pretoka, s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow regulator, made of galvanised sheet metal with acoustic and thermal insulation, with constant flow control function, with fastening and sealing material type:
| - dimenzije Ø125 | - dimensions Ø125
| - pretok q = 250m3/h | - flow rate q = 250m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOTUS-RI-125-M0 | - SYSTEMAIR tip NOTUS-RI-125-M0
| Oznaka: CAV17.201 | Code: CAV17.201 | kpl | 1 |  | 0
11.57 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo regulacije konstantnega pretoka, s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow regulator, made of galvanised sheet metal with acoustic and thermal insulation, with constant flow control function, with fastening and sealing material type:
| - dimenzije Ø100 | - ø100 dimensions
| - pretok q = 200m3/h | - flow rate q = 200m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOTUS-RI-100-M0 | - SYSTEMAIR tip NOTUS-RI-100-M0
| Oznaka: CAV17.202 | Code: CAV17.202 | kpl | 1 |  | 0
11.58 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo regulacije konstantnega pretoka, s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow regulator, made of galvanised sheet metal with acoustic and thermal insulation, with constant flow control function, with fastening and sealing material type:
| - dimenzije Ø140 | - dimensions Ø140
| - pretok q = 360m3/h | - flow rate q = 360m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOTUS-RI-140-M0 | - SYSTEMAIR tip NOTUS-RI-140-M0
| Oznaka: CAV17.251 | Code: CAV17.251 | kpl | 1 |  | 0
11.59 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo regulacije konstantnega pretoka, s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow regulator, made of galvanised sheet metal with acoustic and thermal insulation, with constant flow control function, with fastening and sealing material type:
| - dimenzije Ø80 | - ø80 dimensions
| - pretok q = 90m3/h | - flow rate q = 90m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOTUS-RI-80-M0 | - SYSTEMAIR tip NOTUS-RI-80-M0
| Oznaka: CAV17.252 | Code: CAV17.252 | kpl | 1 |  | 0
11.60 | Volumski regulator pretoka zraka, izdelan iz polimernega materiala, s funkcijo regulacije konstantnega pretoka, s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow regulator, made of polymer material, with constant flow control function, with fastening and sealing material type:
| - dimenzije Ø80 | - ø80 dimensions
| - pretok q = 30m3/h | - flow rate q = 30m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip RDR-80/15-50 | - SYSTEMAIR tip RDR-80/15-50
| Oznaka: CAV17.301; CAV17.302; CAV17.315; CAV17.316; CAV17.351; CAV17.352; CAV17.363; CAV17.364 | Code: CAV17.301; CAV17.302; CAV17.315; CAV17.316; CAV17.351; CAV17.352; CAV17.363; CAV17.364 | kpl | 8 |  | 0
11.61 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo regulacije konstantnega pretoka, s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow regulator, made of galvanised sheet metal with acoustic and thermal insulation, with constant flow control function, with fastening and sealing material type:
| - dimenzije Ø80 | - ø80 dimensions
| - pretok q = 125m3/h | - flow rate q = 125m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOTUS-RI-80-M0 | - SYSTEMAIR tip NOTUS-RI-80-M0
| Oznaka: CAV17.303; CAV17.304 | Code: CAV17.303; CAV17.304 | kpl | 2 |  | 0
11.62 | Volumski regulator pretoka zraka, izdelan iz polimernega materiala, s funkcijo regulacije konstantnega pretoka, s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow regulator, made of polymer material, with constant flow control function, with fastening and sealing material type:
| - dimenzije Ø80 | - ø80 dimensions
| - pretok q = 40m3/h | - flow rate q = 40m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip RDR-80/15-50 | - SYSTEMAIR tip RDR-80/15-50
| Oznaka: CAV17.305; CAV17.306; CAV17.310; CAV17.312; CAV17.313; CAV17.314; CAV17.353; CAV17.354; CAV17.358; CAV17.360; CAV17.361; CAV17.362 | Code: CAV17.305; CAV17.306; CAV17.310; CAV17.312; CAV17.313; CAV17.314; CAV17.353; CAV17.354; CAV17.358; CAV17.360; CAV17.361; CAV17.362 | kpl | 12 |  | 0
11.63 | Volumski regulator pretoka zraka, izdelan iz polimernega materiala, s funkcijo regulacije konstantnega pretoka, s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow regulator, made of polymer material, with constant flow control function, with fastening and sealing material type:
| - dimenzije Ø80 | - ø80 dimensions
| - pretok q = 50m3/h | - flow rate q = 50m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip RDR-80/15-50 | - SYSTEMAIR tip RDR-80/15-50
| Oznaka: CAV17.307; CAV17.355 | Code: CAV17.307; CAV17.355 | kpl | 2 |  | 0
11.64 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo regulacije konstantnega pretoka, s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow regulator, made of galvanised sheet metal with acoustic and thermal insulation, with constant flow control function, with fastening and sealing material type:
| - dimenzije Ø80 | - ø80 dimensions
| - pretok q = 70m3/h | - flow rate q = 70m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOTUS-RI-80-M0 | - SYSTEMAIR tip NOTUS-RI-80-M0
| Oznaka: CAV17.308; CAV17.356 | Code: CAV17.308; CAV17.356 | kpl | 2 |  | 0
11.65 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo regulacije konstantnega pretoka, s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow regulator, made of galvanised sheet metal with acoustic and thermal insulation, with constant flow control function, with fastening and sealing material type:
| - dimenzije Ø80 | - ø80 dimensions
| - pretok q = 90m3/h | - flow rate q = 90m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOTUS-RI-80-M0 | - SYSTEMAIR tip NOTUS-RI-80-M0
| Oznaka: CAV17.309; CAV17.357 | Code: CAV17.309; CAV17.357 | kpl | 2 |  | 0
11.66 | Volumski regulator pretoka zraka, izdelan iz polimernega materiala, s funkcijo regulacije konstantnega pretoka, s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow regulator, made of polymer material, with constant flow control function, with fastening and sealing material type:
| - dimenzije Ø80 | - ø80 dimensions
| - pretok q = 20m3/h | - flow rate q = 20m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip RDR-80/15-50 | - SYSTEMAIR tip RDR-80/15-50
| Oznaka: CAV17.311; CAV17.359 | Code: CAV17.311; CAV17.359 | kpl | 2 |  | 0
11.67 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø200 | - ø200 dimensions
| - pretok q = 620 do 190m3/h | - flow rate q = 620 to 190m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-200 | - SYSTEMAIR tip OPTIMA-LV-RI-200
| Oznaka: VAV17.301 | Code: VAV17.301 | kpl | 1 |  | 0
11.68 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø125 | - dimensions Ø125
| - pretok q = 170 do 150m3/h | - flow rate q = 170 to 150m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-125 | - SYSTEMAIR tip OPTIMA-LV-RI-125
| Oznaka: VAV17.351 | Code: VAV17.351 | kpl | 1 |  | 0
11.69 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø100 | - ø100 dimensions
| - pretok q = 150 do 50m3/h | - flow rate q = 150 to 50m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-100 | - SYSTEMAIR tip OPTIMA-LV-RI-100
| Oznaka: VAV17.302 | Code: VAV17.302 | kpl | 1 |  | 0
11.70 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø125 | - dimensions Ø125
| - pretok q = 170 do 60m3/h | - flow rate q = 170 to 60m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-125 | - SYSTEMAIR tip OPTIMA-LV-RI-125
| Oznaka: VAV17.352 | Code: VAV17.352 | kpl | 1 |  | 0
11.71 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø100 | - ø100 dimensions
| - pretok q = 130 do 50m3/h | - flow rate q = 130 to 50m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-100 | - SYSTEMAIR tip OPTIMA-LV-RI-100
| Oznaka: VAV17.303; VAV17.353 | Code: VAV17.303; VAV17.353 | kpl | 2 |  | 0
11.72 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function and type fastening and sealing material:
| - dimenzije Ø200 | - ø200 dimensions
| - pretok q = 360 do 110m3/h | - flow rate q = 360 to 110m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-200 | - SYSTEMAIR tip OPTIMA-LV-RI-200
| Oznaka: VAV17.304 | Code: VAV17.304 | kpl | 1 |  | 0
11.73 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function and type fastening and sealing material:
| - dimenzije Ø180 | - dimensions Ø180
| - pretok q = 400 do 120m3/h | - flow rate q = 400 to 120m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-180 | - SYSTEMAIR tip OPTIMA-LV-RI-180
| Oznaka: VAV17.354 | Code: VAV17.354 | kpl | 1 |  | 0
11.74 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function and type fastening and sealing material:
| - dimenzije Ø200 | - ø200 dimensions
| - pretok q = 370 do 120m3/h | - flow rate q = 370 to 120m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-200 | - SYSTEMAIR tip OPTIMA-LV-RI-200
| Oznaka: VAV17.305 | Code: VAV17.305 | kpl | 1 |  | 0
11.75 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function and type fastening and sealing material:
| - dimenzije Ø180 | - dimensions Ø180
| - pretok q = 410 do 130m3/h | - flow rate q = 410 to 130m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-180 | - SYSTEMAIR tip OPTIMA-LV-RI-180
| Oznaka: VAV17.355 | Code: VAV17.355 | kpl | 1 |  | 0
11.76 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function and type fastening and sealing material:
| - dimenzije Ø100 | - ø100 dimensions
| - pretok q = 100 do 60m3/h | - flow rate q = 100 to 60m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-100 | - SYSTEMAIR tip OPTIMA-LV-RI-100
| Oznaka: VAV17.306; VAV17.356 | Code: VAV17.306; VAV17.356 | kpl | 2 |  | 0
11.77 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function and type fastening and sealing material:
| - dimenzije Ø100 | - ø100 dimensions
| - pretok q = 100 do 50m3/h | - flow rate q = 100 to 50m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-100 | - SYSTEMAIR tip OPTIMA-LV-RI-100
| Oznaka: VAV17.307; VAV17.357 | Code: VAV17.307; VAV17.357 | kpl | 2 |  | 0
11.78 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø200 | - ø200 dimensions
| - pretok q = 620 do 190m3/h | - flow rate q = 620 to 190m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-200 | - SYSTEMAIR tip OPTIMA-LV-RI-200
| Oznaka: VAV17.308 | Code: VAV17.308 | kpl | 1 |  | 0
11.79 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø250 | - dimensions Ø250
| - pretok q = 680 do 210m3/h | - flow rate q = 680 to 210m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-250 | - SYSTEMAIR tip OPTIMA-LV-RI-250
| Oznaka: VAV17.358 | Code: VAV17.358 | kpl | 1 |  | 0
11.80 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø160 | - ø160 dimensions
| - pretok q = 300 do 90m3/h | - flow rate q = 300 to 90m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-160 | - SYSTEMAIR tip OPTIMA-LV-RI-160
| Oznaka: VAV17.309 | Code: VAV17.309 | kpl | 1 |  | 0
11.81 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø160 | - ø160 dimensions
| - pretok q = 330 do 100m3/h | - flow rate q = 330 to 100m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-160 | - SYSTEMAIR tip OPTIMA-LV-RI-160
| Oznaka: VAV17.359 | Code: VAV17.359 | kpl | 1 |  | 0
11.82 | Elektromotorni pogon z vzmetjo za vstopno/izstopno žaluzijo klimata, vključno z varnostno funkcijo (NC) in stikali položaja, s pritrdilnim in tesnilnim materialom tipa: | Electric motor drive with spring for air-conditioning entry/exit blind, including safety function (NC) and position switches, with fixing and sealing material type:
| - navor 10Nm | - torque 10Nm
| - električno napajanje 24V AC/DC | - 24V AC/DC power supply
| - ON/OFF regulacija delovanja | - ON/OFF operation control
| - za žaluzije do 2m2 | - for blinds up to 2m2
| - zaščita IP54 | - iP54 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip NF24A-S2 | - BELIMO type NF24A-S2
| Oznaka: KD17.101; KD17.202 | Code: KD17.101; KD17.202 | kpl | 2 |  | 0
11.83 | Elektromotorni pogon za žaluzijo obtoka rekuperatorja, vključno s stikali položaja, s pritrdilnim in tesnilnim materialom tipa: | Electric motor drive for the recuperator circulation shutter, including position switches, with fixing and sealing material type:
| - navor 5Nm | - torque 5Nm
| - električno napajanje 24V AC/DC | - 24V AC/DC power supply
| - zvezna regulacija delovanja DC (0)2...10V | - dC continuous operation control (0)2...10V
| - za žaluzije do 1m2 | - for blinds up to 1m2
| - zaščita IP54 | - iP54 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip LM24A-SR | - BELIMO type LM24A-SR
| Oznaka: DY17.105 | Code: DY17.105 | kpl | 1 |  | 0
11.84 | Kanalsko tipalo diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Duct differential pressure sensor, with type fastening and sealing material:
| - območje prikazovanja od 0 do 1500 Pa | - display range 0 to 1500 Pa
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22ADP-184A | - BELIMO type 22ADP-184A
| Oznaka: PICAL17.115; PICAL17.215 | Code: PICAL17.115; PICAL17.215 | kpl | 2 |  | 0
11.85 | Tipalo diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure sensor, with mounting and sealing material type:
| - območje prikazovanja od 0 do 1500 Pa | - display range 0 to 1500 Pa
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22ADP-184A | - BELIMO type 22ADP-184A
| Oznaka: PDIC17.104; PDIC17.204 | Code: PDIC17.104; PDIC17.204 | kpl | 2 |  | 0
11.86 | Diferenčno tlačno stikalo, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure switch, with type fastening and sealing material:
| - območje prikazovanja od 50 do 500Pa | - display range 50 to 500Pa
| - kontaktni tok maksimalno 1,0A / AC 250V | - contact current max 1.0A / AC 250V
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 01APS-10U | - BELIMO type 01APS-10U
| Oznaka: PDSAH17.102; PDSAH17.112; PDSAH17.205; PDSAH17.207 | Code: PDSAH17.102; PDSAH17.112; PDSAH17.205; PDSAH17.207 | kpl | 4 |  | 0
11.87 | Prikazovalnik diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure indicator, with type fixing and sealing material:
| - območje prikazovanja od 50 do 500Pa | - display range 50 to 500Pa
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DWYER tip Magnahelic | - DWYER tip Magnahelic
| Oznaka: PDI17.102; PDI17.112; PDI17.205; PDI17.207 | Code: PDI17.102; PDI17.112; PDI17.205; PDI17.207 | kpl | 4 |  | 0
11.88 | Zunanje tipalo temperature in vlage, s pritrdilnim in tesnilnim materialom tipa: | External temperature and humidity sensor, with fixing and sealing material type:
| - območje prikazovanja od 0 do 100%RH | - display range 0 to 100%RH
| - območje prikazovanja od -40 do 60°C | - display range -40 to 60°C
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22UTH-13M | - BELIMO type 22UTH-13M
| Oznaka: TIC/MIC17.100 | Code: TIC/MIC17.100 | kpl | 1 |  | 0
11.89 | Kanalsko tipalo temperature in vlage, s pritrdilnim in tesnilnim materialom tipa: | Duct temperature and humidity sensor, with fixing and sealing material type:
| - območje prikazovanja od 0 do 100%RH | - display range 0 to 100%RH
| - območje prikazovanja od -40 do 60°C | - display range -40 to 60°C
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22DTH-13M | - BELIMO type 22DTH-13M
| Oznaka: TIC/MIC17.113; TIC/MIC17.208 | Code: TIC/MIC17.113; TIC/MIC17.208 | kpl | 2 |  | 0
11.90 | Prostorsko tipalo kvalitete zraka CO2, s pritrdilnim in tesnilnim materialom tipa: | Room air quality sensor CO2, with fixing and sealing material type:
| - območje CO2 od 0 do 2000ppm | - cO2 range 0 to 2000ppm
| - izhodni signal 0 do 10V | - output signal 0 to 10V
| - izhodni signal MP-Bus | - mP-Bus output signal
| - zaščita IP30 | - iP30 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22RTM-19-1 | - BELIMO type 22RTM-19-1
| Oznaka: QIC17.501; QIC17.502; QIC17.503 | Code: QIC17.501; QIC17.502; QIC17.503 | kpl | 3 |  | 0
11.91 | Protizmrzovalni termostat, s pritrdilnim in tesnilnim materialom tipa: | Anti-freezing thermostat, with fixing and sealing material type:
| - območje od -10 do 15°C | - range -10 to 15°C
| - dolžina kapilare 6m | - capillary length 6m
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 01ATS-105XC | - BELIMO type 01ATS-105XC
| Oznaka: TSZAL17.108 | Code: TSZAL17.108 | kpl | 1 |  | 0
11.92 | Obtočna črpalka, elektronsko regulirana s frekvenčnim pretvornikom, tipalom diferenčnega tlaka, internimi hidravličnimi, električnimi in komunikacijskimi povezavami, PN10, material jeklena litina, skladnost z ErP, pritrdilnim in tesnilnim materialom tipa: | Circulation pump, electronically controlled with frequency converter, differential pressure sensor, internal hydraulic, electrical and communication connections, PN10, material cast steel, ErP compliant, type fastening and sealing material:
| - za obtok ogrevne vode 50/40°C | - for circulating heating water 50/40°C
| - za pretok V = 3,21m3/h, tlačna višina H = 1,8m | - for flow rate V = 3,21m3/h, pressure head H = 1,8m
| - možnost izbire delovanja črpalke na proporcionalni tlak ter optimizacijo delovne obratovalne točke | - option to select proportional pressure pump operation and optimise the operating point
| - napajanje Pel = 0,050kW, 230V / 50Hz | - power supply Pel = 0,050kW, 230V/50Hz
| - navojni priključek G 1 1/2 | - threaded connection G 1 1/2
| - tlačna stopnja PN10 | - pressure rating PN10
| - temperaturno območje ogrevnega medija od -10 do 110°C | - temperature range of the heating medium from -10 to 110°C
| - komunikacija s CNS RS485 | - communication with CNS RS485
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - GRUNDFOS tip MAGNA3 25-40 | - GRUNDFOS type MAGNA3 25-40
| Oznaka: P17.107 | Code: P17.107 | kpl | 1 |  | 0
11.93 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za ogrevno vodo 50/40°C | - for heating water 50/40°C
| - za pretok V = 3,21m3/h | - for a flow rate of V = 3,21m3/h
| - območje regulacije pretoka do 7500 l/h (7,500 m3/h) | - flow control range up to 7,500 m3/h (7,500 l/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - navojni priključek G 2" po ISO 228/1 | - threaded connection G 2" to ISO 228/1
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 30 - 400 kPa, min. dif. tlak 30 kPa | - differential pressure range 30 - 400 kPa, min. differential pressure 30 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM40 | - DANFOS tip AB-QM40
| Oznaka: VA17.107 | Code: VA17.107 | kpl | 1 |  | 0
11.94 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za hladilno vodo 9/14°C | - for cooling water 9/14°C
| - za pretok V = 4,36m3/h | - for a flow rate of V = 4,36 m3/h
| - območje regulacije pretoka do 7500 l/h (7,500 m3/h) | - flow control range up to 7,500 m3/h (7,500 l/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - navojni priključek G 2" po ISO 228/1 | - threaded connection G 2" to ISO 228/1
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 30 - 400 kPa, min. dif. tlak 30 kPa | - differential pressure range 30 - 400 kPa, min. differential pressure 30 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM40 | - DANFOS tip AB-QM40
| Oznaka: VA17.110 | Code: VA17.110 | kpl | 1 |  | 0
| PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS17 | VENTILATION AND AIR CONDITIONING SYSTEM KS17 |  |  |  | 0

## 4.4.12_PrKlim KS18
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.4 | STROJNA DELA | MECHANICAL WORKS
4.4.12 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS18 | VENTILATION AND AIR CONDITIONING SYSTEM KS18 |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
12 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS18 | VENTILATION AND AIR CONDITIONING SYSTEM KS18
12.1 | Klimatska naprava za dovod in odvod zraka KD18/KO18 - glej tudi zavihek Zahteve klimati. | KD18/KO18 supply and extract air conditioner - see also Climate requirements tab.
| Tehnične karakteristike naprave (opis v smeri toka zraka): | Technical characteristics of the appliance (description downstream):
| Dovod: Vdov = 2920 m3/h | Input: Vdov = 2920 m3/h
| - posluževanje dovod: desno v smeri toka zraka! | - inlet: right in the direction of the air flow!
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 10 60% po ISO 16890 (M5 po SIST EN 779), z regulacijsko žaluzijo 780x495x125, s fleksibilnim čelnim priključkom, za pretok zraka 2920m3/h. Maksimalni končni padec tlaka 200Pa. Oznaka: F18.102 | - Filter unit with bag filter cartridge of filtration level ePM 10 60% according to ISO 16890 (M5 according to SIST EN 779), with control shutter 780x495x125, with flexible front connection, for air flow 2920m3/h. Maximum final pressure drop 200Pa. Code: F18.102
| - Rotacijska regeneratorska enota za prenos senzibilne in latentne toplote. Tehnični podatki za zimsko obdobje: - pretok zraka 2920/2670m3/h - stopnja vračanja občutene toplote: 75,8% - stopnja vračanja latentne toplote: 77,2% - vračanje toplotne energije: 32kW - stanje dovodnega zr. pred enoto: -13,00°C/90,0% - stanje dovodnega zraka za enoto: 12,80°C/41,8% Tehnični podatki za poletno obdobje: - pretok zraka 2920/2670m3/h - stopnja vračanja občutene toplote: 75,8% - stopnja vračanja latentne toplote: 73,2% - vračanje toplotne energije: 8,60kW - stanje dovodnega zr. pred enoto: 34,50°C/40,0% - stanje dovodnega zraka za enoto: 28,10°C/54,4% Oznaka: RE18.191 | - Rotary regenerative unit for sensible and latent heat transfer. technical data for the winter period: - air flow 2920/2670m3/h - sensible heat recovery rate: 75.8% - latent heat recovery rate: 77.2% - heat energy recovery: 32kW - supply air condition upstream of the unit: -13.00°C/90.0% - supply air condition for the unit: 12.80°C/41.8% Technical data for the summer period: - air flow 2920/2670m3/h - sensible heat recovery rate: 75.8% - latent heat recovery rate: 73.2% - heat energy recovery: 8.60kW - supply air condition upstream of the unit: 34.50°C/40.0% - supply air condition for the unit: 28.10°C/54.4% Code: RE18.191
| - Enota pred-grelnika zraka s protizmrzovalno zaščito. - pretok zraka 2920m3/h - grelna moč Qg=16,42kW - temperaturni režim ogrevnega medija 50/40°C - pretok ogrevnega medija 1,43m3/h - padec tlaka na zračni strani 33Pa - temperatura zraka vstop 12,80°C - temperatura zraka izstop 29,50°C - padec tlaka na strani ogr. medija (voda) 9,63kPa - priključka navojna 3/4" - tlačna stopnja PN16 Oznaka: HE18.103 | - Air preheater unit with anti-freeze protection. - air flow 2920m3/h - heating power Qg=16,42kW - heating medium temperature 50/40°C - heating medium flow 1,43m3/h - 33Pa pressure drop on the air side - air inlet temperature 12,80°C - air temperature outlet 29,50°C - pressure drop on the heating medium side (water) 9,63kPa - 3/4" threaded connectors - pressure rating PN16 Code: HE18.103
| - Prazna enota. | - Empty unit.
| - Vlažilna enota s kontaktnim vlaženjem zraka. Dovod sveže pripravljene demineralizirane vode, z materialom kontaktnega vlažilnika impregniranim srebrom, črpalko, potrebno merilno regulacijsko opremo, ventili na dovodu sveže vode ter ventilom na odvodu vode iz banje, s funkcijo samodejnega praznjenja banje vlažilnika in polnjenja s svežo pripravljeno mehčano vodo glede na prevodnost vode v banji, oziroma glede na čas ko vlažilnik ni v funkciji. Odvod kondenzata s sifonom z vodno in mehansko smardno zaporo. - pretok zraka 2920m3/h - priključna električna moč 0,05kW, 230V, 50Hz - padec tlaka na zračni strani dpz=9Pa - temperatura zraka vstop 29,5°C - relativna vlaga zraka vstop 15% - temperatura zraka izstop 27,27°C - relativna vlaga izstop 21% - izkoristek vlaženja 14,21% - vlaženje 6,48 kg/h - tipalo prevodonsti vode QICCD18.105 - tipalo zgornjega nivoja vode LICH18.105 - tipalo spodnjega nivoja vode LICL18.105 - elektromagnetni ventil za praznenje VD18.105 - elektromagnetni ventil za dovod sveže vode VD18.205 Oznaka: SH18.105 | - Humidification unit with contact humidification. Freshly prepared demineralised water supply, with silver-impregnated contact humidifier material, pump, necessary metering control equipment, valves at the fresh water inlet and at the water outlet of the humidifier tank, with automatic emptying of the humidifier tank and refilling with freshly prepared softened water according to the conductivity of the water in the tank, or according to the time when the humidifier is not in operation. Condensate drainage with siphon with water and mechanical odour trap. - air flow 2920m3/h - connection power 0,05kW, 230V, 50Hz - pressure drop on the air side dpz=9Pa - air temperature 29,5°C - relative humidity 15% - air temperature outlet 27,27°C - relative humidity 21% exit - humidification efficiency 14.21% - humidification 6,48 kg/h - water conductivity sensor QICCD18.105 - lICH18.105 upper water level sensor - lICL18.105 lower water level sensor - solenoid valve for emptying VD18.105 - fresh water solenoid valve VD18.205 Code: SH18.105
| - Prazna enota. | - Empty unit.
| - Enota hladilnika z eliminatorjem kapljic in koritom za odvod kondenzata. - pretok zraka 2920m3/h - hladilna moč Qhtot=12,54kW - temperaturni režim hladilnega medija 9/14°C - pretok hladilnega medija 2,15m3/h - padec tlaka na zračni strani 44/40Pa - temperatura zraka vstop 28,10°C - temperatura zraka izstop 18,80°C - padec tlaka na strani hl. medija (voda) 18,52kPa - priključka navojna 1" - tlačna stopnja PN16 Oznaka: HE18.106 | - Refrigerator unit with drip eliminator and condensate drain. - air flow 2920m3/h - cooling power Qhtot=12,54kW - cooling medium temperature 9/14°C - coolant flow rate 2,15m3/h - air-side pressure drop 44/40Pa - air temperature inlet 28,10°C - air temperature outlet 18,80°C - pressure drop on the medium side (water) 18,52 kPa - 1" threaded connectors - pressure rating PN16 Code: HE18.106
| - Ventilatorska enota s prostotekočim rotorjem. Elektromotor je EC-motor, s 100% zvezno regulacijo vrtljajev preko potenciometra (0-10V), ki omogoča nastavitev delovanja ventilatorja na ustrezno delovno točko. Enota vsebuje: okence O150 in svetilko s stikalom ter servisno stikalo. - pretok zraka 2920m3/h - eksterni statični padec tlaka dpext=300Pa - priključna električna moč 2,40kW, 3x400V, 50Hz - razred izkoristka elektromotorja IE5/EC - zaščita IP54 Oznaka: FA18.107 | - Fan unit with free-flowing rotor. The electric motor is an EC motor, with 100% continuous speed control via a potentiometer (0-10V), which allows the fan to be set to the appropriate operating point. The unit contains: an O150 window and a lamp with switch and a service switch. - air flow 2920m3/h - external static pressure drop dpext=300Pa - connection power 2,40kW, 3x400V, 50Hz - electric motor efficiency class IE5/EC - iP54 protection Code: FA18.107
| - Dušilna enota. - pretok zraka 2920m3/h - padec tlaka dp=10Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 7 17 18 21 15 11 12 Oznaka: DZ18.108 | - Throttle unit. - air flow 2920m3/h - pressure drop dp=10Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 7 17 18 21 15 11 12 Code: DZ18.108
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 1 75% po ISO 16890 (F8 po SIST EN 779, s fleksibilnim čelnim priključkom, za pretok zraka 2920m3/h. Maksimalni končni padec tlaka 300Pa. Oznaka: F18.109 | - Filter unit with bag filter cartridge of filtration level ePM 1 75% according to ISO 16890 (F8 according to SIST EN 779, with flexible front connection, for air flow 2920m3/h. Maximum final pressure drop 300Pa. Code: F18.109
| Dolžina: 7,010m | Length: 7,010m
| Širina: 1.055m | Width: 1.055m
| Višina: 0,775m | Height: 0,775m
| Kompletno z dobavo dodatne opreme: | Complete with supply of accessories:
| - odtočni sifoni | - drain traps
| - jadrovinasti nastavki | - sailplane spouts
| - s spojnim, tesnilnim in pritrdilnim materialom in priključki za senzorje, | - with jointing, sealing and fixing materials and sensor connectors,
| Odvod: Vodv = 2670 m3/h | Discharge: waterv = 2670 m3/h
| - posluževanje odvod: levo v smeri toka zraka! | - serving outlet: left in the direction of the air flow!
| - Filtrska enota z vrečastim filtrskim vložkom stopnje filtracije ePM 10 60% po ISO 16890 (M5 po SIST EN 779), s fleksibilnim čelnim priključkom, za pretok zraka 2670m3/h. Maksimalni končni padec tlaka 200Pa. Oznaka: F18.207 | - Filter unit with bag filter cartridge of filtration level ePM 10 60% according to ISO 16890 (M5 according to SIST EN 779), with flexible front connection, for an air flow of 2670m3/h. Maximum final pressure drop 200Pa. Code: F18.207
| - Dušilna enota. - pretok zraka 2670m3/h - padec tlaka dp=8Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 7 17 18 21 15 11 12 Oznaka: DZ18.206 | - Throttle unit. - air flow 2670m3/h - pressure drop dp=8Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 7 17 18 21 15 11 12 Code: DZ18.206
| - Ventilatorska enota s prostotekočim rotorjem. Elektromotor je EC-motor, s 100% zvezno regulacijo vrtljajev preko potenciometra (0-10V), ki omogoča nastavitev delovanja ventilatorja na ustrezno delovno točko. Enota vsebuje: okence O150 in svetilko s stikalom ter servisno stikalo. - pretok zraka 2670m3/h - eksterni statični padec tlaka dpext=300Pa - priključna električna moč 0,78kW, 230V, 50Hz - razred izkoristka elektromotorja IE4/EC - zaščita IP54 Oznaka: FA18.205 | - Fan unit with free-flowing rotor. The electric motor is an EC motor, with 100% continuous speed control via a potentiometer (0-10V), which allows the fan to be set to the appropriate operating point. The unit contains: an O150 window and a lamp with switch and a service switch. - air flow 2670m3/h - external static pressure drop dpext=300Pa - connection power 0,78kW, 230V, 50Hz - electric motor efficiency class IE4/EC - iP54 protection Code: FA18.205
| - Dušilna enota. - pretok zraka 2670m3/h - padec tlaka dp=9Pa sred. frekv. oktave [Hz] 63 125 250 500 1000 2000 4000 8000 dušenje zvoka [dB] 3 7 17 18 21 15 11 12 Oznaka: DZ18.204 | - Throttle unit. - air flow 2670m3/h - pressure drop dp=9Pa centre frequency octave [Hz] 63 125 250 500 1000 2000 4000 8000 sound attenuation [dB] 3 7 17 18 21 15 11 12 Code: DZ18.204
| - Prazna enota z regulacijsko žaluzijo 495x305x125, fleksibilnim čelnim priključkom, za pretok zraka 2670m3/h. | - Empty unit with control louvre 495x305x125, flexible front connection, for an air flow of 2670m3/h.
| Dolžina: 4,460m | Length: 4,460m
| Širina: 1,055m | Width: 1,055m
| Višina: 0,650m | Height: 0,650m
| Kompletno z dobavo dodatne opreme: | Complete with supply of accessories:
| - postavitvene noge, gumirane, višine 100-200mm | - rubberised feet, height 100-200mm
| - odtočni sifoni | - drain traps
| - jadrovinasti nastavki | - sailplane spouts
| - postavitev klimata na antivibracijski dušilnik (gumo) za preprečevanje prenosa vibracij in hrupa na konstrukcijo objekta. Dušilniki morajo biti preračunani glede na lastnosti klimata (teža in vrtilna frekvenca ventilatorjev). | - installation of the air conditioner on an anti-vibration damper (rubber) to prevent the transmission of vibrations and noise to the structure of the building. The dampers must be calculated according to the characteristics of the air conditioner (weight and speed of the fans).
| - s spojnim, tesnilnim in pritrdilnim materialom in priključki za senzorje, | - with jointing, sealing and fixing materials and sensor connectors,
| Teža: 1576kg | Weight: 1576kg
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR | - SYSTEMAIR | kpl | 1 |  | 0
12.2 | Okrogli prezračevalni kanali izdelani iz pocinkane pločevine po SIST EN 1506, vključno z revizijskimi odprtinami, oblikovnimi kosi, debeline po standardu. V ceni na enoto (m) je potrebno upoštevati ves spojni in pritrdilni material (prirobnice, odrez, spone, vijaki, tesnila, ojačitve, vključno z obešalnim in pritrdilnim materialom sistemskega proizvajalca z lastnostmi odgovarjajoč zahtevam SIST EN 12236: 2002, vključno pleskanje vseh kovinskih korozijsko nezaščitenih delov, po temeljitem predhodnem čiščenju do kovinskega sijaja. Antikorozijska zaščita se izvaja v skladu z EN 12944 za naslednje pogoje: • Življenjska doba več kot 15 let. • Stopnja korozijske atmosfere C4 (visoka). | Round ventilation ducts made of galvanised sheet metal according to SIST EN 1506, including inspection openings, shaped pieces, thickness according to the standard. The unit price (m) must take into account all joining and fixing material (flanges, cut-offs, clamps, bolts, gaskets, reinforcements, including hanging and fixing material of the system manufacturer with properties according to the requirements of SIST EN 12236: 2002, including painting of all metal corrosion-protected parts, after thorough cleaning to a metallic gloss. The corrosion protection shall be carried out in accordance with EN12944, for the following conditions: - Lifetime over 15 years. - Corrosive atmosphere C4 (high).
| - Okrogli prezračevalni kanali Ø80 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø80 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 25 |  | 0
| - Okrogli prezračevalni kanali Ø100 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø100 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 25 |  | 0
| - Okrogli prezračevalni kanali Ø125 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø125 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 15 |  | 0
| - Okrogli prezračevalni kanali Ø140 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø140 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 4 |  | 0
| - Okrogli prezračevalni kanali Ø150 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø150 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 3 |  | 0
| - Okrogli prezračevalni kanali Ø160 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø160 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 25 |  | 0
| - Okrogli prezračevalni kanali Ø180 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø180 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 15 |  | 0
| - Okrogli prezračevalni kanali Ø200 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø200 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 16 |  | 0
| - Okrogli prezračevalni kanali Ø250 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø250 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 80 |  | 0
| - Okrogli prezračevalni kanali Ø280 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø280 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 16 |  | 0
| - Okrogli prezračevalni kanali Ø300 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø300 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 5 |  | 0
| - Okrogli prezračevalni kanali Ø315 po SIST EN 1506:2007. Klasa tesnosti B po SIST EN 12237:2004. | - Round ventilation ducts Ø315 according to SIST EN 1506:2007. Tightness class B according to SIST EN 12237:2004. | m | 30 |  | 0
12.3 | Okrogli pregibni kanali za priključitev stropnih difuzorjev, izdelani iz Al folije ter polnila iz materiala z dušilnim in toplotno-izolativnim efektom. V ceni na enoto (m) je potrebno upoštevati ves spojni material, pritrdilne objemke in tesnilni material, za podatke: | Round folded ducts for the connection of ceiling diffusers, made of Al foil and filling material with damping and thermal insulation effect. The unit price (m) must include all joining material, fixing clamps and sealing material, for details:
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DEC tip: SONODEC - 25 | - DEC tip: SUNDAY - 25
| - Okroglegi pregibni kanali Ø125 | - Ø125 round flexible ducts | m | 10 |  | 0
| - Okroglegi pregibni kanali Ø160 | - Round flexible ducts Ø160 | m | 5 |  | 0
| - Okroglegi pregibni kanali Ø200 | - Ø200 round flexible ducts | m | 15 |  | 0
| - Okroglegi pregibni kanali Ø250 | - Round flexible ducts Ø250 | m | 6 |  | 0
12.4 | Pravokotni prezračevalni kanali izdelani iz pocinkane pločevine po SIST EN 1505:1999, debeline po DIN 24190, klase tesnosti B po SIST EN 1507:2006, vključno z revizijskimi odprtinami, oblikovnimi kosi. V ceni na enoto (m2) je potrebno upoštevati ves spojni in pritrdilni material (prirobnice, odrez, spone, vijaki, tesnila, usmerjevalniki, ojačitve, vključno z obešalnim in pritrdilnim materialom sistemskega proizvajalca z lastnostmi odgovarjajoč zahtevam SIST EN 12236: 2002, vključno pleskanje vseh kovinskih korozijsko nezaščitenih delov, po temeljitem predhodnem čiščenju do kovinskega sijaja. Antikorozijska zaščita se izvaja v skladu z EN 12944 za naslednje pogoje: • Življenjska doba več kot 15 let. • Stopnja korozijske atmosfere C4 (visoka). | Rectangular ventilation ducts made of galvanised sheet metal according to SIST EN 1505:1999, thickness according to DIN 24190, tightness class B according to SIST EN 1507:2006, including inspection openings, shaped pieces. The unit price (m2) must take into account all joining and fixing material (flanges, cut-off, clamps, bolts, gaskets, guides, reinforcements, including hanging and fixing material of the system manufacturer with properties according to the requirements of SIST EN 12236:2002, including the painting of all metal corrosion-protected parts, after thorough preliminary cleaning to a metallic gloss. The anticorrosive protection shall be performed in accordance with EN12944 for the following conditions: - Lifetime over 15 years. - Corrosive atmosphere C4 (high). | m2 | 145 |  | 0
12.5 | Toplotna izolacija zajemnih, izpušnih ter vtočnih kanalov s parozapornimi ploščami izdelanimi iz sintetičnega kavčuka z zaprto celično strukturo, toplotne prevodnosti manjše ali enake 0,033W/mK pri srednji temperaturi 0 °C, koeficient upora difuziji vodene pare večji ali enak 10000 testirano v skladu z EN 13469 za cevi in EN 12086 za plošče, požarna klasifikacija B/BL-s3,d0 po DIN 4102, oziroma po SIST EN 13501-1. | Thermal insulation of intake, exhaust and inlet ducts with vapour control panels made of synthetic rubber with closed cell structure, thermal conductivity less than or equal to 0,033 W/mK at a mean temperature of 0 °C, resistance coefficient to diffusion of water vapour greater than or equal to 10000 tested in accordance with EN 13469 for pipes and EN 12086 for panels, fire classification B/BL-s3,d0 according to DIN 4102, or according to SIST EN 13501-1.
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - ARMACELL tip: Armaflex AF | - ARMACELL tip: Armaflex AF
| Toplotna izolacija zunanjih kanalov na vtočni strani (VTZ-SUP), debeline s = 50 mm, + original lepilo, + 0,8mm Al pločevine | Thermal insulation of external ducts on the inlet side (VTZ-SUP), thickness s = 50 mm, + original adhesive, + 0.8 mm Al sheet | m2 | 40 |  | 0
| Toplotna izolacija zunanjih kanalov na odtočni strani (ODZ-ETA), debeline s = 50 mm, + original lepilo, + 0,8mm Al pločevine | Thermal insulation of external ducts on the drain side (ODZ-ETA), thickness s = 50 mm, + original adhesive, + 0,8 mm Al sheet | m2 | 52 |  | 0
| Toplotna izolacija notranjih kanalov na vtočni strani (VTZ-SUP), debeline s = 19 mm, + original lepilo | Thermal insulation of internal ducts on the inlet side (VTZ-SUP), thickness s = 19 mm, + original adhesive | m2 | 155 |  | 0
12.6 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z ragulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, soundproof and thermally insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to the client's or architect's preference, with connection chamber, with regulating flap, with connections for air flow measurement, inlet connection of the prepared air to be provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø497, H=252, Ø160 | - dimensions Ø497, H=252, Ø160
| - pretok q = 220 m3/h | - flow rate q = 220 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-C-160 | - SYSTEMAIR tip CAP-C-160
| Oznaka: / | Tag: / | kpl | 3 |  | 0
12.7 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, s ragulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, soundproof and thermally insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to the client's or architect's preference, with connection chamber, with regulating flap, with air flow measurement connections, ready-air inlet connection provided on the side, including all fixing and mounting material, type:
| - dimenzije Ø597, H=287, Ø200 | - dimensions Ø597, H=287, Ø200
| - pretok q = 260 m3/h | - flow rate q = 260 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-C-200 | - SYSTEMAIR tip CAP-C-200
| Oznaka: / | Tag: / | kpl | 2 |  | 0
12.8 | Stropni difuzor za dovod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno in toplotno izolirano, maska je iz plošče s polimernimi šobami, barve (RAL 9003) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, s ragulacijsko loputo, s priključki za meritev pretoka zraka, priključek dovoda pripravljenega zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for air inlet, housing made of galvanised sheet steel, soundproof and thermally insulated, hood made of panel with polymer nozzles, colour (RAL 9003) or colour according to the customer's or architect's preference, with connection chamber, with regulating damper, with connections for air flow measurement, inlet connection of the prepared air to be provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø608, H=332, Ø250 | - dimensions Ø608, H=332, Ø250
| - pretok q = 325/330 m3/h | - flow rate q = 325/330 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip CAP-C-250 | - SYSTEMAIR tip CAP-C-250
| Oznaka: / | Tag: / | kpl | 4 |  | 0
12.9 | Linijski difuzor za dovod zraka, izdelan iz aluminijastih profilov, belo prašnato obarvane v RAL9003 ali po izboru arhitekta in komore iz pocinkane pločevine, kompletno s priključki iz strani in regulacijsko loputo za nastavitev volumskega pretoka zraka, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Linear air inlet diffuser made of aluminium profiles, powder-coated white RAL9003 or architect's choice, and galvanised sheet metal chamber, complete with side connections and volume flow control damper, including all fixing and mounting material, type:
| - dimenzije L=500, H=250, Ø125 | - dimensions L=500, H=250, Ø125
| - pretok q = 80 m3/h | - flow rate q = 80 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip HELLA-2-500 | - SYSTEMAIR tip HELLA-2-500
| Oznaka: / | Tag: / | kpl | 1 |  | 0
12.10 | Linijski difuzor za dovod zraka, izdelan iz aluminijastih profilov, belo prašnato obarvane v RAL9003 ali po izboru arhitekta in komore iz pocinkane pločevine, kompletno s priključki iz strani in regulacijsko loputo za nastavitev volumskega pretoka zraka, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Linear air inlet diffuser made of aluminium profiles, powder-coated white RAL9003 or architect's choice, and galvanised sheet metal chamber, complete with side connections and volume flow control damper, including all fixing and mounting material, type:
| - dimenzije L=500, H=250, Ø125 | - dimensions L=500, H=250, Ø125
| - pretok q = 50 m3/h | - flow rate q = 50 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip HELLA-2-500 | - SYSTEMAIR tip HELLA-2-500
| Oznaka: / | Tag: / | kpl | 3 |  | 0
12.11 | Prezračevalni ventil za dovod zraka, izdelan iz jeklene pločevine, belo prašnato obarvane v RAL9016-90 ali po izboru arhitekta, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Air inlet ventilation valve made of sheet steel, powder-coated white in RAL9016-90 or architect's choice, including all fixing and mounting material, type:
| - dimenzije Ø100 | - ø100 dimensions
| - pretok q = 50 m3/h | - flow rate q = 50 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip TFF-100 | - SYSTEMAIR tip TFF-100
| Oznaka: / | Tag: / | kpl | 1 |  | 0
12.12 | Prezračevalni ventil za dovod zraka, izdelan iz jeklene pločevine, belo prašnato obarvane v RAL9016-90 ali po izboru arhitekta, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Air inlet ventilation valve made of sheet steel, powder-coated white in RAL9016-90 or architect's choice, including all fixing and mounting material, type:
| - dimenzije Ø100 | - ø100 dimensions
| - pretok q = 60 m3/h | - flow rate q = 60 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip TFF-100 | - SYSTEMAIR tip TFF-100
| Oznaka: / | Tag: / | kpl | 1 |  | 0
12.13 | Prezračevalni ventil za dovod zraka, izdelan iz jeklene pločevine, belo prašnato obarvane v RAL9016-90 ali po izboru arhitekta, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Air inlet ventilation valve made of sheet steel, powder-coated white in RAL9016-90 or architect's choice, including all fixing and mounting material, type:
| - dimenzije Ø80 | - ø80 dimensions
| - pretok q = 30 m3/h | - flow rate q = 30 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip TFF-80 | - SYSTEMAIR tip TFF-80
| Oznaka: / | Tag: / | kpl | 3 |  | 0
12.14 | Stropni difuzor za odvod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno izolirano, maska je s fiksnimi lamelami, barve (RAL 9010) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, s ragulacijsko loputo, priključek odvoda zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for exhaust air, housing made of galvanised sheet steel, soundproofed, mask with fixed louvres, colour (RAL 9010) or in the colour of the client's or architect's choice, with connection chamber, with air control damper, exhaust air connection provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø364, H=290, Ø200 | - dimensions Ø364, H=290, Ø200
| - pretok q = 235 m3/h | - flow rate q = 235 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip VVKN-A-R-400 | - SYSTEMAIR type VVKN-A-R-400
| Oznaka: / | Tag: / | kpl | 2 |  | 0
12.15 | Stropni difuzor za odvod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno izolirano, maska je s fiksnimi lamelami, barve (RAL 9010) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, s ragulacijsko loputo, priključek odvoda zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for exhaust air, housing made of galvanised sheet steel, soundproofed, mask with fixed louvres, colour (RAL 9010) or in the colour of the client's or architect's choice, with connection chamber, with air control damper, exhaust air connection provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø364, H=290, Ø200 | - dimensions Ø364, H=290, Ø200
| - pretok q = 295 m3/h | - flow rate q = 295 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip VVKN-A-R-400 | - SYSTEMAIR type VVKN-A-R-400
| Oznaka: / | Tag: / | kpl | 4 |  | 0
12.16 | Stropni difuzor za odvod zraka, ohišje je narejeno iz jeklene pocinkane pločevine zvočno izolirano, maska je s fiksnimi lamelami, barve (RAL 9010) ali v barvi po želji naročnika oziroma arhitekta, s priključno komoro, z regulacijsko loputo, priključek odvoda zraka je predviden s strani, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ceiling diffuser for exhaust air, housing made of galvanised sheet steel, soundproofed, mask with fixed louvres, colour (RAL 9010) or in the colour of the client's or architect's choice, with connection chamber, with control damper, exhaust air connection provided from the side, including all fixing and mounting material, type:
| - dimenzije Ø364, H=290, Ø200 | - dimensions Ø364, H=290, Ø200
| - pretok q = 180 m3/h | - flow rate q = 180 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip VVKN-A-R-400 | - SYSTEMAIR type VVKN-A-R-400
| Oznaka: / | Tag: / | kpl | 1 |  | 0
12.17 | Rešetka za odvod zraka, izdelana iz jeklene pocinkane pločevine, sestavljena iz nosilnega okvirja z navpičnim nastavljivim lamelam, dodatkom za nastavitev količine zraka, pritrditev rešetke na prezračevalni kanal, z ugradim okvirjem, vključno z vsem pritrdilnim in montažnim materialom, barva v skladu z zahtevam načrta arhitekture, tipa: | Air outlet grille made of galvanised sheet steel, consisting of a support frame with vertical adjustable slats, air volume adjustment accessory, grille attachment to the ventilation duct, with a framed frame, including all fixing and mounting material, colour according to the requirements of the architectural plan, type:
| - dimenzije B=400/H=100 | - dimensions B=400/H=100
| - pretok q = 150/145 m3/h | - flow rate q = 150/145 m3/h
| - prost prerez Aef=0,025 m2 | - free cross-section Aef=0,025 m2
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-C-1-400x100-R1 | - SYSTEMAIR tip NOVA-C-1-400x100-R1
| Oznaka: / | Tag: / | kpl | 4 |  | 0
12.18 | Prezračevalni ventil za odvod zraka, izdelan iz jeklene pločevine, belo prašnato obarvane v RAL9016-90 ali po izboru arhitekta, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Air vent valve for exhaust air, made of sheet steel, powder-coated white in RAL9016-90 or architect's choice, including all fixing and mounting material, type:
| - dimenzije Ø100 | - ø100 dimensions
| - pretok q = 50 m3/h | - flow rate q = 50 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip EFF-100 | - SYSTEMAIR tip EFF-100
| Oznaka: / | Tag: / | kpl | 1 |  | 0
12.19 | Prezračevalni ventil za odvod zraka, izdelan iz jeklene pločevine, belo prašnato obarvane v RAL9016-90 ali po izboru arhitekta, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Air vent valve for exhaust air, made of sheet steel, powder-coated white in RAL9016-90 or architect's choice, including all fixing and mounting material, type:
| - dimenzije Ø100 | - ø100 dimensions
| - pretok q = 60 m3/h | - flow rate q = 60 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip EFF-100 | - SYSTEMAIR tip EFF-100
| Oznaka: / | Tag: / | kpl | 1 |  | 0
12.20 | Prezračevalni ventil za odvod zraka, izdelan iz jeklene pločevine, belo prašnato obarvane v RAL9016-90 ali po izboru arhitekta, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Air vent valve for exhaust air, made of sheet steel, powder-coated white in RAL9016-90 or architect's choice, including all fixing and mounting material, type:
| - dimenzije Ø80 | - ø80 dimensions
| - pretok q = 30 m3/h | - flow rate q = 30 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip EFF-80 | - SYSTEMAIR tip EFF-80
| Oznaka: / | Tag: / | kpl | 3 |  | 0
12.21 | Linijski difuzor za odvod zraka, izdelan iz aluminijastih profilov, belo prašnato obarvane v RAL9003 ali po izboru arhitekta in komore iz pocinkane pločevine, kompletno s priključki iz strani in regulacijsko loputo za nastavitev volumskega pretoka zraka, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Linear diffuser for exhaust air, made of aluminium profiles, powder-coated white RAL9003 or architect's choice, and chamber of galvanised sheet metal, complete with side connections and control flap for volume flow adjustment, including all fixing and mounting material, type:
| - dimenzije L=500, H=250, Ø125 | - dimensions L=500, H=250, Ø125
| - pretok q = 50 m3/h | - flow rate q = 50 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip HELLA-2-500 | - SYSTEMAIR tip HELLA-2-500
| Oznaka: / | Tag: / | kpl | 1 |  | 0
12.22 | Prezračevalna rešetka za vgradnjo v vrata, izdelana iz aluminijastih profilov s fiksnimi lamelami, prašnato obarvane v barvi RAL9003 ali po izboru arhitekta, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ventilation grille for installation in doors, made of aluminium profiles with fixed slats, powder-coated RAL9003 or architect's choice, including all fixing and mounting materials, type:
| - dimenzije 300x150 | - dimensions 300x150
| - pretok q = 50 m3/h | - flow rate q = 50 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-D-1-300x150 | - SYSTEMAIR tip NOVA-D-1-300x150
| Oznaka: / | Tag: / | kpl | 2 |  | 0
12.23 | Prezračevalna rešetka za vgradnjo v vrata, izdelana iz aluminijastih profilov s fiksnimi lamelami, prašnato obarvane v barvi RAL9003 ali po izboru arhitekta, vključno z vsem pritrdilnim in montažnim materialom, tipa: | Ventilation grille for installation in doors, made of aluminium profiles with fixed slats, powder-coated RAL9003 or architect's choice, including all fixing and mounting materials, type:
| - dimenzije 300x150 | - dimensions 300x150
| - pretok q = 80 m3/h | - flow rate q = 80 m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOVA-D-1-300x150 | - SYSTEMAIR tip NOVA-D-1-300x150
| Oznaka: / | Tag: / | kpl | 1 |  | 0
12.24 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study with fastening and sealing material type:
| - dimenzije B=300/H=250 | - dimensions B=300/H=250
| - pretok q = 1090 m3/h | - flow rate q = 1090 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-300x250 | - SYSTEMAIR tip FDS-3G-300x250
| Oznaka: KFD18.301 | Code: KFD18.301 | kpl | 1 |  | 0
12.25 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study with fastening and sealing material type:
| - dimenzije B=300/H=250 | - dimensions B=300/H=250
| - pretok q = 1020 m3/h | - flow rate q = 1020 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-300x250 | - SYSTEMAIR tip FDS-3G-300x250
| Oznaka: KFD18.401 | Code: KFD18.401 | kpl | 1 |  | 0
12.26 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study with fastening and sealing material type:
| - dimenzije B=400/H=300 | - dimensions B=400/H=300
| - pretok q = 1830 m3/h | - flow rate q = 1830 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-400x300 | - SYSTEMAIR tip FDS-3G-400x300
| Oznaka: KFD18.302; KFD18.307; KFD18.308 | Code: KFD18.302; KFD18.307; KFD18.308 | kpl | 3 |  | 0
12.27 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study with fastening and sealing material type:
| - dimenzije B=400/H=300 | - dimensions B=400/H=300
| - pretok q = 1650 m3/h | - flow rate q = 1650 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDS-3G-400x300 | - SYSTEMAIR tip FDS-3G-400x300
| Oznaka: KFD18.402; KFD18.407; KFD18.408 | Code: KFD18.402; KFD18.407; KFD18.408 | kpl | 3 |  | 0
12.28 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study with fastening and sealing material type:
| - dimenzije Ø180 | - dimensions Ø180
| - pretok q = 220 m3/h | - flow rate q = 220 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-180 | - SYSTEMAIR tip FDR-3G-180
| Oznaka: KFD18.303 | Code: KFD18.303 | kpl | 1 |  | 0
12.29 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study with fastening and sealing material type:
| - dimenzije Ø140 | - ø140 dimensions
| - pretok q = 110 m3/h | - flow rate q = 110 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-140 | - SYSTEMAIR tip FDR-3G-140
| Oznaka: KFD18.304 | Code: KFD18.304 | kpl | 1 |  | 0
12.30 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study with fastening and sealing material type:
| - dimenzije Ø160 | - ø160 dimensions
| - pretok q = 170 m3/h | - flow rate q = 170 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-160 | - SYSTEMAIR tip FDR-3G-160
| Oznaka: KFD18.403 | Code: KFD18.403 | kpl | 1 |  | 0
12.31 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study with fastening and sealing material type:
| - dimenzije Ø100 | - ø100 dimensions
| - pretok q = 60 m3/h | - flow rate q = 60 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-100 | - SYSTEMAIR tip FDR-3G-100
| Oznaka: KFD18.404 | Code: KFD18.404 | kpl | 1 |  | 0
12.32 | Protipožarna loputa za vgradnjo v suhomontažno ali betonsko steno, krmiljenje lopute od zunanjega signala, z elektromotornim pogonom s končnimi mikrostikali za signalizacijo položaja lopute odprto/zaprto, z vzmetjo, s termičnim sprožilom nastavljenim na +72 °C, odporna na ogenj in hladen dim, požarne odpornosti EIS 90 po EN 13501-3, testirana po EN 1366-2, s certifikatom ZAG, z ohišjem iz pocinkane pločevine, skladna zhatevam elaborata požarne varnosti s pritrdilnim in tesnilnim materialom tipa: | Fire damper for installation in dry-walled or concrete walls, damper control by external signal, with electric motor drive with microswitches for signalling the open/closed position of the damper, spring-loaded, with thermal trigger set at +72 °C, fire and cold smoke resistant, fire resistance EIS 90 according to EN 13501-3, tested according to EN 1366-2, ZAG certified, with galvanised sheet metal housing, complying with the requirements of the fire safety study, with fastening and sealing material type:
| - dimenzije Ø100 | - ø100 dimensions
| - pretok q = 30 m3/h | - flow rate q = 30 m3/h
| - toplotni dilatacijski kompenzator 2xFCS | - 2xFCS thermal expansion compensator
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip FDR-3G-100 | - SYSTEMAIR tip FDR-3G-100
| Oznaka: KFD18.305; KFD18.306; KFD18.405; KFD18.406 | Code: KFD18.305; KFD18.306; KFD18.405; KFD18.406 | kpl | 4 |  | 0
12.33 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø200 | - ø200 dimensions
| - pretok q = 520 do 90m3/h | - flow rate q = 520 to 90m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-200 | - SYSTEMAIR tip OPTIMA-LV-RI-200
| Oznaka: VAV18.101 | Code: VAV18.101 | kpl | 1 |  | 0
12.34 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø200 | - ø200 dimensions
| - pretok q = 470 do 80m3/h | - flow rate q = 470 to 80m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-200 | - SYSTEMAIR tip OPTIMA-LV-RI-200
| Oznaka: VAV18.201 | Code: VAV18.201 | kpl | 1 |  | 0
12.35 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø315 | - dimensions Ø315
| - pretok q = 1310 do 220m3/h | - flow rate q = 1310 to 220m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-315 | - SYSTEMAIR tip OPTIMA-LV-RI-315
| Oznaka: VAV18.102 | Code: VAV18.102 | kpl | 1 |  | 0
12.36 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø315 | - dimensions Ø315
| - pretok q = 1180 do 200m3/h | - flow rate q = 1180 to 200m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-315 | - SYSTEMAIR tip OPTIMA-LV-RI-315
| Oznaka: VAV18.202 | Code: VAV18.202 | kpl | 1 |  | 0
12.37 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø200 | - ø200 dimensions
| - pretok q = 660 do 480m3/h | - flow rate q = 660 to 480m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-200 | - SYSTEMAIR tip OPTIMA-LV-RI-200
| Oznaka: VAV18.103 | Code: VAV18.103 | kpl | 1 |  | 0
12.38 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo zvezne regulacije pretoka s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow controller made of galvanised sheet metal with acoustic and thermal insulation, with continuous flow control function with type fastening and sealing material:
| - dimenzije Ø200 | - ø200 dimensions
| - pretok q = 590 do 430m3/h | - flow rate q = 590 to 430m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip OPTIMA-LV-RI-200 | - SYSTEMAIR tip OPTIMA-LV-RI-200
| Oznaka: VAV18.203 | Code: VAV18.203 | kpl | 1 |  | 0
12.39 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo regulacije konstantnega pretoka, s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow regulator, made of galvanised sheet metal with acoustic and thermal insulation, with constant flow control function, with fastening and sealing material type:
| - dimenzije Ø80 | - ø80 dimensions
| - pretok q = 80m3/h | - flow rate q = 80m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOTUS-RI-80-M0 | - SYSTEMAIR tip NOTUS-RI-80-M0
| Oznaka: CAV18.101 | Code: CAV18.101 | kpl | 1 |  | 0
12.40 | Volumski regulator pretoka zraka, izdelan iz pocinkane pločevine z zvočno in toplotno izolacijo, s funkcijo regulacije konstantnega pretoka, s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow regulator, made of galvanised sheet metal with acoustic and thermal insulation, with constant flow control function, with fastening and sealing material type:
| - dimenzije Ø100 | - ø100 dimensions
| - pretok q = 180m3/h | - flow rate q = 180m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip NOTUS-RI-100-M0 | - SYSTEMAIR tip NOTUS-RI-100-M0
| Oznaka: CAV18.202 | Code: CAV18.202 | kpl | 1 |  | 0
12.41 | Volumski regulator pretoka zraka, izdelan iz polimernega materiala, s funkcijo regulacije konstantnega pretoka, s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow regulator, made of polymer material, with constant flow control function, with fastening and sealing material type:
| - dimenzije Ø100 | - ø100 dimensions
| - pretok q = 50m3/h | - flow rate q = 50m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip RDR-100/15-50 | - SYSTEMAIR tip RDR-100/15-50
| Oznaka: CAV18.102; CAV18.201 | Code: CAV18.102; CAV18.201 | kpl | 2 |  | 0
12.42 | Volumski regulator pretoka zraka, izdelan iz polimernega materiala, s funkcijo regulacije konstantnega pretoka, s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow regulator, made of polymer material, with constant flow control function, with fastening and sealing material type:
| - dimenzije Ø100 | - ø100 dimensions
| - pretok q = 60m3/h | - flow rate q = 60m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip RDR-100/50-100 | - SYSTEMAIR tip RDR-100/50-100
| Oznaka: CAV18.105; CAV18.203 | Code: CAV18.105; CAV18.203 | kpl | 2 |  | 0
12.43 | Volumski regulator pretoka zraka, izdelan iz polimernega materiala, s funkcijo regulacije konstantnega pretoka, s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow regulator, made of polymer material, with constant flow control function, with fastening and sealing material type:
| - dimenzije Ø80 | - ø80 dimensions
| - pretok q = 50m3/h | - flow rate q = 50m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip RDR-80/15-50 | - SYSTEMAIR tip RDR-80/15-50
| Oznaka: CAV18.103; CAV18.104; CAV18.106; CAV18.204 | Code: CAV18.103; CAV18.104; CAV18.106; CAV18.204 | kpl | 4 |  | 0
12.44 | Volumski regulator pretoka zraka, izdelan iz polimernega materiala, s funkcijo regulacije konstantnega pretoka, s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow regulator, made of polymer material, with constant flow control function, with fastening and sealing material type:
| - dimenzije Ø80 | - ø80 dimensions
| - pretok q = 30m3/h | - flow rate q = 30m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - SYSTEMAIR tip RDR-80/15-50 | - SYSTEMAIR tip RDR-80/15-50
| Oznaka: CAV18.107; CAV18.108; CAV18.109; CAV18.205; CAV18.206; CAV18.207 | Code: CAV18.107; CAV18.108; CAV18.109; CAV18.205; CAV18.206; CAV18.207 | kpl | 6 |  | 0
12.45 | Elektromotorni pogon z vzmetjo za vstopno/izstopno žaluzijo klimata, vključno z varnostno funkcijo (NC) in stikali položaja, s pritrdilnim in tesnilnim materialom tipa: | Electric motor drive with spring for air-conditioning entry/exit blind, including safety function (NC) and position switches, with fixing and sealing material type:
| - navor 10Nm | - torque 10Nm
| - električno napajanje 24V AC/DC | - 24V AC/DC power supply
| - ON/OFF regulacija delovanja | - ON/OFF operation control
| - za žaluzije do 2m2 | - for blinds up to 2m2
| - zaščita IP54 | - iP54 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip NF24A-S2 | - BELIMO type NF24A-S2
| Oznaka: KD18.101; KD18.202 | Code: KD18.101; KD18.202 | kpl | 2 |  | 0
12.46 | Kanalsko tipalo diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Duct differential pressure sensor, with type fastening and sealing material:
| - območje prikazovanja od 0 do 1500 Pa | - display range 0 to 1500 Pa
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22ADP-184A | - BELIMO type 22ADP-184A
| Oznaka: PICAL18.112; PICAL18.212 | Code: PICAL18.112; PICAL18.212 | kpl | 2 |  | 0
12.47 | Tipalo diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure sensor, with type fastening and sealing material:
| - območje prikazovanja od 0 do 1500 Pa | - display range 0 to 1500 Pa
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22ADP-184A | - BELIMO type 22ADP-184A
| Oznaka: PDIC18.107; PDIC18.205 | Code: PDIC18.107; PDIC18.205 | kpl | 2 |  | 0
12.48 | Diferenčno tlačno stikalo, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure switch, with type fastening and sealing material:
| - območje prikazovanja od 50 do 500Pa | - display range 50 to 500Pa
| - kontaktni tok maksimalno 1,0A / AC 250V | - contact current max 1.0A / AC 250V
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 01APS-10U | - BELIMO type 01APS-10U
| Oznaka: PDSAH18.102; PDSAH18.109; PDSAH18.203; PDSAH18.207 | Code: PDSAH18.102; PDSAH18.109; PDSAH18.203; PDSAH18.207 | kpl | 4 |  | 0
12.49 | Prikazovalnik diferenčnega tlaka, s pritrdilnim in tesnilnim materialom tipa: | Differential pressure indicator, with type fixing and sealing material:
| - območje prikazovanja od 50 do 500Pa | - display range 50 to 500Pa
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DWYER tip Magnahelic | - DWYER tip Magnahelic
| Oznaka: PDI18.102; PDI18.109; PDI18.203; PDI18.207 | Code: PDI18.102; PDI18.109; PDI18.203; PDI18.207 | kpl | 4 |  | 0
12.50 | Zunanje tipalo temperature in vlage, s pritrdilnim in tesnilnim materialom tipa: | External temperature and humidity sensor, with fixing and sealing material type:
| - območje prikazovanja od 0 do 100%RH | - display range 0 to 100%RH
| - območje prikazovanja od -40 do 60°C | - display range -40 to 60°C
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22UTH-13M | - BELIMO type 22UTH-13M
| Oznaka: TIC/MIC18.100 | Code: TIC/MIC18.100 | kpl | 1 |  | 0
12.51 | Kanalsko tipalo temperature in vlage, s pritrdilnim in tesnilnim materialom tipa: | Duct temperature and humidity sensor, with fixing and sealing material type:
| - območje prikazovanja od 0 do 100%RH | - display range 0 to 100%RH
| - območje prikazovanja od -40 do 60°C | - display range -40 to 60°C
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - izhodni signal 4-20mA | - output signal 4-20mA
| - zaščita IP65 | - iP65 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22DTH-13M | - BELIMO type 22DTH-13M
| Oznaka: TIC/MIC18.110; TIC/MIC18.208 | Code: TIC/MIC18.110; TIC/MIC18.208 | kpl | 2 |  | 0
12.52 | Prostorsko tipalo kvalitete zraka CO2, s pritrdilnim in tesnilnim materialom tipa: | Room air quality sensor CO2, with fixing and sealing material type:
| - območje CO2 od 0 do 2000ppm | - cO2 range 0 to 2000ppm
| - izhodni signal 0 do 10V | - output signal 0 to 10V
| - izhodni signal MP-Bus | - mP-Bus output signal
| - zaščita IP30 | - iP30 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 22RTM-19-1 | - BELIMO type 22RTM-19-1
| Oznaka: QIC18.501; QIC18.502; QIC18.503 | Code: QIC18.501; QIC18.502; QIC18.503 | kpl | 3 |  | 0
12.53 | Protizmrzovalni termostat, s pritrdilnim in tesnilnim materialom tipa: | Anti-freezing thermostat, with fixing and sealing material type:
| - območje od -10 do 15°C | - range -10 to 15°C
| - dolžina kapilare 6m | - capillary length 6m
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BELIMO tip 01ATS-105XC | - BELIMO type 01ATS-105XC
| Oznaka: TSZAL18.104 | Code: TSZAL18.104 | kpl | 1 |  | 0
12.54 | Obtočna črpalka, elektronsko regulirana s frekvenčnim pretvornikom, tipalom diferenčnega tlaka, internimi hidravličnimi, električnimi in komunikacijskimi povezavami, PN10, material jeklena litina, skladnost z ErP, pritrdilnim in tesnilnim materialom tipa: | Circulation pump, electronically controlled with frequency converter, differential pressure sensor, internal hydraulic, electrical and communication connections, PN10, material cast steel, ErP compliant, type fastening and sealing material:
| - za obtok ogrevne vode 50/40°C | - for circulating heating water 50/40°C
| - za pretok V = 1,43m3/h, tlačna višina H = 1,5m | - for flow rate V = 1,43m3/h, pressure head H = 1,5m
| - možnost izbire delovanja črpalke na proporcionalni tlak ter optimizacijo delovne obratovalne točke | - option to select proportional pressure pump operation and optimise the operating point
| - napajanje Pel = 0,050kW, 230V / 50Hz | - power supply Pel = 0,050kW, 230V/50Hz
| - navojni priključek G 1 1/2 | - threaded connection G 1 1/2
| - tlačna stopnja PN10 | - pressure rating PN10
| - temperaturno območje ogrevnega medija od -10 do 110°C | - temperature range of the heating medium from -10 to 110°C
| - komunikacija s CNS RS485 | - communication with CNS RS485
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - GRUNDFOS tip MAGNA3 25-40 | - GRUNDFOS type MAGNA3 25-40
| Oznaka: P18.103 | Code: P18.103 | kpl | 1 |  | 0
12.55 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za ogrevno vodo 50/40°C | - for heating water 50/40°C
| - za pretok V = 1,43m3/h | - for a flow rate of V = 1,43m3/h
| - območje regulacije pretoka do 1700 l/h (1,700 m3/h) | - flow control range up to 1,700 m3/h (1,700 l/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - navojni priključek G 1 1/4" po ISO 228/1 | - threaded connection G 1 1/4" to ISO 228/1
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 20 - 400 kPa, min. dif. tlak 20 kPa | - differential pressure range 20 - 400 kPa, min. differential pressure 20 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM25 | - DANFOS type AB-QM25
| Oznaka: VA18.103 | Code: VA18.103 | kpl | 1 |  | 0
12.56 | Prehodni tlačno neodvisni regulacijski ventil, z elektromotornim zveznim pogonom, z merilnimi priključki, s pritrdilnim in tesnilnim materialom tipa: | Pressure independent control valve, with electric motor drive, with gauge connections, with fastening and sealing material type:
| - za hladilno vodo 9/14°C | - for cooling water 9/14°C
| - za pretok V = 2,15m3/h | - for a flow rate of V = 2,15m3/h
| - območje regulacije pretoka do 3200 l/h (3,200 m3/h) | - flow control range up to 3200 l/h (3,200 m3/h)
| - napajanje 24V AC/DC | - 24V AC/DC power supply
| - vhodni signal 0-20mA/0-10V | - input signal 0-20mA/0-10V
| - navojni priključek G 1 1/2 po ISO 228/1 | - threaded connection G 1 1/2 according to ISO 228/1
| - tlačna stopnja PN16 | - pressure rating PN16
| - obseg diferenčnih tlakov 20 - 400 kPa, min. dif. tlak 20 kPa | - differential pressure range 20 - 400 kPa, min. differential pressure 20 kPa
| - zaščita IP42 | - iP42 protection
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - DANFOS tip AB-QM32 | - DANFOS type AB-QM32
| Oznaka: VA18.106 | Code: VA18.106 | kpl | 1 |  | 0
| PREZRAČEVANJE IN KLIMATIZACIJA SISTEM KS18 | VENTILATION AND AIR CONDITIONING SYSTEM KS18 |  |  |  | 0

## 4.4.13_PrKlim VS21
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.4 | STROJNA DELA | MECHANICAL WORKS
4.4.13 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM VS21 | VENTILATION AND AIR CONDITIONING SYSTEM VS21 |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
13 | PREZRAČEVANJE IN KLIMATIZACIJA SISTEM VS21 | VENTILATION AND AIR CONDITIONING SYSTEM VS21
13.1 | Centrifugalni ventilator v protihrupnem ohišju, izdelan iz ognjevarne plasitke PPs-el, primeren za ATEX cono 2 v notranjosti ventilatorja, z učinkovitim EC motorjem, Moodbus RS485 vmesnikom za povezavo na CNS, potenciometrom za nastavitev hitrosti, varnostnim stikalom, regulatorjem delovanja ventilatorja s funkcijo uzdrževanja konstantnega tlaka, vključno z nosilnim podstavkom, dušilci vibracij, spojnim, tesnilnim in pritrdilnim materialom, glej tudi zavihek Zahteve klimati. Izdelan za podatke: | Centrifugal fan in noise-proof housing, made of refractory PPs-el, suitable for ATEX zone 2 inside the fan, with efficient EC motor, Moodbus RS485 interface for connection to CNS, speed potentiometer, safety switch, fan controller with constant pressure maintenance function, including support base, vibration dampers, coupling, sealing and fixing material, see also Climate Requirements tab. Made for data:
| - pretok zraka 210 - 510m3/h | - air flow 210 - 510m3/h
| - eksterni statični padec tlaka dpext=450Pa | - external static pressure drop dpext=450Pa
| - priključna električna moč 0,37kW, 230V, 50Hz | - connection power 0,37kW, 230V, 50Hz
| - zaščita IP55 | - iP55 protection
| - fleksibilni prikluček 2x | - 2x flexible coupling
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - HLU tip HF R 125-17 D EC | - HLU tip HF R 125-17 D EC
| Oznaka: FA21.201 | Code: FA21.201 | kpl | 1 |  | 0
13.2 | Deflektor za izpuh zraka izdelan iz ognjevarne plasitke PPs-el s pritrdilnim in tesnilnim materialom tipa: | Air deflector made of fire-resistant PPs-el plastic with fastening and sealing material type:
| - dimenzije Ø160 | - ø160 dimensions
| - pretok q = 510 m3/h | - flow rate q = 510 m3/h
| - padec tlaka dpext=35Pa | - pressure drop dpext=35Pa
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BECK tip Rediff Type AUG 10/N RD1-10-0160M | - BECK tip Rediff Type AUG 10/N RD1-10-0160M
| Oznaka: DF21.200 | Code: DF21.200 | kpl | 1 |  | 0
13.3 | Dušilec zvoka, izdelan iz ognjevarne plasitke PPs-el s pritrdilnim in tesnilnim materialom tipa: | Silencer made of fire-resistant PPs-el plastic with fastening and sealing material type:
| - dimenzije Ø160/Ø355/L=500mm | - dimensions Ø160/Ø355/L=500mm
| - pretok q = 510m3/h; d=17dB pri 250Hz | - flow rate q = 510m3/h; d=17dB at 250Hz
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - ALNOR tip SILF Ø160 - 500mm | - ALNOR tip SILF Ø160 - 500mm
| Oznaka: DZ21.201 | Code: DZ21.201 | kpl | 1 |  | 0
13.4 | Volumski regulator pretoka zraka, izdelan iz ognjevarne plasitke PPs-el, s funkcijo regulacije konstantnega pretoka, s pritrdilnim in tesnilnim materialom tipa: | Volumetric air flow regulator, made of refractory PPs-el, with constant flow control function, with fastening and sealing material type:
| - dimenzije Ø90 | - ø90 dimensions
| - pretok q = 60m3/h | - flow rate q = 60m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - HLU tip HF VFL-M 90 | - HLU tip HF VFL-M 90
| Oznaka: CAV21.201 | Code: CAV21.201 | kpl | 1 |  | 0
13.5 | Protipovratna loputa, izdelana iz ognjevarne plasitke PPs-el, s pritrdilnim in tesnilnim materialom tipa: | Anti-return hatch made of fire-resistant PPs-el plastic, with fastening and sealing material type:
| - dimenzije Ø225 | - dimensions Ø225
| - pretok q = 510m3/h | - flow rate q = 510m3/h
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BECK tip RSK1-0225 | - BECK type RSK1-0225
| Oznaka: ND21.201 | Code: ND21.201 | kpl | 1 |  | 0
13.6 | Okrogli prezračevalni kanali, skladni z DIN 4741/1 in 2, iz materiala PPs-el, (negorljiv elektroprevoden polipropilen odporen na kisline in luge) skupaj s fazonskimi kosi. V ceni na enoto (v m) je potrebno upoštevati ves spojni in pritrdilni material ter kolena in odcepe, vključno z obešalnim in pritrdilnim materialom sistemskega proizvajalca z lastnostmi odgovarjajoč zahtevam SIST EN 12236: 2002, za podatke: | Round ventilation ducts complying with DIN 4741/1 and 2, made of PPs-el (flame-retardant, electrically conductive, acid- and alkali-resistant polypropylene), including phase pieces. The unit price (in m) must take into account all joining and fixing material and elbows and branches, including suspension and fixing material from the system manufacturer with properties complying with the requirements of SIST EN 12236: 2002, for data:
| Ø90x3, medium pressure (-1600Pa) | Ø90x3, medium pressure (-1600Pa) | m | 5 |  | 0
| Ø125x3, medium pressure (-1600Pa) | Ø125x3, medium pressure (-1600Pa) | m | 1 |  | 0
| Ø160x3, medium pressure (-1600Pa) | Ø160x3, medium pressure (-1600Pa) | m | 1 |  | 0
| Ø225x3,5, medium pressure (-1600Pa) | Ø225x3,5, medium pressure (-1600Pa) | m | 35 |  | 0
| 90°lok Ø90x3 | 90°arc Ø90x3 | kos | 1 |  | 0
| 90°lok Ø225x4 | 90°arc Ø225x4 | kos | 19 |  | 0
| redukcija Ø225 / Ø125 | ø225 / Ø125 reduction | kos | 1 |  | 0
| redukcija Ø160 / Ø125 | ø160 / Ø125 reduction | kos | 1 |  | 0
| Ustreza proizvod ali enakovredno: | Matching product or equivalent:
| - BECK | - BECK
| PREZRAČEVANJE IN KLIMATIZACIJA SISTEM VS21 | VENTILATION AND AIR CONDITIONING SYSTEM VS21 |  |  |  | 0

## 4.4.14_Skupne postavke
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.4 | STROJNA DELA | MECHANICAL WORKS
4.4.14 | SKUPNE POSTAVKE | COMMON ITEMS |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
14 | SKUPNE POSTAVKE | COMMON ITEMS
14.1 | Odprtine za čiščenje kanalov po SIST ENV 12097, dimenzij najmanj 150 mm x 250 mm, skupaj s tesnenjem, na odvodnem kanalu, mesta vgradnje se določijo na objektu. | Drain cleaning openings in accordance with SIST ENV 12097, minimum dimensions 150 mm x 250 mm, including sealing, in the drainage channel, installation locations to be determined on site. | kpl | 1 |  | 0
14.2 | Preizkus tesnosti prezračevalnih kanalov (DALT- duct air leakage test) jvključno z izdelavo pisnega poročila o uspešno opravljenem tlačnem preikusu, ki se izvede v skladu z naslednjim zahtevam: | The duct air leakage test (DALT) shall include a written report on the successful completion of the pressure test, which shall be carried out in accordance with the following requirements:
| - pravokotne kanale oziroma fazonske komade je treba preizkusiti z nadtlakom 1000 Pa in morajo ustrezati zahtevam po SIST EN 1507:2006, skladeno z opisom v "IZS Priročnik tlačnih preizkusov strojnih inštalacij": | - rectangular ducts or phasing joints must be tested with an overpressure of 1000 Pa and must comply with the requirements of SIST EN 1507:2006, as described in the "IZS Manual for pressure testing of mechanical installations":
| razred tesnosti B, dovoljena propustnost fmax = 0,009 × ptest 0,65 × 10-3 [m3/s/m2] | tightness class B, permissible permeability fmax = 0,009 × ptest 0,65 × 10-3 [m3/s/m2] | kpl | 1 |  | 0
| - okrogle kanale oziroma fazonske komade je treba preizkusiti z nadtlakom 1000 Pa in morajo ustrezati zahtevam po SIST EN 12237:2004, skladeno z opisom v "IZS Priročnik tlačnih preizkusov strojnih inštalacij": | - circular ducts or phasing joints must be tested with an overpressure of 1000 Pa and must comply with the requirements of SIST EN 12237:2004, as described in the "IZS Manual for Pressure Testing of Mechanical Installations":
| razred tesnosti B, dovoljena propustnost fmax = 0,009 × ptest 0,65 × 10-3 [m3/s/m2] | tightness class B, permissible permeability fmax = 0,009 × ptest 0,65 × 10-3 [m3/s/m2] | kpl | 1 |  | 0
14.3 | Izdelava in tesnenje prebojev pri prehodu prezračevalnih kanalov med požarnimi sektorji z ustrezno atestirano sistemsko maso/kitom/izolacijo ustrezne požarne odpornosti skladno s Načrtom požarne varnosti, s SIST EN 13501-2 in preizkušeni po SIST EN 1366-3, proizvod kot npr. HILTI, PROMAT, PIROFIX-PFT. Vsak prehod mora biti označen z nalepko ali tablico z osnovnimi požarnimi podatki. | Making and sealing of penetrations at the passage of ventilation ducts between fire sectors with a suitable certified system compound/kit/insulation of adequate fire resistance in accordance with the Fire Safety Plan, SIST EN 13501-2 and tested in accordance with SIST EN 1366-3, product such as e.g. HILTI, PROMAT, PIROFIX-PFT. Each passage must be marked with a sticker or plaque with basic fire information. | kpl | 1 |  | 0
14.4 | Izvedba meritev pretokov, tlakov, temperatur medijev in regulacija armatur s predajo zapisnika, izdelanega s starni neodvisnega podjetja. | Measurement of flows, pressures, media temperatures and valve regulation, with the submission of a report drawn up by an independent firm. | kpl | 1 |  | 0
14.5 | Izvedba preizkusov in meritev sistema prezračevanja in klimatizacije po zahtevah in obsegu EN 12599:2001, s predajo zapisnika, izdelanega s strani neodvisnega podjetja. | Carry out tests and measurements of the ventilation and air-conditioning system according to the requirements and scope of EN 12599:2001, with the submission of a report produced by an independent company. | kpl | 1 |  | 0
14.6 | PVC cevke za povezavo senzorjev tlaka, vključno z vsem montažnim in tesnilnim materialom. | PVC tubing for connecting pressure sensors, including all mounting and sealing material.
| OCENA | EVALUATION | m | 50 |  | 0
14.7 | Izvedba preizkusnega obratovanja delovanja v obsegu: - delovanje celotnega sklopa sistema prezračevanja, - delovanje avtomatske regulacije, - pregled delovanja ventilatorjev in elementov regulacije. Poizkusno obratovanje traja neprekinjeno 72 ur. | Conduct a full-scale operational test: - the operation of the complete ventilation system, - automatic control operation, - checking the operation of the fans and control elements. The test operation shall be continuous for 72 hours. | kpl | 1 |  | 0
14.8 | Izvedba kvalifikacije montaže IQ-pregledi (instalation qualification) po GEP Commissioning protokolu in dokumentiranje kvalifikacije montaže, vključno z odpravo prvotnih napak montaže; | Performing installation qualification IQ-checks (installation qualification) according to the GEP Commissioning Protocol and documenting the installation qualification, including the correction of the original installation defects; | kpl | 1 |  | 0
14.9 | Izvedba meritev OQ-kvalifikacija (operation qualification) ter dokumentiranje meritev delovanja, vključno z nastavitvijo parametrov; | Performing OQ measurements and documenting performance measurements, including parameter settings; | kpl | 1 |  | 0
14.10 | Tehnično sodelovanje z ustrezno usposobljenim izvajalskim osebjem ter pooblaščenimi serviserji pomembnejše strojno instalacijske opreme in naprav pri izvedbi dveh sklopov: - garancijskih meritev ter - speljavi postopka usposobitve (commissioning) | Technical cooperation with suitably qualified contractor personnel and authorised repairers of major plant and mechanical equipment in the execution of the two lots: - warranty measurements; and - commissioning | kpl | 1 |  | 0
14.11 | Označevanje armatur, merilnih in kontrolnih elementov, sistemov, kanalov... celotne strojno tehnološke opreme s tehnološkimi oznakami navedenimi v shemah. Dobava in montaža napisnih ploščic iz nerjavne pločevine z vgravirano oznako po shemi za opremo in armature, kompletno z jekleno pritrdilno žico. Dobava in pritrditev samolepilnih puščic za označitev smeri pretoka ter z napisom vrste medija. | Marking of fittings, measuring and control elements, systems, ducts, etc. of all mechanical and technological equipment with the technological markings indicated in the diagrams. Supply and installation of stainless steel nameplates with engraved marking according to the diagram for equipment and fittings, complete with steel fixing wire. Supply and installation of self-adhesive arrows to indicate the direction of flow and the type of medium. | kpl | 1 |  | 0
14.12 | Izdelava plana montaže z medsebojno uskladitvijo vseh izvajalcev del, organizacije gradbišča, terminskega plana del, potrjenega s strani vseh udeležencev gradnje. | Preparation of an installation plan with coordination between all contractors, site organisation, and a schedule of works approved by all construction participants. | kpl | 1 |  | 0
14.13 | Izdelava montažnih risb za izvedbo inštalacij med gradnjo objekta, kot so: detajli priključkov, montažne skice, montažni detajli, ipd. | Preparation of assembly drawings for the installation of services during the construction of the building, such as: connection details, assembly sketches, assembly details, etc. | kpl | 1 |  | 0
14.14 | Izdelava shem strojnih instalacij vloženih v okvir in zaščitenih s steklom ter izdelava navodil za obratovanje in vzdrževanje v štirih izvodih v zahtevanem obsegu iz Pravilnika o podrobnejši vsebini dokumentacije in obrazcih , za ta namen upoštevajoč uveljavljene inženirske smernice, kot npr. ASHRAE Guideline 4 - 2019 (Preparation of Operating and Maintenance Documentation for Building Systems). | Drawing up of framed and glass-protected mechanical installation diagrams and preparation of operating and maintenance instructions in quadruplicate to the extent required by the Regulations on the detailed content of documentation and forms, taking into account established engineering guidelines such as ASHRAE Guideline 4 - 2019 (Preparation of Operating and Maintenance Documentation for Building Systems). | kpl | 1 |  | 0
14.15 | Sprotno beleženje vseh sprememb, nastalih med izvedbo z vrisovanjem v PZI načrt v zahtevanem obsegu iz 25. člena Pravilnika o podrobnejši vsebini dokumentacije in obrazcih, povezanih z graditvijo objektov. | Keeping a record of all changes occurring during the execution by drawing them into the PZI plan to the extent required by Article 25 of the Regulation on the detailed content of documentation and forms related to the construction of buildings. | kpl | 1 |  | 0
14.16 | Priprava primopredajne dokumentacije, ki mora vsebovati: izjave, dokazilo o zanesljivosti objekta, certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo in vzdrževanje ter ostalo primopredajno dokumantacijo. Predaja se v dveh mapiranih izvodih ter en izvod v elektronski obliki. | Preparation of the handover documentation, which shall include: declarations, proof of the reliability of the facility, certificates and attestations for the materials and equipment installed, records of tests and measurements, operating and maintenance instructions and other handover documentation. It shall be submitted in two mapped copies and one copy in electronic form. | kpl | 1 |  | 0
14.17 | Zaščitno barvanje prezračevalnih odvodnih kanalov; enkratni premaz s temeljnim antikorozijskim premazom ter dvakratni premaz s prekrivno barvo, antikorozijska zaščita s temeljnimi in prekrivnimi barvami se mora izvesti v skladu s SIST EN ISO 12944-1:2018, korozijskega razreda C1, z življenjsko dobo: zelo visoko trajanje VH (več kot 25 let), prekrivna barva mora biti v RAL7016. | Protective painting of ventilation ducts; one coat of anti-corrosion primer and two coats of overcoat, anti-corrosion protection with primer and overcoat shall be in accordance with SIST EN ISO 12944-1:2018, corrosion class C1, with a service life: very high durability VH (more than 25 years), the overcoat shall be in RAL7016. | m2 | 1680 |  | 0
14.18 | Pripravljalna in zaključna dela - glej tudi točko 0.1 - splošni tehnični pogoji za strojna dela. | Preparatory and finishing works - see also point 0.1 - General technical conditions for mechanical works. | kpl | 1 |  | 0
| SKUPNE POSTAVKE | COMMON ITEMS |  |  |  | 0