## 0_Naslovnica
OPOZORILO! Vsi prevodi v angleščino so strojno izdelani in zgolj informativne narave. V primeru kakršnekoli nejasnosti ali dvoma izključno velja izvirno besedilo v slovenščini. WARNING! All translations into English have been produced by machine translation and are provided for informational purposes only. In the event of any ambiguity or uncertainty, the original Slovenian text shall prevail exclusively.
| / | / | [5 empty] | /
| Sprem./Rev.: | Opis spremembe/Description of Changes: | [5 empty] | Datum/Date: | Podpis/Signature:
| Investitor/Investor: |  |  |  |  | Gradnja/Facility
|  |  | Univerza v Ljubljani Kongresni trg 12 1000 Ljubljana, Slovenija |  |  | Fakulteta za strojništvo/Faculty of Mechanical Engineering
| Projektant/Design Engineer: |  |  |  |  | Del objekta/sistem/Building/System:
|  |  | IBE, svetovanje, projektiranje in inženiring Ljubljana, Slovenija |  |  | STAVBA FAKULTETE/FACULTY BUILDING
| Projektant/Design Engineer: |  |  |  |  | Vrsta načrta/Documentation:
4 NAČRT S PODROČJA STROJNIŠTVA/ DOC. IN THE FIELD OF MECHANICAL ENGINEERING
|  | Ime in priimek/Name and Surname: |  |  | Id. št./Id. No: | Vsebina risbe (dokumenta)/Document Title:
| Vodja proj./ Des. Manager: | Boštjan Vuga, univ. dipl. inž. arh., grad. dip. (AA) |  |  | ZAPS 0035 PA PPN | PR. POPIS STROJNIH DEL/BOQ OF MECH. WORKS 4/5 Sistemi za gašenje požara in hidr. omrežje/Fire ext. systems and Hydrant Network
| Poobl. strok./ Cert. Profess.: | Jure Podobnikar, magi. Inž. str. |  |  | IZS S-1987
| Poobl. strok./ Cert. Profess.: |  |  |  |  | Št. proj./ Proj. No.: | 362-19 |  | Vrsta dokument./ Document. Type: | DZR
| Izdelal/ Creator: | Jure Podobnikar, magi. Inž. str. |  |  | IZS S-1987 | Klas. ozn./ Class. No.: | -- |  | Stran/ Page: | 1/*
| Datum/ Date: | maj/May 2026 |  | Merilo/ Scale: | / | Ident. ozn./ Id. No: | JULFS--6S0502P

## 0_Osebe
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
POOBLAŠČENI STROKOVNJAKI, ODGOVORNI ZA IZDELAVO PROJEKTANTSKEGA POPISA:
Id. št. ZAPS/IZS | Pooblaščeni strokovnjak | Strokovno področje
IZS S-1987 | Jure Podobnikar, mag. inž. str. | Sistemi za gašenje požara in hidrantno omrežje
SODELAVCI PRI IZDELAVI PROJEKTANTSKEGA POPISA:
CERTIFIED EXPERTS RESPONSIBLE FOR ELABORATING THE BILL OF QUANTITIES:
Id. No ZAPS/IZS | Certified Expert | Area of Expertise
IZS S-1987 | Jure Podobnikar, mag. inž. str. | Fire-fighting systems and hydrant network
COLABORATORS IN THE ELABORATING THE BILL OF QUANTITIES:

## 0.1_Uvod-STP
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
0.1 | SPLOŠNI TEHNIČNI POGOJI | GENERAL TECHNICAL CONDITIONS
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic operator with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
0.1.1 | Izvajalec se obveže, da bo upošteval veljavno zakonodajo, ki ureja graditev objektov v Republiki Sloveniji, vključno s povezanimi podzakonskimi akti, predpisi, tehničnimi smernicami, standardi, pravili stroke in dobro gradbeno prakso. Prav tako mora izvajalec upoštevati vse zahteve izdanega integralnega gradbenega dovoljenja in vsa dela izvesti skladno s projektno dokumentacijo ter ostalimi pogoji, objavljenimi v razpisni dokumentaciji. | The Contractor undertakes to comply with the applicable legislation governing the construction of buildings in the Republic of Slovenia, including related by-laws, regulations, technical guidelines, standards, professional rules and good construction practice. The Contractor shall also comply with all the requirements of the integral building permit issued and shall carry out all works in accordance with the project documentation and other conditions published in the tender documentation.
0.1.2 | Dela lahko izvaja samo izvajalec, ki je registriran za opravljanje gradbene dejavnosti in ima za tovrstna dela ustrezno zavarovanje za škodo, certifikate, tehnično izobražen kader, sredstva ter je usposobljen za samostojno pripravo in izvedbo del. | The work may only be carried out by a contractor who is registered to carry out construction work and who has the appropriate insurance for such work, certificates, technically trained staff, resources and is qualified to prepare and carry out the work independently.
0.1.3 | Izvajalec odgovarja za kakovost izvedbe vseh del. | The Contractor shall be responsible for the quality of the execution of all works.
0.1.4 | Izvajalec nosi vso odgovornost za nesreče in škodo, ki nastane na objektu ali v okolici zaradi njegovega dela. | The Contractor shall bear all liability for accidents and damage to the installation or the surrounding area caused by his work.
0.1.5 | Pred oddajo ponudbe se je izvajalec dolžan seznaniti z območjem predvidenim za gradnjo in temu prilagoditi vsa potrebna dela, kar mora biti zajeto v ponudbi. V neposredni bližini predvidene gradnje se nahajajo stavbe, v katerih potekajo izobraževalni in raziskovalni procesi. Zato bo izvajalec moral izvajati kontrolo hrupa in kontrolo vibracij. Dela, ki so hrupna in dela, ki povzročajo vibracije bo izvajalec moral preprečiti oziroma jih izvesti na način, da povzročajo minimalne vplive. Tehnologijo rušenja, pilotiranja in tehnologijo izvedbe ostalih del bo izvajalec moral prilagoditi tako, da bo vpliv minimalen. Izvajalec mora preprečiti in zmanjšati emisije delcev iz gradbišča na najmanjšo možno mero. | Before submitting a tender, the contractor is obliged to familiarise himself with the area to be constructed and to adapt any necessary works accordingly, which must be included in the tender. In the immediate vicinity of the proposed construction, there are buildings in which educational and research processes take place. The contractor will therefore be required to carry out noise and vibration control. Noise and vibration works will have to be avoided or carried out in such a way as to minimise the impact. Demolition, piling and other works will have to be adapted to minimise the impact. The contractor must avoid and minimise the emission of particulates emitted from the construction site as far as is reasonably practicable.
0.1.6 | Izvajalec je pred oddajo ponudbe dolžan pregledati projektno dokumentacijo in ostale pogoje, ki so del razpisne dokumentacije V primeru morebitnih napak in neskladij je izvajalec dolžan na to opozoriti naročnika pred oddajo ponudbe. | The Contractor is obliged to review the project documentation and other conditions forming part of the tender documentation before submitting the tender In case of any errors or inconsistencies, the Contractor is obliged to bring these to the attention of the Contracting Authority before submitting the tender.
0.1.7 | Pred oddajo ponudbe je izvajalec dolžan preveriti ustreznost popisov del in količin v teh popisih ter njihovo skladnost z ostalimi dokumenti projektne dokumentacije, ki so del razpisne dokumentacije. Prav tako je izvajalec dolžan preveriti vse detajle in sheme. Vse izmere je potrebno preveriti po posameznih projektih oz. načrtih, ki sestavljajo razpisno dokumentacijo. V primeru ugotovljenih neskladij je v času priprave ponudbe obvezan o tem obvestiti naročnika. | Before submitting a tender, the Contractor shall check the adequacy of the inventories of works and quantities in these Bills of Quantities and their conformity with the other documents of the project documentation forming part of the tender documentation. The Contractor shall also check all details and diagrams. All measurements shall be checked against the individual projects or plans forming part of the tender documentation. In the event of any discrepancies, the Contractor shall inform the Contracting Authority at the time of preparing the tender.
0.1.8 | Pred oddajo ponudbe je izvajalec dolžan v tem popisu preveriti zmnožke in seštevke ter prenose le-teh v rekapitulacijo. Izvajalec se s pripravo ponudbe obvezuje, da je prebral vse celice in elemente celotnega popisa, vključno z vsemi postavkami in splošnimi navodili ali določili in je preveril pravilnost preračuna ter s tem zagotavlja ponudbeno vrednost. | Before submitting a tender, the Contractor is required to check the products and totals in this Bill of Quantities (BoQ) and their transfer to the recapitulation. The Contractor undertakes, by preparing a tender, to have read all the cells and elements of the complete BoQ, including all headings and general instructions or provisions, and to have checked the correctness of the conversion, thereby guaranteeing the value of the tender.
0.1.9 | Dela bo izvajalec moral izvajati po predloženi projektni dokumentaciji, detajlih in z upoštevanjem navodil in potrditev projektanta, nadzornika in investitorja. Vso potrebno delavniško dokumentacijo zagotovi izvajalec del v okviru ponujene cene. | The Contractor shall carry out the works in accordance with the submitted design documents, details and subject to the instructions and approvals of the Designer, the Supervisor and the Investor. All necessary workshop documentation shall be provided by the Contractor within the scope of the price quoted.
0.1.10 | Pred izvedbo posameznih del je izvajalec dolžan pregledati projektno dokumentacijo za izvedbo gradnje (PZI) in elaborate. Na morebitne napake v dokumentaciji ali neskladja med posameznimi načrti ali deli načrtov (popisi del, tehnična poročila, lokacijski in tehnični prikazi) izvajalec opozori nadzornika in projektanta, in se z njima pravočasno uskladi. | The Contractor shall review the Detailed Design documentation (PZI) and the studies before carrying out the individual works. The Contractor shall draw the attention of the Supervisor and the Designer to any errors in the documentation or discrepancies between the individual designs or parts of designs (BoQ, technical reports, location and technical drawings) and shall coordinate with them in good time.
0.1.11 | Tehnični opisi, prikazi, detajli, sheme ter ostali dokumenti v PZI dokumentaciji predstavljajo dodaten opis popisnih postavk gradbeno obrtniških in inštalacijskih del ter jih je potrebno dosledno upoštevati skupaj s popisom del. | The technical descriptions, illustrations, details, diagrams and other documents in the Detailed Design documentation (PZI) are additional descriptions of the BoQ inventory items of the building, construction and installation works and must be strictly followed together with the BoQ.
0.1.12 | Specifikacije in zahteve, navedene v popisu, se ne smejo upoštevati kot edine zahteve. Izvajalec je dolžan v ceni zajeti in dobaviti vse elemente opreme ter opraviti dela in storitve, ki niso eksplicitno navedeni, a so bistvenega pomena za funkcionalnost, skladnost s predpisi ter kontinuirano, zanesljivo in varno obratovanje opreme. | The specifications and requirements set out in the BoQ shall not be taken as the only requirements. The Contractor shall be obliged to include in the price and supply all items of equipment and to carry out works and services which are not expressly mentioned but which are essential for the functionality, regulatory compliance and continuous, reliable and safe operation of the equipment.
0.1.13 | Vsa dela morajo biti izvedena kvalitetno in iz materialov z zahtevanimi lastnostmi, izvedena skladno z veljavno zakonodajo in z upoštevanjem navodil za vgradnjo za izbrane materiale in opremo, s predložitvijo predpisanih izjav o lastnostih in/ali certifikatov. Vsi gradbeni proizvodi (GP) morajo biti označeni s CE oznako. | All work shall be of good quality and be executed with materials of the required characteristics, in accordance with the applicable legislation and in compliance with the installation instructions for the materials and equipment selected, and shall be accompanied by the prescribed declarations of performance and/or certificates. All construction products (GP) shall bear the CE marking.
0.1.14 | Za vsako opisano delo v popisu je potrebno upoštevati celotno potrebno delo, ves osnovni in pomožni material, prevoz materiala in orodja na objekt, notranje transporte, delovne in pomožne odre, zaključno čiščenje in odstranitev odpadkov po dovršenem delu. | For each work described in the inventory, the total work required, all basic and ancillary materials, the transport of materials and tools to the site, internal transports, working and ancillary scaffolding, final cleaning and the disposal of waste after the work has been completed must be taken into account.
0.1.15 | Vsa delovna sredstva, organizacija in koordinacija del, pripravljalna, spremljajoča in zaključna dela, potrebni montažni in tesnilni materiali ter podkonstrukcije so sestavni del posameznih postavk. | All labour, organisation and coordination of the works, preparatory, accompanying and finishing works, necessary prefabrication and sealing materials and substructures are part of the individual items.
0.1.16 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - načrt organizacije gradbišča s podrobnim terminskim planom in izvedba vseh pripravljalnih del, postavitev, organizacija, zaščita in prijava gradbišča, gradbiščnih objektov, ureditev začasnih deponij, tekoče vzdrževanje, skupaj s plačilom splošnih stroškov pristojbin in davkov upravnih organov, pridobivanju raznih dovoljenj in soglasij za izvedbo, ograditev gradbišča in postavitev gradbene table in prometne signalizacije, zagotavljanje ustrezne varnosti na gradbišču, tekoče vzdrževanje in končna odstranitev gradbišča; - zagotovitev potrebnih začasnih površin za transportne poti in gradnjo izven območja gradbišča s plačilom stroškov za sanacijo in vzpostavitev okoliških zemljišč in objektov v prvotno stanje (soglasja, odškodnine, itd.); - začasni odvoz, deponiranje in vračanje izkopanega materiala, ki ga ne bo možno deponirati na gradbišču; - odvoz in zagotovitev odstranjevanja odpadnega gradbenega materiala skladno z zakonodajo na področju ravnanja z odpadki (odvoz na urejene deponije s plačilom komunalnih prispevkov in taks itd.); - oteženi izkop v mokrem terenu, izkop v vodi, odvod meteorne vode iz gradbene jame in vode, ki se izceja iz bočnih strani izkopov; - ustrezno varovanje izkopa gradbene jame za objekt in ostalih manjših posameznih izkopov za izvedbo komunalne infrastrukture brez posegov na sosednja zemljišča; - ustrezno varovanje obstoječih objektov, infrastrukture in okolice v času gradnje ter dokumentiranje vseh morebitnih škodnih dogodkov; - pripravljalna, spremljajoča in zaključna dela (zakoličbe, zagotovitev potrebnih komunalnih priključkov za potrebe izvajanja gradnje, izvedba začasnih inštalacij, označevanje podzemnih vodov, postavljanje in vzdrževanje zakoličbenih profilov, izvedba in označevanje novih in starih križanj ter morebitna zaščita križanj komunalnih vodov, geodetski posnetki in izdajanje vmesnih posnetkov izvedene infrastrukture naročniku, izdelava zbirnih kart, itd.), v kolikor ni to drugače določeno; - pridobivanje soglasij in izvedba morebitnih zapor na vseh cestah s plačilom stroškov, nadomestil in pristojbin; - zagotovitev oz. postavitev in končna odstranitev po zaključku gradnje začasnih skladišč in začasnega pisarniškega kontejnerskega objekta vključno z opremo za dve delovni mesti in za skupne operativne sestanke vel. ca. 40 m2 za potrebe naročnika, s tekočim vzdrževanjem in čiščenjem. | The following must also be included or taken into account in the uniform prices for individual items: - a construction site organisation plan with a detailed timetable and the execution of all preparatory works, the setting-up, organisation, protection and registration of the construction site, site facilities, the arrangement of temporary storage facilities, ongoing maintenance, including the payment of general costs of fees and taxes of the administrative authorities, the obtaining of various permits and consents for the execution, the fencing of the site and the erection of construction signs and traffic signals, the provision of adequate security on the site, ongoing maintenance and the final dismantling of the construction site; - provision of the necessary temporary areas for transport routes and off-site construction, with costs for restoration and reinstatement of surrounding land and buildings (consents, compensation, etc.); - temporary removal, storage and return of excavated material that cannot be stored on site; - removing and disposing of waste building materials in accordance with waste management legislation (removal to regulated landfill sites with payment of municipal fees and charges, etc.); - difficult excavation in wet ground, excavation in water, drainage of rainwater from the construction pit and water draining from the sides of excavations; - adequate protection of the excavation of the construction pit for the building and other small individual excavations for the implementation of the utility infrastructure without encroaching on neighbouring land; - adequate protection of existing facilities, infrastructure and the surrounding area during construction, and documentation of any damage incidents; - preparatory, accompanying and finishing works (stake-out, provision of the necessary utility connections for the needs of construction, execution of temporary installations, marking of underground lines, installation and maintenance of stake-out profiles, execution and marking of new and old crossings and possible protection of crossings of utility lines, geodetic surveys and issuing of intermediate images of the completed infrastructure to the client, production of summary maps, etc.), unless otherwise specified; - obtaining consents and implementing any road closures, with costs, compensation and fees; - provision or erection and final removal on completion of construction of temporary storage and temporary office container building including equipment for two workstations and for joint operational meetings of approx. 40 m2 for the needs of the client, with ongoing maintenance and cleaning.
0.1.17 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - izdelava montažne tehnične dokumentacije, detajlov izvedbe in vse druge potrebne delavniške dokumentacije (s področja arhitekture, gradbeništva, elektrotehnike, strojništva in zunanje ter krajinske ureditve) ter pridobitev obvezne potrditve s strani projektanta, nadzornika in investitorja; - odprava vseh vrst inštalacijskih kolizij z izvajanjem potrebnih premikov inštalacij in njihovim usklajevanjem na mestu montaže, vse v obsegu, ki ne vpliva na projektirano rešitev ali tip inštalacij oz. opreme; - zagotavljanje kompletnosti elektro-instalacijskih sistemov s področja avtomatike za doseganje njihove popolne funkcionalnosti delovanja; - stroški za nadzor in koordinacijo izvedbe vseh elektro napeljav, ki so predmet končne instalacije proizvoda (senčila, vrata, okna,…); - izdelava montažnih skic in detajlov za izvedbo v dogovoru z vodjo gradnje in nadzornikom; - izdelava in predstavitev vzorcev v ustrezni velikosti za potrditev projektanta, nadzornika in investitorja; - zagotavljanje varnosti in zdravja pri delu, zlasti izvajanje vseh del, ki izhajajo in ukrepov, ki izhajajo iz določil veljavnih predpisov varstva pri delu in zahtev Varnostnega načrta;- stroški garancij, ki jih mora izvajalec predložiti naročniku. | The following must also be included or taken into account in the uniform prices for individual items: - preparation of prefabricated technical documentation, construction details and all other necessary workshop documentation (architectural, civil, electrical, mechanical, exterior and landscaping) and obtaining the mandatory approval of the designer, the supervisor and the investor; - elimination of all types of installation conflicts by carrying out the necessary relocation of installations and their coordination at the installation site, all to the extent that it does not affect the design solution or the type of installation or equipment; - ensuring the completeness of electrical installation systems in the automation sector to achieve their full operational functionality; - the cost of supervising and coordinating the installation of all the electrical installations that are the subject of the final installation of the product (blinds, doors, windows, etc.); - preparation of erection drawings and details for implementation in agreement with the construction manager and supervisor; - production and presentation of samples in appropriate sizes for the approval of the designer, the supervisor and the investor; - ensuring health and safety at work, in particular the implementation of all the works arising from and the measures resulting from the provisions of the applicable occupational safety regulations and the requirements of the Safety Plan; - the cost of the guarantees to be provided by the contractor to the client.
0.1.18 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - strošek vodje del glavnega izvajalca, ki bo izvajal tudi koordinacijo s podizvajalci in z drugimi izvajalci, ki jih bo izbral naročnik in bo opravljal delo vodje gradbišča; - koordinacija del z ostalimi izvajalci oz. podizvajalci del, projektantom, nadzornikom in investitorjem pri medsebojnem usklajevanju organizacije gradbišča in časovnega načrta del ter pri usklajevanju izdelave plana montaže, potrjenih s strani vseh udeležencev gradnje; - stroški koordinacije, sodelovanja in usklajevanja z dobavitelji tehnološke, laboratorijske, eksperimentalne in vse ostale pohištvene ter multimedijske opreme ter z vsemi ostalimi dobavitelji oz. podizvajalci na objektu; - stroški izdelave situacij; - stroški zavarovanja objekta v času izvedbe del in delavcev ter materiala na gradbišču v času izvajanja del, od začetka del do pridobitve uporabnega dovoljenja za objekt. Zavarovanje mora biti sklenjeno pri ustrezni zavarovalni družbi najmanj v višini pogodbene vrednosti ali v zakonsko predpisani vrednosti (v kolikor zavarovanje v višini pogodbene vrednosti presega zakonsko dovoljeno), za ves čas trajanja izvedbe del do uspešne primopredaje objekta; - preizkušanje kvalitete materiala, ki se vgrajuje in dokazovanje kvalitete s certifikati oz. tehničnimi soglasji; - izvedba vseh zahtevanih testov in preizkusov (npr. tlačni preizkusi, termografski pregledi, meritve elektromagnetnega sevanja, hrupa, itd.), poskusnega obratovanja celotnega objekta s poudarkom na vseh inštalacijah ter izvajanje predpisanega monitoringa v skladu s Poročilom o vplivih na okolje (pred gradnjo, med gradnjo in po končani gradnji); - izdelava izkaza požarne varnosti, vključno s sprotnim spremljanjem gradnje in izvajanjem požarnovarnostnih zahtev ter izdelava Požarnega reda z obveznimi prilogami; - izdelava Izkaza zaščite pred hrupom v stavbah; - izdelava Izkaza energijskih lastnosti stavbe in energetske izkaznice; - sodelovanje z izvajalci gradbenega in projektantskega nadzora in investitorjem za izvedbo tehničnega pregleda in priprava primopredaje, ki mora vsebovati vso zahtevano dokumentacijo, predvsem pa: izjave o skladnosti, požarni izkaz in ostale izkaze ter obvezne tabele, dokazilo o zanesljivosti objekta (DZO), certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo in vzdrževanje ter vse ostale dokumente v skladu s predpisi in pogodbenimi določili. | The following must also be included or taken into account in the uniform prices of the individual items: - the cost of a works manager for the main contractor, who will also coordinate with subcontractors and other contractors selected by the client and act as site manager; - coordination of the works with other contractors or subcontractors, the designer, the supervisor and the investor in coordinating the organisation of the construction site and the timetable for the works, and in coordinating the production of an installation plan approved by all the participants in the construction; - the costs of coordination, cooperation and coordination with suppliers of technological, laboratory, experimental and all other furniture and multimedia equipment, as well as with all other suppliers or subcontractors on the site; - the cost of drawing up situations; - the cost of insuring the building during the execution of the works and the workers and materials on site during the execution of the works, from the start of the works until the building has been licensed for occupation. The insurance must be taken out with a suitable insurance company for at least the contract value or the legal value (if the insurance for the contract value exceeds the legal value), for the entire duration of the works until the successful handover of the building; - testing the quality of the material to be installed and proving it with certificates or technical approvals; - carrying out all required tests and trials (e.g. pressure tests, thermographic inspections, electromagnetic radiation measurements, noise measurements, etc.), trial operation of the entire building, with emphasis on all installations, and carrying out the required monitoring in accordance with the Environmental Impact Assessment Report (before, during and after construction); - preparation of a fire safety statement, including ongoing monitoring of construction and implementation of fire safety requirements, and preparation of a Fire Safety Order with mandatory annexes; - preparation of a Noise Protection Statement for buildings; - preparation of the Building Energy Performance Report and Energy Performance Certificate; - cooperation with the construction and design supervision contractors and the investor to carry out the technical inspection and prepare the handover, which must include all the required documentation, in particular: declarations of conformity, fire and other statements and mandatory tables, proof of reliability of the building (DZO), certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use and maintenance, and all other documents in accordance with the regulations and the contractual provisions.
0.1.19 | V enotnih cenah posameznih postavk, ki se nanašajo na opremo in posamezne sisteme, mora biti zajeto oz. upoštevano tudi naslednje: - dobava oz. transport, - stroški za vse delovne stroje za dvigovanje bremen in delovne košare za dostope do delovišč; - morebitni stroški povzročeni upravljavcem GJI, ki bi nastali v zvezi s predmetno gradnjo; - montaža, vključno s pomožnim montažnim materialom (vezni, tesnilni in pritrdilni material, sidra, nosilni profili, podkonstrukcije in podobno) in navodili proizvajalca, - odprava vseh kolizij sistemov s stenami in med sistemi, - izvedba vseh potrebnih tesnjenj, - priključitev in nastavitve, vključno z morebitnim kalibriranjem, - zagon, testiranje in meritve, vključno s poročili, - šolanje uporabnikov oz. vzdrževalnega osebja za uporabo in vzdrževanje sistemov, - navodila za obratovanje in vzdrževanje, - vsi potrebni certifikati, izjave o skladnosti oz. potrdila ter - vsa druga pomožna dela in material, da se zagotovi funkcionalnost posamezne postavke popisa. | The following must also be included or taken into account in the uniform prices for individual items relating to equipment and individual systems: - delivery/transport, - the cost of all lifting machines and work baskets for access to work sites; - any costs incurred to the operators of utility infrastructure (GJI) in connection with the subject construction; - installation, including ancillary installation materials (bonding, sealing and fixing materials, anchors, support profiles, substructures, etc.) and manufacturer's instructions, - eliminating all system-to-wall and system-to-system collisions, - all necessary sealing work, - connection and set-up, including calibration if necessary, - commissioning, testing and measurements, including reports, - training users or maintenance staff in the use and maintenance of the systems, - operating and maintenance instructions, - any necessary certificates, declarations of conformity or attestations; and - all other ancillary works and materials to ensure the functionality of each inventory item.
0.1.20 | Vsi odri morajo biti upoštevani v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All scaffolding must be included in the uniform prices of the items listed, except where specifically mentioned.
0.1.21 | Vsi delovni in pomožni odri, lestve in ostala potrebna pomožna sredstva, kot tudi čiščenje vseh elementov po končanih delih, mora biti upoštevano v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All working and auxiliary scaffolding, ladders and other necessary ancillaries, as well as the cleaning of all elements after completion of the works, shall be included in the uniform prices of the items listed, except those specifically mentioned.
0.1.22 | Delavniško dokumentacijo za vse nosilne jeklene konstrukcije in podkonstrukcije izdela izvajalec, strošek izdelave delavniške dokumentacije se upošteva v ponujenih cenah in se ne obračuna posebej. | The cost of the shop drawings for all steelwork and substructures shall be included in the prices quoted and shall not be charged separately.
0.1.23 | V enotnih cenah postavk mora biti vključeno tudi vgrajevanje vseh instalacijskih razvodov v opaže armirano betonskih elementov in izdelava prehodov inštalacij ter dodatno izrezovanje utorov in prebojev v kamnite, zidane ali armirano-betonske stene, ponovno demontiranje in montiranje vseh vrst montažnih sten, vsa dodatna dela za zagotavljanje primernih križanj med posameznimi instalacijskimi vodi, izdelava vseh vrst ojačitev konstrukcij in podobna dela, ki zagotavljajo kakovostno vgradnjo vseh vrst instalacijskih vodov in niso posebej navedena v popisu GOI del. V ponudbi morajo biti upoštevana vsa drobna strojna in elektro instalacijska dela in transporti. | The installation of all installation ducts in the formwork of reinforced concrete elements and the construction of installation penetrations, as well as the additional cutting of grooves and penetrations in stone, masonry or reinforced concrete walls, the reassembly and reinstallation of all types of prefabricated walls, all additional work to ensure adequate crossings between individual installation ducts, the construction of all types of structural reinforcement and similar work to ensure the quality installation of all types of installation ducts and not specifically mentioned in the BoQ of the Construction, installation and finishing works (GOI) shall also be included in the uniform prices of the items. The tender shall take into account all minor mechanical and electrical installation work and transport.
0.1.24 | Vsi kovinski elementi in konstrukcije, ki bi lahko bili izpostavljeni atmosferskim in ostalim korozijskim vplivom, morajo biti ustrezno protikorozijsko zaščiteni. | All metallic elements and structures that could be exposed to atmospheric and other corrosive influences must be adequately protected against corrosion.
0.1.25 | Za vse večje jeklene dele se skladno s predpisi, izdelajo ustrezne ozemljitve, nevidno pritrjene in speljane na splošno ozemljitev objekta. | For all major steel parts, appropriate earth connections shall be made in accordance with the regulations, invisibly attached and connected to the general earth of the building.
0.1.26 | Za vse vidne elemente in serijske elemente je obvezna predhodna uskladitev obdelav, barv in materialov s projektantom na podlagi dostavljenih vzorcev v ustrezni velikosti. Obvezna je preveritev dejanskih mer na licu mesta in posledična prilagoditev elementov in njihove montaže. | For all visible elements and serial elements, it is mandatory to coordinate the finishes, colours and materials with the designer beforehand on the basis of the supplied samples in the appropriate size. It is mandatory to check the actual dimensions on site and to adjust the elements and their installation accordingly.
0.1.27 | Dimenzije obrtniških izdelkov in količine je potrebno pred naročanjem preveriti na objektu. Potrebna je uskladitev vseh elementov (kljuke, okovje, detajlne konstrukcije in obdelave, itd.) s projektantom, nadzornikom in investitorjem. Izvajalec je dolžan pred izdelavo predložiti projektantu v potrditev ustrezne delavniške načrte in detajle. | The dimensions of the workmanship and quantities must be checked on site before ordering. All elements (hooks, fittings, detailed construction and finishes, etc.) must be coordinated with the designer, the supervisor and the investor. The contractor is obliged to submit the relevant workshop plans and details to the designer for approval before manufacture.
0.1.28 | V posameznih postavkah popisa so navedeni proizvajalci in/ali tipi posameznih sistemov, materialov ali opreme, s čimer so zgolj natančno opredeljene zahtevane tehnične lastnosti. Izvajalec del lahko ponudi nadomesten sistem, material ali opremo drugega proizvajalca in tipa, pri čemer morajo biti tehnične lastnosti ponujenega sistema, materiala ali opreme enakovredne ali boljše od opredeljenih v popisu, dimenzijsko pa ne smejo presegati projektiranih dimenzij. Vse funkcijske in tehnične karakteristike nadomestnih sistemov, materialov ali opreme mora izvajalec dokazati z ustrezno dokumentacijo. Vse morebitne posledice zaradi spremembe sistemov, materialov ali opreme vključno z morebitnimi spremembami oz. dopolnitvami BIM modelov in projektne dokumentacije, stroškovno in časovno bremenijo izvajalca. | The individual items of the Inventory shall specify the manufacturers and/or types of the individual systems, materials or equipment, thereby merely specifying the required technical characteristics. The Contractor may offer a substitute system, material or equipment of a different manufacturer and type, provided that the technical characteristics of the offered system, material or equipment shall be equivalent to or better than those specified in the BoQ, and shall not exceed the design dimensions. All functional and technical characteristics of the substitute systems, materials or equipment shall be demonstrated by the Contractor with appropriate documentation. Any consequences resulting from changes to systems, materials or equipment, including any changes or additions to the BIM models and project documentation, shall be borne by the Contractor in terms of cost and time.
0.1.29 | Vsako zamenjavo, uporabo in končni izbor nadomestnih sistemov, materialov, proizvodov in opreme morajo obvezno in pravočasno (pred dobavo in vgradnjo) pisno potrditi projektant (vseh sodelujočih strok), nadzornik in investitor. | Any replacement, use and final selection of alternative systems, materials, products and equipment must be approved in writing by the designer (of all disciplines involved), the supervisor and the investor in a timely manner (prior to delivery and installation).
0.1.30 | Izvajalec mora v ponudbeno ceno vključiti tudi: - ves čas gradnje sprotno beleženje sprememb oz. odstopanj od PZI dokumentacije, vključno z izdelavo tekstualnega opisa sprememb, - pripravo podlog na nivoju PZI, ki so potrebne za posodobitev oz. uskladitev BIM modela z izvedenim stanjem (LOD 500) in izdelavo projektne dokumentacije izvedenih del (PID), - mesečno predajanje potrjenih sprememb opreme in materiala, ki vplivajo na BIM model, v formatu IFC, - vzdrževanje in uporabljanje pri izvedbi zadnje veljavne revizije PZI dokumentacije, vključno z dopolnitvami PZI načrtov, ki so nastali zaradi sprememb med gradnjo. | The contractor must also include in the tender price: - keeping a record of changes or deviations from the construction documentation (PZI) throughout construction, including a textual description of the changes, - preparation of the Detailed Design (PZI) level documents required to update or align the BIM model with the as-built condition (LOD 500) and the preparation of the as-built project documentation for the works (PID), - monthly submission of approved equipment and material changes affecting the BIM model in IFC format, - maintenance and use in the execution of the last valid revision of the construction documentation (PZI), including additions to the construction design documentation (PZI) resulting from changes during construction.

## 0.2_Uvod-DGNB
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
0.2 | SPLOŠNI TEHNIČNI POGOJI ZA PODROČJE DGNB CERTIFICIRANJA | GENERAL TECHNICAL CONDITIONS FOR DGNB CERTIFICATION
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic entity with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
| Splošni pogoji za področje DGNB certificiranja predstavljajo dopolnilo splošnim tehničnim pogojem in ne odpravljajo drugih obveznosti in odgovornosti, ki jih ima izvajalec v skladu s predpisi in pogodbo. | The General Conditions for DGNB Certification are complementary to the General Technical Conditions and do not exclude other obligations and responsibilities that the Contractor has under the Regulations and the Contract.
0.2.1 | Izvajalec mora v svojih ponudbah upoštevati, da se bo objekt certificiral v skladu z zahtevami DGNB sistema certificiranja trajnostne gradnje, ter pravočasno (vsaj 60 dni pred vgradnjo posameznega produkta) dostaviti vso ustrezno dokumentacijo za vse v ponudbi zajete materiale, elemente in opremo. Zahtevana je uporaba materialov, elementov ali opreme, ki so okolju in ljudem prijazni, energetsko učinkoviti in obenem ustrezajo zahtevam DGNB sistema. Zahtevan nivo certifikata je: ZLATI CERTIFIKAT | The Contractor shall take into account in its tenders that the building will be certified in accordance with the requirements of the DGNB Sustainable Building Certification Scheme and shall deliver all relevant documentation for all materials, elements and equipment included in the tender in a timely manner (at least 60 days before the installation of each product). The use of materials, elements or equipment that are environmentally and human friendly, energy efficient and at the same time meet the requirements of the DGNB system is required. The required level of certification is: GOLD CERTIFICATE
0.2.2 | Podrobnejši opis DGNB sistema in navodila za posamezne kriterije so dostopna v dokumentu"DGNB Criteria Set New Construction Buildings, Version 2020 International", ki je na voljo na DGNB spletni strani https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria | A more detailed description of the DGNB system and guidance on the individual criteria is available in the document "DGNB Criteria Set New Construction Buildings, Version 2020 International", available on the DGNB website https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria
0.2.3 | Izvajalec mora v svojih ponudbah upoštevati, da je potrebno skladno z določili DGNB certifikacijskega sistema, pravočasno (pred pričetkom gradnje) dostaviti vso ustrezno dokumentacijo, za vse v ponudbi zajete materiale, elemente in opremo (tehnični list, varnostni list, izjava o lastnostih, tehnična navodila za ravnanje, servisiranje, vzdrževanje,...) v slovenskem jeziku. Vgradnja kakršnihkoli materialov, elementov ali opreme, se izvede zgolj na podlagi predhodne preveritve posredovane dokumentacije in obenem potrditve s strani nadzornika. | The Contractor must take into account in its tenders that, in accordance with the provisions of the DGNB certification system, all relevant documentation for all materials, elements and equipment included in the tender (technical data sheet, safety data sheet, declaration of properties, technical instructions for handling, servicing, maintenance,...) must be delivered on time (prior to the start of construction) in the Slovene language (in accordance with the provisions of the DGNB certification system). The installation of any materials, elements or equipment shall be subject to prior checking of the submitted documentation and, at the same time, to the approval of the Supervisor.
0.2.4 | Izbrani materiali, elementi, naprave, sistemi in oprema morajo prispevati k večji trajnosti stavbe v smeri zagotavljanja energetske učinkovitosti, ekonomičnega in enostavnega vzdrževanja ter čiščenja, dolge življenjske dobe, uporabe okolju prijaznih materialov ipd. | The materials, elements, appliances, systems and equipment chosen must contribute to the sustainability of the building in terms of energy efficiency, economic and easy maintenance and cleaning, long lifetime, use of environmentally friendly materials, etc.
0.2.5 | Predloženi dokumenti za vse uporabljene materiale, elemente in opremo morajo izpolnjevati zahteve najmanj kakovostne stopnje QS3 (zaželeno QS4), iz dokumenta: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001) | The documents submitted for all materials, components and equipment used shall meet the requirements of at least quality level QS3 (preferably QS4) of the document DGNB Quality Grades for Materials, Components and Equipment (JULFS--7X9001)
0.2.6 | V kolikor izbrani materiali oz. elementi, navedeni v posameznih postavkah, ne ustrezajo vsaj kakovostni stopnji QS3 iz seznama: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), je izvajalec dolžan na to opozoriti projektanta, nadzor in investitorja ter podati predlog ustreznega materiala oz. elementa. | If the selected materials or elements listed in the individual items do not meet at least quality level QS3 of the list of DGNB quality classes for materials, elements and equipment (JULFS--7X9001), the Contractor shall draw this to the attention of the Designer, the Supervisor and the Investor, and shall make a proposal for a suitable material or element.
0.2.7 | Izvajalec lahko v svoji ponudbi predlaga alternativne produkte in rešitve glede na predvidene s projektom, pod pogojem, da le-te prav tako izpolnjujejo vse navedene zahteve. Pri morebitnih predlaganih alternativnih produktih oz. rešitvah je potrebno upoštevati najmanj enake ali boljše lastnosti v smislu življenjske dobe, obstojnosti, ter enostavnosti in stroška čiščenja ter vzdrževanja v primerjavi s projektom predpisanimi rešitvami. Za alternativne rešitve izvajalec pridobi soglasje projektanta, nadzornika in investitorja pred pričetkom gradnje. | The Contractor may propose alternative products and solutions to those envisaged by the project in its tender, provided that they also meet all the requirements set out above. Any alternative products or solutions proposed shall have at least the same or better characteristics in terms of service life, durability, and ease and cost of cleaning and maintenance compared to the solutions envisaged by the project. For alternative solutions, the contractor shall obtain the agreement of the designer, the supervisor and the investor before starting construction.
0.2.8 | Izvajalec med gradnjo dnevno beleži vsa eventualna odstopanja od PZI projektne dokumentacije ter podatke pravočasno posreduje naročniku, nadzoru in projektantu. Potrjene spremembe vnese v podlage za izdelavo PID in posodobitev BIM modelov. | During construction, the Contractor shall record on a daily basis any deviations from the Detailed Design documentation (PZI) and shall provide the information to the Client, Supervision and the Designer in a timely manner. Confirmed changes shall be entered into the basis for the As-built documentation (PID) and BIM model updates.
0.2.9 | Izvajalec med gradnjo sproti izpolnjuje Seznam vseh konstrukcijskih sestav s pripadajočimi vgrajenimi gradbenimi materiali in dokumentira naslednje podatke o vgrajenih materialih (v slovenskem jeziku): - Varnostni list - Tehnični list - Izjavo o lastnostih (če je relevantno) - Izkazovanje morebiti obstoječega okoljskega certifikata (Tip I - okoljski znak ali Tip III - okoljska produktna deklaracija /EPD) - Izjavo proizvajalca ali dobavitelja, da produkt ustreza zahtevam ENV1.2 - Tehnična navodila za ravnanje, servisiranje, vzdrževanje oziroma ostale, z zakonom predpisane dokumente in dokumentacijo. | During construction, the Contractor shall keep a List of all structural assemblies with their associated construction materials and document the following information on the materials installed (in Slovene language): - Safety Data Sheet - Technical Data Sheet - Declaration of performance (if applicable) - Demonstration of any existing environmental certification (Type I - Ecolabel or Type III - Environmental Product Declaration /EPD) - A declaration by the manufacturer or supplier that the product complies with the requirements of ENV1.2 - Technical instructions for handling, servicing, maintenance or other documents and documentation required by law.
0.2.10 | Za vse vgrajene bistvene tehnične sisteme mora izvajalec zagotoviti obstoj pooblaščenega servisa, ki deluje na območju Republike Slovenije, da ima investitor možnost skleniti ustrezno pogodbo o vzdrževanju. Med bistvene tehnične sisteme sodijo npr.: sistemi ogrevanja in hlajenja, priprava tehnoloških medijev, prezračevanje in klimatizacija, sistemi detekcije in gašenja požara, sistemi tehničnega varovanja, BMS in CNS sistemi upravljanja stavbe, razsvetljava, komunikacijski in WI-FI sistemi,... | For all installed essential technical systems, the contractor must ensure the existence of an authorised service centre operating in the territory of the Republic of Slovenia, so that the investor has the possibility of concluding an appropriate maintenance contract. The essential technical systems include, for example: heating and cooling systems, technological media preparation, ventilation and air conditioning, fire detection and extinguishing systems, technical security systems, BMS and CNS building management systems, lighting, communication and WI-FI systems,...
0.2.11 | Zaželeno je, da imajo uporabljeni elementi in materiali okoljsko oznako Tip I. (kot npr. ENCODE, BLUE ANGEL, ipd...). | It is preferable that the elements and materials used have a Type I environmental label (such as ENCODE, BLUE ANGEL, etc...).
0.2.12 | Izvajalec bo za elemente iz lesa moral dokazovati izvor z navedbo izvorne države in tipa lesa, FSC / PEFC certifikat z dodatnim pripadajočim potrdilom Chain of custody-trgovski certifikat dobavitelja - ta se dokazuje z dobavnicami, računi ali enakovredno. Za izdelke iz naravnega kamna iz EU držav je potrebna deklaracija, da je izvor in procesiranje teh izdelkov v celoti v EU državah. Za izdelke iz naravnega kamna, ki prihajajo iz držav izven EU, je potrebno predložiti dokazilo o izpolnjevanju ILO konvencije 182, ki vključuje neodvisna inšpekcijska poročila. | For wood elements, the contractor will be required to provide proof of origin, indicating the country of origin and the type of wood, FSC/PEFC certification with an additional Chain of Custody certificate - the supplier's trade certificate - this shall be evidenced by delivery notes, invoices or equivalent. For natural stone products from EU countries, a declaration that the sourcing and processing of these products is entirely in EU countries is required. For natural stone products from non-EU countries, proof of compliance with ILO Convention 182, including independent inspection reports, is required.
0.2.13 | Izobraževanje udeležencev pri gradnji Izvajalec je dolžan vse udeležence pri gradnji podrobneje seznaniti tudi z relevantnimi koncepti, študijami, elaborati, ki opredelujejo trajnostni način gradnje za naslednja področja: - zaščita pred hrupom (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)) - zaščita pred prašenjem - zaščita tal in podzemne vode (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)), Analiza tveganja za onesnaženje vodnega telesa podzemne vode št. 0346-023/2023, maj 2023 (Geološko projektiranje d.o.o.)) - ravnanje z gradbenimi odpadki (Načrt gospodarjenja z gradbenimi odpadki) Izobraževanja se izvajajo skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.1 1.2, 2.2, 3.2 in 4.2 Training for the parties implementing the construction work | Training of construction participants The contractor is also obliged to inform all construction participants in detail about relevant concepts, studies, elaborations defining sustainable construction methods for the following areas: - noise protection (Environmental Impact Assessment Report No 100123-11523, dated 11.5.2023, supplemented on 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.)) - dust protection - protection of soil and groundwater (Environmental Impact Assessment Report No. 100123-11523, dated 11.5.2023, supplemented 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.), Risk analysis for contamination of the groundwater No. 0346-023/2023, May 2023 (Geološko projektiranje d.o.o.)) - construction waste management (Construction Waste Management Plan) The training shall be carried out in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.1 1.2, 2.2, 3.2 and 4.2 Training for the parties implementing the construction work
0.2.14 | Navodila za obratovanje in vzdrževanje objekta Izvajalec pripravi Navodila za obratovanje in vzdrževanje objekta skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilih: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual | Instructions for the operation and maintenance of the facility The Contractor shall prepare the Operation and Maintenance Instructions for the Facility in accordance with the applicable Slovenian legislation and the DGNB System Instructions specified in the Criteria: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual
0.2.15 | Meritve kontrole kakovosti gradnje Izvajalec mora upoštevati, da se bodo po koncu gradnje izvedle naslednje meritve: - meritve zrakotesnosti - meritve s termokamero (termografija) - meritve akustike - meritve zvočne zaščite ovoja stavbe - meritve zvočne zaščite ločilnih elementov med posameznimi prostori različnih namembnosti - meritve udarnega zvoka - meritve vlažnosti vgrajenih elementov, pred vgradnjo finalnih tlakov - test odvoda dima in toplote Meritve morajo opraviti ustrezno usposobljeni preskusni organi ali strokovnjaki ter rezultate oceniti in primerjati z zahtevami. Obseg opravljenih meritev mora biti sorazmeren z velikostjo zgradbe in mora ustrezno odražati cilj preverjanja kakovosti zgradbe. Smiselno je, da izvajalec del tekom gradnje za sprotno kontrolo kakovosti vgrajenih materialov, elementov in opreme, sam izvaja meritve. Končne meritve (ob primopredaji) izvede tretja oseba kot neodvisna potrditev doseganja zahtev. Meritve se izvajajo skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 2. Quality control measurements | Construction quality control measurements The contractor must take into account that the following measurements will be carried out after completion of the construction: - airtightness measurements - thermal camera measurements (thermography) - acoustics measurements - measurements of the sound insulation of the building envelope - measurements of the sound insulation of the separating elements between different rooms of different uses - impact sound measurements - moisture measurements of the installed elements, prior to the installation of the final flooring - smoke and heat extraction test The measurements shall be carried out by suitably qualified test bodies or experts and the results evaluated and compared with the requirements. The extent of the measurements carried out shall be proportionate to the size of the building and shall adequately reflect the objective of the building quality verification. It is reasonable for the contractor to carry out his own measurements during construction to check the quality of the materials, elements and equipment installed. Final measurements (at handover) are carried out by a third party as an independent confirmation of compliance with the requirements. The measurements shall be carried out in accordance with the applicable Slovenian legislation and the DGNB system instructions specified in the benchmark: PRO 2.2 2. Quality control measurements
0.2.16 | Zagotavljanje kakovosti za uporabljene gradbene proizvode Izvajalec mora zagotavljati izvajanje primerjav med definiranim in dejansko uporabljenim materialom, elementom ali opremo skladno seznamom: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), vključno z dokazno dokumentacijo ugotovitev primerjav ter skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 3.1 Quality assurance for the used construction products | Quality assurance for the construction products used The Contractor shall ensure that comparisons are made between the defined and the actual material, element or equipment used in accordance with the list: DGNB Quality Grades of Installed Materials, Elements and Equipment (JULFS--7X9001), including supporting documentation of the findings of the comparisons, and in accordance with the DGNB system instructions defined in the Criterion: PRO 2.2 3.1 Quality assurance for the used construction products
0.2.17 | Zaščita pred vlago Izvajalec predloži dokumentacijo, ki dokazuje, da je bil izveden program prezračevanja, prilagojen stavbi, s čimer se zagotovi pogoje, da so vgrajeni gradbeni elementi ustrezno suhi, skladno z navodili DGNB opredeljenimi v merilu: PRO 2.2 4.1 Mould prevention | Protection against moisture The Contractor shall provide documentation demonstrating that a building-specific ventilation programme has been implemented to ensure that the building elements installed are adequately dry, in accordance with the DGNB guidelines specified in the criteria: PRO 2.2 4.1 Mould prevention
0.2.18 | Preizkusi delovanja sistemov Izvajalec sodeluje pri izvedbi predhodnega in končnega preizkusa delovanja vseh bistvenih tehničnih komponent stavbe in pripravi ustrezne dokazne dokumentacije ter pri usposabljanju vzdrževalcev/upravljalcev stavbe, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators | System performance tests The Contractor shall be involved in the performance of the preliminary and final performance tests of all essential technical components of the building and the preparation of the relevant supporting documentation, as well as in the training of the maintenance/management staff of the building, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators
0.2.19 | Poročilo o zagonu objekta Izvajalec sodeluje pri pripravi končnega poročila o zagonu objekta, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 5.1 Creation of a detailed final report | Commissioning report The Contractor shall be involved in the preparation of the final commissioning report, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 5.1 Creation of a detailed final report
0.2.20 | Koncept celovitega delovanja sistemov v stavbi Izvajalec sodeluje pri procesu implementiranja stalnega nadzora in nastavitev delovanja stavbe ter usposabljanju vzdrževalcev/upravljalcev stavbe. Navedeno se izvede v skladu z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 6.1 Creation and handover of an integral operating concept | The concept of integrated building systems The contractor is involved in the process of implementing the building's continuous monitoring and settings and training the building's maintenance/management staff. This shall be done in accordance with the DGNB system instructions defined in the benchmark: PRO 2.3 6.1 Creation and handover of an integral operating concept
0.2.21 | Prilagoditev nastavitev sistemov po začetni fazi uporabe objekta Izvajalec sodeluje pri ponovnem pregledu delovanja vseh bistvenih tehničnih sistemov ter eventualni ponovni prilagoditvi teh sistemov s strani strokovnjaka oz. (neodvisne) tretje osebe. Postopek se izvede po približno 10–14 mesecih po zaključku gradnje, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 7.1 Readjustment of the system following initial operating phase | Adjusting system settings after the initial phase of use of the building The Contractor shall be involved in the re-examination of the functioning of all essential technical systems and the possible re-adjustment of these systems by an expert or (independent) third party. The procedure shall be carried out approximately 10-14 months after completion of construction, in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.3 7.1 Readjustment of the system following initial operating phase

## 4.5.0_Rekapitulacija
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
| REKAPITULACIJA STROŠKOV STROJNIH DEL | COST SUMMARY OF MECHANICAL WORKS
| 4 NAČRT S PODROČJA STROJNIŠTVA | 4 DOCUMENTATION IN THE FIELD OF MECHANICAL ENGINEERING
| 4/5 Sistemi za gašenje požara in hidrantno omrežje | 4/5 Fire extinguishing systems and Hydrant Network
4.5 | STROJNA DELA | MECHANICAL WORKS
4.5.1 | ŠPRINKLERSKI GASILNI SISTEM | SPRINKLER EXTINGUISHING SYSTEM | 0
4.5.2 | HIDRANTNO OMREŽJE IN GASILNI APARATI | HYDRANT NETWORK AND FIRE EXTINGUISHERS | 0
4.5.3 | SISTEM ZA GAŠENJE KUHALNIH ELEMENTOV | COOKING ELEMENT EXTINGUISHING SYSTEM | 0
4.5.4 | SKUPNE POSTAVKE | COMMON ITEMS | 0
0
0% | NEPREDVIDENA DELA | UNFORSEEN WORKS | 0
| SKUPAJ STROJNA DELA | TOTAL MECHANICAL WORKS | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT

## 4.5.1_Šprinkler
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.5 | STROJNA DELA IN MATERIAL | MECHANICAL WORKS IN MATERIAL
4.5.1 | ŠPRINKLERSKI GASILNI SISTEM | SPRINKLER EXTINGUISHING SYSTEM |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
1 | ŠPRINKLERSKI GASILNI SISTEM | SPRINKLER EXTINGUISHING SYSTEM
| Namestitev šprinklerskega gasilnega sistema mora biti izvedena v skladu s smernico VdS CEA 4001:2024 s strani izvajalca s VdS pooblastilom za izvajanje šprinklerskih gasilnih sistemov. Če lokalni predpisi za določena dela zahtevajo podizvajalce, jih mora pooblaščeni izvajalec poučiti o posebnih zahtevah VdS smernice. | The installation of the sprinkler system must be carried out in accordance with VdS guideline CEA 4001:2024 by a contractor authorised by VdS to carry out sprinkler systems. If local regulations require subcontractors for certain works, the authorised contractor must inform them of the specific requirements of the VdS guideline.
1.1 | Nizkotlačna centrifugalna črpalka na elektromotorni pogon skladna z EN 733:2000. Črpalka mora imeti VdS certfikat in biti sposobna zagotoviti prostorninsai pretoka 925 l/min pri tlaku 6,6 bar in 1480 l/min pri tlaku 6,0 bar. Postavka vključuje tlačni stikali za zagon (PS 09.32 in PS 09.34) krmilno omaro za krmiljenje glavne elektro črpalke, črpalke za vzdrževanje statičnega tlaka in kompresorja. Omara mora imeti VdS certifikat in biti združljiva z glavno črpalko na elektromotroni pogon ter s črpalko za polnjenje tlačnega zalogovnika. Ustreza KSB Etanorm FXV 080-065-250 pri 2940 obratih na minuto. Oznaka: P 03.10 | Low-pressure centrifugal pump, electric motor driven, complying with EN 733:2000. The pump shall be VdS-certified and capable of delivering a flow volume of 925 l/min at 6,6 bar and 1480 l/min at 6,0 bar. The item shall include pressure switches for starting (PS 09.32 and PS 09.34), a control cabinet for the control of the main electric pump, the static pressure pump and the compressor. The cabinet shall be VdS-certified and shall be compatible with the main electric motor driven pump and the pressure reservoir priming pump. It corresponds to KSB Etanorm FXV 080-065-250 at 2940 rpm. Code: P 03.10 | kpl | 1 |  | 0
1.2 | Nizkotlačna centrifugalna črpalka na dizelski pogon skladna z EN 733:2000. Črpalka mora imeti VdS certfikat o ustreznosti za sprinkler sisteme. Sposobna mora biti 925 l/min pri 6,6 bar in 1480 l/min pri 6,0 bar. Diesel motor mora biti opremljen z akumulatorjem, mehansko napravo za nastavitev vrtljajev, stikalnimi kontakti za avtomatsko kontrolo tlaka mazalnega olja in temperature hladilne vode, števcem vrtljajev in števcem obratovalnih ur. V komplet spadajo še: - dnevni rezervoar goriva prostornine 200 litrov (za 8 ur delovanja po VdS) z navojnimi priključki za cevi in opremo ter prirobničnim priključkom za nivojsko stikalo, oljekazno steklo in nosilnim okvirjem za rezervoar; - ročna črplaka za prečrpavanje goriva z navojnimi priključki in protipovratnimi ventili; - tlačni stikali za zagon (PS 09.36 in PS 09.38) - elektrokrmilna omarica v skladu s VdS za šprinklersko diesel črpalko z napajanjem iz električnega omrežja in kabelskimi povezavami ter - blažilnike vibracij, protiprirobnice, vijačni in tesnilni material. Ustreza KSB Etanorm FXV 080-065-250 pri 2940 obratih na minuto. Oznaka: P 04.10 | Low-pressure diesel-powered centrifugal pump complying with EN 733:2000. The pump must have a VdS certificate of suitability for sprinkler systems. It must be capable of 925 l/min at 6.6 bar and 1480 l/min at 6.0 bar. The diesel engine must be equipped with an accumulator, a mechanical speed adjustment device, switch contacts for automatic control of lubricating oil pressure and cooling water temperature, a rev counter and an operating hours counter. The following items are also included in the set: - 200 litre daily fuel tank (for 8 hours of VdS operation) with threaded connections for hoses and fittings and flanged connections for level switch, oil glass and tank support frame; - manual fuel pumps with threaded connections and non-return valves; - pressure switches for starting (PS 09.36 and PS 09.38) - an electrical control cabinet in accordance with the VdS for the diesel sprinkler pump with mains supply and cable connections; and - vibration dampers, anti-friction, bolting and sealing materials. It corresponds to KSB Etanorm FXV 080-065-250 at 2940 rpm. Code: P 04.10 | kpl | 1 |  | 0
1.3 | Črpalni sklop z visokotlačno centrifugalno elektromotorno črpalko. Črpalka mora biti sposobna zagotavljati prostorninski pretok vsaj 100 l/min pri tlaku 8 bar. Ustreza KSB DeltaSolo D 1/0611 B. Oznaka: P 07.10 | Pumping set with high pressure centrifugal electric motor pump. The pump shall be capable of providing a volumetric flow of at least 100 l/min at a pressure of 8 bar. It shall comply with KSB DeltaSolo D 1/0611 B. Code: P 07.10 | kpl | 1 |  | 0
1.4 | Kompenzator vibracij črpalk v obliki treh fleksibilnih spojk (štejejo se kot en komplet) za ožlebljene cevi z VdS certifikatom in tlačno stopnjo vsaj PN16. Ustreza Victaulic Style 75. | Pump vibration compensator in the form of three flexible couplings (counted as one set) for VdS-certified grooved pipes with a pressure rating of at least PN16. Corresponds to Victaulic Style 75.
| DN32 (VX 07.08; VX 07.11) | DN32 (VX 07.08; VX 07.11) | kpl | 2 |  | 0
| DN80 (VX 03.09; VX 03.11; VX 04.09; VX 04.11 ) | DN80 (VX 03.09; VX 03.11; VX 04.09; VX 04.11 ) | kpl | 4 |  | 0
1.5 | Sesalna košara s protipovratno loputo. Sesalna košara mora biti iz nerjavnega jekla, protipovratna loputa pa iz nodularne litine. Ustreza Zagožen "sesalni koš s protipovratnim ventilom". | Suction basket with non-return flap. The suction basket shall be made of stainless steel and the non-return flap of ductile cast iron. Corresponds to the Zagozena "suction bin with non-return valve".
| DN 65 (FO 07.01 + CV 07.02) | DN 65 (FO 07.01 + CV 07.02) | kpl | 1 |  | 0
| DN 150 (FO 03.01 + CV 03.02; FO 04.01 + CV 04.02) | DN 150 (FO 03.01 + CV 03.02; FO 04.01 + CV 04.02) | kpl | 2 |  | 0
1.6 | Preprečevalnik vrtinčenja iz nerjavnega jekla skladen z zahtevami smernice VdS CEA 4001:2021. | Stainless steel swirl arrestor complying with the requirements of VdS guideline CEA 4001:2021.
| DN 65× Ø600 (FO 07.03) | DN 65× Ø600 (FO 07.03) | kpl | 1 |  | 0
| DN 150 × Ø800 (FO 03.03; FO 04.03) | DN 150 × Ø800 (FO 03.03; FO 04.03) | kpl | 2 |  | 0
1.7 | Tlačni zalogovnik ležeče izvedbe s prostornino 25 m3 in tlačno stopnjo vsaj PN10. Posoda mora biti izdelana iz jekla, ki je zunaj in znotraj ustrezno korozijsko zaščiteno. Tlačni zalogovnik mora imeti revizijsko odprtino, priključek DN 20 za komprimiran zrak, DN 40 za vodo, DN 32 za izpust in priključek za prikazovalnik nivoja. Ustreza Minimax "water pressure vessel with riser tube". Oznaka: PX 09.00 | The pressure vessel shall be of a floating design with a capacity of 25 m3 and a pressure rating of at least PN10. The vessel shall be constructed of steel with adequate corrosion protection externally and internally. The pressure vessel shall have an inspection opening, a DN 20 connection for compressed air, a DN 40 connection for water, a DN 32 connection for the outlet and a connection for a level display. Corresponds to Minimax "water pressure vessel with riser tube". Code: PX 09.00 | kos | 1 |  | 0
1.8 | Sklop za indikacijo nivoja kapljevine v tlačnem zalogovniku. Postavka vključuje tudi eno tlačno in dve nivojski stikali, dva manometra ter ostali pripadajoči material. Ustreza Minimax "liquid level indicator DWX2 with monitoring". Oznaka: FV 09.02 + PI 09.03 + PS 09.04 + FV 09.05 + PG 09.06 + LS 09.07 + LS 09.08 + LG 09.09 | Assembly for indicating the level of liquid in the pressure reservoir. The item also includes one pressure switch, two level switches, two pressure gauges and other related material. Corresponds to Minimax "liquid level indicator DWX2 with monitoring". Code: FV 09.02 + PI 09.03 + PS 09.04 + FV 09.05 + PG 09.06 + LS 09.07 + LS 09.08 + LG 09.09 | kpl | 1 |  | 0
1.9 | Varnostni ventil za namestitev na tlačni zalogovnik nastavljen na odpiranje pri 12 bar. Ustreza IMI PNEUMATEX DSV 15-10.0 F. Oznaka: RV 09.01 | Safety valve for installation on pressure tank set to open at 12 bar. Meets IMI PNEUMATEX DSV 15-10.0 F. Code: RV 09.01 | kos | 1 |  | 0
1.10 | Kompresor zraka s tlačnim rezervoarjem prostornine najmanj 50 litrov, elektromotornim pogonom, vključno z varnostnim ventilom, gibljivo cevno povezavo, manometrom, nepovratnim ventilom, elektromagnetnim razbremenilnim ventilom in montažnim materialom. Ostale tehnične lastnosti so: - minimalni tlak: 7,6 bar; - minimalni efektivni prostorninski pretok: 300 l/min; - minimalna stopnja zaščite proti vdoru: IP44. Ustreza Minimax Classic 460-50 W. Oznaka: C 08.01–FV 08.06 | Air compressor with a minimum 50 litre pressure reservoir, electric motor drive, including safety valve, flexible hose connection, pressure gauge, non-return valve, solenoid relief valve and mounting material. Other technical characteristics are: - minimum pressure: 7,6 bar; - minimum effective volumetric flow rate: 300 l/min; - minimum ingress protection rating: IP44. It corresponds to the Minimax Classic 460-50 W. Code: C 08.01-FV 08.06 | kpl | 1 |  | 0
1.11 | Kompresor zraka s tlačnim rezervoarjem prostornine najmanj 50 litrov, elektromotorim pogonom, vključno z varnostnim ventilom, gibljivo cevno povezavo, manometrom, nepovratnim ventilom, elektromagnetnim razbremenilnim ventilom in montažnim materialom. Ostale tehnične lastnosti so: - minimalni efektivni prostorninski pretok: 134 l/min; - minimalna stopnja zaščite proti vdoru: IP44 Ustreza Minimax Classic 210-50 W. Oznaka: C 15.01–FV 15.06; C 16.01–FV 16.06 | Air compressor with a minimum 50 litre pressure reservoir, electric motor drive, including safety valve, flexible hose connection, pressure gauge, non-return valve, solenoid relief valve and mounting material. Other technical characteristics are: - minimum effective volumetric flow rate: 134 l/min; - minimum ingress protection rating: IP44 It corresponds to the Minimax Classic 210-50 W. Code: C 15.01-FV 15.06; C 16.01-FV 16.06 | kpl | 2 |  | 0
1.12 | Komplet za dopolnjevanje šprinklerskega omrežja s komprimiranim zrakom sestavljen iz krogelnega ventila DN15 z zaklepom, ključavnico, dušilke v glavnem vodu in obvodne (ang. "bypass") povezave iz nerjavne cevi s spojkami. Ustreza Victaulic 757 Oznaka: FV 17.01 – FV 17.04 | Compressed air sprinkler replenishment kit consisting of a DN15 ball valve with lock, lock, throttle valve in the main line and a bypass connection made of stainless steel pipe with couplings. Corresponds to Victaulic 757 Code: FV 17.01 - FV 17.04 | kpl | 1 |  | 0
1.13 | Gasilski priključek za napajanje šprinklerskega stabilnega gasilnega sistema preko gasilskih vozil, vključno s: - zbiralno cevjo 1 × Ø114,3 mm × 3,6 mm skladno z EN 10216-1:2019 in VdS CEA 4001:2021, - dvema zapornima zasunoma imenske velikosti DN65; - dvema priključkoma dimenzije DN65 v obliki stabilnih gasilskih spojk vrste B in pripadajočima slepima spojkama; - napisno tablico s spodnjim besedilom: "ŠPRINKLER SISTEM GASILSKI PRIKLJUČEK UPORABA DOVOLJENA GASILCEM" Oznake: YV 10.97, YV 10.98, YP 10.99 | Firefighting connection for supplying the sprinkler stable firefighting system via firefighting vehicles, including: - 1 × Ø114.3 mm × 3.6 mm collector pipe in accordance with EN 10216-1:2019 and VdS CEA 4001:2021, - two DN65 nominal size stopcocks; - two DN65 connectors in the form of type B stable fire-fighting couplings and associated blind couplings; - a plaque with the text below: "SPRINKLER SYSTEM fIRE CONNECTION uSE PERMITTED FOR FIREFIGHTERS" Tags: YV 10.97, YV 10.98, YP 10.99 | kpl | 1 |  | 0
1.14 | Cevni razdelilnik izdelan iz brezšivne jeklene cevi iz ogljikovega jekla (P235TR2) skladne z EN 10216-1:2014. Imenski premer glavne cevi mora biti vsaj DN125, imenski premer vseh odcepov za pa DN80. Tlačna stopnja razdelilnika mora biti vsaj PN16. Razdelilnik je predvidoma ležeče izvedbe, z bombiranima ali prirobničnima zaključkoma. Priključki morajo biti skladni s shemo. Okvirna dolžina razdelilca je 13 metrov. Postavka vključuje izdelavo delavniške risbe, protiprirobnice, varilni, pritrdilni in tesnilni material. Oznaka: FX 10.00 | The manifold shall be made of seamless carbon steel pipe (P235TR2) complying with EN 10216-1:2014. The nominal diameter of the main pipe shall be at least DN125 and the nominal diameter of all branch pipes shall be DN80. The pressure rating of the manifold shall be at least PN16. The manifold shall be of the clamped design, with either bomb- or flanged ends. The connections shall be in accordance with the diagram. The approximate length of the manifold shall be 13 m. The item shall include the production of a shop drawing, a counter-plate, welding, fixing and sealing material. Code: FX 10.00
1.15 | Mokri alarmni ventil z naslednjimi tehničnimi zahtevami: - imenski premer DN80; - minimalna tlačna stopnja PN16; - VdS certifikat; - spajanje s spojkami za ožlebljene cevi; Poleg alarmnega ventila postavka zajema še: - armature za testiranje in praznenje, - ostale pripadajoče armature (čistilni kos, odzračevalni ventil, nepovratni ventil, zaporni ventili, manometroi ipd.); - 2 × alarmno tlačno stikalo z navojnim priključkom DN15, tlačne stopnje PN16, 24 V-DC, z nastavljivim območjem od 4–13 bar, s kontrolno lučko, z zaščito proti vdoru IP 54; - zakasnilni rezervoar z zaslonko; - cevne povezave med elementi - in ves preostali pripadajoči material. Ustreza Victaulic FireLockTM Series 751 Oznake: AV 21.02; AV 22.02; AV 23.02; AV 24.02; AV 25.02 | A wet-type alarm valve with the following technical requirements: - dN80 nominal diameter; - minimum pressure rating PN16; - VdS certificate; - joining with couplings for grooved pipes; In addition to the alarm valve, the item also includes: - fittings for testing and emptying, - other associated fittings (cleaner, vent valve, non-return valve, shut-off valves, pressure gauges, etc.); - 2 × alarm pressure switch with DN15 threaded connection, pressure rating PN16, 24 V-DC, adjustable range from 4-13 bar, with indicator light, ingress protection IP 54; - a delay tank with a diaphragm; - pipe connections between elements - and all other related materials. Meets Victaulic FireLockTM Series 751 Tags: AV 21.02; AV 22.02; AV 23.02; AV 24.02; AV 25.02 | kpl | 5 |  | 0
1.16 | Suhi alarmni ventil s pospeševalnikom z naslednjimi tehničnimi zahtevami: - imenska velikost: DN100; - tlačna stopnje PN16; - VdS certifikat; - spajanje s spojkami za ožlebljene cevi; - izvedba za hitro praznjenje. Poleg alarmnega ventila postavka zajema še: - armature za testiranje in praznenje; - ostale pripadajoče armature; - 2 × alarmno tlačno stikalo z navojnim priključkom DN15, tlačne stopnje PN16, 24 V-DC ali 250V-DC napajanjem, z nastavljivim območjem od 4-13 bar, s kontrolno lučko, z zaščito proti vdoru IP 54; - cevne povezave med elementi. Ustreza Victaulic FireLock NXT 768N + 746-LPA. Oznake: AV 11.02; AV 12.02; AV 13.02; AV 14.02 | Dry Accelerator Alarm Valve with the following technical requirements: - nominal size: DN100; - pressure rating PN16; - VdS certificate; - joining with couplings for grooved pipes; - quick-discharge version. In addition to the alarm valve, the item also includes: - fittings for testing and emptying; - other associated fittings; - 2 × alarm pressure switch with DN15 threaded connection, pressure rating PN16, 24 V-DC or 250 V-DC power supply, adjustable range from 4-13 bar, with indicator light, ingress protection IP 54; - pipe connections between elements. Meets Victaulic FireLock NXT 768N + 746-LPA. Tags: AV 11.02; AV 12.02; AV 13.02; AV 14.02 | kpl | 4 |  | 0
1.17 | Praznilno korito izdelano iz vsaj 3 mm debele nerjavne pločevine (1.4301) ojačano s profili, z nogami za postavitev na tla. V korito se na delovišču izreže luknja za priključitev na sistem odpadnih vod. | Emptying trough made of stainless steel sheet (1.4301) at least 3 mm thick, reinforced with profiles, with feet for placing on the ground. A hole shall be cut in the trough at the work site for connection to the waste water system.
| 12800 × 800 × 650 mm (YX 99.99), | 12800 × 800 × 650 mm (YX 99.99), | kpl | 1 |  | 0
| 1000 × 500 × 650 mm (YX 98.99). | 1000 × 500 × 650 mm (YX 98.99). | kpl | 1 |  | 0
1.18 | Plovni ventil za polnjenje bazena požarne vode, imenskega premera DN 50 in tlačne stopnje vsaj PN10. Ventil mora biti skladen s standardi za pitno vodo EN 805:2000, EN 806:2000 in imeti VdS certifikat. Ustreza Minimax SV2. Oznaka: LV 01.03 | Float valve for filling a fire water tank, nominal diameter DN 50 and pressure rating at least PN10. The valve shall comply with the drinking water standards EN 805:2000, EN 806:2000 and be VdS certified. Corresponds to Minimax SV2. Code: LV 01.03 | kpl | 1 |  | 0
1.19 | Zaporni zasun za uporabo v sistemih z vodo, tlačne stopnje vsaj PN16, s stikalom za nadzor položaja odprto/zaprto ter z VdS certifikatom. Ustreza Minimax NRG11 ali NRF11. | Gate valve for use in water systems, pressure rating at least PN16, with open/closed position control switch and VdS certified. Fits Minimax NRG11 or NRF11.
| DN50 (YV 01.02 + GS 01.02) | DN50 (YV 01.02 + GS 01.02) | kpl | 1 |  | 0
| DN65 (YV 02.01 + GS 02.01) | DN65 (YV 02.01 + GS 02.01) | kpl | 1 |  | 0
| DN100 (FV 09.01 + GS 09.01; FV 09.03 + GS 10.03) | DN100 (FV 09.01 + GS 09.01; FV 09.03 + GS 10.03) | kpl | 2 |  | 0
| DN125 (YV 03.31 + GS 03.31; YV 04.31 + GS 04.31) | DN125 (YV 03.31 + GS 03.31; YV 04.31 + GS 04.31) | kpl | 2 |  | 0
1.20 | Zaporna loputa za uporabo v sistemih z vodo, z ožlebljenima priključkoma, normalno odprta, tlačne stopnje vsaj PN16, s stikalom za nadzor položaja odprto/zaprto in z VdS certifikatom. Ustreza Victaulic Series 765. | Butterfly valve for use in water systems, with two grooved connections, normally open, pressure rating at least PN16, with open/closed position control switch and VdS certified. Corresponds to Victaulic Series 765.
| DN50 (FV 07.15 + GS 07.15) | DN50 (FV 07.15 + GS 07.15) | kpl | 1 |  | 0
| DN65 (FV 07.05 + GS 07.05) | DN65 (FV 07.05 + GS 07.05) | kpl | 1 |  | 0
| DN80 (FV 11.01 + GS 11.01; FV 11.07 + GS 11.07; FV 12.01 + GS 12.01; FV 12.07 + GS 12.07; FV 13.01 + GS 13.01; FV 13.07 + GS 13.07; FV 14.01 + GS 14.01; FV 14.07 + GS 14.07; FV 21.01 + GS 21.01; FV 21.08 + GS 21.08; FV 22.01 + GS 22.01; FV 22.08 + GS 22.08; FV 23.01 + GS 23.01; FV 23.08 + GS 23.08; FV 24.01 + GS 24.01; FV 24.08 + GS 24.08; FV 25.01 + GS 25.01; FV 25.08 + GS 25.08; FV 21.21 + GS 21.21; FV 21.31 + GS 21.31; FV 22.21 + GS 22.21; FV 22.31 + GS 22.31; FV 22.41 + GS 22.41; FV 22.51 + GS 22.51; FV 23.21 + GS 23.21; FV 23.31 + GS 23.31; FV 23.41 + GS 23.41; FV 23.51 + GS 23.51; FV 24.21 + GS 24.21; FV 24.31 + GS 24.31; FV 24.41 + GS 24.41; FV 24.51 + GS 24.51; FV 25.21 + GS 25.21; FV 25.31 + GS 25.31; FV 25.41 + GS 25.41; FV 25.51 + GS 25.51) | DN80 (FV 11.01 + GS 11.01; FV 11.07 + GS 11.07; FV 12.01 + GS 12.01; FV 12.07 + GS 12.07; FV 13.01 + GS 13.01; FV 13.07 + GS 13.07; FV 14.01 + GS 14.01; FV 14.07 + GS 14.07; FV 21.01 + GS 21.01; FV 21.08 + GS 21.08; FV 22.01 + GS 22.01; FV 22.08 + GS 22.08; FV 23.01 + GS 23.01; FV 23.08 + GS 23.08; FV 24.01 + GS 24.01; FV 24.08 + GS 24.08; FV 25.01 + GS 25.01; FV 25.08 + GS 25.08; FV 21.21 + GS 21.21; FV 21.31 + GS 21.31; FV 22.21 + GS 22.21; FV 22.31 + GS 22.31; FV 22.41 + GS 22.41; FV 22.51 + GS 22.51; FV 23.21 + GS 23.21; FV 23.31 + GS 23.31; FV 23.41 + GS 23.41; FV 23.51 + GS 23.51; FV 24.21 + GS 24.21; FV 24.31 + GS 24.31; FV 24.41 + GS 24.41; FV 24.51 + GS 24.51; FV 25.21 + GS 25.21; FV 25.31 + GS 25.31; FV 25.41 + GS 25.41; FV 25.51 + GS 25.51) | kpl | 36 |  | 0
| DN100 (FV 10.95 + GS 10.95) | DN100 (FV 10.95 + GS 10.95) | kpl | 1 |  | 0
| DN125 (FV 03.14 + GS 03.14; FV 04.14 + GS 04.14) | DN125 (FV 03.14 + GS 03.14; FV 04.14 + GS 04.14) | kpl | 2 |  | 0
| DN150 (FV 03.05 + GS 03.05; FV 04.05 + GS 04.05) | DN150 (FV 03.05 + GS 03.05; FV 04.05 + GS 04.05) | kpl | 2 |  | 0
1.21 | Zaporni ventil za uporabo v sistemih z vodo, imenskega premera DN 40, z ožlebljenima ali navojnima priključkoma, tlačne stopnje vsaj PN16, s stikalom za nadzor položaja odprto/zaprto in z VdS certifikatom. Ustreza Victaulic Series 728. Oznaka: FV 04.21 + GS 04.21 | Shutoff valve for use in water systems, nominal diameter DN 40, with two grooved or threaded connections, pressure rating at least PN16, with open/closed position control switch and VdS certified. Corresponds to Victaulic Series 728. Code: FV 04.21 + GS 04.21 | kos | 1 |  | 0
1.22 | Zaporni ventil za uporabo v sistemih z vodo, z ožlebljenima priključkoma, tlačne stopnje vsaj PN16 in z enim od VdS, FM ali UL certifikatov. Ustreza Victaulic Series 722. | Shutoff valve for use in water systems, with two grooved connections, pressure rating at least PN16 and with one of the VdS, FM or UL approvals. Corresponds to Victaulic Series 722.
| DN 15 | DN 15 | kos | 10 |  | 0
| DN 20 | DN 20 | kos | 5 |  | 0
| DN 40 | DN 40 | kos | 5 |  | 0
| DN 50 | DN 50 | kos | 120 |  | 0
1.23 | Protipovratna loputa za uporabo v sistemih z vodo, tlačne stopnje vsaj PN16, z ožlebljenima priključkoma in VdS certifikatom. Ustreza Victaulic Series 717 ali 717H. | Check valve for use in water systems, pressure rating at least PN16, with two grooved connections and VdS certificate. Fits Victaulic Series 717 or 717H.
| DN 50 (CV 07.14) | DN 50 (CV 07.14) | kos | 1 |  | 0
| DN 80 (CV 21.22; CV 21.32; CV 22.22; CV 22.32; CV 22.42; CV 22.52; CV 23.22; CV 23.32; CV 23.42; CV 23.52; CV 24.22; CV 24.32; CV 24.42; CV 24.52; CV 22.52; CV 25.32; CV 25.42; CV 25.52) | DN 80 (CV 21.22; CV 21.32; CV 22.22; CV 22.32; CV 22.42; CV 22.52; CV 23.22; CV 23.32; CV 23.42; CV 23.52; CV 23.42; CV 23.52; CV 23.42; CV 23.52; CV 23.52; CV 24.22; CV 24.32; CV 24.32; CV 24.42; CV 24.52; CV 22.52; CV 22.52; CV 25.32; CV 25.42; CV 25.52) | kos | 18 |  | 0
| DN 100 (CV 09.12; CV 10.94) | DN 100 (CV 09.12; CV 10.94) | kos | 2 |  | 0
| DN 125 (CV 03.13, CV 04.13) | DN 125 (CV 03.13, CV 04.13) | kos | 2 |  | 0
1.24 | Tlačni varnostni ventil za uporabo v sistemih z vodo, z VdS, FM ali UL ceritifikatom, navojnim spajanjem, možnostjo nastavitve na 12 bar in s ključavnico proti nepooblaščeni uporabi. Ustreza AGF model 7000 + ključavnica. Oznake: RV 21.10; RV 22.10; RV 23.10; RV 24.10; RV 25.10 | Pressure relief valve for use in water systems, with VdS, FM or UL certification, threaded coupling, adjustable to 12 bar and with lock against unauthorised use. Fits AGF model 7000 + lock. Tags: rv 21.10; rv 22.10; rv 23.10; rv 24.10; rv 25.10 | kpl | 5 |  | 0
1.25 | Avtomatski prezračevalno-odzračevalni ventil z VdS, FM ali UL certifikatom, tlačno stopnjo vsaj PN16, z zapornim krogelnim ventilom, praznilnim ventilom s priključkom za cev, zbiralnikom za vodno paro, mehanskim zaklepom proti nepooblaščeni uporabi (ključavnica), z neodvisnimi avtomatskimi funkcijami odvajanja zraka pri polnjenju sistema, dovajanjem zraka pri praznjenju sistema in odvajanjem oziroma dovajanjem zraka med obratovanjem. Ustrezajo proizvodi AGF Manufacturing serije PURGEnVENT + 7920AI. Oznake: RV 09.21; RV 21.26; RV 21.36; RV 22.26; RV 22.36; RV 22.46; RV 22.56; RV 23.26; RV 23.36; RV 23.46; RV 23.56; RV 24.26; RV 24.36; RV 24.46; RV 24.56; RV 25.26; RV 25.36; RV 25.46; RV 25.56; | Automatic ventilation/exhaust valve with VdS, FM or UL certification, pressure rating not less than PN16, with stop ball valve, discharge valve with hose connection, water vapour collector, mechanical lock against unauthorised use (lock), with independent automatic functions for venting air when filling the system, for supplying air when emptying the system, and for venting or supplying air during operation. AGF Manufacturing products of the PURGEnVENT + 7920AI series are suitable. Codes: RV 09.21; RV 21.26; RV 21.36; RV 22.26; RV 22.36; RV 22.46; RV 22.56; RV 23.26; RV 23.36; RV 23.46; RV 23.56; RV 23.46; RV 23.56; RV 24.26; RV 24.36; RV 24.36; RV 24.46; RV 24.56; RV 25.26; RV 25.36; RV 25.46; RV 25.56; | kpl | 19 |  | 0
1.26 | Ročni odzračevalni ventil z VdS, FM ali UL certifikatom, tlačno stopnjo vsaj PN16, s krogelnim ventilom, mehanskim zaklepom proti nepooblaščeni uporabi (ključavnica). Ustrezajo proizvodi AGF Manufacturing 7910MAV Oznake: RV ##.#5.## | Manual vent valve with VdS, FM or UL certification, pressure rating at least PN16, ball valve, mechanical lock against unauthorised use (lock). AGF Manufacturing 7910MAV products are compatible Tags: RV ##.#5.## | kpl | 100 |  | 0
1.27 | Preizkuševalno-praznilni ventil z VdS, FM ali UL certifikatom, K-faktorjem K80 (metrično), tlačno stopnjo vsaj PN16, z navojnimi priključki DN50, manometrom (0-16 bar) in tlačnim varnostnim ventilom. Ustreza AGF Manufacturing 1011 with T Kit + LockingKit ali 2511 with T Kit + LockingKit. Oznake: TDV 11.99; TDV 12.99; TDV 13.99; TDV 14.99; TDV 21.24; TDV 21.34; TDV 22.24; TDV 22.34; TDV 22.44; TDV 22.54; TDV 23.24; TDV 23.34; TDV 23.44; TDV 23.54; TDV 24.24; TDV 24.34; TDV 24.44; TDV 24.54; TDV 25.24; TDV 25.34; TDV 25.44; TDV 25.59; | Test-empty valve with VdS, FM or UL certification, K-factor K80 (metric), pressure rating at least PN16, with DN50 threaded connections, pressure gauge (0-16 bar) and pressure relief valve. Fits AGF Manufacturing 1011 with T Kit + LockingKit or 2511 with T Kit + LockingKit. Codes: TDV 11.99; TDV 12.99; TDV 13.99; TDV 14.99; TDV 21.24; TDV 21.34; TDV 22.24; TDV 22.34; TDV 22.44; TDV 22.54; TDV 23.24; TDV 23.34; TDV 23.44; TDV 23.44; TDV 23.54; TDV 24.24; TDV 24.34; TDV 24.44; TDV 24.54; TDV 25.24; TDV 25.34; TDV 25.44; TDV 25.59; | kpl | 22 |  | 0
1.28 | Vgradna omara ustreznih dimenzij za namestitev preizkuševalno-praznilnega ventila TDV 25.59 iz postavke 1.27. Zapiranje mora biti na ključ, barva pa usklajena z zahtevami arhitekturno-gradbenega načrta. Ustreza kovinska omara 540 × 580 × 250 mm | A built-in enclosure of suitable dimensions for the installation of the TDV 25.59 test and emptying valve referred to in item 1.27. The closure shall be key-operated and the colour shall be in accordance with the requirements of the architectural and construction plan. Fits metal cabinet 540 × 580 × 250 mm | kpl | 1 |  | 0
1.29 | Stabilna gasilska spojka s slepo spojko | Stable firefighting coupling with blind coupling
| DN50 (C) | DN50 (C) | kpl | 120 |  | 0
1.30 | Gasilna šprinklerska šoba z naslednjimi tehničnimi lastnostmi: - usmerjenost: stoječa (ang. "upright"); - vrsta pršilnega vzorca: paraboličen (ang. "spray"); - K-faktor: K80 (SI); - odzivni čas: kratek (RTI < 50); - nazivna temperatura odprtja: 68°C (rdeča kapsula); - imenska velikost priključka: DN15; - material šobe: medenina; - obvezni certifikati: VdS. Ustreza Minimax MX3-SU 1/2"-K80-68°-Ms. Oznaka: S1 | Fire sprinkler nozzle with the following technical characteristics: - orientation: upright; - type of spray pattern: parabolic; - K-factor: K80 (SI); - response time: short (RTI < 50); - nominal opening temperature: 68°C (red capsule); - nominal connection size: DN15; - nozzle material: brass; - mandatory certificates. Fits Minimax MX3-SU 1/2"-K80-68°-Ms. Code: S1 | kos | 3200 |  | 0
1.31 | Gasilna šprinklerska šoba z naslednjimi tehničnimi lastnostmi: - usmerjenost: stoječa (ang. "upright"); - vrsta pršilnega vzorca: paraboličen (ang. "spray"); - K-faktor: K80 (SI); - odzivni čas: kratek (RTI < 50); - nazivna temperatura odprtja: 68°C (rdeča kapsula); - imenska velikost priključka: DN15; - material šobe: medenina; - obvezni certifikati: VdS; - z zaščito proti omočenju in - z zaščito proti mehanskim poškodbam. Ustreza Minimax MX3-SU 1/2"-K80-68°-Ms. Oznaka: S1c | Fire sprinkler nozzle with the following technical characteristics: - orientation: upright; - type of spray pattern: parabolic; - K-factor: K80 (SI); - response time: short (RTI < 50); - nominal opening temperature: 68°C (red capsule); - nominal connection size: DN15; - nozzle material: brass; - mandatory certificates; - with anti-wetting protection and - with protection against mechanical damage. Fits Minimax MX3-SU 1/2"-K80-68°-Ms. Code: S1c | kos | 250 |  | 0
1.32 | Gasilne šprinklerska šoba z naslednjimi tehničnimi lastnostmi: - usmerjenost: viseča (ang. "pendent"); - vrsta pršilnega vzorca: paraboličen ("spray"); - K-faktor: K80 (SI); - odzivni čas:kratek (RTI < 50); - nazivna temperatura odprtja: 68°C (rdeča kapsula); - imenska velikost priključka: DN15; - material šobe: medenina; - obvezni certifikati: VdS. Ustreza Minimax MX3-SP 1/2"-K80-68°-Ms. Oznaka: S2 | Fire sprinkler nozzle with the following technical characteristics: - orientation: pendent; - type of spray pattern: parabolic ("spray"); - K-factor: K80 (SI); - response time:short (RTI < 50); - nominal opening temperature: 68°C (red capsule); - nominal connection size: DN15; - nozzle material: brass; - mandatory certificates. Fits Minimax MX3-SP 1/2"-K80-68°-Ms. Tag: S2 | kos | 1500 |  | 0
1.33 | Gasilne šprinklerska šoba z naslednjimi tehničnimi lastnostmi: - usmerjenost: viseča (ang. "pendent"); - vrsta pršilnega vzorca: paraboličen ("spray"); - K-faktor: K80 (SI); - odzivni čas: kratek (RTI < 50); - nazivna temperatura odprtja: 68°C (rdeča kapsula); - imenska velikost priključka: DN15; - material šobe: medenina; - obvezni certifikati: VdS; - z zaščito proti omočenju in - z zaščito proti mehanskim poškodbam. Ustreza Minimax MX3-SP 1/2"-K80-68°-Ms. Oznaka: S2c | Fire sprinkler nozzle with the following technical characteristics: - orientation: pendent; - type of spray pattern: parabolic ("spray"); - K-factor: K80 (SI); - response time: short (RTI < 50); - nominal opening temperature: 68°C (red capsule); - nominal connection size: DN15; - nozzle material: brass; - mandatory certificates; - with anti-wetting protection and - with protection against mechanical damage. Fits Minimax MX3-SP 1/2"-K80-68°-Ms. Code: S2c | kos | 150 |  | 0
1.34 | Gasilne šprinklerska šoba z naslednjimi tehničnimi lastnostmi: - usmerjenost: viseča (ang. "pendent"); - vrsta pršilnega vzorca: paraboličen ("spray"); - K-faktor: K80 (SI); - odzivni čas: kratek (RTI < 50); - nazivna temperatura odprtja: 68°C (rdeča kapsula); - imenska velikost priključka: DN15; - material šobe: medenina; - obvezni certifikati: VdS; - z rozeto za namestitev v spuščen strop. Ustreza Minimax MX3-SP 1/2"-K80-68°-Ms + Escutcheon type D. Oznaka: S2e | Fire sprinkler nozzle with the following technical characteristics: - orientation: pendent; - type of spray pattern: parabolic ("spray"); - K-factor: K80 (SI); - response time: short (RTI < 50); - nominal opening temperature: 68°C (red capsule); - nominal connection size: DN15; - nozzle material: brass; - mandatory certificates; - with a rosette for installation in dropped ceilings. Fits Minimax MX3-SP 1/2"-K80-68°-Ms + Escutcheon type D. Code: S2e | kos | 100 |  | 0
1.35 | Gasilna šprinklerska šoba z naslednjimi tehničnimi lastnostmi: - usmerjenost: stoječa (ang. "upright"); - vrsta pršilnega vzorca: ploščat (ang. "flat"); - K-faktor: K80 (SI); - odzivni čas: kratek (RTI < 50); - nazivna temperatura odprtja: 68°C (rdeča kapsula); - imenska velikost priključka: DN15; - material šobe: medenina; - obvezni certifikati: VdS. Ustreza Minimax MX3-FU 1/2“-K80-68°C-Ms. Oznaka: S3 | Fire sprinkler nozzle with the following technical characteristics: - orientation: upright; - type of spray pattern: flat; - K-factor: K80 (SI); - response time: short (RTI < 50); - nominal opening temperature: 68°C (red capsule); - nominal connection size: DN15; - nozzle material: brass; - mandatory certificates. Fits Minimax MX3-FU 1/2"-K80-68°C-Ms. Tag: S3 | kos | 350 |  | 0
1.36 | Gasilna šprinklerska šoba z naslednjimi tehničnimi lastnostmi: - usmerjenost: viseča (ang. "pendent"); - vrsta pršilnega vzorca: ploščat (ang. "flat"); - K-faktor: K80 (SI); - odzivni čas: kratek (RTI < 50); - nazivna temperatura odprtja: 68°C (rdeča kapsula); - imenska velikost priključka: DN15; - material šobe: medenina; - obvezni certifikati: VdS. Ustreza Minimax MX3-FP 1/2“-K80-68°C-Ms. Oznaka: S4 | Fire sprinkler nozzle with the following technical characteristics: - orientation: pendent; - type of spray pattern: flat; - K-factor: K80 (SI); - response time: short (RTI < 50); - nominal opening temperature: 68°C (red capsule); - nominal connection size: DN15; - nozzle material: brass; - mandatory certificates. Fits Minimax MX3-FP 1/2"-K80-68°C-Ms. Tag: S4 | kos | 400 |  | 0
1.37 | Gasilna šprinklerska šoba z naslednjimi tehničnimi lastnostmi: - usmerjenost: viseča (ang. "pendent"); - vrsta pršilnega vzorca: ploščat (ang. "flat"); - K-faktor: K80 (SI); - odzivni čas: kratek (RTI < 50); - nazivna temperatura odprtja: 68°C (rdeča kapsula); - imenska velikost priključka: DN15; - material šobe: medenina; - obvezni certifikati: VdS; - z zaščito proti omočenju in - z zaščito proti mehanskim poškodbam. Ustreza Minimax MX3-FP 1/2“-K80-68°C-Ms. Oznaka: S4c | Fire sprinkler nozzle with the following technical characteristics: - orientation: pendent; - type of spray pattern: flat; - K-factor: K80 (SI); - response time: short (RTI < 50); - nominal opening temperature: 68°C (red capsule); - nominal connection size: DN15; - nozzle material: brass; - mandatory certificates; - with anti-wetting protection and - with protection against mechanical damage. Fits Minimax MX3-FP 1/2"-K80-68°C-Ms. Tag: S4c | kos | 50 |  | 0
1.38 | Gasilna šprinklerska šoba z naslednjimi tehničnimi lastnostmi: - usmerjenost: skrita viseča (ang. "concealed pendent"); - vrsta pršilnega vzorca: paraboličen (ang. "spray"); - K-faktor: K80 (SI); - odzivni čas: kratek (RTI < 50); - nazivna temperatura odprtja: 68°C (rdeča kapsula); - imenska velikost priključka: DN15; - material šobe: medenina; - obvezni certifikati: VdS. Ustreza Minimax MX3-CCP 1/2“x16-K80-68°C weiß. Oznaka: S5 | Fire sprinkler nozzle with the following technical characteristics: - orientation: concealed pendent; - type of spray pattern: parabolic; - K-factor: K80 (SI); - response time: short (RTI < 50); - nominal opening temperature: 68°C (red capsule); - nominal connection size: DN15; - nozzle material: brass; - mandatory certificates. Fits Minimax MX3-CCP 1/2 "x16-K80-68°C weiß. Tag: S5 | kos | 100 |  | 0
1.39 | Gasilna šprinklerska šoba za vgradnjo v hladilnice z naslednjimi tehničnimi lastnostmi: - vrsta: vgreznjena suha viseča (ang. "reccesed dry pendent"); - vrsta pršilnega vzorca: paraboličen (ang. "spray"); - K-faktor: K80 (SI); - odzivni čas: običajen (RTI > 80); - nazivna temperatura odprtja: 68°C (rdeča kapsula); - imenska velikost priključka: DN25; - material šobe: medenina; - obvezni certifikati: VdS; Ustreza Viking VK1590. Oznaka: S6 | Fire sprinkler nozzle for installation in cold stores with the following technical characteristics: - type: reccesed dry drift pendent"); - type of spray pattern: parabolic; - K-factor: K80 (SI); - response time: normal (RTI > 80); - nominal opening temperature: 68°C (red capsule); - nominal connection size: DN25; - nozzle material: brass; - mandatory certificates; Corresponds to Viking VK1590. Tag: S6 | kos | 3 |  | 0
1.40 | Gasilna šprinklerska šoba z naslednjimi tehničnimi lastnostmi: - vrsta: stoječa (ang. "upright"); - vrsta pršilnega vzorca: paraboličen (ang. "spray"); - K-faktor: K80 (SI); - odzivni čas: običajen (RTI > 80); - nazivna temperatura odprtja: 68°C (rdeča kapsula); - imenska velikost priključka: DN15; - material šobe: medenina; - obvezni certifikati: VdS; Ustreza Minimax MX5-SU 3/8“-K57-68°C-Ms. Oznaka: S7 | Fire sprinkler nozzle with the following technical characteristics: - type: upright; - type of spray pattern: parabolic; - K-factor: K80 (SI); - response time: normal (RTI > 80); - nominal opening temperature: 68°C (red capsule); - nominal connection size: DN15; - nozzle material: brass; - mandatory certificates; Fits Minimax MX5-SU 3/8"-K57-68°C-Ms. Tag: S7 | kos | 1700 |  | 0
1.41 | Prilagodljiva cev iz nerjavnega jekla za priklop visečih šprinklerskih šob, z reducirnim kosom iz DN25/DN15, z VdS certifikatom, vključno s podporno nosilno konstrukcijo šob (pred naročilom preveriti vrsto spuščenega stropa). Ustreza Victaulic Vicflex. | Flexible stainless steel hose for connection of suspended sprinkler nozzles, with DN25/DN15 reducing piece, VdS certified, including nozzle support structure (check type of dropped ceiling before ordering). It corresponds to the Victaulic Vicflex. | kos | 1000 |  | 0
1.42 | Pločevinasta kaseta za shrambo rezervnih gasilnih šprinklerskih šob, vključno z rezervnimi ključi (za vsak tip šobe) ter konzolnim nosilcem za montažo na steno. | Sheet metal cassette for storage of spare fire sprinkler nozzles, including spare keys (for each nozzle type) and bracket for wall mounting. | kpl | 7 |  | 0
1.43 | Rezervni šprinklerji, katerih število je določeno glede na najmanjše dovoljeno število na zalogi za sisteme z običajno požarno ogroženestjo po VdS (ang. "Ordinary Hazard - OH").; | Spare sprinklers, the number of which is determined according to the minimum number allowed in the stock for VdS Ordinary Hazard (OH) systems.;
| S1 | S1 | kos | 24 |  | 0
| S2 | S2 | kos | 24 |  | 0
| S3 | S3 | kos | 24 |  | 0
| S4 | S4 | kos | 24 |  | 0
| S5 | S5 | kos | 24 |  | 0
| S6 | S6 | kos | 1 |  | 0
| S7 | S7 | kos | 24 |  | 0
1.44 | Brezšivna jeklena cev iz ogljikovega jekla (P235TR2) skladna z EN 10216-1:2014. Postavka vključuje, izdelavo žlebov, VdS certificirane spojke za ožlebljene cevi (ustrezajo Victaulic 009N, 108, 109 spojke), obešanje cevovodov s predfabriciranimi predizoliranimi obešali, kompletno s profili za obešanje (ustrezajo proizvodi Hilti ali enakovredno), čiščenje jeklenih cevi rje, dvakratni premaz celotnega cevnega omrežja s temeljnim temperaturno odpornim antikorozijskim premazom in površinski premaz z barvo po izbiri arhitekta (če ni določeno, se uporabi odtenek RAL 3000). Cevi, žlebovi za spajanje, spojke in obešalni elementi morajo biti skladni s standardom VdS CEA 4001:2021. *Opomba: lahko se uporabi tudi navojno spajanje. | Brezšivna jeklena cev iz ogljikovega jekla (P235TR2) skladna z EN 10216-1:2014. Postavka vključuje, izdelavo žlebov, VdS certificirane spojke za ožlebljene cevi (ustrezajo Victaulic 009N, 108, 109 spojke), obešanje cevovodov s predfabriciranimi predizoliranimi obešali, kompletno s profili za obešanje (ustrezajo proizvodi Hilti ali enakovredno), čiščenje jeklenih cevi rje, dvakratni premaz celotnega cevnega omrežja s temeljnim temperaturno odpornim antikorozijskim premazom in površinski premaz z barvo po izbiri arhitekta (če ni določeno, se uporabi odtenek RAL 3000). Cevi, žlebovi za spajanje, spojke in obešalni elementi morajo biti skladni s standardom VdS CEA 4001:2021. *Note: threaded joints can also be used.
| DN15 → Ø21,3 mm × 2,6 mm | DN15 → Ø21.3 mm × 2.6 mm | m | 210 |  | 0
| DN20 → Ø26,9 mm × 2,6 mm | DN20 → Ø26.9 mm × 2.6 mm | m | 24 |  | 0
| DN25 → Ø33,7 mm × 2,6 mm | DN25 → Ø33.7 mm × 2.6 mm | m | 4920 |  | 0
| DN32 → Ø42,4 mm × 2,6 mm | DN32 → Ø42.4 mm × 2.6 mm | m | 2760 |  | 0
| DN40 → Ø48,3 mm × 2,6 mm | DN40 → Ø48.3 mm × 2.6 mm | m | 840 |  | 0
| DN50 → Ø60,3 mm × 2,9 mm | DN50 → Ø60.3 mm × 2.9 mm | m | 1440 |  | 0
| DN65 → Ø76,1 mm × 2,9 mm | DN65 → Ø76.1 mm × 2.9 mm | m | 600 |  | 0
| DN80 → Ø88,9 mm × 3,2 mm | DN80 → Ø88.9 mm × 3.2 mm | m | 4800 |  | 0
| DN100 → Ø114,3 mm × 3,6 mm | DN100 → Ø114.3 mm × 3.6 mm | m | 42 |  | 0
| DN125 → Ø139,7 mm × 4,0 mm | DN125 → Ø139.7 mm × 4.0 mm | m | 60 |  | 0
| DN150 → Ø168,3 mm × 4,5 mm | DN150 → Ø168.3 mm × 4.5 mm | m | 12 |  | 0
| Cena metra cevi mora zajemati tudi cevne oblikovne kose za uporabo na ožlebljenih ceveh iz zgornje postavke. Oblikovni kosi morajo imeti VdS certifikat oziroma izpolnjevati zahteve smernice VdS CEA 4001:2021. Ustreza nabor oblikovnih kosov Victaulic FireLock. *Opombi: - v primeru varjenja, se morajo uporabiti oblikovni kosi v skladu z EN 10253-1:2000; -v primeru navojnega spajanja pa se morajo uporabiti oblikovni kosi skladni z EN 10241:2001. | The price per metre of pipe shall also include pipe formers for use on the grooved pipes referred to in the above item. The formers shall be VdS certified or meet the requirements of the VdS guideline CEA 4001:2021. Corresponds to the Victaulic FireLock set of design pieces. *Reminder: - in the case of welding, the shaped pieces shall be used in accordance with eN 10253-1:2000; -in the case of threaded joints, shaped pieces must be used compliant with EN 10241:2001.
| Prirobnica DN 32 | Flange DN 32 | kos | 4 |  | 0
| Prirobnica DN 65 | Flange DN 65 | kos | 5 |  | 0
| Prirobnica DN 100 | Flange DN 100 | kos | 3 |  | 0
| Prirobnica DN 125 | Flange DN 125 | kos | 3 |  | 0
| Reducirni kos (C) DN 25 - DN 15 | Reducing piece (C) DN 25 - DN 15 | kos | 1150 |  | 0
| Reducirni kos (C) DN 32 - DN 25 | Reducing piece (C) DN 32 - DN 25 | kos | 1400 |  | 0
| Reducirni kos (C) DN 40 - DN 32 | Reducing piece (C) DN 40 - DN 32 | kos | 450 |  | 0
| Reducirni kos (C) DN 50 - DN 25 | Reducing piece (C) DN 50 - DN 25 | kos | 30 |  | 0
| Reducirni kos (C) DN 50 - DN 32 | Reducing piece (C) DN 50 - DN 32 | kos | 230 |  | 0
| Reducirni kos (C) DN 50 - DN 40 | Reducing piece (C) DN 50 - DN 40 | kos | 180 |  | 0
| Reducirni kos (C) DN 65 - DN 25 | Reducing piece (C) DN 65 - DN 25 | kos | 3 |  | 0
| Reducirni kos (C) DN 65 - DN 32 | Reducing piece (C) DN 65 - DN 32 | kos | 7 |  | 0
| Reducirni kos (C) DN 65 - DN 40 | Reducing piece (C) DN 65 - DN 40 | kos | 15 |  | 0
| Reducirni kos (C) DN 65 - DN 50 | Reducing piece (C) DN 65 - DN 50 | kos | 30 |  | 0
| Reducirni kos (C) DN 80 - DN 32 | Reducing piece (C) DN 80 - DN 32 | kos | 5 |  | 0
| Reducirni kos (C) DN 80 - DN 40 | Reducing piece (C) DN 80 - DN 40 | kos | 13 |  | 0
| Reducirni kos (C) DN 80 - DN 50 | Reducing piece (C) DN 80 - DN 50 | kos | 25 |  | 0
| Reducirni kos (C) DN 80 - DN 65 | Reducing piece (C) DN 80 - DN 65 | kos | 13 |  | 0
| Koleno DN 25 | Elbow DN 25 | kos | 1300 |  | 0
| Koleno DN 32 | Elbow DN 32 | kos | 500 |  | 0
| Koleno DN 40 | Elbow DN 40 | kos | 250 |  | 0
| Koleno DN 50 | Elbow DN 50 | kos | 170 |  | 0
| Koleno DN 65 | Elbow DN 65 | kos | 70 |  | 0
| Koleno DN 80 | Elbow DN 80 | kos | 360 |  | 0
| Koleno DN 100 | Elbow DN 100 | kos | 6 |  | 0
| Koleno DN 125 | Elbow DN 125 | kos | 15 |  | 0
| T- kos DN 25 - DN 25 - DN 25 | T-piece DN 25 - DN 25 - DN 25 | kos | 400 |  | 0
| T- kos DN 32 - DN 32 - DN 32 | T-piece DN 32 - DN 32 - DN 32 | kos | 40 |  | 0
| T- kos DN 40 - DN 40 - DN 40 | T-piece DN 40 - DN 40 - DN 40 | kos | 25 |  | 0
| T- kos DN 50 - DN 50 - DN 50 | T-piece DN 50 - DN 50 - DN 50 | kos | 120 |  | 0
| T- kos DN 65 - DN 65 - DN 65 | T-piece DN 65 - DN 65 - DN 65 | kos | 20 |  | 0
| T- kos DN 80 - DN 80 - DN 80 | T-piece DN 80 - DN 80 - DN 80 | kos | 150 |  | 0
| T- kos DN 125 - DN 125 - DN 125 | T-piece DN 125 - DN 125 - DN 125 | kos | 5 |  | 0
| T- kos (reducirni) DN 32 - DN 32 - DN 15 | T-piece (reducing) DN 32 - DN 32 - DN 15 | kos | 1000 |  | 0
| T- kos (reducirni) DN 32 - DN 32 - DN 25 | T-piece (reducing) DN 32 - DN 32 - DN 25 | kos | 290 |  | 0
| T- kos (reducirni) DN 40 - DN 40 - DN 15 | T-piece (reducing) DN 40 - DN 40 - DN 15 | kos | 320 |  | 0
| T- kos (reducirni) DN 40 - DN 40 - DN 25 | T-piece (reducing) DN 40 - DN 40 - DN 25 | kos | 135 |  | 0
| T- kos (reducirni) DN 40 - DN 40 - DN 32 | T-piece (reducing) DN 40 - DN 40 - DN 32 | kos | 10 |  | 0
| T- kos (reducirni) DN 50 - DN 50 - DN 15 | T-piece (reducing) DN 50 - DN 50 - DN 15 | kos | 250 |  | 0
| T- kos (reducirni) DN 50 - DN 50 - DN 25 | T-piece (reducing) DN 50 - DN 50 - DN 25 | kos | 220 |  | 0
| T- kos (reducirni) DN 50 - DN 50 - DN 32 | T-piece (reducing) DN 50 - DN 50 - DN 32 | kos | 150 |  | 0
| T- kos (reducirni) DN 50 - DN 50 - DN 40 | T-piece (reducing) DN 50 - DN 50 - DN 40 | kos | 50 |  | 0
| T- kos (reducirni) DN 65 - DN 65 - DN 15 | T-piece (reducing) DN 65 - DN 65 - DN 15 | kos | 20 |  | 0
| T- kos (reducirni) DN 65 - DN 65 - DN 25 | T-piece (reducing) DN 65 - DN 65 - DN 25 | kos | 180 |  | 0
| T- kos (reducirni) DN 65 - DN 65 - DN 32 | T-piece (reducing) DN 65 - DN 65 - DN 32 | kos | 70 |  | 0
| T- kos (reducirni) DN 65 - DN 65 - DN 40 | T-piece (reducing) DN 65 - DN 65 - DN 40 | kos | 85 |  | 0
| T- kos (reducirni) DN 65 - DN 65 - DN 50 | T-piece (reducing) DN 65 - DN 65 - DN 50 | kos | 20 |  | 0
| T- kos (reducirni) DN 80 - DN 80 - DN 25 | T-piece (reducing) DN 80 - DN 80 - DN 25 | kos | 1100 |  | 0
| T- kos (reducirni) DN 80 - DN 80 - DN 32 | T-piece (reducing) DN 80 - DN 80 - DN 32 | kos | 860 |  | 0
| T- kos (reducirni) DN 80 - DN 80 - DN 40 | T-piece (reducing) DN 80 - DN 80 - DN 40 | kos | 300 |  | 0
| T- kos (reducirni) DN 80 - DN 80 - DN 50 | T-piece (reducing) DN 80 - DN 80 - DN 50 | kos | 370 |  | 0
| T- kos (reducirni) DN 80 - DN 80 - DN 65 | T-piece (reducing) DN 80 - DN 80 - DN 65 | kos | 150 |  | 0
| T- kos (reducirni) DN 125 - DN 125 - DN 80 | T-piece (reducing) DN 125 - DN 125 - DN 80 | kos | 10 |  | 0
| T- kos (reducirni) DN 125 - DN 125 - DN 100 | T-piece (reducing) DN 125 - DN 125 - DN 100 | kos | 3 |  | 0
| Cena metra cevi mora zajemati tudi ukrepe za preprečevanje širjenja hrupa iz in med hrupnimi območji, kot jih določa Elaborat zaščite pred hrupom v stabvah. Postavka zajema izdelavo 3D lir in Z odsekov ter izdelavo sklopov za kompenzacijo zvočnih vibracij v obliki treh fleksibilnih spojk (štejejo se kot 1 komplet) za ožlebljene cevi z VdS certifikatom in tlačno stopnjo vsaj PN16. Ustreza Victaulic Style 75. | The price per metre of the pipe must also include measures to prevent the propagation of noise from and between noise sensitive areas, as defined in the Stables Noise Protection Laboratory. The item covers the production of 3D lyres and Z sections and the production of acoustic vibration compensation kits in the form of 3 flexible couplings (counted as 1 set) for VdS-certified grooved pipes with a pressure rating of at least PN16. Corresponds to Victaulic Style 75.
| 3D lire in Z odseki | 3D lyre and Z sections | kpl | 30 |  | 0
| Kompenzacijski sklopi | Compensation kits | kpl | 200 |  | 0
1.45 | Pocinkana brezšivna jeklena cev iz ogljikovega jekla (P235TR2) skladna z EN 10216-1:2014. Postavka vključuje, izdelavo žlebov, VdS certificirane toge spojke za ožlebljene cevi (ustrezajo ustrezajo Victaulic 009N, 108, 109 spojke), obešanje cevovodov s predfabriciranimi predizoliranimi obešali, kompletno s profili za obešanje (ustrezajo proizvodi Hilti).Cevi, žlebovi za spajanje, spojke in obešalni elementi morajo biti skladni s standardom VdS CEA 4001:2021. Cevi morajo biti pocinkane skladno z EN 10240:1997. | Galvanised seamless carbon steel pipe (P235TR2) complying with EN 10216-1:2014. The item includes, the manufacture of gutters, VdS certified rigid couplings for grooved pipes (corresponding Victaulic 009N, 108, 109 couplings), hanging of pipelines with prefabricated preinsulated hangers, complete with hanging profiles (corresponding Hilti products).Pipes, jointing gutters, couplings and hanging elements shall be in accordance with VdS CEA 4001:2021. Pipes shall be galvanised in accordance with EN 10240:1997.
| DN15 → Ø21,3 mm × 2,6 mm | DN15 → Ø21.3 mm × 2.6 mm | m | 36 |  | 0
| DN20 → Ø26,9 mm × 2,6 mm | DN20 → Ø26.9 mm × 2.6 mm | m | 36 |  | 0
| DN25 → Ø33,7 mm × 2,6 mm | DN25 → Ø33.7 mm × 2.6 mm | m | 1500 |  | 0
| DN32 → Ø42,4 mm × 2,6 mm | DN32 → Ø42.4 mm × 2.6 mm | m | 1080 |  | 0
| DN40 → Ø48,3 mm × 2,6 mm | DN40 → Ø48.3 mm × 2.6 mm | m | 1320 |  | 0
| DN50 → Ø60,3 mm × 2,9 mm | DN50 → Ø60.3 mm × 2.9 mm | m | 2460 |  | 0
| DN65 → Ø76,1 mm × 2,9 mm | DN65 → Ø76.1 mm × 2.9 mm | m | 60 |  | 0
| DN80 → Ø88,9 mm × 3,2 mm | DN80 → Ø88.9 mm × 3.2 mm | m | 1140 |  | 0
| Cena metra cevi mora zajemati tudi pocinkane cevne oblikovne kose za uporabo na ožlebljenih ceveh. Oblikovni kosi morajo imeti in VdS certifikat oziroma izpolnjevati zahteve smernice VdS CEA 4001:2021. Tlačna stopnja vseh oblikovnih kosov mora biti vsaj PN16. Ustreza nabor oblikovnih kosov Victaulic FireLock. *Opombe: - namesto reducirnega T-kosa se lahko uporabi navrtalne oklepe (ang. Mechanical Tee) - v primeru varjenja, se morajo uporabiti oblikovni kosi v skladu z EN 10253-1:2000; -v primeru navojnega spajanja pa se morajo uporabiti oblikovni kosi skladni z EN 10241:2001. | The price per metre of pipe shall also include galvanised pipe fittings for use on grooved pipes. The fittings shall be VdS certified or meet the requirements of VdS guideline CEA 4001:2021. The pressure rating of all fittings shall be at least PN16. Corresponds to the Victaulic FireLock set of design pieces. *Notes: - drill collars can be used instead of the reducing T-piece (Mechanical Tee) - in the case of welding, the shaped pieces shall be used in accordance with eN 10253-1:2000; -in the case of threaded joints, shaped pieces must be used compliant with EN 10241:2001.
| Reducirni kos (C) DN 25 - DN 15 | Reducing piece (C) DN 25 - DN 15 | kos | 1200 |  | 0
| Reducirni kos (C) DN 32 - DN 25 | Reducing piece (C) DN 32 - DN 25 | kos | 270 |  | 0
| Reducirni kos (C) DN 40 - DN 25 | Reducing piece (C) DN 40 - DN 25 | kos | 50 |  | 0
| Reducirni kos (C) DN 40 - DN 32 | Reducing piece (C) DN 40 - DN 32 | kos | 250 |  | 0
| Reducirni kos (C) DN 50 - DN 25 | Reducing piece (C) DN 50 - DN 25 | kos | 5 |  | 0
| Reducirni kos (C) DN 50 - DN 32 | Reducing piece (C) DN 50 - DN 32 | kos | 35 |  | 0
| Reducirni kos (C) DN 50 - DN 40 | Reducing piece (C) DN 50 - DN 40 | kos | 280 |  | 0
| Reducirni kos (C) DN 65 - DN 25 | Reducing piece (C) DN 65 - DN 25 | kos | 3 |  | 0
| Reducirni kos (C) DN 65 - DN 32 | Reducing piece (C) DN 65 - DN 32 | kos | 5 |  | 0
| Reducirni kos (C) DN 65 - DN 40 | Reducing piece (C) DN 65 - DN 40 | kos | 5 |  | 0
| Reducirni kos (C) DN 65 - DN 50 | Reducing piece (C) DN 65 - DN 50 | kos | 10 |  | 0
| Reducirni kos (C) DN 80 - DN 32 | Reducing piece (C) DN 80 - DN 32 | kos | 5 |  | 0
| Reducirni kos (C) DN 80 - DN 40 | Reducing piece (C) DN 80 - DN 40 | kos | 5 |  | 0
| Reducirni kos (C) DN 80 - DN 50 | Reducing piece (C) DN 80 - DN 50 | kos | 5 |  | 0
| Reducirni kos (C) DN 80 - DN 65 | Reducing piece (C) DN 80 - DN 65 | kos | 5 |  | 0
| Koleno (reducirno) DN 25 - DN 15 | Elbow (reducing) DN 25 - DN 15 | kos | 80 |  | 0
| Koleno DN 25 | Elbow DN 25 | kos | 271 |  | 0
| Koleno DN 32 | Elbow DN 32 | kos | 30 |  | 0
| Koleno DN 40 | Elbow DN 40 | kos | 40 |  | 0
| Kolenoe DN 50 | Elbow DN 50 | kos | 240 |  | 0
| Koleno DN 65 | Elbow DN 65 | kos | 10 |  | 0
| Koleno DN 80 | Elbow DN 80 | kos | 70 |  | 0
| T- kos DN 25 - DN 25 - DN 25 | T-piece DN 25 - DN 25 - DN 25 | kos | 10 |  | 0
| T- kos DN 32 - DN 32 - DN 32 | T-piece DN 32 - DN 32 - DN 32 | kos | 10 |  | 0
| T- kos DN 40 - DN 40 - DN 40 | T-piece DN 40 - DN 40 - DN 40 | kos | 5 |  | 0
| T- kos DN 50 - DN 50 - DN 50 | T-piece DN 50 - DN 50 - DN 50 | kos | 35 |  | 0
| T- kos DN 65 - DN 65 - DN 65 | T-piece DN 65 - DN 65 - DN 65 | kos | 5 |  | 0
| T- kos DN 80 - DN 80 - DN 80 | T-piece DN 80 - DN 80 - DN 80 | kos | 15 |  | 0
| T- kos (reducirni) DN 32 - DN 32 - DN 15 | T-piece (reducing) DN 32 - DN 32 - DN 15 | kos | 70 |  | 0
| T- kos (reducirni) DN 32 - DN 32 - DN 25 | T-piece (reducing) DN 32 - DN 32 - DN 25 | kos | 220 |  | 0
| T- kos (reducirni) DN 40 - DN 40 - DN 15 | T-piece (reducing) DN 40 - DN 40 - DN 15 | kos | 40 |  | 0
| T- kos (reducirni) DN 40 - DN 40 - DN 25 | T-piece (reducing) DN 40 - DN 40 - DN 25 | kos | 330 |  | 0
| T- kos (reducirni) DN 40 - DN 40 - DN 32 | T-piece (reducing) DN 40 - DN 40 - DN 32 | kos | 5 |  | 0
| T- kos (reducirni) DN 50 - DN 50 - DN 15 | T-piece (reducing) DN 50 - DN 50 - DN 15 | kos | 50 |  | 0
| T- kos (reducirni) DN 50 - DN 50 - DN 25 | T-piece (reducing) DN 50 - DN 50 - DN 25 | kos | 430 |  | 0
| T- kos (reducirni) DN 50 - DN 50 - DN 32 | T-piece (reducing) DN 50 - DN 50 - DN 32 | kos | 5 |  | 0
| T- kos (reducirni) DN 50 - DN 50 - DN 40 | T-piece (reducing) DN 50 - DN 50 - DN 40 | kos | 5 |  | 0
| T- kos (reducirni) DN 65 - DN 65 - DN 15 | T-piece (reducing) DN 65 - DN 65 - DN 15 | kos | 10 |  | 0
| T- kos (reducirni) DN 65 - DN 65 - DN 25 | T-piece (reducing) DN 65 - DN 65 - DN 25 | kos | 5 |  | 0
| T- kos (reducirni) DN 65 - DN 65 - DN 32 | T-piece (reducing) DN 65 - DN 65 - DN 32 | kos | 5 |  | 0
| T- kos (reducirni) DN 65 - DN 65 - DN 40 | T-piece (reducing) DN 65 - DN 65 - DN 40 | kos | 5 |  | 0
| T- kos (reducirni) DN 65 - DN 65 - DN 50 | T-piece (reducing) DN 65 - DN 65 - DN 50 | kos | 5 |  | 0
| T- kos (reducirni) DN 80 - DN 80 - DN 25 | T-piece (reducing) DN 80 - DN 80 - DN 25 | kos | 20 |  | 0
| T- kos (reducirni) DN 80 - DN 80 - DN 32 | T-piece (reducing) DN 80 - DN 80 - DN 32 | kos | 15 |  | 0
| T- kos (reducirni) DN 80 - DN 80 - DN 40 | T-piece (reducing) DN 80 - DN 80 - DN 40 | kos | 10 |  | 0
| T- kos (reducirni) DN 80 - DN 80 - DN 50 | T-piece (reducing) DN 80 - DN 80 - DN 50 | kos | 150 |  | 0
| T- kos (reducirni) DN 80 - DN 80 - DN 65 | T-piece (reducing) DN 80 - DN 80 - DN 65 | kos | 5 |  | 0
1.46 | Cev iz nerjavnega jekla (1.4404/AISI 316L) skladna z EN 10217-7:2021. Postavka vključuje spajanje cevi s TIG varjenjem), obešanje cevovodov s predfabriciranimi predizoliranimi obešali, kompletno s profili za obešanje (ustrezajo proizvodi Hilti ali Sikla). Cevi in obešalni elementi morajo biti skladni s standardom VdS CEA 4001:2021. *Opomba: Cevi zunaj bazena se lahko spaja tudi s VdS certificiranimi togimi spojkami za ožlebljene cevi (ustreza Victaulic). | Stainless steel pipe (1.4404/AISI 316L) complying with EN 10217-7:2021. The item includes TIG welding of the pipes), hanging of the pipelines with prefabricated pre-insulated hangers, complete with hanging profiles (corresponding to Hilti or Sikla products). The pipes and the hanging elements shall comply with VdS CEA 4001:2021. *Note: Pipes outside the pool can also be joined with VdS certified rigid couplings for grooved pipes (Victaulic equivalent).
| DN15 → Ø21,3 mm × 2,6 mm | DN15 → Ø21.3 mm × 2.6 mm | m | 24 |  | 0
| DN20 → Ø26,9 mm × 2,6 mm | DN20 → Ø26.9 mm × 2.6 mm | m | 24 |  | 0
| DN25 → Ø33,7 mm × 2,6 mm | DN25 → Ø33.7 mm × 2.6 mm | m | 18 |  | 0
| DN32 → Ø42,4 mm × 2,6 mm | DN32 → Ø42.4 mm × 2.6 mm | m | 18 |  | 0
| DN40 → Ø48,3 mm × 2,6 mm | DN40 → Ø48.3 mm × 2.6 mm | m | 18 |  | 0
| DN50 → Ø60,3 mm × 3,0 mm | DN50 → Ø60.3 mm × 3.0 mm | m | 18 |  | 0
| DN65 → Ø76,1 mm × 3,0 mm | DN65 → Ø76.1 mm × 3.0 mm | m | 18 |  | 0
| DN80 → Ø88,9 mm × 3,0 mm | DN80 → Ø88.9 mm × 3.0 mm | m | 18 |  | 0
| DN100 → Ø114,3 mm × 3,6 mm | DN100 → Ø114.3 mm × 3.6 mm | m | 18 |  | 0
| DN125 → Ø139,7 mm × 4,0 mm | DN125 → Ø139.7 mm × 4.0 mm | m | 24 |  | 0
| DN150 → Ø168,3 mm × 4,0 mm | DN150 → Ø168.3 mm × 4.0 mm | m | 18 |  | 0
| Cena metra cevi mora zajemati tudi cevne oblikovne kose za varilno spajanje s cevmi Oblikovni kosi morajo biti skladni z EN 10253-4:2008. | The price per metre of the pipe shall also include the pipe formers for welding joints with the pipes The formers shall comply with EN 10253-4:2008.
| Reducirni kos (C) DN20 - DN15 | Reducing piece (C) DN20 - DN15 | kos | 2 |  | 0
| Koleno (3D) DN15 | Elbow (3D) DN15 | kos | 30 |  | 0
| Koleno (3D) DN20 | Elbow (3D) DN20 | kos | 10 |  | 0
| Koleno (3D) DN40 | Elbow (3D) DN40 | kos | 3 |  | 0
| Koleno (3D) DN65 | Elbow (3D) DN65 | kos | 2 |  | 0
| Koleno (3D) DN100 | Elbow (3D) DN100 | kos | 3 |  | 0
| Koleno (3D) DN125 | Elbow (3D) DN125 | kos | 4 |  | 0
| Koleno (3D) DN150 | Elbow (3D) DN150 | kos | 3 |  | 0
| T-kos DN15 - DN15 - DN15 | T-piece DN15 - DN15 - DN15 | kos | 9 |  | 0
1.47 | Polietilenska cev visoke gostote (PEHD) primerna za namestitev v zemljo, tlačne stopnje vsaj PN16, iz materiala PE100, skladna s standardom EN 12201-2:2024 in z DVGW certifikatom. | High density polyethylene hose (PEHD) suitable for underground installation, pressure rating at least PN16, made of PE100 material, complying with EN 12201-2:2024 and DVGW certified.
| Ø125 mm × 11,4 mm | Ø125 mm × 11,4 mm | m | 12 |  | 0
| Cena metra cevi mora zajemati tudi cevne oblikovne kose za spajanje s spojkami skladni s cevmi iz postavke 1.49. Oblikovni kosi morajo biti skladni z EN 12201-3:2024 ali imeti FM certifikat. | The price per metre of the pipe shall also include pipe fittings for jointing with couplings compatible with the pipes referred to in item 1.49. The fittings shall comply with EN 12201-3:2024 or be FM-certified.
| Prirobnica → Ø125 (združljiva z jekleno DN100) | Flange → Ø125 (compatible with steel DN100) | kos | 2 |  | 0
| Koleno → Ø125 mm × 11,4 mm | Elbow → Ø125 mm × 11.4 mm | kos | 2 |  | 0
1.48 | Troslojni dimniški sistem skladen s standardom EN 1856-1:2009. Stena dimnika naj bo sestavljena iz notranje cevi iz nerjavne pločevine (1.4404 / AISI 316L) debeline 0,5 mm, toplotne izolacije iz mineralne volne debeline 50 mm in zunanje cevi iz nerjavne pločevine (1.4301 / AISI 304) debeline 0,5 mm. Postavka vključuje vodotesno izvedbo preboja na strehi. Ustreza Schiedel ICS. | Three-layer chimney system complying with EN 1856-1:2009. The chimney wall shall consist of a 0,5 mm thick stainless steel (1.4404 / AISI 316L) inner pipe, 50 mm thick mineral wool thermal insulation and a 0,5 mm thick stainless steel (1.4301 / AISI 304) outer pipe. The item shall include the watertight construction of the roof penetrations. Meets Schiedel ICS.
| Cev → notranji premer Ø150 mmm | Hose → internal diameter Ø150 mmm | m | 55 |  | 0
| Koleno → notranji premer Ø150 mmm | Elbow → internal diameter Ø150 mmm | kos | 6 |  | 0
| T-kos → notranji premer Ø150 mmm | T-piece → internal diameter Ø150 mmm | kos | 1 |  | 0
| Prehodni kos → na notranji premer Ø150 mmm | Transition piece → to internal diameter Ø150 mmm | kos | 2 |  | 0
| Čistilni element (BX 05.02) | Cleaning element (BX 05.02) | kos | 1 |  | 0
| Kondenzna posoda (BX 05.01) | Condensate container (BX 05.01) | kos | 1 |  | 0
| Dušilec zvoka (BX 05.03) | Silencer (BX 05.03) | kos | 1 |  | 0
| Pokrov proti padavinam (BX 05.04) | Rain cover (BX 05.04) | kos | 1 |  | 0
1.49 | Krmilna plošča za gasilni sistem z ustreznim številom vhodno / izhodnih signalov, komplet z akumulatorji ustrezne kapacitete in s VdS certfikatom. Ustreza Minimax FMZ 5000. Oznaka: UC 00.00 | Control panel for the fire extinguishing system with the appropriate number of input/output signals, complete with batteries of the appropriate capacity and VdS certficate. It corresponds to the Minimax FMZ 5000. Code: UC 00.00 | kpl | 1 |  | 0
1.50 | Ultrazvočni merilnik nivoja kapljevine z merilno razdaljo vsaj 4 metre. Naprava mora imeti vsaj enega izmed VdS, FM ali UL certifikatov. Zmožna mora biti delovanja pri temperaturah od -20°C do 60°C in pri absolutnem tlaku od 1 bar do 2 bar. Zagotovljena mora biti stopnja zaščita proti vdoru vsaj IP65. Napajanje mora biti 24V z 4–20mA izhodom. Ustreza ENDRESS+HAUSER tip FDU91 + FMU90. ALI Magnetno zaznavalo nivoja kapljevine, zmožna delovanja pri temperaturah od -20°C do 60°C in pri absolutnem tlaku od 1 bar do 2 bar. Zagotovljena mora biti stopnja zaščita proti vdoru vsaj IP65. Napajanje mora biti 24V z 4–20mA izhodom. Ustreza AECO SLM-08 NO GM1. Oznaka: LE 01.004 + LS 01.004 | Ultrasonic liquid level gauge with a measuring distance of at least 4 m. The device shall have at least one of the VdS, FM or UL certifications. It shall be capable of operating at temperatures from -20°C to 60°C and at absolute pressures from 1 bar to 2 bar. It shall have an ingress protection rating of at least IP65. The power supply shall be 24V with a 4-20mA output. Corresponds to ENDRESS+HAUSER type FDU91 + FMU90. OR Magnetic liquid level sensor, capable of operating at temperatures from -20°C to 60°C and at absolute pressures from 1 bar to 2 bar. The ingress protection rating shall be at least IP65. The power supply shall be 24V with 4-20mA output. Corresponds to AECO SLM-08 NO GM1. Code: LE 01.004 + LS 01.004 | kos | 1 |  | 0
1.51 | Elektromagnetni merilnik prostorninskega pretoka imenskega premera DN 125 za merjenje pretokov vode od najmanj 100 l/min do vsaj 2000 l/min. Tlačna stopnja merilnika mora biti vsaj PN 16, obratovati pa mora biti sposoben pri temperaturah od -20°C do 50°C. Napajanje mora biti 24V z 4–20mA izhodom. Ustreza Endress+Hauser Promag W10/P10. ALI Zaslonka za merjenje prostorninskega pretoka, imenskega premera DN 100 za merjenje pretoka vode do vsaj 2000 l/min. Vključen je manometer za merjenje diferenčnega tlaka in neposrednim prikazom prostorninskega pretoka. Tlačna stopnja merilnika mora biti vsaj PN 16, obratovati pa mora biti sposoben pri temperaturah od 4°C do 50°C. Ustreza Mecon Turbo-Lux 3. Oznaka: FE 06.02 + FG 06.02 | An electromagnetic volumetric flowmeter of nominal diameter DN 125 for measuring water flows from a minimum of 100 l/min to a minimum of 2000 l/min. The pressure rating of the meter shall be at least PN 16 and it shall be capable of operation at temperatures from -20°C to 50°C. The power supply shall be 24V with 4-20mA output. Corresponds to Endress+Hauser Promag W10/P10. OR A volumetric flow measuring orifice, nominal diameter DN 100, for measuring water flow up to at least 2000 l/min. A manometer for differential pressure measurement and direct display of volumetric flow shall be included. The pressure rating of the gauge shall be at least PN 16 and it shall be capable of operation at temperatures between 4°C and 50°C. Meets Mecon Turbo-Lux 3. Code: FE 06.02 + FG 06.02 | kos | 1 |  | 0
1.52 | Manometer z Bourdonovo cevjo primeren za uporabo v sistemih z vodo. Manometer mora imeti območje merjenja od 0 bar do 16 bar z delitvijo največ 0,5 bar, prikazovalno okno ø100 mm, tlačno stopnjo vsaj PN16 in enega izmed VdS, FM ali UL certfikatov. Ustreza Minimax "pressure gauge 16 bar - 2 pointers AR/ER". Oznaka: PG 03.07; PG 03.13; PG 04.07; PG 04.13; PG 07.07; PG 07.13; PG 09.32; PG 09.34; PG 09.36; PG 09.38 | Bourdon tube manometer suitable for use in water systems. The manometer shall have a measuring range of 0 bar to 16 bar with a maximum separation of 0,5 bar, a display window of ø100 mm, a pressure rating of at least PN16 and one of the VdS, FM or UL certifications. Minimax "pressure gauge 16 bar - 2 pointers AR/ER" shall comply. Code: PG 03.07; PG 03.13; PG 04.07; PG 04.13; PG 07.07; PG 07.13; PG 09.32; PG 09.34; PG 09.36; PG 09.38 | kos | 10 |  | 0
1.53 | Alarmna hupa za namestitev na zunanjo fasado objekta. Hupa mora imeti VdS certifikat in biti odporna na vremenske pojave. Ustreza Pfannenber DS 10. Oznaka: HA 10.95, HA 10.96 | Alarm horn for installation on the external façade of a building. The horn must be VdS certified and weatherproof. Corresponds to Pfannenber DS 10. Code: HA 10.95, HA 10.96 | kos | 2 |  | 0
1.54 | Alarmna bliskavka za namestitev nad alarmni ventil. Bliskavka mora imeti VdS certifikat. Ustreza Pfannenber PY X-S-05. Oznaka: AL 11.08, AL 12.08, AL 13.08, AL 14.08, AL 21.11, 22.11, 23.11, 23.11, 25.11 | Alarm flash for installation above the alarm valve. The flash must be VdS certified. Corresponds to Pfannenber PY X-S-05. Mark: AL 11.08, AL 12.08, AL 13.08, AL 14.08, AL 21.11, 22.11, 23.11, 23.11, 25.11 | kos | 9 |  | 0
1.55 | Prostorsko temperaturno stikalo za namestitev v šprinklersko strojnico. Stikalo mora omogočati, da nadzornemu sistemu pošlje signal, v primeru, da temperatura pade pod 5°C. IP stopnja stikala na bo vsaj IP65. Ustreza Minimax ÜWA-FMZ4100. Oznaka: TS 10.11 | Room temperature switch to be installed in the sprinkler room. The switch shall be able to send a signal to the control system in case the temperature drops below 5°C. The IP rating of the switch shall be at least IP65. Meets Minimax ÜWA-FMZ4100. Code: TS 10.11 | kos | 1 |  | 0
1.56 | Javljalnik pretoka oziroma pretočno stikalo imenskega premera DN80 za zaznavanje pretoka vode. Javljalnik mora imeti VdS certifikat, nastavljivo zakasnitev do 30 sekund in električno napajanje 24V DC. Ustreza Potter Electric VSR-EU. Oznake: FS 21.23; FS 21.33; FS 22.23; FS 22.33; FS 22.43; FS 22.53; FS 23.23; FS 23.33; FS 23.43; FS 23.53; FS 24.23; FS 24.33; FS 24.43; FS 24.53; FS 25.23; FS 25.33; FS 25.43; FS 25.53 | Flow alarm or flow switch with nominal diameter DN80 for water flow detection. The flow alarm shall be VdS certified, have an adjustable delay of up to 30 seconds and a 24V DC power supply. Corresponds to Potter Electric VSR-EU. Tags: FS 21.23; FS 21.33; FS 22.23; FS 22.33; FS 22.43; FS 22.53; FS 23.23; FS 23.33; FS 23.43; FS 23.53; FS 24.23; FS 24.33; FS 24.43; FS 24.53; FS 25.23; FS 25.33; FS 25.43; FS 25.53 | kos | 18 |  | 0
1.57 | Serijski uporovni grelni kabel za zaščito pred zmrzovanjem vode v cevovodih. Minimalna dolžina kabla je 80 metrov. Kabel mora zagotavljati vsaj 10 W/m. Napajanje naj bo 230 V AC. Ustreza Danfoss DEVIpipeguard (B) + DEVIreg. Oznaka: IE 21.12 + TS 21.13; IE 21.14 + TS 21.15; IE 22.12 + TS 22.13; IE 22.14 + TS 22.15; IE 23.12 + TS 23.13; IE 23.14 + TS 23.15; IE 24.12 + TS 24.13; IE 24.14 + TS 24.15; IE 25.12 + TS 25.13; IE 25.14 + TS 25.15; | Serial resistive heating cable for protection against freezing of water in pipelines. The minimum cable length shall be 80 m. The cable shall provide at least 10 W/m. The power supply shall be 230 V AC. Fits Danfoss DEVIpipeguard (B) + DEVIreg. Code: IE 21.12 + TS 21.13; IE 21.14 + TS 21.15; IE 22.12 + TS 22.13; IE 22.14 + TS 22.15; IE 23.12 + TS 23.13; IE 23.14 + TS 23.15; IE 24.12 + TS 24.13; IE 24.14 + TS 24.15; IE 25.12 + TS 25.13; IE 25.14 + TS 25.15; | kpl | 10 |  | 0
1.58 | Toplotna izolacija skladna s standardom EN 14303:2015, debeline 50 mm, s toplotno prevodnostjo k ≤ 0,035 W/(m K), klasifikacijo A po EN 13501-1:2018, za temperature do 250 °C. Toplotna izolacija mora imeti na zunanji površini sloj za zaščito pred mehanskimi poškodbami in razpadanjem. Izolacija mora biti odporna proti kondenziranju. Ustreza Knauf Insulation Thermo-teK PS Cld ALS za zunanje premere cevi: | Thermal insulation complying with EN 14303:2015, 50 mm thick, with a thermal conductivity k ≤ 0,035 W/(m K), classification A according to EN 13501-1:2018, for temperatures up to 250 °C. The thermal insulation shall have a layer on the outer surface to protect against mechanical damage and decay. The insulation shall be resistant to condensation. Corresponds to Knauf Insulation Thermo-teK PS Cld ALS for external pipe diameters:
| Ø21,3 → 25 mm | Ø21.3 → 25 mm | m | 10 |  | 0
| Ø33,7 → 25 mm | Ø33.7 → 25 mm | m | 160 |  | 0
| Ø42,4→ 25 mm | Ø42.4→ 25 mm | m | 100 |  | 0
| Ø48,3→ 25 mm | Ø48,3→ 25 mm | m | 40 |  | 0
| Ø60,3→ 25 mm | Ø60,3→ 25 mm | m | 30 |  | 0
| Ø76,1→ 25 mm | Ø76.1→ 25 mm | m | 25 |  | 0
| Ø88,9→ 25 mm | Ø88,9→ 25 mm | m | 170 |  | 0
| Ø88,9→ 50 mm | Ø88,9→ 50 mm | m | 350 |  | 0
1.59 | Komplet za vodotesen prehod skozi betonsko steno proti bazenu gasilne vode. Komplet mora zagotavljati vodotenost pri tlaku do 10 metrov vodnega stolpca oziroma razred vodotesnosti W2-B po DIN 18535:2017. Cevna uvodnica in njena namestitev sta del arhitekturno-gradbenega popisa. Ustreza Hauff-technik HSD: | Kit for watertight passage through the concrete wall towards the fire water basin. The kit shall guarantee a watertightness at a pressure of up to 10 metres water column or watertightness class W2-B according to DIN 18535:2017. The pipe inlet and its installation shall be part of the architectural and constructional inventory. Corresponds to Hauff-technik HSD:
| 100 1x48 b40 (PC-W 04.23); | 100 1x48 b40 (PC-W 04.23); | kpl | 1 |  | 0
| 100 1x60 b40 (PC-W 01.01); | 100 1x60 b40 (PC-W 01.01); | kpl | 1 |  | 0
| 125 1x75 b40 (PC-W 02.02, PC-W 07.04); | 125 1x75 b40 (PC-W 02.02, PC-W 07.04); | kpl | 2 |  | 0
| 200 1x114 b40 (PC-W 02.03); | 200 1x114 b40 (PC-W 02.03); | kpl | 1 |  | 0
| 200 1x139 b40 (PC-W 06.03); | 200 1x139 b40 (PC-W 06.03); | kpl | 1 |  | 0
| 250 1x168 b40 (PC-W 03.04, PC-W 04.04). | 250 1x168 b40 (PC-W 03.04, PC-W 04.04). | kpl | 2 |  | 0
1.60 | Komplet za vodotesen prehod skozi betonsko steno proti zemljini za prehod cevi z zunanjim premerom 125 mm. Komplet mora zagotavljati vodotenost pri tlaku do 10 metrov vodnega stolpca oziroma razred vodotesnosti W2-B po DIN 18535:2017. Cevna uvodnica in njena namestitev sta del arhitekturno-gradbenega popisa. Ustreza Hauff-technik HSD200 1x114 b40. Oznaka: PC-W 10.96 | A watertight passage kit for the passage of pipes with an outer diameter of 125 mm through a concrete wall towards the soil. The kit shall guarantee a watertightness at a pressure of up to 10 metres water column or a watertightness class W2-B according to DIN 18535:2017. The pipe inlet and its installation shall be part of the architectural and constructional inventory. Corresponds to Hauff-technik HSD200 1x114 b40. Code: PC-W 10.96 | kpl | 1 |  | 0
1.61 | Vrtanje luknje v armirano betonsko ali opečnato konstrukcijo na višini do 3 metrov. | Drilling a hole in a reinforced concrete or brick structure at a height of up to 3 metres.
| do Ø62 × 300 mm | up to Ø62 × 300 mm | kos | 25 |  | 0
| do Ø62 × 800 mm | up to Ø62 × 800 mm | kos | 30 |  | 0
| do Ø119 × 300 mm | up to Ø119 × 300 mm | kos | 10 |  | 0
| do Ø119 × 800 mm | up to Ø119 × 800 mm | kos | 15 |  | 0
1.62 | Vrtanje luknje v armirano betonsko ali opečnato konstrukcijo na višini od 3 do 5 metrov. | Drilling a hole in a reinforced concrete or brick structure at a height of 3 to 5 metres.
| do Ø62 × 300 mm | up to Ø62 × 300 mm | kos | 15 |  | 0
| do Ø62 × 500 mm | up to Ø62 × 500 mm | kos | 20 |  | 0
| do Ø119 × 300 mm | up to Ø119 × 300 mm | kos | 10 |  | 0
| do Ø119 × 500 mm | up to Ø119 × 500 mm | kos | 60 |  | 0
1.63 | Vrtanje luknje v armirano betonsko ali opečnato konstrukcijo na višini več kot 5 metrov. | Drilling a hole in a reinforced concrete or brick structure at a height of more than 5 metres.
| do Ø62 × 300 mm | up to Ø62 × 300 mm | kos | 20 |  | 0
| do Ø62 × 500 mm | up to Ø62 × 500 mm | kos | 90 |  | 0
| do Ø119 × 300 mm | up to Ø119 × 300 mm | kos | 20 |  | 0
| do Ø119 × 500 mm | up to Ø119 × 500 mm | kos | 50 |  | 0
1.64 | Pregled PZI dokumentacije in Načrta požarne varnosti z namenom umestitve in popisa požarnih tesnenj prehodov cevi preko mej požarnih sektorjev na podlagi PZI in načrta požarne varnosti. | Review of the PZI documentation and the Fire Safety Plan in order to locate and inventory the fire sealing of pipe penetrations across fire compartment boundaries on the basis of the PZI and the Fire Safety Plan. | kpl | 1 |  | 0
1.65 | Dobava materiala in izvedba ognjeodpornega tesnenja prehoda cevne inštalacije čez mejo požarnega sektorja. Polnila iz ognjevarne mase z ustreznim atestom za požarno varovanje prehodov skozi požarno steno (med posameznimi požarnimi sektorji) za čas z načrtom požarne varnosti. Vključno certifikat in pritrditev oznake preboja. | Supply of materials and execution of fire-resistant sealing of pipe penetrations across fire sector boundaries. Fire-resistant compound fillings with appropriate certification for fire protection of penetrations through the fire wall (between individual fire sectors) for the duration of the fire safety plan. Including certification and fixing of the puncture marking. | kpl | 1 |  | 0
1.66 | Umestitev in označevanje zvočnih tesnenj prehodov cevi preko mej hrupnih con na podlagi PZI in Elaborata zaščite pred hrupom. | Placement and marking of acoustic seals of pipe crossings over noise zone boundaries based on the PZI and the Noise Protection Study. | kpl | 1 |  | 0
1.67 | Dobava materiala in izvedba zvočnega tesnenja prehoda cevne inštalacije preko mej hrupnih con. | Supply of materials and installation of acoustic sealing of the pipe installation crossing the boundaries of the noise zones. | kpl | 1 |  | 0
1.68 | Izpiranje cevovodov s hladno sanitarno vodo v celotnem razvodov. Postavka zajema tudi izdelavo poročila. | Flushing of cold water pipelines throughout the distribution system. The item also covers the production of a report. | kpl | 1 |  | 0
1.69 | Polnjenje in odzračevanje sistema | Charging and venting the system | kpl | 1 |  | 0
1.70 | Tlačni preizkus trdnosti in tesnjenja cevovoda skladen s smernico VdS CEA 4001:2021. Preizkus se po posameznih odsekih izvede s hladno vodo za mokri šprinklerski sistem in zrakom za suho mrežo. Preizkusni tlak mora znašati 1,5 × delovnega tlaka vendar ne manj kot 15 bar za mokro mrežo in 2,5 bar za suho mrežo. Najkrajši čas trajanja je 24h. Postavka vključuje ves potrebni material (čepi) in njegovo odstranitev po končanem tlačnem preizkusu ter izdelavo pisnega poročila o uspešno opravljenem tlačnem preizkusu. | Pressure test of the strength and sealing of the pipeline in accordance with VdS guideline CEA 4001:2021. The test shall be carried out section by section with cold water for the wet sprinkler system and with air for the dry net. The test pressure shall be 1,5 × the working pressure but not less than 15 bar for the wet net and 2,5 bar for the dry net. The minimum duration shall be 24 h. The item shall include all the necessary material (plugs) and its removal after the pressure test and the production of a written report on the successful completion of the pressure test. | kpl | 1 |  | 0
1.71 | Pregled in preizkus delovanja opreme v skladu z zahtevami smernice VdS CEA 4001:2021 in lokalnih predpisov. | Inspection and performance test of the equipment in accordance with the requirements of VdS guideline CEA 4001:2021 and local regulations. | kpl | 1 |  | 0
1.72 | Izdelava funkcionalne sheme avtomatskega šprinklerskega sistema, skladno s priporočili VdS CEA 4001:2024 za pritrditev na steno v šprinklerski podpostaji. | Drawing up of the functional scheme of the automatic sprinkler system, in accordance with the recommendations of VdS CEA 4001:2024 for wall mounting in the sprinkler sub-station. | kpl | 1 |  | 0
1.73 | Izdaja potrdila o izvedenih delih s priloženimi prilogami v skladu z poglavjem 17.2 smernice VdS CEA 4001:2024. | Issue of a certificate of completion with attached annexes in accordance with Chapter 17.2 of VdS CEA 4001:2024. | kpl | 1 |  | 0
1.74 | Priprava na delo, ki mora obsegati pregled projektne dokumentacije za izvedbo (PZI) del, identifikacijo morebitnih neskladij, napak ali pomanjkljivosti ter pravočasno pisno obveščanje projektanta o ugotovljenih nepravilnostih. V sklop priprave sodijo tudi vsi usklajevalni sestanki, tehnična priprava na izvedbo, izdelava montažnih in delavniških risb ter razreševanje kolizij, ki ne vplivajo na delovanje sistema, kot so lokalni odmiki cevi zaradi ovir, prilagajanje višine, smeri ali naklona, zagotavljanje praznjenja ali odzračevanja. O spremembah je treba obveščati nadzornika. | Preparation for the work, which shall include review of the design documentation for the execution (PZI) of the works, identification of any discrepancies, defects or deficiencies, and timely written notification to the designer of any identified anomalies. Preparation shall also include all coordination meetings, technical preparation for execution, preparation of erection and shop drawings, and resolution of conflicts that do not affect the operation of the system, such as local deviations of pipes due to obstructions, adjustments to height, direction or slope, provision of emptying, or venting. Changes shall be notified to the supervisor. | kpl | 1 |  | 0
| ŠPRINKLERSKI GASILNI SISTEM | SPRINKLER EXTINGUISHING SYSTEM |  |  |  | 0

## 4.5.2_HidrantnoOmrežje
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.5 | STROJNA DELA IN MATERIAL | MECHANICAL WORKS IN MATERIAL
4.5.2 | HIDRANTNO OMREŽJE IN GASILNI APARATI | HYDRANT NETWORK AND FIRE EXTINGUISHERS |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
2 | HIDRANTNO OMREŽJE IN GASILNI APARATI | HYDRANT NETWORK AND FIRE EXTINGUISHERS
| Izvajalec hidrantnega omrežja z gasilnimi aparati je dolžan sistem izvesti v skladu z Tehnično smernico o graditvi TSG-1-001:2019 (Požarna varnost v stavbah), Pravilnikom o preizkušanju hidrantnih omrežij, DIN 14461-1:2016 in Pravilnikom o izbiri in namestitvi gasilnih aparatov. | The contractor of the hydrant system with fire extinguishers is obliged to implement the system in accordance with the Technical Construction Guideline TSG-1-001:2019 (Fire Safety in Buildings), the Regulations on Testing of Hydrant Networks, DIN 14461-1:2016 and the Regulations on the Selection and Installation of Fire Extinguishers.The contractor is obliged to install the hydrant system in accordance with the Technical Construction Guideline TSG-1-001:2019 (Fire Safety in Buildings), the Hydrant System Testing Regulation, DIN 14461-1:2016 and the Fire Extinguisher Selection and Installation Regulation.
2.1 | Sklop za dvig tlaka s frekvenčno vodenimi črpalkami centrifugalnima črpalkama. Sklop črpalk mora biti sposoben zagotavljati prostorninska pretoka vsaj 32 l/min pri tlaku 6 bar bar in 140 l/min pri tlaku pri tlaku 4 bar. Obratuje ena črpalka, drugač pa je predvidena za rezervo. Ustreza Grundfos Hydro Multi CRE 5-9. Oznaka: P 60.10 | A pressure booster assembly with two frequency-controlled centrifugal pumps. The pump set shall be capable of delivering volumetric flows of at least 32 l/min at 6 bar and 140 l/min at 4 bar. One pump shall be operated and the other shall be provided for reserve. Fits Grundfos Hydro Multi CRE 5-9. Code: P 60.10 | kpl | 1 |  | 0
2.2 | Kompenzator vibracij črpalk v obliki treh fleksibilnih spojk (štejejo se kot en komplet) za ožlebljene cevi z VdS certifikatom in tlačno stopnjo vsaj PN16. Ustreza Victaulic Style 75. Oznaki: VX 60.08; VX 60.11 | Pump vibration compensator in the form of three flexible couplings (counted as one set) for VdS-certified grooved pipes with a pressure rating of at least PN16. Corresponds to Victaulic Style 75. Labels: VX 60.08; VX 60.11 | kpl | 2 |  | 0
2.3 | Sesalna košara s protipovratno loputo imenskega premera DN80. Sesalna košara mora biti iz nerjavnega jekla, protipovratna lopta pa iz nodularne litine. Postavka vključuje pritrdilni in tesnilni in material. Ustreza Zagožen sesalni koš s protipovratnim ventilom. Oznaka: FO 60.01 + CV 60.02 | Suction basket with non-return flap of nominal diameter DN80. The suction basket shall be of stainless steel and the non-return flap of ductile cast iron. The item shall include fixing and sealing material. Corresponds to Angled inlet bin with backflow preventer valve. Code: FO 60.01 + CV 60.02 | kpl | 1 |  | 0
2.4 | Preprečevalnik vrtinčenja iz nerjavnega jekla za namestitev na cev imenskega premera DN80. Premer preprečevalnika vrtinčenja mora biti vsaj Ø600 mm. Oznaka: FO 60.03 | Stainless steel swirl arrestor for fitting to a DN80 nominal diameter pipe. The diameter of the swirl arrestor shall be at least Ø600 mm. Code: FO 60.03 | kpl | 1 |  | 0
2.5 | Zaporna loputa za uporabo v sistemih z vodo, z ožlebljenima priključkoma, normalno odprta, tlačne stopnje vsaj PN16 in s stikalom za nadzor položaja odprto/zaprto. Ustreza Victaulic Series 765. | Shutoff valve for use in water systems, with two grooved connections, normally open, pressure rating at least PN16 and with open/closed position control switch. Corresponds to Victaulic Series 765.
| DN80 (FV 60.05+YS 60.05; YV 61.01 + YS 61.01; FV 62.01 + YS 62.01) | DN80 (FV 60.05+YS 60.05; YV 61.01 + YS 61.01; FV 62.01 + YS 62.01) | kpl | 3 |  | 0
2.6 | Zaporni ventil za uporabo v sistemih z vodo, z ožlebljenima priključkoma, tlačne stopnje vsaj PN16 in z enim od VdS, FM ali UL certifikatov. Ustreza Victaulic Series 722. | Shutoff valve for use in water systems, with two grooved connections, pressure rating at least PN16 and with one of the VdS, FM or UL approvals. Corresponds to Victaulic Series 722.
| DN 15 (FV 60.06; FV 60.12) | DN 15 (FV 60.06; FV 60.12) | kos | 2 |  | 0
| DN 50 (YV 60.14) | DN 50 (YV 60.14) | kos | 1 |  | 0
2.7 | Protipovratna loputa za uporabo v sistemih z vodo, tlačne stopnje vsaj PN16 in z ožlebljenima priključkoma. Ustreza Victaulic Series 717 ali 717H. | Check valve for use in water systems with a pressure rating of at least PN16 and with two grooved connections. Fits Victaulic Series 717 or 717H.
| DN 80 (CV 62.02) | DN 80 (CV 62.02) | kos | 1 |  | 0
2.8 | Avtomatski prezračevalno-odzračevalni ventil z VdS, FM ali UL cerifikatom, tlačno stopnjo vsaj PN16, z zapornim krogelnim ventilom, praznilnim ventilom s priključkom za cev, zbiralnikom za vodno paro, mehanskim zaklepom proti nepooblaščeni uporabi (ključavnica), z neodvisnimi avtomatskimi funkcijami odvajanja zraka pri polnjenju sistema, dovajanjem zraka pri praznjenju sistema in odvajanjem oziroma dovajanjem zraka med obratovanjem. Ustrezajo proizvodi AGF PURGEnVENT + 7920AI. Oznake: RV 60.99; | Automatic ventilation-vent valve with VdS, FM or UL certification, pressure rating at least PN16, with shut-off ball valve, discharge valve with hose connection, water vapour collector, mechanical locking against unauthorised use (lock), with independent automatic functions for venting air when filling the system, for supplying air when emptying the system, and for venting or supplying air during operation. AGF PURGEnVENT + 7920AI products are suitable. RV 60.99; | kpl | 1 |  | 0
2.9 | Ročni odzračevalni ventil z VdS, FM ali UL cerifikatom, tlačno stopnjo vsaj PN16, mehanskim zaklepom proti nepooblaščeni uporabi (ključavnica). Ustreza AGF Manufacturing 7910MAV. Oznake: RV 62.11.99; RV 62.12.99; RV 62.21.99; RV 62.22.99; RV 62.23.99; RV 62.24.99; RV 62.25.99; RV 62.26.99; RV 62.27.99; RV 62.28.99; RV 62.29.99; RV 62.30.99; RV 62.31.99; RV 62.32.99 | Manual vent valve with VdS, FM or UL certification, pressure rating at least PN16, mechanical lock against unauthorised use (lock). Corresponds to AGF Manufacturing 7910MAV. Codes: RV 62.11.99; RV 62.12.99; RV 62.21.99; RV 62.22.99; RV 62.23.99; RV 62.24.99; RV 62.25.99; RV 62.26.99; RV 62.27.99; RV 62.28.99; RV 62.29.99; RV 62.30.99; RV 62.31.99; RV 62.32.99 | kpl | 14 |  | 0
2.10 | Preizkuševalno-praznilni ventil z VdS, FM ali UL certifikatom, K-faktorjem K40, tlačno stopnjo vsaj PN16, z navojnimi priključki DN50, manometrom (0-16 bar) in tlačnim varnostnim ventilom. Ustreza AGF Manufacturing 1011 with T Kit + LockingKit ali 2511 with T Kit + LockingKit. Oznake: TDV 62.04 | Test-empty valve with VdS, FM or UL certification, K-factor K40, pressure rating at least PN16, threaded connections DN50, pressure gauge (0-16 bar) and pressure relief valve. Fits AGF Manufacturing 1011 with T Kit + LockingKit or 2511 with T Kit + LockingKit. Tags: TDV 62.04 | kpl | 22 |  | 0
2.11 | Stabilna gasilska spojka s slepo spojko skladnih z DIN 14317:1985 oziroma DIN 14311:1985. Imenski premer spojke mora biti DN 50 (C). | Stable fire protection coupling with blind coupling complying with DIN 14317:1985 or DIN 14311:1985. The nominal diameter of the coupling must be DN 50 (C). | kpl | 1 |  | 0
2.12 | EURO hidrant skladen z EN 671-1:2012 v obliki pločevinaste omarice iz dekapirane pločevine protikorozijsko zaščitene v rdečem barvnem tonu RAL3000, z vratci na tečaje in pripadajočo oznako. Omara vsebuje priključni medeninasti ventil 2" (DIN 14461-3:2020) s stabilno spojko 2" (DIN 86204:1993); gibljivi nastavek 2" (DIN 14461-5:2008); 30 metersko gumirano cev imenskega premera DN25 (EN 694:2014) navito na kolutu (EN 671-1:2012) in ročnik (Euro EN 671) imenskega premera DN25/6mm. Ustrezajo Gallus: | EURO hydrant complying with EN 671-1:2012 in the form of a sheet metal cabinet made of corrosion-protected decapitated sheet metal in red RAL3000, with hinged door and associated marking. The cabinet contains a 2" (DIN 14461-3:2020) brass connection valve with 2" stable coupling (DIN 86204:1993); a 2" (DIN 14461-5:2008) flexible spigot; a 30 metre rubber hose DN25 nominal diameter (EN 694:2014) wound on a reel (EN 671-1:2012); and a DN25/6mm nominal diameter handpiece (Euro EN 671). They correspond to Gallus:
| 1-C/K-30 kombinirana omarica dimenzij (W × H × D) 840 × 1040 × 250 mm, za podometno vgradnjo in z desnim priklopom; | 1-C/K-30 combination cabinet dimensions (W × H × D) 840 × 1040 × 250 mm, for flush mounting and with right-hand connection; | kos | 12 |  | 0
| 1-C/K-30 kombinirana omarica dimenzij (W × H × D) 840 × 1040 × 250 mm, za podometno vgradnjo in z levim priklopom; | 1-C/K-30 combination cabinet dimensions (W × H × D) 840 × 1040 × 250 mm, for flush mounting and with left-hand connection; | kos | 17 |  | 0
| 1-C/K-30-LEF kombinirana omarica dimenzij (W × H × D) 740 × 1090 × 250 mm, za podometno vgradnjo in z desnim priklopom; | 1-C/K-30-LEF combination cabinet dimensions (W × H × D) 740 × 1090 × 250 mm, for flush mounting and with right-hand connection; | kos | 7 |  | 0
| 1-C/K-30-LEF kombinirana omarica dimenzij (W × H × D) 740 × 1090 × 250 mm, za podometno vgradnjo in z levim priklopom; | 1-C/K-30-LEF combination cabinet dimensions (W × H × D) 740 × 1090 × 250 mm, for flush mounting and with left-hand connection; | kos | 15 |  | 0
| 1-C/K2-30 kombinirana omarica dimenzij (W × H × D) 840 × 1240 × 250 mm, za podometno vgradnjo in z desnim priklopom; | 1-C/K2-30 Combination cabinet dimensions (W × H × D) 840 × 1240 × 250 mm, for flush mounting and with right-hand connection; | kos | 2 |  | 0
2.13 | Gasilni aparat na ABC prah z najmanj 12 EG in skladen z EN 3. Ustreza Fipis GEN S6. | ABC dust extinguisher with at least 12 EG and complying with EN 3. Corresponds to Fipis GEN S6. | kos | 170 |  | 0
2.14 | Gasilni aparat na CO2 z najmanj 5 kg gasilnega sredstva in skladen z EN 3. Ustreza Gallus CO2-5kg. | CO2 extinguisher with at least 5 kg extinguishing agent and complying with EN 3. Corresponds to Gallus CO2-5kg. | kos | 38 |  | 0
2.15 | Omarica za gasilni aparat na ABC prah z 12EG. Omarica mora biti kovinska, njene dimenzije pa ne smejo presegati 290 × 580 × 250 mm. Omarica naj se odpira na gumb. Ustreza Gallus 24 00 01. | Fire extinguisher cabinet for ABC dust with 12EG. The cabinet shall be of metal and its dimensions shall not exceed 290 × 580 × 250 mm. The cabinet shall be push-button opening. Corresponds to Gallus 24 00 01. | kos | 109 |  | 0
2.16 | Omarica za gasilni aparat na CO2 prah z 12EG. Omarica mora biti kovinska, njene dimenzije pa ne smejo presegati 290 × 740 × 250 mm. Omarica naj se odpira na gumb. Ustreza Gallus 24 00 03. | 12EG CO2 powder extinguisher cabinet. The cabinet shall be of metal and shall not exceed dimensions of 290 × 740 × 250 mm. The cabinet shall be push-button opening. Corresponds to Gallus 24 00 03. | kos | 36 |  | 0
2.17 | Pocinkana brezšivna jeklena cev iz ogljikovega jekla (P235TR2) skladna z EN 10216-1:2014. Postavka vključuje, izdelavo žlebov, VdS certificirane toge spojke za ožlebljene cevi (ustrezajo ustrezajo Victaulic 009N, 108, 109 spojke), obešanje cevovodov s predfabriciranimi predizoliranimi obešali, kompletno s profili za obešanje (ustrezajo proizvodi Hilti).Cevi, žlebovi za spajanje, spojke in obešalni elementi morajo biti skladni s standardom VdS CEA 4001:2021. Cevi morajo biti pocinkane skladno z EN 10240:1997. | Galvanised seamless carbon steel pipe (P235TR2) conforming to EN 10216-1:2014. The item includes, the manufacture of gutters, VdS certified rigid couplings for grooved pipes (corresponding Victaulic 009N, 108, 109 couplings), hanging of pipelines with prefabricated preinsulated hangers, complete with hanging profiles (corresponding Hilti products).The pipes, jointing gutters, couplings and hanging elements shall conform to VdS CEA 4001:2021. The pipes shall be galvanised in accordance with EN 10240:1997.
| DN50 → Ø60,3 mm × 2,9 mm | DN50 → Ø60.3 mm × 2.9 mm | m | 1500 |  | 0
| DN80 → Ø88,9 mm × 3,2 mm | DN80 → Ø88.9 mm × 3.2 mm | m | 120 |  | 0
2.18 | Cena metra cevi mora zajemati tudi pocinkane cevne oblikovne kose za uporabo na ožlebljenih ceveh. Oblikovni kosi morajo imeti in VdS certifikat oziroma izpolnjevati zahteve smernice VdS CEA 4001:2021. Tlačna stopnja vseh oblikovnih kosov mora biti vsaj PN16. Ustreza nabor oblikovnih kosov Victaulic FireLock. *Opombe: - namesto reducirnega T-kosa se lahko uporabi navrtalne oklepe (ang. Mechanical Tee) - v primeru varjenja, se morajo uporabiti oblikovni kosi v skladu z EN 10253-1:2000; -v primeru navojnega spajanja pa se morajo uporabiti oblikovni kosi skladni z EN 10241:2001. | The price per metre of pipe shall also include galvanised pipe fittings for use on grooved pipes. The fittings shall be VdS certified or meet the requirements of VdS guideline CEA 4001:2021. The pressure rating of all fittings shall be at least PN16. Corresponds to the Victaulic FireLock set of design pieces. *Notes: - drill collars can be used instead of the reducing T-piece (Mechanical Tee) - in the case of welding, the shaped pieces shall be used in accordance with eN 10253-1:2000; -in the case of threaded joints, shaped pieces must be used compliant with EN 10241:2001.
| Prirobnica DN 50 | Flange DN 50 | kos | 4 |  | 0
| Reducirni kos (C) DN 80 - DN 50 | Reducing piece (C) DN 80 - DN 50 | kos | 6 |  | 0
| Koleno DN 50 | Elbow DN 50 | kos | 280 |  | 0
| Koleno DN 80 | Elbow DN 80 | kos | 15 |  | 0
| T- kos DN 50 - DN 50 - DN 50 | T-piece DN 50 - DN 50 - DN 50 | kos | 60 |  | 0
| T- kos DN 80 - DN 80 - DN 80 | T-piece DN 80 - DN 80 - DN 80 | kos | 4 |  | 0
| T- kos (reducirni) DN 80 - DN 80 - DN 50 | T-piece (reducing) DN 80 - DN 80 - DN 50 | kos | 3 |  | 0
2.19 | Cev iz nerjavnega jekla (1.4404 / AISI 316L) skladna z EN 10217-7:2021. Postavka vključuje spajanje cevi s TIG varjenjem), obešanje cevovodov s predfabriciranimi predizoliranimi obešali, kompletno s profili za obešanje (ustrezajo proizvodi Hilti ali Sikla). *Opomba: Cevi zunaj bazena se lahko spaja tudi s VdS certificiranimi spojkami za ožlebljene cevi (ustreza Victaulic 75). | Stainless steel pipe (1.4404 / AISI 316L) complying with EN 10217-7:2021. Item includes TIG welding of the pipe), hanging of the pipelines with prefabricated preinsulated hangers, complete with hanging profiles (corresponding to Hilti or Sikla products). *Note: Pipes outside the basin can also be connected with VdS-certified couplings for grooved pipes (corresponding to Victaulic 75).
| DN80 → Ø88,9 mm × 3,0 mm | DN80 → Ø88.9 mm × 3.0 mm | m | 18 |  | 0
| Cena metra cevi mora zajemati tudi cevne oblikovne kose za varilno spajanje s cevmi Oblikovni kosi morajo biti skladni z EN 10253-4:2008. | The price per metre of the pipe shall also include the pipe formers for welding joints with the pipes. The formers shall comply with EN 10253-4:2008.
| Koleno (3D) DN80 → → Ø88,9 mm × 3,0 mm | Elbow (3D) DN80 → → Ø88.9 mm × 3.0 mm | kos | 3 |  | 0
2.20 | Manometer z Bourdonovo cevjo primeren za uporabo v sistemih z vodo. Manometer mora imeti območje merjenja od 0 bar do 16 bar z delitvijo največ 0,5 bar, prikazovalno okno ø100 mm, tlačno stopnjo vsaj PN16 in enega izmed VdS, FM ali UL certfikatov. Ustreza Minimax "pressure gauge 16 bar - 2 pointers AR/ER". Oznaka: PG 60.07; PG 60.13 | Bourdon tube manometer suitable for use in water systems. The manometer shall have a measuring range of 0 bar to 16 bar with a maximum separation of 0,5 bar, a display window of ø100 mm, a pressure rating of at least PN16 and one of the VdS, FM or UL certifications. Minimax "pressure gauge 16 bar - 2 pointers AR/ER" shall comply. Code: PG 60.07; PG 60.13 | kos | 2 |  | 0
2.21 | Serijski uporovni grelni kabel za zaščito pred zmrzovanjem vode v cevovodih. Minimalna dolžina kabla je 20 metrov. Kabel mora zagotavljati vsaj 10 W/m. Napajanje naj bo 230 V AC. Ustreza Danfoss DEVIpipeguard (B) + DEVIreg. Oznaka: IE 62.05.01 + TS 62.05.01; IE 62.05.02 + TS 62.05.02; IE 62.05.03 + TS 62.05.03; IE 62.05.04 + TS 62.05.04; IE 62.05.05 + TS 62.05.05; IE 62.05.06 + TS 62.05.06; IE 62.05.07 + TS 62.05.07; IE 62.05.08 + TS 62.05.08; IE 62.05.09 + TS 62.05.09; | Serial resistive heating cable for protection against freezing of water in pipelines. The minimum cable length shall be 20 m. The cable shall provide at least 10 W/m. The power supply shall be 230 V AC. Fits Danfoss DEVIpipeguard (B) + DEVIreg. Code: IE 62.05.01 + TS 62.05.01; IE 62.05.02 + TS 62.05.02; IE 62.05.03 + TS 62.05.03; IE 62.05.04 + TS 62.05.04; IE 62.05.05 + TS 62.05.05; IE 62.05.05 + TS 62.05.05; IE 62.05.06 + TS 62.05.06; IE 62.05.07 + TS 62.05.07; IE 62.05.08 + TS 62.05.08; IE 62.05.09 + TS 62.05.09; | kpl | 9 |  | 0
2.22 | Toplotna izolacija skladna s standardom EN 14303:2015, debeline 50 mm, s toplotno prevodnostjo k ≤ 0,035 W/(m K), klasifikacijo A po EN 13501-1:2018, za temperature do 250 °C. Toplotna izolacija mora imeti na zunanji površini sloj za zaščito pred mehanskimi poškodbami in razpadanjem. Izolacija mora biti odporna proti kondenziranju. Ustreza Knauf Insulation Thermo-teK PS Cld ALS za zunanje premere cevi: | Thermal insulation complying with EN 14303:2015, 50 mm thick, with a thermal conductivity k ≤ 0,035 W/(m K), classification A according to EN 13501-1:2018, for temperatures up to 250 °C. The thermal insulation shall have a layer on the outer surface to protect against mechanical damage and decay. The insulation shall be resistant to condensation. Corresponds to Knauf Insulation Thermo-teK PS Cld ALS for external pipe diameters:
| Ø60,3→ 50 mm | Ø60,3→ 50 mm | m | 80 |  | 0
2.23 | Komplet za vodotesen prehod skozi betonsko steno proti bazenu. Komplet mora zagotavljati vodotenost pri tlaku do 10 metrov vodnega stolpca oziroma razred vodotesnosti W2-B po DIN 18535:2017. Cevna uvodnica in njena namestitev sta del arhitekturno-gradbenega popisa. Ustreza Hauff-technik HSD | A kit for a watertight passage through the concrete wall towards the swimming pool. The kit must guarantee a watertightness at a pressure of up to 10 metres water column or a watertightness class W2-B according to DIN 18535:2017. The pipe inlet and its installation shall be part of the architectural and construction inventory. Corresponds to Hauff-technik HSD
| 150 1x88 b40 (PC-W 60.04; PC-W 61.02) | 150 1x88 b40 (PC-W 60.04; PC-W 61.02) | kpl | 2 |  | 0
2.24 | Pregled PZI dokumentacije in Načrta požarne varnosti z namenom umestitve in popisa požarnih tesnenj prehodov cevi preko mej požarnih sektorjev na podlagi PZI in načrta požarne varnosti. | Review of the PZI documentation and the Fire Safety Plan in order to locate and inventory the fire sealing of pipe penetrations across fire compartment boundaries based on the PZI and the Fire Safety Plan. | kpl | 1 |  | 0
2.25 | Dobava materiala in izvedba ognjeodpornega tesnenja prehoda cevne inštalacije čez mejo požarnega sektorja. Polnila iz ognjevarne mase z ustreznim atestom za požarno varovanje prehodov skozi požarno steno (med posameznimi požarnimi sektorji) za čas z načrtom požarne varnosti. Vključno certifikat in pritrditev oznake preboja. *Opomba: Posatvka vključuje obdajanje hidrantnih omar, ki so umeščene v montažne stene inštalacijskih jaškov, z požarno odpornihmi oblogami. | Supply of materials and execution of fire-resistant sealing of pipe penetrations across fire sector boundaries. Fire-resistant compound fillings with appropriate certification for fire protection of penetrations through the fire wall (between individual fire sectors) for the duration of the fire safety plan. Including certification and fixing of the puncture marking. *Remark: The provision shall include the enclosure of the hydrant cabinets, which shall be located in the prefabricated walls of the manholes, with fire-resistant linings. | kpl | 1 |  | 0
2.26 | Umestitev in označevanje zvočnih tesnenj prehodov cevi preko mej hrupnih con na podlagi PZI in Elaborata zaščite pred hrupom. | Placement and marking of acoustic seals of pipe crossings over noise zone boundaries based on the PZI and the Noise Protection Study. | kpl | 1 |  | 0
2.27 | Dobava materiala in izvedba zvočnega tesnenja prehoda cevne inštalacije preko mej hrupnih con. | Supply of materials and installation of acoustic sealing of the pipe installation crossing the boundaries of the noise zones. | kpl | 1 |  | 0
2.28 | Izpiranje cevovodov s hladno sanitarno vodo v celotnem sistemu novoinstaliranih razvodov skupaj z izdelavo poročila. | Flushing of cold water piping throughout the newly installed piping system, including the production of a report. | kpl | 1 |  | 0
2.29 | Polnjenje in odzračevanje sistema | Charging and venting the system | kpl | 1 |  | 0
2.30 | Tlačni preizkus trdnosti in tesnjenja cevovoda zunanjega dela hidrantnega omrežja, ki je predvidoma izveden z jeklenih cevi. Preizkus se mora izvesti v skladu z SIST EN 805:2000 in poglavjem 2.2 IZS priročnika o tlačnih preskusih strojnih inštalacij. Postavka vključuje ves potrebni material (čepi) in njegovo odstranitv po končanem tlačnem preizkusu ter izdelavo pisnega poročila o uspešno opravljenem tlačnem preizkusu. | Pressure test of the strength and sealing of the piping of the external part of the hydrant network, which is planned to be made of steel pipes. The test shall be carried out in accordance with SIST EN 805:2000 and Chapter 2.2 of the IZS Manual on Pressure Testing of Mechanical Installations. The item includes all the necessary material (plugs) and its disposal after the pressure test has been completed, and the production of a written report on the successful completion of the pressure test. | kpl | 1 |  | 0
2.31 | Izvedba preizkušanja tlakov in pretokov na hidrantih s strani pooblaščene organizacije, v skladu s Pravilnikom o preizkušanju hidrantnih omrežij (Ur.l. RS, št. 22/95 in 102/09), vključno z izdelavo pisnega poročila o rezultatih preiskušanja. | Testing of hydrant pressures and flows by an authorised organisation, in accordance with the Rules on Testing of Hydrant Networks (Official Gazette of the Republic of Slovenia, No. 22/95 and 102/09), including the preparation of a written report on the results of the testing. | kpl | 1 |  | 0
2.32 | Izdelava shem hidrantne mreže z navodili za obratovanje, vloženo v zaščitni okvir s steklom ali plastificirano, vključno s pritrditvijo na notranji zid v strojnici objekta. | Drawing up of hydrant network diagrams with operating instructions, enclosed in a protective frame with glass or plasticised, including fixing to the internal wall in the engine room of the building. | kpl | 1 |  | 0
2.33 | Priprava na delo, ki mora obsegati pregled projektne dokumentacije za izvedbo (PZI) del, identifikacijo morebitnih neskladij, napak ali pomanjkljivosti ter pravočasno pisno obveščanje projektanta o ugotovljenih nepravilnostih. V sklop priprave sodijo tudi vsi usklajevalni sestanki, tehnična priprava na izvedbo, izdelava montažnih in delavniških risb ter razreševanje kolizij, ki ne vplivajo na delovanje sistema, kot so lokalni odmiki cevi zaradi ovir, prilagajanje višine, smeri ali naklona, zagotavljanje praznjenja ali odzračevanja. O spremembah je treba obveščati nadzornika. | Preparation for the work, which shall include review of the design documentation for the execution (PZI) of the works, identification of any discrepancies, defects or deficiencies, and timely written notification to the designer of any identified anomalies. Preparation shall also include all coordination meetings, technical preparation for execution, preparation of erection and shop drawings, and resolution of conflicts that do not affect the operation of the system, such as local deviations of pipes due to obstructions, adjustments to height, direction or slope, provision of emptying, or venting. Changes shall be notified to the supervisor. | kpl | 1 |  | 0
| HIDRANTNO OMREŽJE IN GASILNI APARATI | HYDRANT NETWORK AND FIRE EXTINGUISHERS |  |  |  | 0

## 4.5.3_GašenjeKuhinje
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.5 | STROJNA DELA IN MATERIAL | MECHANICAL WORKS IN MATERIAL
4.5.3 | SISTEM ZA GAŠENJE KUHALNIH ELEMENTOV | COOKING ELEMENT EXTINGUISHING SYSTEM |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
3 | SISTEM ZA GAŠENJE KUHALNIH ELEMENTOV | COOKING ELEMENT EXTINGUISHING SYSTEM
| Namestitev mokrega kemičnega sistema za gašenje kuhinje mora opraviti ustrezno usposobljen izvajalec, in sicer v skladu z navodili proizvajalca izbranega sistema. | The installation of a wet chemical kitchen fire-extinguishing system shall be carried out by a suitably qualified contractor in accordance with the instructions of the manufacturer of the system selected.
3.1 | Stabilni mokri kemični gasilni sistem za namestitev v napi nad osrednjima toplotnima blokoma (2,7 m × 1,9 m in 0,8 m × 1,9 m) v prostoru za toplotno obdelavo. Sistem mora biti izveden v skladu z EN 16282-7, UL300, NFPA 17A. Sestavljen je iz jeklenk s potisnim plinom in jeklenk z gasilnim sredstvom (oboje je nameščeno v dveh tipskih omarah), cevnega razvoda, prožilnega mehanizema, termo členov, šob (19×), varnostne in krmilne opreme, nadometno nameščenega ročnega prožilnega mehanizema na poteg ter mikro breznapetostnih stikal (2×) za proženje požarnega signala proti požarni centrali objekta (prekinitev dovoda energije toplotnima blokoma). Ustreza Johnson Controls ANSUL R-102. Opomba: Pred izvedbo je obvezna preverba tehnologije kuhinje ter izvedba končnih izračunov gasilnega sredstva in poteka cevovodov. | Stable wet chemical extinguishing system to be installed in the hood above the two central heat blocks (2.7 m × 1.9 m and 0.8 m × 1.9 m) in the heat treatment room. The system shall be constructed in accordance with EN 16282-7, UL300, NFPA 17A. It shall consist of propellant gas cylinders and extinguishing agent cylinders (both installed in two standard cabinets), piping, actuator, thermocouples, nozzles (19×), safety and control equipment, overhead mounted manual pull-type actuator and micro-voltage-free switches (2×) for triggering the fire signal to the building's fire control panel (interrupting the power supply to the thermal units). Corresponds to Johnson Controls ANSUL R-102. Note: Before implementation, it is mandatory to check the kitchen technology and to make final calculations of the extinguishing agent and piping routing. | kpl | 1 |  | 0
3.2 | Alarmna hupa za namestitev v prostor za toplotno obdelavo hrane. Ustreza Pfannenber DS 10. Oznaka: HA 50.11 | Alarm horn for installation in a food heat treatment room. Corresponds to Pfannenber DS 10. Code: HA 50.11 | kos | 1 |  | 0
3.3 | Alarmna bliskavka za namestitev v prostor za toplotno obdelavo hrane. Ustreza Pfannenber PY X-S-05. Oznaka: AL 50.12, AL 50.21 | Alarm flash for installation in a food heat treatment room. Corresponds to Pfannenber PY X-S-05. Code: AL 50.12, AL 50.21 | kos | 2 |  | 0
3.4 | Tehnična dokumentacija, tesnostni preizkus, poučevanje osebja, pregled preglednika in izdaja potrdila o ustreznosti stabilnega mokrega kemičnega gasilnega sistema. | Technical documentation, leak test, staff training, surveyor review and certificate of adequacy for a stable wet chemical fire extinguishing system. | kpl | 1 |  | 0
3.5 | Priprava na delo, ki mora obsegati pregled projektne dokumentacije za izvedbo (PZI) del, identifikacijo morebitnih neskladij, napak ali pomanjkljivosti ter pravočasno pisno obveščanje projektanta o ugotovljenih nepravilnostih. V sklop priprave sodijo tudi vsi usklajevalni sestanki, tehnična priprava na izvedbo, izdelava montažnih in delavniških risb ter razreševanje kolizij, ki ne vplivajo na delovanje sistema, kot so lokalni odmiki cevi zaradi ovir, prilagajanje višine, smeri ali naklona, zagotavljanje praznjenja ali odzračevanja. O spremembah je treba obveščati nadzornika. | Preparation for the work, which shall include review of the design documentation for the execution (PZI) of the works, identification of any discrepancies, defects or deficiencies, and timely written notification to the designer of any identified anomalies. Preparation shall also include all coordination meetings, technical preparation for execution, preparation of erection and shop drawings, and resolution of conflicts that do not affect the operation of the system, such as local deviations of pipes due to obstructions, adjustments to height, direction or slope, provision of emptying, or venting. Changes shall be notified to the supervisor. | kpl | 1 |  | 0
| SISTEM ZA GAŠENJE KUHALNIH ELEMENTOV | COOKING ELEMENT EXTINGUISHING SYSTEM |  |  |  | 0

## 4.5.4_SkupnePostavke
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.5 | STROJNA DELA IN MATERIAL | MECHANICAL WORKS IN MATERIAL
4.5.4 | SKUPNE POSTAVKE | COMMON ITEMS |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
4 | SKUPNE POSTAVKE | COMMON ITEMS
4.1 | Napisne ploščice izdelane iz nosilnega in pritrdilnega dela ter nalepljeno oznako po shemi za opremo in armature vključno s samolepilnimi puščicami za označitev smeri pretoka ter z napisom vrste medija. | Nameplates made up of a support and a fixing part and labelled according to the scheme for equipment and fittings including self-adhesive arrows to indicate the direction of flow and the type of media. | kpl | 1 |  | 0
4.2 | Barvanje inštalacij z barvo po izbiri arhitekta (predvidoma RAL 7016). | Painting of the installations with a colour of the architect's choice (presumably RAL 7016). | kpl | 1 |  | 0
4.3 | Pregled in izdaja poročila o pregledu aktivne požarne zaščite s strani pooblaščene ustanove. | Review and issue of an inspection report on active fire protection by an approved institution. | kpl | 1 |  | 0
4.4 | Izdelava montažnih in delavniških risb za izvedbo inštalacij med gradnjo objekta. | Preparation of erection and shop drawings for the installation of services during the construction of the building. | kpl | 1 |  | 0
4.5 | Sprotno dopolnjevanje PZI dokumentacije z vsemi spremembami, ki so se zgodile v času izvedbe. Papirnato in elektronso različico se preda projektantu, ki bo spremembe vnašal v elektronsko verzijo in na koncu izdal Projekt izvedenih del (PID). | Keeping the PZI documentation up to date with any changes that have occurred during the execution. The paper and electronic versions shall be handed over to the designer who will incorporate the changes into the electronic version and finally issue the Project Implementation Design (PID). | kpl | 1 |  | 0
4.6 | Izdelava navodil za obratovanje in vzdrževanje NOV (2 × tiskana izdaja, 1 × elektronska izdaja) ter dokazila o zanesljivosti objekta DZO (2 × tiskana izdaja, 1 × elektronska izdaja) | Production of the operation and maintenance manuals for the NOC (2 × hard copy, 1 × electronic) and the proof of reliability of the DZO facility (2 × hard copy, 1 × electronic) | kpl | 1 |  | 0
4.7 | Varilska dokumentacija (certifikat podjetja, vhodna kontrola materiala, atesti varilcev, varilski dnevnik, ročne izometrične sheme, poročilo o endoskopskem pregledu cevnih instalacij). Kontrola varilskih del, ki zajema videoskopski nadzor varilskih del s poročilom in pripravo sprostitvene dokumentacije ter testov za pričetek varilskih del. Videoskopsko kontrolo lahko izvaja oseba, ki je usposobljena po SIST EN ISO 9712:2022, končno poročilo pa potrjuje samo neodvisni kontrolni organ. Dela obsegajo 100% zunanji vizualni pregled in 10% videoskopska kontrola s poročilom (mesta kontrol določi nadzornik). V primeru, da se odkrije napaka na več kot enem zvaru se obseg poveča na 100%, razliko kontrole plača izvajalec varilskih del. | Welding documentation (company certificate, incoming material inspection, welder's certificates, welding log, manual isometric diagrams, endoscopic inspection report of pipe installations). Inspection of welding works, comprising videoscopic inspection of welding works with report and preparation of release documentation and tests for the start of welding works. Videoscopic inspection may be carried out by a person qualified according to SIST EN ISO 9712:2022, and the final report shall be certified only by an independent inspection body. The works shall consist of 100% external visual inspection and 10% videoscopic inspection with report (inspection sites to be determined by the supervisor). In the case of a defect being found in more than one weld, the scope shall be increased to 100%, the difference of the inspection to be paid by the contractor of welding works. | kpl | 1 |  | 0
4.8 | Kvalifikacija montaže (ang. Installation qualification – IQ) skladno s protokolom dobre inženirske prakse (ang. Good Engineering Practice – GEP). Postavka vključuje dokumentiranje in odpravo prvotnih napak pri montaži; | Installation qualification (IQ) in accordance with Good Engineering Practice (GEP) protocol. Item includes documentation and correction of original installation defects; | kpl | 1 |  | 0
4.9 | Kvalifikacija obratovanja (ang. Operational Qualification – OQ)) ter dokumentiranje meritev delovanja vključno z nastavitvijo parametrov; | Operational Qualification (OQ)) and documentation of performance measurements including parameter settings; | kpl | 1 |  | 0
4.10 | Priprava primopredajne dokumentacije, ki mora vsebovati: izjave, dokazilo o zanesljivosti objekta, certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo in vzdrževanje ter ostalo primopredajno dokumantacijo. Predaja se v dveh mapiranih izvodih ter enem izvodu v elektronski obliki; | Preparation of the handover documentation, which shall include: declarations, proof of the reliability of the facility, certificates and attestations for the materials and equipment installed, records of tests and measurements, operating and maintenance instructions and other handover documentation. It shall be submitted in two mapped copies and one electronic copy; | kpl | 1 |  | 0
| SKUPNE POSTAVKE | COMMON ITEMS |  |  |  | 0