## 0_Naslovnica
OPOZORILO! Vsi prevodi v angleščino so strojno izdelani in zgolj informativne narave. V primeru kakršnekoli nejasnosti ali dvoma izključno velja izvirno besedilo v slovenščini. WARNING! All translations into English have been produced by machine translation and are provided for informational purposes only. In the event of any ambiguity or uncertainty, the original Slovenian text shall prevail exclusively.
| / | / | [5 empty] | /
| Sprem./Rev.: | Opis spremembe/Description of Changes: | [5 empty] | Datum/Date: | Podpis/Signature:
| Investitor/Investor: |  |  |  |  | Gradnja/Facility
|  |  | Univerza v Ljubljani Kongresni trg 12 1000 Ljubljana, Slovenija |  |  | Fakulteta za strojništvo/Faculty of Mechanical Engineering
| Projektant/Design Engineer: |  |  |  |  | Del objekta/sistem/Building/System:
|  |  | IBE, svetovanje, projektiranje in inženiring Ljubljana, Slovenija |  |  | STAVBA FAKULTETE/FACULTY BUILDING
| Projektant/Design Engineer: |  |  |  |  | Vrsta načrta/Documentation:
4 NAČRT S PODROČJA STROJNIŠTVA/ DOC. IN THE FIELD OF MECHANICAL ENGINEERING
|  | Ime in priimek/Name and Surname: |  |  | Id. št./Id. No: | Vsebina risbe (dokumenta)/Document Title:
| Vodja proj./ Des. Manager: | Boštjan Vuga, univ. dipl. inž. arh., grad. dip. (AA) |  |  | ZAPS 0035 PA PPN | PR. POPIS STROJNIH DEL/BOQ OF MECHANICAL WORKS 4/6 Geosonde/Borehole Heat Exchangers
| Poobl. strok./ Cert. Profess.: | Sašo Ocvirk, univ. dipl. inž. str. |  |  | IZS S-0717
| Poobl. strok./ Cert. Profess.: |  |  |  |  | Št. proj./ Proj. No.: | 362-19 |  | Vrsta dokument./ Document. Type: | DZR
| Izdelal/ Creator: | Sašo Ocvirk, univ. dipl. inž. str. |  |  | IZS S-0717 | Klas. ozn./ Class. No.: | -- |  | Stran/ Page: | 1/*
| Datum/ Date: | maj/May 2026 |  | Merilo/ Scale: | / | Ident. ozn./ Id. No: | JULFS--6S0602P

## 0_Osebe
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
POOBLAŠČENI STROKOVNJAKI, ODGOVORNI ZA IZDELAVO PROJEKTANTSKEGA POPISA:
Id. št. ZAPS/IZS | Pooblaščeni strokovnjak | Strokovno področje
IZS S-0717 | Sašo Ocvirk, univ. dipl. inž. str. | Geosonde
SODELAVCI PRI IZDELAVI PROJEKTANTSKEGA POPISA:
CERTIFIED EXPERTS RESPONSIBLE FOR ELABORATING THE BILL OF QUANTITIES:
Id. No ZAPS/IZS | Certified Expert | Area of Expertise
IZS S-0717 | Sašo Ocvirk, univ. dipl. inž. str. | Borehole Heat Exchangers
COLABORATORS IN THE ELABORATING THE BILL OF QUANTITIES:

## 0.1_Uvod-STP
Investitor: | UNIVERZA V LJUBLJANI | UNIVERZA V LJUBLJANI
Gradnja: | FAKULTETA ZA STROJNIŠTVO | FAKULTETA ZA STROJNIŠTVO
Objekt: | STAVBA FAKULTETE | STAVBA FAKULTETE
0.1 | SPLOŠNI TEHNIČNI POGOJI | GENERAL TECHNICAL CONDITIONS
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic operator with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
0.1.1 | Izvajalec se obveže, da bo upošteval veljavno zakonodajo, ki ureja graditev objektov v Republiki Sloveniji, vključno s povezanimi podzakonskimi akti, predpisi, tehničnimi smernicami, standardi, pravili stroke in dobro gradbeno prakso. Prav tako mora izvajalec upoštevati vse zahteve izdanega integralnega gradbenega dovoljenja in vsa dela izvesti skladno s projektno dokumentacijo ter ostalimi pogoji, objavljenimi v razpisni dokumentaciji. | The Contractor undertakes to comply with the applicable legislation governing the construction of buildings in the Republic of Slovenia, including related by-laws, regulations, technical guidelines, standards, professional rules and good construction practice. The Contractor shall also comply with all the requirements of the integral building permit issued and shall carry out all works in accordance with the project documentation and other conditions published in the tender documentation.
0.1.2 | Dela lahko izvaja samo izvajalec, ki je registriran za opravljanje gradbene dejavnosti in ima za tovrstna dela ustrezno zavarovanje za škodo, certifikate, tehnično izobražen kader, sredstva ter je usposobljen za samostojno pripravo in izvedbo del. | The work may only be carried out by a contractor who is registered to carry out construction work and who has the appropriate insurance for such work, certificates, technically trained staff, resources and is qualified to prepare and carry out the work independently.
0.1.3 | Izvajalec odgovarja za kakovost izvedbe vseh del. | The Contractor shall be responsible for the quality of the execution of all works.
0.1.4 | Izvajalec nosi vso odgovornost za nesreče in škodo, ki nastane na objektu ali v okolici zaradi njegovega dela. | The Contractor shall bear all liability for accidents and damage to the installation or the surrounding area caused by his work.
0.1.5 | Pred oddajo ponudbe se je izvajalec dolžan seznaniti z območjem predvidenim za gradnjo in temu prilagoditi vsa potrebna dela, kar mora biti zajeto v ponudbi. V neposredni bližini predvidene gradnje se nahajajo stavbe, v katerih potekajo izobraževalni in raziskovalni procesi. Zato bo izvajalec moral izvajati kontrolo hrupa in kontrolo vibracij. Dela, ki so hrupna in dela, ki povzročajo vibracije bo izvajalec moral preprečiti oziroma jih izvesti na način, da povzročajo minimalne vplive. Tehnologijo rušenja, pilotiranja in tehnologijo izvedbe ostalih del bo izvajalec moral prilagoditi tako, da bo vpliv minimalen. Izvajalec mora preprečiti in zmanjšati emisije delcev iz gradbišča na najmanjšo možno mero. | Before submitting a tender, the contractor is obliged to familiarise himself with the area to be constructed and to adapt any necessary works accordingly, which must be included in the tender. In the immediate vicinity of the proposed construction, there are buildings in which educational and research processes take place. The contractor will therefore be required to carry out noise and vibration control. Noise and vibration works will have to be avoided or carried out in such a way as to minimise the impact. Demolition, piling and other works will have to be adapted to minimise the impact. The contractor must avoid and minimise the emission of particulates emitted from the construction site as far as is reasonably practicable.
0.1.6 | Izvajalec je pred oddajo ponudbe dolžan pregledati projektno dokumentacijo in ostale pogoje, ki so del razpisne dokumentacije V primeru morebitnih napak in neskladij je izvajalec dolžan na to opozoriti naročnika pred oddajo ponudbe. | The Contractor is obliged to review the project documentation and other conditions forming part of the tender documentation before submitting the tender In case of any errors or inconsistencies, the Contractor is obliged to bring these to the attention of the Contracting Authority before submitting the tender.
0.1.7 | Pred oddajo ponudbe je izvajalec dolžan preveriti ustreznost popisov del in količin v teh popisih ter njihovo skladnost z ostalimi dokumenti projektne dokumentacije, ki so del razpisne dokumentacije. Prav tako je izvajalec dolžan preveriti vse detajle in sheme. Vse izmere je potrebno preveriti po posameznih projektih oz. načrtih, ki sestavljajo razpisno dokumentacijo. V primeru ugotovljenih neskladij je v času priprave ponudbe obvezan o tem obvestiti naročnika. | Before submitting a tender, the Contractor shall check the adequacy of the inventories of works and quantities in these Bills of Quantities and their conformity with the other documents of the project documentation forming part of the tender documentation. The Contractor shall also check all details and diagrams. All measurements shall be checked against the individual projects or plans forming part of the tender documentation. In the event of any discrepancies, the Contractor shall inform the Contracting Authority at the time of preparing the tender.
0.1.8 | Pred oddajo ponudbe je izvajalec dolžan v tem popisu preveriti zmnožke in seštevke ter prenose le-teh v rekapitulacijo. Izvajalec se s pripravo ponudbe obvezuje, da je prebral vse celice in elemente celotnega popisa, vključno z vsemi postavkami in splošnimi navodili ali določili in je preveril pravilnost preračuna ter s tem zagotavlja ponudbeno vrednost. | Before submitting a tender, the Contractor is required to check the products and totals in this Bill of Quantities (BoQ) and their transfer to the recapitulation. The Contractor undertakes, by preparing a tender, to have read all the cells and elements of the complete BoQ, including all headings and general instructions or provisions, and to have checked the correctness of the conversion, thereby guaranteeing the value of the tender.
0.1.9 | Dela bo izvajalec moral izvajati po predloženi projektni dokumentaciji, detajlih in z upoštevanjem navodil in potrditev projektanta, nadzornika in investitorja. Vso potrebno delavniško dokumentacijo zagotovi izvajalec del v okviru ponujene cene. | The Contractor shall carry out the works in accordance with the submitted design documents, details and subject to the instructions and approvals of the Designer, the Supervisor and the Investor. All necessary workshop documentation shall be provided by the Contractor within the scope of the price quoted.
0.1.10 | Pred izvedbo posameznih del je izvajalec dolžan pregledati projektno dokumentacijo za izvedbo gradnje (PZI) in elaborate. Na morebitne napake v dokumentaciji ali neskladja med posameznimi načrti ali deli načrtov (popisi del, tehnična poročila, lokacijski in tehnični prikazi) izvajalec opozori nadzornika in projektanta, in se z njima pravočasno uskladi. | The Contractor shall review the Detailed Design documentation (PZI) and the studies before carrying out the individual works. The Contractor shall draw the attention of the Supervisor and the Designer to any errors in the documentation or discrepancies between the individual designs or parts of designs (BoQ, technical reports, location and technical drawings) and shall coordinate with them in good time.
0.1.11 | Tehnični opisi, prikazi, detajli, sheme ter ostali dokumenti v PZI dokumentaciji predstavljajo dodaten opis popisnih postavk gradbeno obrtniških in inštalacijskih del ter jih je potrebno dosledno upoštevati skupaj s popisom del. | The technical descriptions, illustrations, details, diagrams and other documents in the Detailed Design documentation (PZI) are additional descriptions of the BoQ inventory items of the building, construction and installation works and must be strictly followed together with the BoQ.
0.1.12 | Specifikacije in zahteve, navedene v popisu, se ne smejo upoštevati kot edine zahteve. Izvajalec je dolžan v ceni zajeti in dobaviti vse elemente opreme ter opraviti dela in storitve, ki niso eksplicitno navedeni, a so bistvenega pomena za funkcionalnost, skladnost s predpisi ter kontinuirano, zanesljivo in varno obratovanje opreme. | The specifications and requirements set out in the BoQ shall not be taken as the only requirements. The Contractor shall be obliged to include in the price and supply all items of equipment and to carry out works and services which are not expressly mentioned but which are essential for the functionality, regulatory compliance and continuous, reliable and safe operation of the equipment.
0.1.13 | Vsa dela morajo biti izvedena kvalitetno in iz materialov z zahtevanimi lastnostmi, izvedena skladno z veljavno zakonodajo in z upoštevanjem navodil za vgradnjo za izbrane materiale in opremo, s predložitvijo predpisanih izjav o lastnostih in/ali certifikatov. Vsi gradbeni proizvodi (GP) morajo biti označeni s CE oznako. | All work shall be of good quality and be executed with materials of the required characteristics, in accordance with the applicable legislation and in compliance with the installation instructions for the materials and equipment selected, and shall be accompanied by the prescribed declarations of performance and/or certificates. All construction products (GP) shall bear the CE marking.
0.1.14 | Za vsako opisano delo v popisu je potrebno upoštevati celotno potrebno delo, ves osnovni in pomožni material, prevoz materiala in orodja na objekt, notranje transporte, delovne in pomožne odre, zaključno čiščenje in odstranitev odpadkov po dovršenem delu. | For each work described in the inventory, the total work required, all basic and ancillary materials, the transport of materials and tools to the site, internal transports, working and ancillary scaffolding, final cleaning and the disposal of waste after the work has been completed must be taken into account.
0.1.15 | Vsa delovna sredstva, organizacija in koordinacija del, pripravljalna, spremljajoča in zaključna dela, potrebni montažni in tesnilni materiali ter podkonstrukcije so sestavni del posameznih postavk. | All labour, organisation and coordination of the works, preparatory, accompanying and finishing works, necessary prefabrication and sealing materials and substructures are part of the individual items.
0.1.16 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - načrt organizacije gradbišča s podrobnim terminskim planom in izvedba vseh pripravljalnih del, postavitev, organizacija, zaščita in prijava gradbišča, gradbiščnih objektov, ureditev začasnih deponij, tekoče vzdrževanje, skupaj s plačilom splošnih stroškov pristojbin in davkov upravnih organov, pridobivanju raznih dovoljenj in soglasij za izvedbo, ograditev gradbišča in postavitev gradbene table in prometne signalizacije, zagotavljanje ustrezne varnosti na gradbišču, tekoče vzdrževanje in končna odstranitev gradbišča; - zagotovitev potrebnih začasnih površin za transportne poti in gradnjo izven območja gradbišča s plačilom stroškov za sanacijo in vzpostavitev okoliških zemljišč in objektov v prvotno stanje (soglasja, odškodnine, itd.); - začasni odvoz, deponiranje in vračanje izkopanega materiala, ki ga ne bo možno deponirati na gradbišču; - odvoz in zagotovitev odstranjevanja odpadnega gradbenega materiala skladno z zakonodajo na področju ravnanja z odpadki (odvoz na urejene deponije s plačilom komunalnih prispevkov in taks itd.); - oteženi izkop v mokrem terenu, izkop v vodi, odvod meteorne vode iz gradbene jame in vode, ki se izceja iz bočnih strani izkopov; - ustrezno varovanje izkopa gradbene jame za objekt in ostalih manjših posameznih izkopov za izvedbo komunalne infrastrukture brez posegov na sosednja zemljišča; - ustrezno varovanje obstoječih objektov, infrastrukture in okolice v času gradnje ter dokumentiranje vseh morebitnih škodnih dogodkov; - pripravljalna, spremljajoča in zaključna dela (zakoličbe, zagotovitev potrebnih komunalnih priključkov za potrebe izvajanja gradnje, izvedba začasnih inštalacij, označevanje podzemnih vodov, postavljanje in vzdrževanje zakoličbenih profilov, izvedba in označevanje novih in starih križanj ter morebitna zaščita križanj komunalnih vodov, geodetski posnetki in izdajanje vmesnih posnetkov izvedene infrastrukture naročniku, izdelava zbirnih kart, itd.), v kolikor ni to drugače določeno; - pridobivanje soglasij in izvedba morebitnih zapor na vseh cestah s plačilom stroškov, nadomestil in pristojbin; - zagotovitev oz. postavitev in končna odstranitev po zaključku gradnje začasnih skladišč in začasnega pisarniškega kontejnerskega objekta vključno z opremo za dve delovni mesti in za skupne operativne sestanke vel. ca. 40 m2 za potrebe naročnika, s tekočim vzdrževanjem in čiščenjem. | The following must also be included or taken into account in the uniform prices for individual items: - a construction site organisation plan with a detailed timetable and the execution of all preparatory works, the setting-up, organisation, protection and registration of the construction site, site facilities, the arrangement of temporary storage facilities, ongoing maintenance, including the payment of general costs of fees and taxes of the administrative authorities, the obtaining of various permits and consents for the execution, the fencing of the site and the erection of construction signs and traffic signals, the provision of adequate security on the site, ongoing maintenance and the final dismantling of the construction site; - provision of the necessary temporary areas for transport routes and off-site construction, with costs for restoration and reinstatement of surrounding land and buildings (consents, compensation, etc.); - temporary removal, storage and return of excavated material that cannot be stored on site; - removing and disposing of waste building materials in accordance with waste management legislation (removal to regulated landfill sites with payment of municipal fees and charges, etc.); - difficult excavation in wet ground, excavation in water, drainage of rainwater from the construction pit and water draining from the sides of excavations; - adequate protection of the excavation of the construction pit for the building and other small individual excavations for the implementation of the utility infrastructure without encroaching on neighbouring land; - adequate protection of existing facilities, infrastructure and the surrounding area during construction, and documentation of any damage incidents; - preparatory, accompanying and finishing works (stake-out, provision of the necessary utility connections for the needs of construction, execution of temporary installations, marking of underground lines, installation and maintenance of stake-out profiles, execution and marking of new and old crossings and possible protection of crossings of utility lines, geodetic surveys and issuing of intermediate images of the completed infrastructure to the client, production of summary maps, etc.), unless otherwise specified; - obtaining consents and implementing any road closures, with costs, compensation and fees; - provision or erection and final removal on completion of construction of temporary storage and temporary office container building including equipment for two workstations and for joint operational meetings of approx. 40 m2 for the needs of the client, with ongoing maintenance and cleaning.
0.1.17 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - izdelava montažne tehnične dokumentacije, detajlov izvedbe in vse druge potrebne delavniške dokumentacije (s področja arhitekture, gradbeništva, elektrotehnike, strojništva in zunanje ter krajinske ureditve) ter pridobitev obvezne potrditve s strani projektanta, nadzornika in investitorja; - odprava vseh vrst inštalacijskih kolizij z izvajanjem potrebnih premikov inštalacij in njihovim usklajevanjem na mestu montaže, vse v obsegu, ki ne vpliva na projektirano rešitev ali tip inštalacij oz. opreme; - zagotavljanje kompletnosti elektro-instalacijskih sistemov s področja avtomatike za doseganje njihove popolne funkcionalnosti delovanja; - stroški za nadzor in koordinacijo izvedbe vseh elektro napeljav, ki so predmet končne instalacije proizvoda (senčila, vrata, okna,…); - izdelava montažnih skic in detajlov za izvedbo v dogovoru z vodjo gradnje in nadzornikom; - izdelava in predstavitev vzorcev v ustrezni velikosti za potrditev projektanta, nadzornika in investitorja; - zagotavljanje varnosti in zdravja pri delu, zlasti izvajanje vseh del, ki izhajajo in ukrepov, ki izhajajo iz določil veljavnih predpisov varstva pri delu in zahtev Varnostnega načrta;- stroški garancij, ki jih mora izvajalec predložiti naročniku. | The following must also be included or taken into account in the uniform prices for individual items: - preparation of prefabricated technical documentation, construction details and all other necessary workshop documentation (architectural, civil, electrical, mechanical, exterior and landscaping) and obtaining the mandatory approval of the designer, the supervisor and the investor; - elimination of all types of installation conflicts by carrying out the necessary relocation of installations and their coordination at the installation site, all to the extent that it does not affect the design solution or the type of installation or equipment; - ensuring the completeness of electrical installation systems in the automation sector to achieve their full operational functionality; - the cost of supervising and coordinating the installation of all the electrical installations that are the subject of the final installation of the product (blinds, doors, windows, etc.); - preparation of erection drawings and details for implementation in agreement with the construction manager and supervisor; - production and presentation of samples in appropriate sizes for the approval of the designer, the supervisor and the investor; - ensuring health and safety at work, in particular the implementation of all the works arising from and the measures resulting from the provisions of the applicable occupational safety regulations and the requirements of the Safety Plan; - the cost of the guarantees to be provided by the contractor to the client.
0.1.18 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - strošek vodje del glavnega izvajalca, ki bo izvajal tudi koordinacijo s podizvajalci in z drugimi izvajalci, ki jih bo izbral naročnik in bo opravljal delo vodje gradbišča; - koordinacija del z ostalimi izvajalci oz. podizvajalci del, projektantom, nadzornikom in investitorjem pri medsebojnem usklajevanju organizacije gradbišča in časovnega načrta del ter pri usklajevanju izdelave plana montaže, potrjenih s strani vseh udeležencev gradnje; - stroški koordinacije, sodelovanja in usklajevanja z dobavitelji tehnološke, laboratorijske, eksperimentalne in vse ostale pohištvene ter multimedijske opreme ter z vsemi ostalimi dobavitelji oz. podizvajalci na objektu; - stroški izdelave situacij; - stroški zavarovanja objekta v času izvedbe del in delavcev ter materiala na gradbišču v času izvajanja del, od začetka del do pridobitve uporabnega dovoljenja za objekt. Zavarovanje mora biti sklenjeno pri ustrezni zavarovalni družbi najmanj v višini pogodbene vrednosti ali v zakonsko predpisani vrednosti (v kolikor zavarovanje v višini pogodbene vrednosti presega zakonsko dovoljeno), za ves čas trajanja izvedbe del do uspešne primopredaje objekta; - preizkušanje kvalitete materiala, ki se vgrajuje in dokazovanje kvalitete s certifikati oz. tehničnimi soglasji; - izvedba vseh zahtevanih testov in preizkusov (npr. tlačni preizkusi, termografski pregledi, meritve elektromagnetnega sevanja, hrupa, itd.), poskusnega obratovanja celotnega objekta s poudarkom na vseh inštalacijah ter izvajanje predpisanega monitoringa v skladu s Poročilom o vplivih na okolje (pred gradnjo, med gradnjo in po končani gradnji); - izdelava izkaza požarne varnosti, vključno s sprotnim spremljanjem gradnje in izvajanjem požarnovarnostnih zahtev ter izdelava Požarnega reda z obveznimi prilogami; - izdelava Izkaza zaščite pred hrupom v stavbah; - izdelava Izkaza energijskih lastnosti stavbe in energetske izkaznice; - sodelovanje z izvajalci gradbenega in projektantskega nadzora in investitorjem za izvedbo tehničnega pregleda in priprava primopredaje, ki mora vsebovati vso zahtevano dokumentacijo, predvsem pa: izjave o skladnosti, požarni izkaz in ostale izkaze ter obvezne tabele, dokazilo o zanesljivosti objekta (DZO), certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo in vzdrževanje ter vse ostale dokumente v skladu s predpisi in pogodbenimi določili. | The following must also be included or taken into account in the uniform prices of the individual items: - the cost of a works manager for the main contractor, who will also coordinate with subcontractors and other contractors selected by the client and act as site manager; - coordination of the works with other contractors or subcontractors, the designer, the supervisor and the investor in coordinating the organisation of the construction site and the timetable for the works, and in coordinating the production of an installation plan approved by all the participants in the construction; - the costs of coordination, cooperation and coordination with suppliers of technological, laboratory, experimental and all other furniture and multimedia equipment, as well as with all other suppliers or subcontractors on the site; - the cost of drawing up situations; - the cost of insuring the building during the execution of the works and the workers and materials on site during the execution of the works, from the start of the works until the building has been licensed for occupation. The insurance must be taken out with a suitable insurance company for at least the contract value or the legal value (if the insurance for the contract value exceeds the legal value), for the entire duration of the works until the successful handover of the building; - testing the quality of the material to be installed and proving it with certificates or technical approvals; - carrying out all required tests and trials (e.g. pressure tests, thermographic inspections, electromagnetic radiation measurements, noise measurements, etc.), trial operation of the entire building, with emphasis on all installations, and carrying out the required monitoring in accordance with the Environmental Impact Assessment Report (before, during and after construction); - preparation of a fire safety statement, including ongoing monitoring of construction and implementation of fire safety requirements, and preparation of a Fire Safety Order with mandatory annexes; - preparation of a Noise Protection Statement for buildings; - preparation of the Building Energy Performance Report and Energy Performance Certificate; - cooperation with the construction and design supervision contractors and the investor to carry out the technical inspection and prepare the handover, which must include all the required documentation, in particular: declarations of conformity, fire and other statements and mandatory tables, proof of reliability of the building (DZO), certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use and maintenance, and all other documents in accordance with the regulations and the contractual provisions.
0.1.19 | V enotnih cenah posameznih postavk, ki se nanašajo na opremo in posamezne sisteme, mora biti zajeto oz. upoštevano tudi naslednje: - dobava oz. transport, - stroški za vse delovne stroje za dvigovanje bremen in delovne košare za dostope do delovišč; - morebitni stroški povzročeni upravljavcem GJI, ki bi nastali v zvezi s predmetno gradnjo; - montaža, vključno s pomožnim montažnim materialom (vezni, tesnilni in pritrdilni material, sidra, nosilni profili, podkonstrukcije in podobno) in navodili proizvajalca, - odprava vseh kolizij sistemov s stenami in med sistemi, - izvedba vseh potrebnih tesnjenj, - priključitev in nastavitve, vključno z morebitnim kalibriranjem, - zagon, testiranje in meritve, vključno s poročili, - šolanje uporabnikov oz. vzdrževalnega osebja za uporabo in vzdrževanje sistemov, - navodila za obratovanje in vzdrževanje, - vsi potrebni certifikati, izjave o skladnosti oz. potrdila ter - vsa druga pomožna dela in material, da se zagotovi funkcionalnost posamezne postavke popisa. | The following must also be included or taken into account in the uniform prices for individual items relating to equipment and individual systems: - delivery/transport, - the cost of all lifting machines and work baskets for access to work sites; - any costs incurred to the operators of utility infrastructure (GJI) in connection with the subject construction; - installation, including ancillary installation materials (bonding, sealing and fixing materials, anchors, support profiles, substructures, etc.) and manufacturer's instructions, - eliminating all system-to-wall and system-to-system collisions, - all necessary sealing work, - connection and set-up, including calibration if necessary, - commissioning, testing and measurements, including reports, - training users or maintenance staff in the use and maintenance of the systems, - operating and maintenance instructions, - any necessary certificates, declarations of conformity or attestations; and - all other ancillary works and materials to ensure the functionality of each inventory item.
0.1.20 | Vsi odri morajo biti upoštevani v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All scaffolding must be included in the uniform prices of the items listed, except where specifically mentioned.
0.1.21 | Vsi delovni in pomožni odri, lestve in ostala potrebna pomožna sredstva, kot tudi čiščenje vseh elementov po končanih delih, mora biti upoštevano v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All working and auxiliary scaffolding, ladders and other necessary ancillaries, as well as the cleaning of all elements after completion of the works, shall be included in the uniform prices of the items listed, except those specifically mentioned.
0.1.22 | Delavniško dokumentacijo za vse nosilne jeklene konstrukcije in podkonstrukcije izdela izvajalec, strošek izdelave delavniške dokumentacije se upošteva v ponujenih cenah in se ne obračuna posebej. | The cost of the shop drawings for all steelwork and substructures shall be included in the prices quoted and shall not be charged separately.
0.1.23 | V enotnih cenah postavk mora biti vključeno tudi vgrajevanje vseh instalacijskih razvodov v opaže armirano betonskih elementov in izdelava prehodov inštalacij ter dodatno izrezovanje utorov in prebojev v kamnite, zidane ali armirano-betonske stene, ponovno demontiranje in montiranje vseh vrst montažnih sten, vsa dodatna dela za zagotavljanje primernih križanj med posameznimi instalacijskimi vodi, izdelava vseh vrst ojačitev konstrukcij in podobna dela, ki zagotavljajo kakovostno vgradnjo vseh vrst instalacijskih vodov in niso posebej navedena v popisu GOI del. V ponudbi morajo biti upoštevana vsa drobna strojna in elektro instalacijska dela in transporti. | The installation of all installation ducts in the formwork of reinforced concrete elements and the construction of installation penetrations, as well as the additional cutting of grooves and penetrations in stone, masonry or reinforced concrete walls, the reassembly and reinstallation of all types of prefabricated walls, all additional work to ensure adequate crossings between individual installation ducts, the construction of all types of structural reinforcement and similar work to ensure the quality installation of all types of installation ducts and not specifically mentioned in the BoQ of the Construction, installation and finishing works (GOI) shall also be included in the uniform prices of the items. The tender shall take into account all minor mechanical and electrical installation work and transport.
0.1.24 | Vsi kovinski elementi in konstrukcije, ki bi lahko bili izpostavljeni atmosferskim in ostalim korozijskim vplivom, morajo biti ustrezno protikorozijsko zaščiteni. | All metallic elements and structures that could be exposed to atmospheric and other corrosive influences must be adequately protected against corrosion.
0.1.25 | Za vse večje jeklene dele se skladno s predpisi, izdelajo ustrezne ozemljitve, nevidno pritrjene in speljane na splošno ozemljitev objekta. | For all major steel parts, appropriate earth connections shall be made in accordance with the regulations, invisibly attached and connected to the general earth of the building.
0.1.26 | Za vse vidne elemente in serijske elemente je obvezna predhodna uskladitev obdelav, barv in materialov s projektantom na podlagi dostavljenih vzorcev v ustrezni velikosti. Obvezna je preveritev dejanskih mer na licu mesta in posledična prilagoditev elementov in njihove montaže. | For all visible elements and serial elements, it is mandatory to coordinate the finishes, colours and materials with the designer beforehand on the basis of the supplied samples in the appropriate size. It is mandatory to check the actual dimensions on site and to adjust the elements and their installation accordingly.
0.1.27 | Dimenzije obrtniških izdelkov in količine je potrebno pred naročanjem preveriti na objektu. Potrebna je uskladitev vseh elementov (kljuke, okovje, detajlne konstrukcije in obdelave, itd.) s projektantom, nadzornikom in investitorjem. Izvajalec je dolžan pred izdelavo predložiti projektantu v potrditev ustrezne delavniške načrte in detajle. | The dimensions of the workmanship and quantities must be checked on site before ordering. All elements (hooks, fittings, detailed construction and finishes, etc.) must be coordinated with the designer, the supervisor and the investor. The contractor is obliged to submit the relevant workshop plans and details to the designer for approval before manufacture.
0.1.28 | V posameznih postavkah popisa so navedeni proizvajalci in/ali tipi posameznih sistemov, materialov ali opreme, s čimer so zgolj natančno opredeljene zahtevane tehnične lastnosti. Izvajalec del lahko ponudi nadomesten sistem, material ali opremo drugega proizvajalca in tipa, pri čemer morajo biti tehnične lastnosti ponujenega sistema, materiala ali opreme enakovredne ali boljše od opredeljenih v popisu, dimenzijsko pa ne smejo presegati projektiranih dimenzij. Vse funkcijske in tehnične karakteristike nadomestnih sistemov, materialov ali opreme mora izvajalec dokazati z ustrezno dokumentacijo. Vse morebitne posledice zaradi spremembe sistemov, materialov ali opreme vključno z morebitnimi spremembami oz. dopolnitvami BIM modelov in projektne dokumentacije, stroškovno in časovno bremenijo izvajalca. | The individual items of the Inventory shall specify the manufacturers and/or types of the individual systems, materials or equipment, thereby merely specifying the required technical characteristics. The Contractor may offer a substitute system, material or equipment of a different manufacturer and type, provided that the technical characteristics of the offered system, material or equipment shall be equivalent to or better than those specified in the BoQ, and shall not exceed the design dimensions. All functional and technical characteristics of the substitute systems, materials or equipment shall be demonstrated by the Contractor with appropriate documentation. Any consequences resulting from changes to systems, materials or equipment, including any changes or additions to the BIM models and project documentation, shall be borne by the Contractor in terms of cost and time.
0.1.29 | Vsako zamenjavo, uporabo in končni izbor nadomestnih sistemov, materialov, proizvodov in opreme morajo obvezno in pravočasno (pred dobavo in vgradnjo) pisno potrditi projektant (vseh sodelujočih strok), nadzornik in investitor. | Any replacement, use and final selection of alternative systems, materials, products and equipment must be approved in writing by the designer (of all disciplines involved), the supervisor and the investor in a timely manner (prior to delivery and installation).
0.1.30 | Izvajalec mora v ponudbeno ceno vključiti tudi: - ves čas gradnje sprotno beleženje sprememb oz. odstopanj od PZI dokumentacije, vključno z izdelavo tekstualnega opisa sprememb, - pripravo podlog na nivoju PZI, ki so potrebne za posodobitev oz. uskladitev BIM modela z izvedenim stanjem (LOD 500) in izdelavo projektne dokumentacije izvedenih del (PID), - mesečno predajanje potrjenih sprememb opreme in materiala, ki vplivajo na BIM model, v formatu IFC, - vzdrževanje in uporabljanje pri izvedbi zadnje veljavne revizije PZI dokumentacije, vključno z dopolnitvami PZI načrtov, ki so nastali zaradi sprememb med gradnjo. | The contractor must also include in the tender price: - keeping a record of changes or deviations from the construction documentation (PZI) throughout construction, including a textual description of the changes, - preparation of the Detailed Design (PZI) level documents required to update or align the BIM model with the as-built condition (LOD 500) and the preparation of the as-built project documentation for the works (PID), - monthly submission of approved equipment and material changes affecting the BIM model in IFC format, - maintenance and use in the execution of the last valid revision of the construction documentation (PZI), including additions to the construction design documentation (PZI) resulting from changes during construction.

## 0.2_Uvod-DGNB
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
0.2 | SPLOŠNI TEHNIČNI POGOJI ZA PODROČJE DGNB CERTIFICIRANJA | GENERAL TECHNICAL CONDITIONS FOR DGNB CERTIFICATION
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic entity with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
| Splošni pogoji za področje DGNB certificiranja predstavljajo dopolnilo splošnim tehničnim pogojem in ne odpravljajo drugih obveznosti in odgovornosti, ki jih ima izvajalec v skladu s predpisi in pogodbo. | The General Conditions for DGNB Certification are complementary to the General Technical Conditions and do not exclude other obligations and responsibilities that the Contractor has under the Regulations and the Contract.
0.2.1 | Izvajalec mora v svojih ponudbah upoštevati, da se bo objekt certificiral v skladu z zahtevami DGNB sistema certificiranja trajnostne gradnje, ter pravočasno (vsaj 60 dni pred vgradnjo posameznega produkta) dostaviti vso ustrezno dokumentacijo za vse v ponudbi zajete materiale, elemente in opremo. Zahtevana je uporaba materialov, elementov ali opreme, ki so okolju in ljudem prijazni, energetsko učinkoviti in obenem ustrezajo zahtevam DGNB sistema. Zahtevan nivo certifikata je: ZLATI CERTIFIKAT | The Contractor shall take into account in its tenders that the building will be certified in accordance with the requirements of the DGNB Sustainable Building Certification Scheme and shall deliver all relevant documentation for all materials, elements and equipment included in the tender in a timely manner (at least 60 days before the installation of each product). The use of materials, elements or equipment that are environmentally and human friendly, energy efficient and at the same time meet the requirements of the DGNB system is required. The required level of certification is: GOLD CERTIFICATE
0.2.2 | Podrobnejši opis DGNB sistema in navodila za posamezne kriterije so dostopna v dokumentu"DGNB Criteria Set New Construction Buildings, Version 2020 International", ki je na voljo na DGNB spletni strani https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria | A more detailed description of the DGNB system and guidance on the individual criteria is available in the document "DGNB Criteria Set New Construction Buildings, Version 2020 International", available on the DGNB website https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria
0.2.3 | Izvajalec mora v svojih ponudbah upoštevati, da je potrebno skladno z določili DGNB certifikacijskega sistema, pravočasno (pred pričetkom gradnje) dostaviti vso ustrezno dokumentacijo, za vse v ponudbi zajete materiale, elemente in opremo (tehnični list, varnostni list, izjava o lastnostih, tehnična navodila za ravnanje, servisiranje, vzdrževanje,...) v slovenskem jeziku. Vgradnja kakršnihkoli materialov, elementov ali opreme, se izvede zgolj na podlagi predhodne preveritve posredovane dokumentacije in obenem potrditve s strani nadzornika. | The Contractor must take into account in its tenders that, in accordance with the provisions of the DGNB certification system, all relevant documentation for all materials, elements and equipment included in the tender (technical data sheet, safety data sheet, declaration of properties, technical instructions for handling, servicing, maintenance,...) must be delivered on time (prior to the start of construction) in the Slovene language (in accordance with the provisions of the DGNB certification system). The installation of any materials, elements or equipment shall be subject to prior checking of the submitted documentation and, at the same time, to the approval of the Supervisor.
0.2.4 | Izbrani materiali, elementi, naprave, sistemi in oprema morajo prispevati k večji trajnosti stavbe v smeri zagotavljanja energetske učinkovitosti, ekonomičnega in enostavnega vzdrževanja ter čiščenja, dolge življenjske dobe, uporabe okolju prijaznih materialov ipd. | The materials, elements, appliances, systems and equipment chosen must contribute to the sustainability of the building in terms of energy efficiency, economic and easy maintenance and cleaning, long lifetime, use of environmentally friendly materials, etc.
0.2.5 | Predloženi dokumenti za vse uporabljene materiale, elemente in opremo morajo izpolnjevati zahteve najmanj kakovostne stopnje QS3 (zaželeno QS4), iz dokumenta: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001) | The documents submitted for all materials, components and equipment used shall meet the requirements of at least quality level QS3 (preferably QS4) of the document DGNB Quality Grades for Materials, Components and Equipment (JULFS--7X9001)
0.2.6 | V kolikor izbrani materiali oz. elementi, navedeni v posameznih postavkah, ne ustrezajo vsaj kakovostni stopnji QS3 iz seznama: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), je izvajalec dolžan na to opozoriti projektanta, nadzor in investitorja ter podati predlog ustreznega materiala oz. elementa. | If the selected materials or elements listed in the individual items do not meet at least quality level QS3 of the list of DGNB quality classes for materials, elements and equipment (JULFS--7X9001), the Contractor shall draw this to the attention of the Designer, the Supervisor and the Investor, and shall make a proposal for a suitable material or element.
0.2.7 | Izvajalec lahko v svoji ponudbi predlaga alternativne produkte in rešitve glede na predvidene s projektom, pod pogojem, da le-te prav tako izpolnjujejo vse navedene zahteve. Pri morebitnih predlaganih alternativnih produktih oz. rešitvah je potrebno upoštevati najmanj enake ali boljše lastnosti v smislu življenjske dobe, obstojnosti, ter enostavnosti in stroška čiščenja ter vzdrževanja v primerjavi s projektom predpisanimi rešitvami. Za alternativne rešitve izvajalec pridobi soglasje projektanta, nadzornika in investitorja pred pričetkom gradnje. | The Contractor may propose alternative products and solutions to those envisaged by the project in its tender, provided that they also meet all the requirements set out above. Any alternative products or solutions proposed shall have at least the same or better characteristics in terms of service life, durability, and ease and cost of cleaning and maintenance compared to the solutions envisaged by the project. For alternative solutions, the contractor shall obtain the agreement of the designer, the supervisor and the investor before starting construction.
0.2.8 | Izvajalec med gradnjo dnevno beleži vsa eventualna odstopanja od PZI projektne dokumentacije ter podatke pravočasno posreduje naročniku, nadzoru in projektantu. Potrjene spremembe vnese v podlage za izdelavo PID in posodobitev BIM modelov. | During construction, the Contractor shall record on a daily basis any deviations from the Detailed Design documentation (PZI) and shall provide the information to the Client, Supervision and the Designer in a timely manner. Confirmed changes shall be entered into the basis for the As-built documentation (PID) and BIM model updates.
0.2.9 | Izvajalec med gradnjo sproti izpolnjuje Seznam vseh konstrukcijskih sestav s pripadajočimi vgrajenimi gradbenimi materiali in dokumentira naslednje podatke o vgrajenih materialih (v slovenskem jeziku): - Varnostni list - Tehnični list - Izjavo o lastnostih (če je relevantno) - Izkazovanje morebiti obstoječega okoljskega certifikata (Tip I - okoljski znak ali Tip III - okoljska produktna deklaracija /EPD) - Izjavo proizvajalca ali dobavitelja, da produkt ustreza zahtevam ENV1.2 - Tehnična navodila za ravnanje, servisiranje, vzdrževanje oziroma ostale, z zakonom predpisane dokumente in dokumentacijo. | During construction, the Contractor shall keep a List of all structural assemblies with their associated construction materials and document the following information on the materials installed (in Slovene language): - Safety Data Sheet - Technical Data Sheet - Declaration of performance (if applicable) - Demonstration of any existing environmental certification (Type I - Ecolabel or Type III - Environmental Product Declaration /EPD) - A declaration by the manufacturer or supplier that the product complies with the requirements of ENV1.2 - Technical instructions for handling, servicing, maintenance or other documents and documentation required by law.
0.2.10 | Za vse vgrajene bistvene tehnične sisteme mora izvajalec zagotoviti obstoj pooblaščenega servisa, ki deluje na območju Republike Slovenije, da ima investitor možnost skleniti ustrezno pogodbo o vzdrževanju. Med bistvene tehnične sisteme sodijo npr.: sistemi ogrevanja in hlajenja, priprava tehnoloških medijev, prezračevanje in klimatizacija, sistemi detekcije in gašenja požara, sistemi tehničnega varovanja, BMS in CNS sistemi upravljanja stavbe, razsvetljava, komunikacijski in WI-FI sistemi,... | For all installed essential technical systems, the contractor must ensure the existence of an authorised service centre operating in the territory of the Republic of Slovenia, so that the investor has the possibility of concluding an appropriate maintenance contract. The essential technical systems include, for example: heating and cooling systems, technological media preparation, ventilation and air conditioning, fire detection and extinguishing systems, technical security systems, BMS and CNS building management systems, lighting, communication and WI-FI systems,...
0.2.11 | Zaželeno je, da imajo uporabljeni elementi in materiali okoljsko oznako Tip I. (kot npr. ENCODE, BLUE ANGEL, ipd...). | It is preferable that the elements and materials used have a Type I environmental label (such as ENCODE, BLUE ANGEL, etc...).
0.2.12 | Izvajalec bo za elemente iz lesa moral dokazovati izvor z navedbo izvorne države in tipa lesa, FSC / PEFC certifikat z dodatnim pripadajočim potrdilom Chain of custody-trgovski certifikat dobavitelja - ta se dokazuje z dobavnicami, računi ali enakovredno. Za izdelke iz naravnega kamna iz EU držav je potrebna deklaracija, da je izvor in procesiranje teh izdelkov v celoti v EU državah. Za izdelke iz naravnega kamna, ki prihajajo iz držav izven EU, je potrebno predložiti dokazilo o izpolnjevanju ILO konvencije 182, ki vključuje neodvisna inšpekcijska poročila. | For wood elements, the contractor will be required to provide proof of origin, indicating the country of origin and the type of wood, FSC/PEFC certification with an additional Chain of Custody certificate - the supplier's trade certificate - this shall be evidenced by delivery notes, invoices or equivalent. For natural stone products from EU countries, a declaration that the sourcing and processing of these products is entirely in EU countries is required. For natural stone products from non-EU countries, proof of compliance with ILO Convention 182, including independent inspection reports, is required.
0.2.13 | Izobraževanje udeležencev pri gradnji Izvajalec je dolžan vse udeležence pri gradnji podrobneje seznaniti tudi z relevantnimi koncepti, študijami, elaborati, ki opredelujejo trajnostni način gradnje za naslednja področja: - zaščita pred hrupom (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)) - zaščita pred prašenjem - zaščita tal in podzemne vode (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)), Analiza tveganja za onesnaženje vodnega telesa podzemne vode št. 0346-023/2023, maj 2023 (Geološko projektiranje d.o.o.)) - ravnanje z gradbenimi odpadki (Načrt gospodarjenja z gradbenimi odpadki) Izobraževanja se izvajajo skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.1 1.2, 2.2, 3.2 in 4.2 Training for the parties implementing the construction work | Training of construction participants The contractor is also obliged to inform all construction participants in detail about relevant concepts, studies, elaborations defining sustainable construction methods for the following areas: - noise protection (Environmental Impact Assessment Report No 100123-11523, dated 11.5.2023, supplemented on 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.)) - dust protection - protection of soil and groundwater (Environmental Impact Assessment Report No. 100123-11523, dated 11.5.2023, supplemented 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.), Risk analysis for contamination of the groundwater No. 0346-023/2023, May 2023 (Geološko projektiranje d.o.o.)) - construction waste management (Construction Waste Management Plan) The training shall be carried out in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.1 1.2, 2.2, 3.2 and 4.2 Training for the parties implementing the construction work
0.2.14 | Navodila za obratovanje in vzdrževanje objekta Izvajalec pripravi Navodila za obratovanje in vzdrževanje objekta skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilih: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual | Instructions for the operation and maintenance of the facility The Contractor shall prepare the Operation and Maintenance Instructions for the Facility in accordance with the applicable Slovenian legislation and the DGNB System Instructions specified in the Criteria: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual
0.2.15 | Meritve kontrole kakovosti gradnje Izvajalec mora upoštevati, da se bodo po koncu gradnje izvedle naslednje meritve: - meritve zrakotesnosti - meritve s termokamero (termografija) - meritve akustike - meritve zvočne zaščite ovoja stavbe - meritve zvočne zaščite ločilnih elementov med posameznimi prostori različnih namembnosti - meritve udarnega zvoka - meritve vlažnosti vgrajenih elementov, pred vgradnjo finalnih tlakov - test odvoda dima in toplote Meritve morajo opraviti ustrezno usposobljeni preskusni organi ali strokovnjaki ter rezultate oceniti in primerjati z zahtevami. Obseg opravljenih meritev mora biti sorazmeren z velikostjo zgradbe in mora ustrezno odražati cilj preverjanja kakovosti zgradbe. Smiselno je, da izvajalec del tekom gradnje za sprotno kontrolo kakovosti vgrajenih materialov, elementov in opreme, sam izvaja meritve. Končne meritve (ob primopredaji) izvede tretja oseba kot neodvisna potrditev doseganja zahtev. Meritve se izvajajo skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 2. Quality control measurements | Construction quality control measurements The contractor must take into account that the following measurements will be carried out after completion of the construction: - airtightness measurements - thermal camera measurements (thermography) - acoustics measurements - measurements of the sound insulation of the building envelope - measurements of the sound insulation of the separating elements between different rooms of different uses - impact sound measurements - moisture measurements of the installed elements, prior to the installation of the final flooring - smoke and heat extraction test The measurements shall be carried out by suitably qualified test bodies or experts and the results evaluated and compared with the requirements. The extent of the measurements carried out shall be proportionate to the size of the building and shall adequately reflect the objective of the building quality verification. It is reasonable for the contractor to carry out his own measurements during construction to check the quality of the materials, elements and equipment installed. Final measurements (at handover) are carried out by a third party as an independent confirmation of compliance with the requirements. The measurements shall be carried out in accordance with the applicable Slovenian legislation and the DGNB system instructions specified in the benchmark: PRO 2.2 2. Quality control measurements
0.2.16 | Zagotavljanje kakovosti za uporabljene gradbene proizvode Izvajalec mora zagotavljati izvajanje primerjav med definiranim in dejansko uporabljenim materialom, elementom ali opremo skladno seznamom: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), vključno z dokazno dokumentacijo ugotovitev primerjav ter skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 3.1 Quality assurance for the used construction products | Quality assurance for the construction products used The Contractor shall ensure that comparisons are made between the defined and the actual material, element or equipment used in accordance with the list: DGNB Quality Grades of Installed Materials, Elements and Equipment (JULFS--7X9001), including supporting documentation of the findings of the comparisons, and in accordance with the DGNB system instructions defined in the Criterion: PRO 2.2 3.1 Quality assurance for the used construction products
0.2.17 | Zaščita pred vlago Izvajalec predloži dokumentacijo, ki dokazuje, da je bil izveden program prezračevanja, prilagojen stavbi, s čimer se zagotovi pogoje, da so vgrajeni gradbeni elementi ustrezno suhi, skladno z navodili DGNB opredeljenimi v merilu: PRO 2.2 4.1 Mould prevention | Protection against moisture The Contractor shall provide documentation demonstrating that a building-specific ventilation programme has been implemented to ensure that the building elements installed are adequately dry, in accordance with the DGNB guidelines specified in the criteria: PRO 2.2 4.1 Mould prevention
0.2.18 | Preizkusi delovanja sistemov Izvajalec sodeluje pri izvedbi predhodnega in končnega preizkusa delovanja vseh bistvenih tehničnih komponent stavbe in pripravi ustrezne dokazne dokumentacije ter pri usposabljanju vzdrževalcev/upravljalcev stavbe, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators | System performance tests The Contractor shall be involved in the performance of the preliminary and final performance tests of all essential technical components of the building and the preparation of the relevant supporting documentation, as well as in the training of the maintenance/management staff of the building, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators
0.2.19 | Poročilo o zagonu objekta Izvajalec sodeluje pri pripravi končnega poročila o zagonu objekta, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 5.1 Creation of a detailed final report | Commissioning report The Contractor shall be involved in the preparation of the final commissioning report, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 5.1 Creation of a detailed final report
0.2.20 | Koncept celovitega delovanja sistemov v stavbi Izvajalec sodeluje pri procesu implementiranja stalnega nadzora in nastavitev delovanja stavbe ter usposabljanju vzdrževalcev/upravljalcev stavbe. Navedeno se izvede v skladu z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 6.1 Creation and handover of an integral operating concept | The concept of integrated building systems The contractor is involved in the process of implementing the building's continuous monitoring and settings and training the building's maintenance/management staff. This shall be done in accordance with the DGNB system instructions defined in the benchmark: PRO 2.3 6.1 Creation and handover of an integral operating concept
0.2.21 | Prilagoditev nastavitev sistemov po začetni fazi uporabe objekta Izvajalec sodeluje pri ponovnem pregledu delovanja vseh bistvenih tehničnih sistemov ter eventualni ponovni prilagoditvi teh sistemov s strani strokovnjaka oz. (neodvisne) tretje osebe. Postopek se izvede po približno 10–14 mesecih po zaključku gradnje, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 7.1 Readjustment of the system following initial operating phase | Adjusting system settings after the initial phase of use of the building The Contractor shall be involved in the re-examination of the functioning of all essential technical systems and the possible re-adjustment of these systems by an expert or (independent) third party. The procedure shall be carried out approximately 10-14 months after completion of construction, in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.3 7.1 Readjustment of the system following initial operating phase

## 4.6.0_Rekapitulacija
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
| REKAPITULACIJA STROŠKOV STROJNIH DEL | COST SUMMARY OF MECHANICAL WORKS
| 4 NAČRT S PODROČJA STROJNIŠTVA | 4 DOCUMENTATION IN THE FIELD OF MECHANICAL ENGINEERING
| 4/6 Geosonde | 4/6 Borehole Heat Exchangers
4.6 | STROJNA DELA | MECHANICAL WORKS
4.6.1 | GEOSONDE | BOREHOLE HEAT EXCHANGERS | 0
0
0 | NEPREDVIDENA DELA | UNFORSEEN WORKS | 0
| SKUPAJ STROJNA DELA: | TOTAL MECHANICAL WORKS: | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT

## 4.6.1_Geosonde
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.6 | STROJNA DELA | MECHANICAL WORKS
4.6.1 | GEOSONDE | BOREHOLE HEAT EXCHANGERS |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
1 | GEOSONDE | BOREHOLE HEAT EXCHANGERS
| Izvajalec del in dobavitelj opreme geosond mora imeti delovne reference za izdelavo geosond (vertikalnimi zemeljskimi prenosniki toplote) za globine do najmanj 140 m. | The contractor and supplier of the geoprobe equipment shall have a working reference for the construction of geoprobes (vertical ground heat exchangers) for depths of at least 140 m.
| Vse postavke v nadalevanju zajemajo dobavo in montažo (razen tam kjer je to posebej navedeno). | All items below include delivery and installation (except where specifically indicated).
1.1 | Zakoličba za geosonde, vzdrževanje točk vrtanja ter koordinacija vgradnje geosonde: | Geoprobe emplacement, maintenance of drilling points and coordination of geoprobe installation:
| - zakoličbo geosond izvede geodet, ki izvaja zakoličbo pilotov in temeljev, | - the geoprobe is located by the surveyor who locates the piles and foundations,
| - razporditev pozicij geosond po načrtu glede na pozicije pilotov in temeljev stavbe, | - alignment of the geoprobe positions according to the plan with respect to the pile and foundation positions of the building,
| - zakoličbeni zapisnik ter certifikat geodeta, | - a record of the location and a surveyor's certificate,
| - vzdrževanje točk vrtanja | - maintenance of drilling points
| - koordinacija vgradnje geosonde | - coordinating the installation of a geoprobe | kpl | 230 |  | 0
1.2 | Vrtanje za geosonde, sodelovanje pri zakoličbi, pripravljalna dela vrtanja, vrtenje v večih stopnjah, čiščenje vrtine, hidravlično testiranje, odvoz materiala ter koordinacija vgradnje geosonde: | Drilling for geoprobes, participation in the logging, drilling preparation, multi-stage drilling, borehole cleaning, hydraulic testing, material removal and coordination of the geoprobe installation:
| - sodelovanje pri zakoličbi, razporditev pozicij geosond po načrtu glede na pozicije pilotov in temeljev stavbe, | - participation in the stake-out, alignment of the geoprobe positions according to the plan with respect to the pile and foundation positions of the building,
| - pripravljalna dela vrtanja in postavitev opreme: ureditev delovnega platoja, postavitev vrtalnih garnitur, kompresorja, vrtalnega drogovja, obložne cevi, agregata in ostale pripadajoče opreme, premikanje opreme med lokacijami geosond, | - preparatory drilling and equipment set-up: setting up the working pad, setting up the drill sets, compressor, drill rod, casing, aggregate and other associated equipment, moving equipment between geoprobe locations,
| - globinsko vrtanje uvodnega dela vrtine Ø237/219/175 mm po metodi nadprofilnega obložnega vrtanja, predvidoma do globine 50 m, | - drilling of the Ø237/219/175 mm borehole in the initial part of the borehole to a depth of 50 m, using the super-profile casing method,
| - jedrovanje z enostenskim jedrnikom premera krone Ø131 mm ter povrtavanje z dletom premera Ø155,6 mm s hkratnim cevljenjem z obložno kolono Ø152/133 mm od globine 50 m do predkvartarne podlage na ca 75 m, | - single core drilling with a Ø131 mm diameter crown core and chisel drilling with a Ø155.6 mm diameter chisel and simultaneous tubing with a Ø152/133 mm casing column from a depth of 50 m to the pre-quarry subsoil at a depth of approx. 75 m,
| - dvig drogovja iz vrtine, spuščanje začasne jeklene filtrske kolone Ø114,3 mm, delni izvlek jeklenih obložnih cevi premera Ø152/133 mm iz vrtine, | - lifting of the mast from the borehole, lowering of the temporary Ø114.3 mm steel filter column, partial extraction of the Ø152/133 mm steel casing pipes from the borehole,
| - čiščenje vrtine z dvojnim air-liftom in aktivacija vrtine z batom DN100, | - cleaning the borehole with a double air-lift and activating the borehole with a DN100 piston,
| - hidravlično testiranje vrtine, | - hydraulic testing of the borehole,
| - nadaljevanje globinskega vrtanje za dodatno globino ca 55 m, vrtanje vrtine od 75 m do 130 m z dletom Ø127 mm in obložno kolono Ø152/133 mm, | - continuation of the depth drilling for an additional depth of approx. 55 m, drilling a borehole from 75 m to 130 m with a Ø127 mm chisel and a Ø152/133 mm casing column,
| - odvoz navrtanine in ostankov delovnega platoja (ocena zemljine 3. kategorije) na odlagališče (ocena ca 30 m3 na vrtino) ter ureditev evidenc | - removal of spoil and residues from the working pad (estimated to be Category 3 soil) to a disposal site (estimated at approx. 30 m3 per borehole) and record keeping
| - koordinacija vgradnje geosonde | - coordinating the installation of a geoprobe | kpl | 230 |  | 0
1.3 | Geosonda izdelana iz polietilenske cevi visoke gostote in dodatnih geosondnih oblikovnih kosov PE100-RC, oprema in material namenska za geosonde, tlačna stopnja PN16 oziroma PN20 za dobo vsaj 50 let po DIN8074, skladnost s standardi DIN8074, VDI4640, DVS, toplotna prevodnost λ=0,40W/mK, komplet z elektrofuzijskim materilom za varjenje, distančniki, utežjo, pritrdilnim materialom, polaganjem geosonde v vrtino ter izdelavo preizkusov pred injektiranjem, ustreza proizvod FRANK tip geothermal PE100-RC s pripadajočo opremo: | Geoprobe made of high-density polyethylene pipe and additional geoprobe shaped pieces PE100-RC, equipment and material dedicated for geoprobes, pressure rating PN16 or PN20 for a lifetime of at least 50 years according to DIN8074, compliance with DIN8074, VDI4640, DVS, thermal conductivity λ=0,40W/mK, complete with electrofusion welding material, spacers, weights, fixing material, installation of the geoprobe in the borehole and pre-grouting tests, corresponds to the FRANK product type geothermal PE100-RC with associated equipment:
| - geotermalna energetska sonda: dvojna U cev, 4x Ø32x3 (4 cev v skupnem snopu 2x dovod in 2x povratek) z originalnim tovarniško izdelanim zaključkom dna sonde, dolžina sonde 130 m ter opremo za pritrditev uteži; | - geothermal energy probe: double U-pipe, 4x Ø32x3 (4 pipes in a common bundle 2x inlet and 2x return) with original factory-built probe bottom termination, probe length 130 m and equipment for attaching weights;
| - cevni kolektor za spajanje dveh U cevi (Y kos): 2x Ø32x3 z 1x Ø40x3,7 - komplet 2x | - pipe manifold for connecting two U-pipes (Y piece): 2x Ø32x3 with 1x Ø40x3,7 - complete 2x
| - cevni kolektor za spajanje dveh U cevi: 2x Ø32x3 z 1x Ø40x3,7 - komplet 2x | - a tube manifold for connecting two U-tubes: 2x Ø32x3 with 1x Ø40x3,7 - complete 2x
| - spojni kos Ø32x3 - 4x | - coupling piece Ø32x3 - 4x
| - spojni kos Ø40x3,7 - 2x | - connecting piece Ø40x3,7 - 2x
| - distančniki geosonde za dvojno U cev , 4x Ø32x3, na sredini prostor za polnilno cev predvidoma Ø25x3, vgradnja distančnikov na razdalji 2 ÷ 4 m, ocena 50 distančnikov | - geoprobe spacers for double U-pipe, 4x Ø32x3, space in the middle for the filling pipe, Ø25x3, installation of spacers at a distance of 2 ÷ 4 m, estimate 50 spacers
| - utež za geosondo z opremo za pritrjevanje uteži za globino do 140m, predvidoma do 20 kg | - geopressure weight with weight attachment equipment for depths up to 140 m, up to 20 kg
| - zaščita cevovodov geosond s čepi (preprečevanje vstopa umazanije v notranjost cevovodov geosonde) | - protection of geoprobe pipelines with plugs (to prevent dirt from entering the inside of the geoprobe pipelines)
| - injektirna cev za geosonde predvidoma Ø25x3 | - injection pipe for geoprobes, assumed Ø25x3
| - preskus geosonde na pretok, predviden pretok v U cevi 1 m3/h oziroma dvojni U cevi 2 m3/h | - geoprobe flow test, assumed flow in U-pipe 1 m3/h or double U-pipe 2 m3/h
| - tlačni preskus geosonde: tlak na vrhu geosonde do 2 bar, tlak na dnu geosonde do 15 bar. Tlak na dnu geosonde ne sme preseči PN16 ! | - pressure test of the geoprobe: pressure at the top of the geoprobe up to 2 bar, pressure at the bottom of the geoprobe up to 15 bar. The pressure at the bottom of the geoprobe shall not exceed PN16 !
| - koordinacija vgradnje geosonde | - coordinating the installation of a geoprobe | kpl | 230 |  | 0
1.4 | Injektiranje geosonde z injekcisko maso za geosonde oziroma termobetonom ter zaščita ustja geosonde: | Injection of the geoprobe with geoprobe grout or thermocrete and protection of the geoprobe mouth:
| - injektiranje in stabilizacija sonde z injekcijsko mešanico preko injektirne naprave, injekcijska masa, termobeton za geosonde, skladnost z VDI4640, toplotna prevodnost λ ≥ 2,0W/mK, protizmrzovalna odpornost po DIN CEN/TS 12390-9, ustreza kot na primer Fischer GeoSolid 240HS ali enakovredno; ocena 5 t / geosondo; | - injection and stabilisation of the probe with grout via injection device, grout, thermoconcrete for geoprobes, VDI4640 compliant, thermal conductivity λ ≥ 2.0W/mK, antifreeze resistance according to DIN CEN/TS 12390-9, equivalent to e.g. Fischer GeoSolid 240HS or equivalent; rating 5 t/geoprobe;
| - izdelava in zaščita ustja geosonde in vgradnja betonske cevi s pokrovom DN500 | - construction and protection of the geoprobe mouth and installation of a concrete pipe with DN500 cap
| - koordinacija vgradnje geosonde | - coordinating the installation of a geoprobe | kpl | 230 |  | 0
1.5 | Polietilenske cevi visoke gostote za sisteme geosond, material PE100-RC, tlačna stopnja PN16 za dobo vsaj 50 let po DIN8074, skladnost s standardi DIN8074, VDI4640, DVS, vključno z elekrofuzijskimi oblikovnimi kosi (spojke, loki, redukcije, T kosi, ...) ter elektrofuzijskim materilom za varjenje, (OD x s = zunanji premer cevi x debelina stene cevi), ustreza proizvod FRANK tip geothermal PE100-RC ali enakovredno, komplet s polaganjem podzemnega voda v peščeni posteljici ter s PVC označevalnim trakom geosondnih razvodov; | High-density polyethylene pipes for geoprobe systems, material PE100-RC, pressure rating PN16 for a lifetime of at least 50 years according to DIN8074, compliance with DIN8074, VDI4640, DVS, including electrofusion fittings (couplings, bends, reducers, T-pieces, etc.) and electrofusion welding material, (OD x s = pipe outer diameter x pipe wall thickness), corresponding to the FRANK product type geothermal PE100-RC or equivalent, complete with underground pipe laying in a sand bed and with PVC marking tape for the geoprobe piping;
| - zaščita cevovodov geosond s čepi (prepčevanje vstopa umazanije v notranjost cevovodov) | - protection of geoprobe pipelines with plugs (to prevent dirt from entering the interior of the pipelines)
| - hidravlična vezava Tiechelmann posamezne skupine geosond (3 do 4 geosonde v skupini) | - tiechelmann hydraulic coupling of each group of geoprobes (3 to 4 geoprobes per group)
| OD 40 (ø 40 x 3,7) | OD 40 (ø 40 x 3,7) | m | 920 |  | 0
| OD 63 (ø 63 x 5,8) | OD 63 (ø 63 x 5,8) | m | 300 |  | 0
| OD 75 (ø 75 x 6,8) | OD 75 (ø 75 x 6,8) | m | 9360 |  | 0
| spojni kos OD 40 (ø 40 x 3,7) | coupling piece OD 40 (ø 40 x 3,7) | kos | 460 |  | 0
| spojni kos OD 75 (ø 75 x 6,8) | coupling piece OD 75 (ø 75 x 6,8) | kos | 920 |  | 0
| 90°lok OD 40 (ø 40 x 3,7) | 90°block OD 40 (ø 40 x 3,7) | kos | 980 |  | 0
| 90°lok OD 75 (ø 75 x 6,8) | 90°block OD 75 (ø 75 x 6,8) | kos | 680 |  | 0
| 45°lok OD 40 (ø 40 x 3,7) | 45°block OD 40 (ø 40 x 3,7) | kos | 650 |  | 0
| 45°lok OD 75 (ø 75 x 6,8) | 45°block OD 75 (ø 75 x 6,8) | kos | 230 |  | 0
| T kos OD 75 / odcep OD 40 | T piece OD 75 / branch OD 40 | kos | 400 |  | 0
| redukcija OD 75 / OD 40 | reduction OD 75 / OD 40 | kos | 130 |  | 0
| redukcija OD 75 / OD 63 | reduction OD 75 / OD 63 | kos | 130 |  | 0
| OD 50 (ø 50 x 4,6) | OD 50 (ø 50 x 4,6) | m | 24 |  | 0
| prirobnica OD 63 / DN 50 | flange OD 63 / DN 50 | kpl | 130 |  | 0
| označevalni trak geosondni razvod | marker tape geoprobe duct | m | 6000 |  | 0
1.6 | Vodotesno tesnilo za prehod cevi skozi betonsko steno zemlja / klet objekta, vodotesnost W2.1-E po DIN18533 za hidrostatični tlak do 3 m, sestavljeno iz: elastomernih tesnil EPDM ali NBR, z zategovalnimi korozijsko odpornimi prirobnicami in vijačnim materialom iz nerjavnega jekla; | Watertight seal for the passage of pipes through the concrete wall of a soil/basement building, watertightness W2.1-E according to DIN18533 for hydrostatic pressure up to 3 m, consisting of: elastomeric EPDM or NBR seals, with corrosion-resistant tightening flanges and stainless steel screw material;
| - zaščitna cev za vbetoniranje oziroma uvodnica in njena namestitev je del načrtov s področja arhitekture ter gradbeništva; | - the concrete protection pipe or introducer and its installation is part of the architectural and civil engineering plans;
| - ustreza proizvod HAUFF TECHNIK tip HSD ali enakovredno; | - corresponds to HAUFF TECHNIK product type HSD or equivalent;
| - prehod cevi geosondnega razvoda PE100-RC PN16: OD 63 (ø 63 x 5,8) | - pE100-RC PN16 geoprobe pipe crossing: OD 63 (ø 63 x 5.8) | kpl | 124 |  | 0
1.7 | Tlačni preskus trdnosti in tesnjenja sistema geosond iz PE100-RC oziroma vsi razvodi v zemlji pod in ob objektu, vključno s potrebnim materialom za izvedbo preizkusa, ter izdelavo pisnega poročila o uspešno opravljenem tlačnem preskusu; | Pressure test of the strength and leak tightness of the PE100-RC geoprobe system or all pipelines in the ground under and adjacent to the building, including the necessary materials to perform the test, and the production of a written report on the successful completion of the pressure test;
| - preskusni tlak: tlak na vrhu sistema geosond pri vstopu cevovoda v objekt od zunaj mora biti do 1 bar, tlak na dnu geosonde do 15 bar. Tlak na dnu geosonde ne sme preseči PN16 ! | - test pressure: the pressure at the top of the geoprobe system at the entrance of the pipeline to the building from the outside must be up to 1 bar, the pressure at the bottom of the geoprobe up to 15 bar. The pressure at the bottom of the geoprobe must not exceed PN16 ! | kpl | 62 |  | 0
1.8 | Razdelilnik / zbiralnik izdelan iz jeklene nerjavne cevi DN150 Ø168,3x2,6 po EN ISO 1127, iz materiala AISI304, PN16, ležeče izvedbe, z bombiranima ali prirobničnima zaključkoma, komplet z vsemi priključki, izdelano po delavniški risbi dobavitelja, skladno s shemo in v načrtu, vključno s potiprirobnicami, varilnim, pritrdilnim, tesnilnim materialom; | Manifold / manifold made of stainless steel pipe DN150 Ø168,3x2,6 according to EN ISO 1127, material AISI304, PN16, of creep design, with bomb-coated or flanged ends, complete with all connections, made according to the supplier's shop drawings, in accordance with the scheme and in the plan, including sub-fittings, welding, fixing, sealing material;
| - za distribucijo glikolnega medija geosond | - for the distribution of the glycol medium geosond
| - komplet s toplotna parozaporna izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +105°C, debelina 40mm | - complete with thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, classification B-s3-d0 according to EN13501-1, for temperatures -50 to +105°C, thickness 40mm
| komplet z nerjavnim ali pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno; | complete with stainless steel or galvanised hanging material (threaded rods, brackets, anchors, etc.) and hose clamps with noise damping lining, suitable for HILTI or SIKLA, or equivalent;
| - dimenzije: premer D x dolžina L = DN150 x 1500 mm, z podkonstrukcijo za pritrditev na tla /strop, - glavni priključek desno, prirobnični DN80, - navojni priključki: 3x DN50, 1x DN15 | - dimensions: diameter D x length L = DN150 x 1500 mm, with substructure for floor/ceiling mounting, - main connection right, flanged DN80, - threaded connections: 3x DN50, 1x DN15 | kpl | 4 |  | 0
| - dimenzije: premer D x dolžina L = DN150 x 2000 mm, z podkonstrukcijo za pritrditev na tla /strop, - glavni priključek desno, prirobnični DN100, - navojni priključki: 4x DN50, 1x DN15 | - dimensions: diameter D x length L = DN150 x 2000 mm, with substructure for floor/ceiling mounting, - main connection right, flanged DN100, - threaded connections: 4x DN50, 1x DN15 | kpl | 4 |  | 0
| - dimenzije: premer D x dolžina L = DN150 x 2500 mm, z podkonstrukcijo za pritrditev na tla /strop, - glavni priključek desno, prirobnični DN100, - navojni priključki: 5x DN50, 1x DN15 | - dimensions: diameter D x length L = DN150 x 2500 mm, with substructure for floor/ceiling mounting, - main connection right, flanged DN100, - threaded connections: 5x DN50, 1x DN15 | kpl | 8 |  | 0
| - dimenzije: premer D x dolžina L = DN150 x 3000 mm, z podkonstrukcijo za pritrditev na tla /strop, - glavni priključek desno, prirobnični DN100, - navojni priključki: 6x DN50, 1x DN15 | - dimensions: diameter D x length L = DN150 x 3000 mm, with substructure for floor/ceiling mounting, - main connection right, flanged DN100, - threaded connections: 6x DN50, 1x DN15 | kpl | 4 |  | 0
| - dimenzije: premer D x dolžina L = DN150 x 2500 mm, z podkonstrukcijo za pritrditev na tla /strop, - glavni priključek levo, prirobnični DN100, - navojni priključki: 5x DN50, 1x DN15 | - dimensions: diameter D x length L = DN150 x 2500 mm, with substructure for floor/ceiling mounting, - main connection left, flanged DN100, - threaded connections: 5x DN50, 1x DN15 | kpl | 4 |  | 0
| - dimenzije: premer D x dolžina L = DN150 x 3000 mm, z podkonstrukcijo za pritrditev na tla /strop, - glavni priključek levo, prirobnični DN100, - navojni priključki: 6x DN50, 1x DN15 | - dimensions: diameter D x length L = DN150 x 3000 mm, with substructure for floor/ceiling mounting, - main connection left, flanged DN100, - threaded connections: 6x DN50, 1x DN15 | kpl | 2 |  | 0
1.9 | Razdelilnik in zbiralnik povezana v eno celoto, kot enako-tlačni element (v obliki podkve), izdelano iz jeklene nerjavne cevi DN400 Ø406,4x4,0 po EN ISO 1127 ter dveh 90°lokov DN400, iz materiala AISI304, PN16, ležeče izvedbe, z bombiranima ali prirobničnima zaključkoma, komplet z vsemi priključki, izdelano po delavniški risbi dobavitelja, skladno s shemo in v načrtu, vključno s potiprirobnicami, varilnim, pritrdilnim, tesnilnim materialom; | Manifold and manifold connected as a single unit, as an equal-pressure element (horseshoe-shaped), made of stainless steel pipe DN400 Ø406,4x4,0 according to EN ISO 1127 and two 90° bends DN400, made of AISI304 material, PN16, of canted design, with bomb-proof or flanged ends, complete with all connections, made according to the supplier's shop drawing, in accordance with the scheme and in the plan, including sub-pieces, welding, fixing, sealing material;
| - za distribucijo glikolnega medija geosond do naprav TCHA (toplotna črpalka, hladilni agregat) | - for the distribution of the glycol medium geosondes to the TCHA equipment (heat pump, chiller)
| - razdelilni del na glavne distribucijske veje geosond in zbiralni del na TCHA - dimenzije: premer D x dolžina L = DN400 x 6800 mm | - distribution section to the main distribution branches of the geoprobes and collection section to the TCHA - dimensions: diameter D x length L = DN400 x 6800 mm
| - zbiralni del na glavne distribucijske veje geosond in razdelilni del na TCHA - dimenzije: premer D x dolžina L = DN400 x 6800 mm | - collection section to the main distribution branches of the geoprobes and distribution section to the TCHA - dimensions: diameter D x length L = DN400 x 6800 mm
| - dva povezovalna 90°loka DN400 zgoraj navedenega razdelilnega in zbiralnega dela | - two connecting 90° DN400 bends of the above mentioned distribution and collection section
| - s podkonstrukcijo za pritrditev na tla /strop | - with substructure for floor/ceiling mounting
| - priključki za veje geosond, prirobnični PN16: 2x DN200, 4x DN150 | - geoprobe branch connections, flanged PN16: 2x DN200, 4x DN150
| - priključki za TCHA, prirobnični PN16: 8x DN150 | - tCHA connections, flanged PN16: 8x DN150
| - priključek za EPK ekspanzijsko napravo, prirobničnii PN16: 1x DN50 | - connection for EPC expansion device, flanged PN16: 1x DN50
| - priključka za NOD napravo za odplinjevanje sistema in dopolnjevanje z glikolsko mešanico, prirobničnii PN16: 2x DN32 | - connections for NOD device for system degassing and glycol top-up, flanged PN16: 2x DN32
| - priključki za izpust, navojni: 2x DN20 | - outlet connections, threaded: 2x DN20
| - komplet s toplotna parozaporna izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +105°C, debelina 40mm | - complete with thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, classification B-s3-d0 according to EN13501-1, for temperatures -50 to +105°C, thickness 40mm
| komplet z nerjavnim ali pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno; | complete with stainless steel or galvanised hanging material (threaded rods, brackets, anchors, etc.) and hose clamps with noise damping lining, suitable for HILTI or SIKLA, or equivalent; | kpl | 1 |  | 0
1.10 | Obtočna črpalka, centrifugalna inline, s suhim rotorjem, PN16, skladnost z ErP, elektronsko regulirana z integriranim frekvenčnim pretvornikom, s tipalom diferenčnega tlaka, upravljalnikom nastavitev s prikazovalnikom parametrov, internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, centrifugal inline, dry-running, PN16, ErP-compliant, electronically controlled with integrated frequency converter, differential pressure sensor, setting control with parameter display, internal hydraulic, electrical and communication connections, pump material grey cast iron with suitable medium seal, flanged design, including counter flanges, fixing and sealing material. Technical data:
| - za distribucijo glikolnega medija geosond | - for the distribution of the glycol medium geosond
| - pretok V= 159 m3/h, tlačna višina H= 150 kPa | - flow rate V= 159 m3/h, pressure head H= 150 kPa
| - možnost izbire delovanja črpalke na proporcionalni tlak ter optimizacijo delovne točke z avtomatsko nastavitvijo pretoka ali glede na trenutne potrebe obratovanja | - option to choose proportional pressure operation and optimise the operating point by automatically adjusting the flow rate or according to the current operating needs
| - komunikacija s CNS: RS485 / Modbus RTU | - communication with CNS: RS485 / Modbus RTU
| - elektro podatki Pel= 11 kW, 400V /3/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 11 kW, 400V /3/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip TPE3 125-290 ali enakovredno | - corresponds to GRUNDFOS product type TPE3 125-290 or equivalent
| Oznaka: P48.091 | Code: P48.091 | kpl | 1 |  | 0
1.11 | Obtočna črpalka, centrifugalna inline, s suhim rotorjem, PN16, skladnost z ErP, elektronsko regulirana z integriranim frekvenčnim pretvornikom, s tipalom diferenčnega tlaka, upravljalnikom nastavitev s prikazovalnikom parametrov, internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, centrifugal inline, dry-running, PN16, ErP-compliant, electronically controlled with integrated frequency converter, differential pressure sensor, setting control with parameter display, internal hydraulic, electrical and communication connections, pump material grey cast iron with suitable medium seal, flanged design, including counter flanges, fixing and sealing material. Technical data:
| - za distribucijo glikolnega medija geosond | - for the distribution of the glycol medium geosond
| - pretok V= 116 m3/h, tlačna višina H= 150 kPa | - flow rate V= 116 m3/h, pressure head H= 150 kPa
| - možnost izbire delovanja črpalke na proporcionalni tlak ter optimizacijo delovne točke z avtomatsko nastavitvijo pretoka ali glede na trenutne potrebe obratovanja | - option to choose proportional pressure operation and optimise the operating point by automatically adjusting the flow rate or according to the current operating needs
| - komunikacija s CNS: RS485 / Modbus RTU | - communication with CNS: RS485 / Modbus RTU
| - elektro podatki Pel= 7,5 kW, 400V /3/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 7,5 kW, 400V /3/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip TPE3 100-260 ali enakovredno | - corresponds to GRUNDFOS product type TPE3 100-260 or equivalent
| Oznaka: P48.092 | Code: P48.092 | kpl | 1 |  | 0
1.12 | Obtočna črpalka, centrifugalna inline, s suhim rotorjem, PN16, skladnost z ErP, elektronsko regulirana z integriranim frekvenčnim pretvornikom, s tipalom diferenčnega tlaka, upravljalnikom nastavitev s prikazovalnikom parametrov, internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, centrifugal inline, dry-running, PN16, ErP-compliant, electronically controlled with integrated frequency converter, differential pressure sensor, setting control with parameter display, internal hydraulic, electrical and communication connections, pump material grey cast iron with suitable medium seal, flanged design, including counter flanges, fixing and sealing material. Technical data:
| - za distribucijo glikolnega medija geosond | - for the distribution of the glycol medium geosond
| - pretok V= 123 m3/h, tlačna višina H= 150 kPa | - flow rate V= 123 m3/h, pressure head H= 150 kPa
| - možnost izbire delovanja črpalke na proporcionalni tlak ter optimizacijo delovne točke z avtomatsko nastavitvijo pretoka ali glede na trenutne potrebe obratovanja | - option to choose proportional pressure operation and optimise the operating point by automatically adjusting the flow rate or according to the current operating needs
| - komunikacija s CNS: RS485 / Modbus RTU | - communication with CNS: RS485 / Modbus RTU
| - elektro podatki Pel= 7,5 kW, 400V /3/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 7,5 kW, 400V /3/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip TPE3 100-260 ali enakovredno | - corresponds to GRUNDFOS product type TPE3 100-260 or equivalent
| Oznaka: P48.093 | Code: P48.093 | kpl | 1 |  | 0
1.13 | Obtočna črpalka, centrifugalna inline, s suhim rotorjem, PN16, skladnost z ErP, elektronsko regulirana z integriranim frekvenčnim pretvornikom, s tipalom diferenčnega tlaka, upravljalnikom nastavitev s prikazovalnikom parametrov, internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, centrifugal inline, dry-running, PN16, ErP-compliant, electronically controlled with integrated frequency converter, differential pressure sensor, setting control with parameter display, internal hydraulic, electrical and communication connections, pump material grey cast iron with suitable medium seal, flanged design, including counter flanges, fixing and sealing material. Technical data:
| - distribucija glikolnega medija geosond na TCHA40.1, TCHA40.2, TCHA40.3, TCHA40.4 | - distribution of the glycol medium geosond on TCHA40.1, TCHA40.2, TCHA40.3, TCHA40.4
| - preklapljanje režimov glede na potrebe po ogrevni vodi OV 45°C ali hladilni vodi HV 9°C | - switching modes according to heating water demand OV 45°C or cooling water demand HV 9°C
| - TC priprava OV 45°C pretok V= 67,9 m3/h, tlačna višina H= 60 kPa | - TC preparation OV 45°C flow V= 67,9 m3/h, pressure head H= 60 kPa
| - HA priprava HV 9°C pretok V= 113,5 m3/h, tlačna višina H= 140 kPa | - HA preparation HV 9°C flow V= 113,5 m3/h, pressure head H= 140 kPa
| - možnost izbire delovanja črpalke na proporcionalni tlak ter optimizacijo delovne točke z avtomatsko nastavitvijo pretoka ali glede na trenutne potrebe obratovanja | - option to choose proportional pressure operation and optimise the operating point by automatically adjusting the flow rate or according to the current operating needs
| - komunikacija s CNS: RS485 / Modbus RTU | - communication with CNS: RS485 / Modbus RTU
| - elektro podatki Pel= 5,5 kW, 400V /3/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 5,5 kW, 400V /3/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip TPE3 100-230 ali enakovredno | - corresponds to GRUNDFOS product type TPE3 100-230 or equivalent
| Oznaka: P48.081, P48.082, P48.083, P48.084 | Code: P48.081, P48.082, P48.083, P48.084 | kpl | 4 |  | 0
1.14 | Ekspanzijska naprava za kompenzacijo temperaturnih raztezkov v sistemu skladno z EN12828, naprava za vzdrževanje tlaka z dvema kompresorjema ter kompaktno regulacijsko enoto z vsemi funkcijskimi elementi in komunikacijo s CNS, RS485 / Modbus RTU ter možnostjo povezave večih naprav kot Master / Slave, vključno s pritrdilnim in tesnilnim materialom; | Expansion device for temperature expansion compensation in the system according to EN12828, pressure maintenance device with two compressors and compact control unit with all functional elements and communication with CNS, RS485 / Modbus RTU and possibility of connection of several devices as Master / Slave, including fastening and sealing material;
| - za sistem glikolnega medija geosond | - for the geosond glycol media system
| - natančnost vzdrževanja tlaka ± 0,1 bar z dvema kompresorema (eden delovni, drugi je rezerva), sklop z dvema prelivnima ventiloma in varnostnim ventilom, preklapljanje je odvisno od časa in obremenitve | - pressure maintenance accuracy ± 0.1 bar with two compressors (one working, one reserve), set with two overflow valves and a safety valve, switching time and load dependent
| - primarna posoda V= 4000 l, podnožje s senzorjem za merjenje količine vode | - primary tank V= 4000 l, base with sensor for measuring water quantity
| - električna moč 2x 1,2 kW pri 230 V / 1 / 50 Hz | - electrical power 2x 1,2 kW at 230 V / 1 / 50 Hz
| - PN10, CE skladno s PED | - PN10, CE according to PED
| - nivo hrupa kompresorja do 60 dB(A) | - compressor noise level up to 60 dB(A)
| - ustreza proizvod PNEUMATEX tip C 10.2-3.0 Connect + CG 4000.6 ali enakovredno | - corresponds to PNEUMATEX product type C 10.2-3.0 Connect + CG 4000.6 or equivalent
| Oznaka: EPK48.21 | Code: EPC48.21 | kpl | 1 |  | 0
1.15 | Varnostni ventil po TRD 721, PN16, varnostna funkcija izpusta medija zaradi toplotnih raztezkov v sistemu, vzmetno delovanje, možnost ročnega odzračenja, prostor vzmeti zaščiten z membrano, prirobnična izvedba, vključno s pritrdilnim in tesnilnim materialom; | Safety valve according to TRD 721, PN16, safety function of medium discharge due to thermal expansion in the system, spring operation, manual venting possible, spring space protected by diaphragm, flanged version, including fastening and sealing material;
| - za sistem glikolnega medija geosond | - for the geosond glycol media system
| - tlak odpiranja 2,5 barg, | - opening pressure 2,5 barg,
| - z navojnima priključkoma DN 50 / 80, komplet z ventilom s ključavnico 2" (DN50) | - with DN 50 / 80 threaded connections, complete with 2" (DN50) locking valve
| - ustreza proizvod IMI PNEUMATEX tip DSV 50 - 2.5 DGH + dodatna oprema ali enakovredno | - corresponds to IMI PNEUMATEX product type DSV 50 - 2.5 DGH + accessories or equivalent
| Oznaka: VV48.23 | Code: VV48.23 | kpl | 1 |  | 0
1.16 | Naprava za odplinjevanje sistema skladno z EN12828 in dopolnjevanje z medijem ter s hidravlično ločitvijo tip AB po EN1717 komplet z kompaktno regulacijsko enoto z vsemi funkcijskimi elementi in komunikacijo s CNS, RS485 / Modbus RT ter možnostjo povezave večih naprav kot Master / Slave, vključno s pritrdilnim in tesnilnim materialom; | System degassing device according to EN12828 and medium make-up and hydraulic separation type AB according to EN1717 complete with compact control unit with all functional elements and communication with CNS, RS485/Modbus RT and possibility of connection of several devices as Master/Slave, including fixing and sealing material;
| - za sistem glikolnega medija geosond | - for the geosond glycol media system
| - natančnost vzdrževanja tlaka ± 0,1 bar z dvema kompresorema (eden delovni, drugi je rezerva), sklop z dvema prelivnima ventiloma in varnostnim ventilom, preklapljanje je odvisno od časa in obremenitve | - pressure maintenance accuracy ± 0.1 bar with two compressors (one working, one reserve), set with two overflow valves and a safety valve, switching time and load dependent
| - za dopolnjevanje delovnega tlaka v sistemu od 1,0 do 2,5 bar | - for replenishing the working pressure of the system from 1.0 to 2.5 bar
| - električna moč 0,75 kW pri 230 V / 1 / 50 Hz | - electrical power 0,75 kW at 230 V / 1 / 50 Hz
| - krmilnik z dodatno komunikacijo s stikalom nivoja in alarmom LSA | - controller with additional communication with level switch and LSA alarm
| - PN10, CE skladno z evropskimi direktivami 2004/108/EC, 2006/95/EC | - PN10, CE compliant with European Directives 2004/108/EC, 2006/95/EC
| - nivo hrupa pri dopolnjevanju do 60 dB(A) | - replenishment noise level up to 60 dB(A)
| - rezervoar za glikolno mešanico 200 litrov, atmosferski, material nerjavno jeklo AISI304, pokončna izvedba v obliki valja premer D x višina H = Ø500 x 1200 mm na nogah 200 mm, priključki 2x DN20-3/4", 2x DN15-1/2"; | - glycol mixture tank 200 litres, atmospheric, material stainless steel AISI304, upright cylindrical design diameter D x height H = Ø500 x 1200 mm on legs 200 mm, connections 2x DN20-3/4", 2x DN15-1/2";
| - stikalo nivoja z alamom za rezervoar glikolske mešanice, ustreza vibracijsko stikalo DN15-1/2" | - level switch with alam for glycol mix tank, fits vibrating switch DN15-1/2"
| - ustreza proizvod IMI PNEVMATEX tip Vento Connect V 4.1 EC + rezervoar 200 l + EH tip FTL31 ali enakovredno | - iMI PNEVMATEX product type Vento Connect V 4.1 EC + 200 l tank + EH type FTL31 or equivalent
| Oznaka: NOD48.22, LSA48.031 | Code: NOD48.22, LSA48.031 | kpl | 1 |  | 0
1.17 | Tipalo tlaka s pretvornikom, za mertev tlaka v območju od 0 do 6 barg (relativno) ter nastavljivim alarmnim tlakom, navojni priključek 1/2" (DN15), material nerjavno jeklo, električni podatki: napajanje 24V, izhod 4-20mA, kompletno z ventilom za tipalo tlaka 1/2" (DN15) ter tesnilnim in pritrdilnim materialom; | Pressure sensor with transducer, for pressure measurement in the range from 0 to 6 barg (relative) and adjustable alarm pressure, threaded connection 1/2" (DN15), material stainless steel, electrical data: power supply 24V, output 4-20mA, complete with pressure sensor valve 1/2" (DN15) and sealing and fixing material;
| - glikolni medij geosond | - geosond glycol medium
| - alarma: spodnji p ≤ 1,0 barg, zgornji p ≥ 1,6 barg (nastavitev na tipalu ali programska nastavitev) | - alarm: lower p ≤ 1.0 barg, upper p ≥ 1.6 barg (sensor setting or software setting)
| - ustreza proizvod ENDRESS+HAUSER tip PTC31B + PZAV ali enakovredno | - corresponds to ENDRESS+HAUSER product type PTC31B + PZAV or equivalent
| Oznaka: PIA48.009 | Code: PIA48.009 | kpl | 1 |  | 0
1.18 | Temperaturno tipalo, potopno, za merilno območje od -10 do +50°C, potopna dolžina L=100mm, v tulki iz nerjavnega materiala z navojnim priključkom 1/2" (DN15), električni podatki: napajanje 24V, izhod 4-20mA, komplet s pritrdilnim in tesnilnim materialom; | Temperature sensor, immersion, for measuring range -10 to +50°C, immersion length L=100mm, in stainless steel sleeve with threaded connection 1/2" (DN15), electrical data: power supply 24V, output 4-20mA, complete with fixing and sealing material;
| - glikolni medij geosond | - geosond glycol medium
| - ustreza proizvod ELEKTRONIKA PAHOR, tip CVB ali enakovredno | - corresponds to the product ELEKTRONIKA PAHOR, type CVB or equivalent
| Oznaka: TI48.001, TI48.002, TI48.003, TI48.004, TI48.005, TI48.006 | Code: TI48.001, TI48.002, TI48.003, TI48.004, TI48.005, TI48.006 | kpl | 6 |  | 0
1.19 | Temperaturno tipalo, potopno, za merilno območje od -10 do +50°C, potopna dolžina L=100mm, v tulki iz nerjavnega materiala z navojnim priključkom 1/2" (DN15), električni podatki: napajanje 24V, izhod 4-20mA, komplet s pritrdilnim in tesnilnim materialom; | Temperature sensor, immersion, for measuring range -10 to +50°C, immersion length L=100mm, in stainless steel sleeve with threaded connection 1/2" (DN15), electrical data: power supply 24V, output 4-20mA, complete with fixing and sealing material;
| - glikolni medij geosond | - geosond glycol medium
| - alarm če je t < -5°C in izklop pripadajoče TCHA | - alarm if t < -5°C and switching off the associated TCHA
| - ustreza proizvod ELEKTRONIKA PAHOR, tip CVB ali enakovredno | - corresponds to the product ELEKTRONIKA PAHOR, type CVB or equivalent
| Oznaka: TICA48.011, TICA48.012, TICA48.013, TICA48.014 | Code: TICA48.011, TICA48.012, TICA48.013, TICA48.014 | kpl | 4 |  | 0
1.20 | Regulacijski ventil, tropotni mešalni, z elektromotornim zveznim pogonom, 24V, IP54, PN16, material ventila siva litina, nerjavno jeklo / EPDM, prirobnična izvedba, komplet s protiprirobnicami, vijačnim in tesnilnim materialom; | Control valve, tropical mixing, with electric motor continuous drive, 24V, IP54, PN16, valve material grey cast iron, stainless steel / EPDM, flanged version, complete with anti-seize, screwing and sealing material;
| - glikolni medij geosond, mešanje pred TCHA40.1, TCHA40.2, TCHA40.3, TCHA40.4 | - glycol geoprobe medium, mixing before TCHA40.1, TCHA40.2, TCHA40.3, TCHA40.4
| - DN125, kvs = 220 m3/h | - DN125, kvs = 220 m3/h
| - ustreza proizvod BELIMO tip H7125N, tip pogona RV24A-SR ali enakovredno | - corresponds to BELIMO product type H7125N, actuator type RV24A-SR or equivalent
| Oznaka: VY48.051, VY48.052, VY48.053, VY48.054 | Code: VY48.051, VY48.052, VY48.053, VY48.054 | kpl | 4 |  | 0
1.21 | Krogelni ventil s priklučkom za praznenje oz. polnenje, navojna izvedba, PN16, z ročico, material nerjavno jeklo / PTFE, vključno s pritrdilnim in tesnilnim materialom: | Ball valve with union for emptying or filling, threaded version, PN16, with handle, material stainless steel/PTFE, incl. fitting and sealing material:
| - glikolni medij geosond | - geosond glycol medium
| - ustreza proizvod END ARMATUREN ali enakovredno | - eND ARMATUREN or equivalent
| DN 15 | DN 15 | kos | 228 |  | 0
| DN 20 | DN 20 | kos | 6 |  | 0
| DN 25 | DN 25 | kos | 6 |  | 0
1.22 | Krogelni ventil, navojna izvedba, PN16, z ročico, material nerjavno jeklo / PTFE, vključno s pritrdilnim in tesnilnim materialom: | Ball valve, threaded version, PN16, with handle, material stainless steel/PTFE, incl. fitting and sealing material:
| - glikolni medij geosond | - geosond glycol medium
| - ustreza proizvod END ARMATUREN ali enakovredno | - eND ARMATUREN or equivalent
| DN 32 | DN 32 | kos | 2 |  | 0
| DN 50 | DN 50 | kos | 194 |  | 0
1.23 | Zaporna loputa, prirobnična izvedba, mehko tesnenje, PN16, z ročnim pogonom z ročico do vključno DN100 oziroma z ročnim polžnim pogonom nad vključno DN125, material nodularna litina / EPDM, za vgradnjo med prirobnice, komplet s protiprirobnicama, vijačnim in tesnilnim materialom; | Butterfly valve, flanged version, soft sealing, PN16, with manual lever actuator up to and including DN100 or with manual screw actuator up to and including DN125, material ductile iron / EPDM, for installation between flanges, complete with two anti-seize plates, screw and sealing material;
| - glikolni medij geosond | - geosond glycol medium
| - ustreza proizvod IMP ARMATURE ali enakovredno | - iMP ARMATURE or equivalent
| DN 80 | DN 80 | kpl | 6 |  | 0
| DN 100 | DN 100 | kpl | 33 |  | 0
| DN 125 | DN 125 | kpl | 8 |  | 0
| DN 150 | DN 150 | kpl | 24 |  | 0
| DN 200 | DN 200 | kpl | 4 |  | 0
1.24 | Nepovratna loputa, z vmetjo, prirobnična izvedba, material nodularna litina / EPDM, vzmet nerjavno jeklo, za vgradnjo med prirobnice, komplet s protiprirobnicama, vijačnim in tesnilnim materialom; | Non-return hatch, with spout, flanged version, material ductile iron / EPDM, spring stainless steel, for installation between flanges, complete with two counter flanges, screwing and sealing material;
| - glikolni medij geosond | - geosond glycol medium
| - ustreza proizvod END ARMATUREN ali enakovredno | - eND ARMATUREN or equivalent
| DN 150 | DN 150 | kpl | 6 |  | 0
| DN 200 | DN 200 | kpl | 1 |  | 0
1.25 | Lovilnik nesnage, prirobnična izvedba, z normalnim sitom, PN16, material siva litina, sito nerjavno jeklo, komplet s krogelnim ventilom DN15 za praznenje in izpiranje, vključno s protiprirobnicama, vijačnim in tesnilnim materialom; | Debris trap, flanged version, with normal sieve, PN16, material grey cast iron, sieve stainless steel, complete with ball valve DN15 for emptying and flushing, incl. counter flanges, screwing and sealing material;
| - glikolni medij geosond | - geosond glycol medium
| - ustreza proizvod IMP ARMATURE ali enakovredno | - iMP ARMATURE or equivalent
| DN 150 | DN 150 | kpl | 6 |  | 0
| DN 200 | DN 200 | kpl | 1 |  | 0
1.26 | Izločevalnika nečistoč, magnetita in mikro mehurčkov, ciklonsko izločanje, PN16, skladno s PED, material jeklo, prirobnični priključki, z dvema krogelnim ventilom DN15 za izpust nečistoč in odzračevanje ter avtomatskim odzračevalnim ventilom, vključno s protiprirobnicama, vijačnim in tesnilnim materialom; | Impurity, magnetite and micro-bubble eliminators, cyclonic elimination, PN16, PED-compliant, material steel, flanged connections, with two DN15 ball valves for impurity discharge and venting and an automatic vent valve, incl. counter flanges, screwing and sealing material;
| - glikolni medij geosond | - geosond glycol medium
| - ustreza proizvod IMI PMEUMATEX tip Zeparo G-Force ZG ... + ZUTX 25 ali enakovredno | - iMI PMEUMATEX product type Zeparo G-Force ZG ... + ZUTX 25 or equivalent
| DN 80 | DN 80 | kpl | 2 |  | 0
| DN 100 | DN 100 | kpl | 11 |  | 0
1.27 | Ventil za hidravlično uravnoteženje, nastavitev pretoka, navojna izvedba, PN16, s priključkoma za priklop naprave za merjenje pretoka, z zaporno funkcijo brez prenastavitve pretoka, material siva litina, nerjavno jeklo, EPDM, PTFE, vključno z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Hydraulic balancing valve, flow adjustment, threaded version, PN16, with two connections for connection of flow measuring device, with shut-off function without flow reset, material grey cast iron, stainless steel, EPDM, PTFE, incl. threaded plugs, fastening and sealing material;
| - glikolni medij geosond | - geosond glycol medium
| - ustreza proizvod IMI TA tip STAD ali enakovredno | - the product conforms to IMI TA type STAD or equivalent
| DN 50 | DN 50 | kos | 62 |  | 0
1.28 | Ventil za hidravlično uravnoteženje, nastavitev pretoka, prirobnična izvedba, PN16, s priključkoma za priklop naprave za merjenje pretoka, z zaporno funkcijo brez prenastavitve pretoka, material siva litina, nerjavno jeklo, EPDM, PTFE, vključno s protiprirobnicama, vijačnim in tesnilnim materialom; | Hydraulic balancing valve, flow adjustable, flanged version, PN16, with two connections for connection to a flow measuring device, with shut-off function without flow reset, material grey cast iron, stainless steel, EPDM, PTFE, incl. anti-seize, screwing and sealing material;
| - glikolni medij geosond | - geosond glycol medium
| - ustreza proizvod IMI TA tip STAF ali enakovredno | - corresponds to IMI TA type STAF or equivalent
| DN 80 | DN 80 | kpl | 2 |  | 0
| DN 100 | DN 100 | kpl | 11 |  | 0
1.29 | Kompenzator vibracij iz strojne opreme na cevovod, prirobnična izvedba, PN16, material pocinkano jeklo, EPDM, vključno s protiprirobnicama, vijačnim in tesnilnim materialom; | Vibration compensator from hardware to pipeline, flanged version, PN16, material galvanised steel, EPDM, incl. anti-friction, screwing and sealing material;
| - glikolni medij geosond | - geosond glycol medium
| - ustreza proizvod END ARMATUREN tip KP ali enakovredno | - corresponds to END ARMATUREN type KP or equivalent
| DN 100 | DN 100 | kpl | 20 |  | 0
| DN 125 | DN 125 | kpl | 2 |  | 0
1.30 | Termometer, tekočinski, dolžina skale 100mm, kotni 90°, potopna dolžina 40mm, v zaščitni cevi - tulki, klasa točnosti 1%, navojni priključek 1/2" (DN15), material medenina, aluminij, steklo, nerjavno jeklo, vključno s pritrdilnim in tesnilnim materialom; | Thermometer, liquid, scale length 100mm, angle 90°, immersion length 40mm, in protective tube - sleeves, accuracy class 1%, threaded connection 1/2" (DN15), material brass, aluminium, glass, stainless steel, incl. fixing and sealing material;
| - ustreza proizvod INOL ali enakovredno | - corresponds to INOL or equivalent
| - glikolni medij geosond | - geosond glycol medium
| - območjem merjenja: -10 do 50°C | - measuring range: -10 to 50°C | kpl | 168 |  | 0
1.31 | Manometer ø 68 mm, klasa točnosti 1,6% po EN837-1, navojni radialni priključek, material medenina, nerjavno jeklo, steklo / EPDM, komplet z manometrskim ventilom DN15 (1/2"), vključno s pritrdilnim in tesnilnim materialom; | Pressure gauge ø 68 mm, accuracy class 1.6% according to EN837-1, threaded radial connection, material brass, stainless steel, glass / EPDM, complete with pressure gauge valve DN15 (1/2"), including fitting and sealing material;
| - ustreza proizvod INOL ali enakovredno | - corresponds to INOL or equivalent
| - glikolni medij geosond | - geosond glycol medium
| - območjem merjenja: 0 do 6 bar | - measuring range: 0 to 6 bar | kpl | 171 |  | 0
1.32 | Avtomatski odzračevalnik, z zapornim in ročno odzračevalnim ventilom PN10 material medenina / PTFE, vključno z navojnim holandcem in tesnilnim materialom; | Automatic vent, with stop and manual vent valve PN10 material brass/PTFE, incl. threaded dutch and sealing material;
| - glikolni medij geosond | - geosond glycol medium
| DN25 - ustreza proizvod IMI PNEUMATEX tip ZUTX 25 ali enakovredno | DN25 - corresponds to IMI PNEUMATEX product type ZUTX 25 or equivalent | kpl | 136 |  | 0
1.33 | Odzračitveni lonček, volumen V ≥ 2 litra, izdelan iz cevi DN100, ø114x2,3 mm po EN ISO1127, dolžina L=300mm, z bombiranima zaključkoma, material AISI304, vključno z varilnim materialom; | Refrigerated crucible, volume V ≥ 2 litres, made of DN100 pipe, ø114x2,3 mm according to EN ISO1127, length L=300mm, with bomb-coated ends, material AISI304, incl. welding consumables;
| - glikolni medij geosond | - geosond glycol medium | kpl | 168 |  | 0
1.34 | Jeklene nerjavne cevi izdelane po EN ISO1127, material AISI304 ali boljši, vključno z oblikovnimi kosi (loki, redukcije, T kosi, ...) in varilnim materialom, varjenje TIG pod inertnim plinom, | Stainless steel tubes manufactured according to EN ISO1127, material AISI304 or better, including forming pieces (bends, reductions, T-pieces, etc.) and welding consumables, TIG welding under inert gas,
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and hose clamps with noise damping lining, suitable for HILTI or SIKLA, or equivalent;
| DN 15, ø 21,3 x 1,6 | DN 15, ø 21,3 x 1,6 | m | 570 |  | 0
| DN 20, ø 26,9 x 1,6 | DN 20, ø 26,9 x 1,6 | m | 2 |  | 0
| DN 25, ø 33,7 x 2,0 | DN 25, ø 33,7 x 2,0 | m | 2 |  | 0
| DN 32, ø 42,4 x 2,0 | DN 32, ø 42,4 x 2,0 | m | 30 |  | 0
| DN 50, ø 60,3 x 2,0 | DN 50, ø 60,3 x 2,0 | m | 660 |  | 0
| DN 80, ø 88,9 x 2,3 | DN 80, ø 88,9 x 2,3 | m | 90 |  | 0
| DN 100, ø 114,3 x 2,3 | DN 100, ø 114,3 x 2,3 | m | 420 |  | 0
| DN 125, ø 139,7 x 2,6 | DN 125, ø 139,7 x 2,6 | m | 180 |  | 0
| DN 150, ø 168,3 x 2,6 | DN 150, ø 168,3 x 2,6 | m | 150 |  | 0
| DN 200, ø 219,1 x 2,6 | DN 200, ø 219,1 x 2,6 | m | 360 |  | 0
| 90°lok DN 15, ø 21,3 x 1,6 | 90°lok DN 15, ø 21,3 x 1,6 | kos | 390 |  | 0
| 90°lok DN 32, ø 42,4 x 2,0 | 90°lok DN 32, ø 42,4 x 2,0 | kos | 4 |  | 0
| 90°lok DN 50, ø 60,3 x 2,0 | 90°lok DN 50, ø 60,3 x 2,0 | kos | 150 |  | 0
| 90°lok DN 80, ø 88,9 x 2,3 | 90°lok DN 80, ø 88,9 x 2,3 | kos | 52 |  | 0
| 90°lok DN 100, ø 114,3 x 2,3 | 90°block DN 100, ø 114,3 x 2,3 | kos | 46 |  | 0
| 90°lok DN 125, ø 139,7 x 2,6 | 90°lok DN 125, ø 139,7 x 2,6 | kos | 24 |  | 0
| 90°lok DN 150, ø 168,3 x 2,6 | 90°lok DN 150, ø 168,3 x 2,6 | kos | 16 |  | 0
| 90°lok DN 200, ø 219,1 x 2,6 | 90°lok DN 200, ø 219.1 x 2.6 | kos | 24 |  | 0
| 45°lok DN 80, ø 88,9 x 2,3 | 45°block DN 80, ø 88,9 x 2,3 | kos | 8 |  | 0
| 45°lok DN 200, ø 219,1 x 2,6 | 45°block DN 200, ø 219.1 x 2.6 | kos | 4 |  | 0
| T kos DN 100 / odcep DN 80 | T piece DN 100 / branch DN 80 | kos | 2 |  | 0
| T kos DN 125 / odcep DN 100 | T piece DN 125 / branch DN 100 | kos | 8 |  | 0
| T kos DN 125 / odcep DN 125 | T piece DN 125 / branch DN 125 | kos | 2 |  | 0
| T kos DN 150 / odcep DN 100 | T piece DN 150 / branch DN 100 | kos | 4 |  | 0
| T kos DN 150 / odcep DN 150 | T piece DN 150 / branch DN 150 | kos | 2 |  | 0
| T kos DN 200 / odcep DN 200 | T piece DN 200 / branch DN 200 | kos | 2 |  | 0
| redukcija DN 32 / DN 25 | dN 32 / DN 25 reduction | kos | 2 |  | 0
| redukcija DN 100 / DN 80 | dN 100 / DN 80 reduction | kos | 24 |  | 0
| redukcija DN 125 / DN 100 | dN 125 / DN 100 reduction | kos | 10 |  | 0
| redukcija DN 150 / DN 125 | reduction DN 150 / DN 125 | kos | 6 |  | 0
| redukcija DN 200 / DN 125 | reduction DN 200 / DN 125 | kos | 2 |  | 0
| redukcija DN 200 / DN 150 | reduction DN 200 / DN 150 | kos | 2 |  | 0
| prirobnica DN 50 / OD 63 | flange DN 50 / OD 63 | kpl | 130 |  | 0
1.35 | Toplotna izolacija cevovodov in cevnih armatur s parozaporno izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z naslednjimi lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, požarna klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +110°C, lepljeno na cevovode in armature z originalnim lepilom proizvajalca, vključno s trakovi za šive; | Thermal insulation of pipelines and pipe fittings with vapour barrier insulation made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, fire classification B-s3-d0 according to EN13501-1, for temperatures from -50 to +110°C, bonded to pipelines and fittings with the original manufacturer's adhesive, including seam tapes;
| - ustreza proizvod ARMACELL tip Armaflex ACE Plus ali enakovredno | - corresponds to ARMACELL product type Armaflex ACE Plus or equivalent
| DN 15 ; debelina 13 mm | DN 15 ; thickness 13 mm | m | 680 |  | 0
| DN 20 ; debelina 19 mm | DN 20 ; thickness 19 mm | m | 2 |  | 0
| DN 25 ; debelina 19 mm | DN 25 ; thickness 19 mm | m | 2 |  | 0
| DN 32 ; debelina 25 mm | DN 32 ; thickness 25 mm | m | 36 |  | 0
| DN 50 ; debelina 40 mm | DN 50 ; thickness 40 mm | m | 790 |  | 0
| DN 80 ; debelina 40 mm | DN 80 ; thickness 40 mm | m | 100 |  | 0
| DN 100 ; debelina 40 mm | DN 100 ; thickness 40 mm | m | 500 |  | 0
| DN 125 ; debelina 40 mm | DN 125 ; thickness 40 mm | m | 220 |  | 0
| DN 150 ; debelina 40 mm | DN 150 ; thickness 40 mm | m | 180 |  | 0
| DN 200 ; debelina 40 mm | DN 200 ; thickness 40 mm | m | 440 |  | 0
| v ploščah ; debelina 40 mm | in panels ; thickness 40 mm | m2 | 40 |  | 0
1.36 | Tlačni preskus trdnosti in tesnenja notranjega razvoda v objektu, vključno s potrebnim materialom za izvedbo preizkusa, ter izdelavo pisnega poročila o uspešno opravljenem tlačnem preskusu; | Pressure test of the strength and tightness of the internal ductwork in the building, including the necessary materials to perform the test and the production of a written report on the successful completion of the pressure test;
| - preskusni tlak predvidoma 4,5 bar, pri čemer morajo biti vsi ventili proti zunanjim razvodom geosond zaprti (predvidoma 124 ventilov) Tlak na dnu geosonde ne sme preseči PN16 ! | - a test pressure of 4,5 bar, with all valves to the external geoprobe piping closed (124 valves expected) The pressure at the bottom of the geoprobe shall not exceed PN16 ! | kpl | 1 |  | 0
1.37 | Izpiranje cevovodov s sanitarno hladno vodo v celotnem sistemu novoinstaliranih razvodov z namenom odstranjevanja nečistoč v sistemu cevovodov, vključno s čiščenjem lovilnikov nesnage in drugih elementov; | Flushing of sanitary cold water piping throughout the newly installed piping system to remove impurities in the piping system, including cleaning of debris traps and other elements; | kpl | 1 |  | 0
1.38 | Kvalifikacija zvarov ter izdelava dokumentacije o zvarih: | Weld qualification and documentation of welds:
| - zvare lahko izvajajo samo varilci s certifikatom pooblaščenih organizacij, | - welding can only be carried out by welders certified by approved organisations,
| - postopek vizualne kontrole zvarov, kontrolirajo se vsi zvari - 100% zvarov, | - visual weld inspection procedure, all welds are inspected - 100% of welds,
| - postopek kontrole s snemanja zvarov - 10% zvarov, kjer so enakomerno zastopani vsi premeri, | - weld stripping inspection procedure - 10% of welds where all diameters are equally represented,
| - označevanje zvarov, izdelava dokumentacije z dokazili o ustreznosti ter slikovnim materialom; | - marking welds, producing documentation with proof of conformity and pictorial material; | kpl | 1 |  | 0
1.39 | Glikolni medij za geosonde in polnjenje sistema; glikolni medij je mešanica mehčane vode in glikola za geosonde, pričetek zmrzovanja -10°C; | Glycol medium for geoprobes and system filling; the glycol medium is a mixture of softened water and glycol for geoprobes, freezing point -10°C;
| - glikol mora biti okoljevarstveno sprejemljiv, nestrupen in ne sme predstavlja nevarnosti za zdravje, primeren mora biti za prenos toplote pri ogrevalnih in hladilnih procesih ter mora imeti certifikat skladnosti za navedene zahteve, | - the glycol must be environmentally acceptable, non-toxic and not present a health hazard, suitable for heat transfer in heating and cooling processes and certified for compliance with these requirements,
| - glikolni medij geosonde: predvidoma 25% glikola za geosonde, 75% mehčane vode, | - geoprobe glycol medium: assumed to be 25% geoprobe glycol, 75% softened water,
| - glikolni medij je potrebno pred polnjenjem zmešati v homogeno mešanico in šele nato napolniti sistem; | - the glycol medium must be mixed into a homogeneous mixture before filling and only then the system must be filled;
| - količina glikola cca 15.500 litrov = 15,5 m3 | - glycol quantity approx. 15,500 litres = 15.5 m3
| - količina glikolnega medija za geosonde (glikolna mešanica) cca 62.000 litrov = 62 m3 | - quantity of glycol medium for geoprobes (glycol mix) approx. 62,000 litres = 62 m3 | kpl | 1 |  | 0
1.40 | Ognjeodporna tesnilna masa, vgradnja na prehodu cevovoda skozi zid med požarnima sektortjema, požarna odpornost 90 minut, ustreza proizvod HILTI ali enakovredno. | Fire-resistant sealant, for installation at the pipeline passage through the wall between the two fire sectors, fire resistance 90 minutes, equivalent to HILTI or equivalent.
| Vsak prehod mora biti označen z nalepko ali tablico z osnovnimi požarnimi podatki; | Each passageway must be marked with a sticker or placard with basic fire information; | kpl | 1 |  | 0
1.41 | Preizkusno obratovanje delovanja sistema v obsegu: | Operational test of the system in scope:
| - pregled instalacije, armatur in opreme, | - inspection of plumbing, fixtures and fittings,
| - pregled delovanja naprav, elementov regulacije in nastavitve parametrov, | - overview of the operation of the devices, control elements and parameter settings,
| - obtok glikolnega medija, | - circulation of the glycol medium,
| - kontrola predpisanih parametrov glikolnega medija. | - control of the prescribed parameters of the glycol medium.
| Preizkusno obratovanje traja neprekinjeno 72 ur. | The test operation shall be continuous for 72 hours. | kpl | 1 |  | 0
1.42 | Napisne ploščice iz nerjavne pločevine z vgravirano oznako po shemi za opremo in armature, kompletno z jekleno pritrdilno žico ali visoko kvalitetne nalepke; visoko trajanje H (več kot 15 let) | Stainless steel nameplates with engraved marking according to the scheme for fittings and fixtures, complete with steel fixing wire or high quality stickers; high durability H (more than 15 years) | kpl | 1 |  | 0
1.43 | Samolepilne puščice za označitev smeri pretoka ter z napisom vrste medija: visoko trajanje H (več kot 15 let) | Self-adhesive arrows to indicate the direction of flow and the type of media: high durability H (more than 15 years) | kpl | 1 |  | 0
1.44 | Izdelava montažnih risb za izvedbo inštalacij med gradnjo objekta, kot so: detajli priključkov, montažne skice, montažni detajli, ipd. | Preparation of assembly drawings for the installation of services during the construction of the building, such as: connection details, assembly sketches, assembly details, etc. | kpl | 1 |  | 0
1.45 | Kvalifikacije montaže IQ-pregledi (instalation qualification) po GEP Commissioning protokolu in dokumentiranje kvalifikacije montaže, vključno z odpravo prvotnih napak montaže; | Installation qualification IQ checks (installation qualification) according to the GEP Commissioning Protocol and documentation of installation qualification, including correction of original installation faults; | kpl | 1 |  | 0
1.46 | Meritve delovanja OQ-kvalifikacija (operation qualification) ter dokumentiranje meritev delovanja, vključno z nastavitvijo parametrov; | OQ (operation qualification) measurements and documentation of performance measurements, including parameter settings; | kpl | 1 |  | 0
1.47 | Posnetki izvedenega stanja, sprotno beleženje vseh sprememb nastalih med izvedbo, vrisovanje in vpisovanje v PZI projektno dokumentacijo; | Recording of the as-built condition, keeping a running record of any changes made during the execution, plotting and recording in the PZI project documentation; | kpl | 1 |  | 0
1.48 | Stenska shema sistema, vloženo v zaščitni okvir s prosojnim umetnim steklom (plastika) ali plastificirano, vključno s pritrditvijo na notranjo steno v strojnici objekta; | A wall diagram of the system, encased in a protective frame with transparent plastic or plasticised glass, including fixing to an internal wall in the mechanical room of the building; | kpl | 1 |  | 0
1.49 | Primopredajna dokumentacija, ki mora vsebovati: izjave, dokazilo o zanesljivosti objekta, certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo, obratovanje in vzdrževanje ter ostalo primopredajno dokumentacijo. Predaja se v dveh mapiranih izvodih ter en izvod v elektronski obliki; | The handover documentation, which shall include: declarations, proof of the reliability of the facility, certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use, operation and maintenance, and other handover documentation. It shall be handed over in two mapped copies and one copy in electronic form; | kpl | 1 |  | 0
| GEOSONDE | BOREHOLE HEAT EXCHANGERS |  |  |  | 0