## 0_Naslovnica
OPOZORILO! Vsi prevodi v angleščino so strojno izdelani in zgolj informativne narave. V primeru kakršnekoli nejasnosti ali dvoma izključno velja izvirno besedilo v slovenščini. WARNING! All translations into English have been produced by machine translation and are provided for informational purposes only. In the event of any ambiguity or uncertainty, the original Slovenian text shall prevail exclusively.
| / | / | [5 empty] | /
| Sprem./Rev.: | Opis spremembe/Description of Changes: | [5 empty] | Datum/Date: | Podpis/Signature:
| Investitor/Investor: |  |  |  |  | Gradnja/Facility
|  |  | Univerza v Ljubljani Kongresni trg 12 1000 Ljubljana, Slovenija |  |  | Fakulteta za strojništvo/Faculty of Mechanical Engineering
| Projektant/Design Engineer: |  |  |  |  | Del objekta/sistem/Building/System:
|  |  | IBE, svetovanje, projektiranje in inženiring Ljubljana, Slovenija |  |  | STAVBA FAKULTETE/FACULTY BUILDING
| Projektant/Design Engineer: |  |  |  |  | Vrsta načrta/Documentation:
4 NAČRT S PODROČJA STROJNIŠTVA/ DOC. IN THE FIELD OF MECHANICAL ENGINEERING
|  | Ime in priimek/Name and Surname: |  |  | Id. št./Id. No: | Vsebina risbe (dokumenta)/Document Title:
| Vodja proj./ Des. Manager: | Boštjan Vuga, univ. dipl. inž. arh., grad. dip. (AA) |  |  | ZAPS 0035 PA PPN | PR. POPIS STROJNIH DEL/BOQ OF MECHANICAL WORKS 4/7 Ogrevanje in hlajenje/Heating and Cooling
| Poobl. strok./ Cert. Profess.: | Sašo Ocvirk, univ. dipl. inž. str. |  |  | IZS S-0717
| Poobl. strok./ Cert. Profess.: |  |  |  |  | Št. proj./ Proj. No.: | 362-19 |  | Vrsta dokument./ Document. Type: | DZR
| Izdelal/ Creator: | Sašo Ocvirk, univ. dipl. inž. str. |  |  | IZS S-0717 | Klas. ozn./ Class. No.: | -- |  | Stran/ Page: | 1/*
| Datum/ Date: | maj/May 2026 |  | Merilo/ Scale: | / | Ident. ozn./ Id. No: | JULFS--6S0702P

## 0_Osebe
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
POOBLAŠČENI STROKOVNJAKI, ODGOVORNI ZA IZDELAVO PROJEKTANTSKEGA POPISA:
Id. št. ZAPS/IZS | Pooblaščeni strokovnjak | Strokovno področje
IZS S-0717 | Sašo Ocvirk, univ. dipl. inž. str. | Ogrevanje in hlajenje
SODELAVCI PRI IZDELAVI PROJEKTANTSKEGA POPISA:
CERTIFIED EXPERTS RESPONSIBLE FOR ELABORATING THE BILL OF QUANTITIES:
Id. No ZAPS/IZS | Certified Expert | Area of Expertise
IZS S-0717 | Sašo Ocvirk, univ. dipl. inž. str. | Heating and cooling
COLABORATORS IN THE ELABORATING THE BILL OF QUANTITIES:

## 0.1_Uvod-STP
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
0.1 | SPLOŠNI TEHNIČNI POGOJI | GENERAL TECHNICAL CONDITIONS
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic operator with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
0.1.1 | Izvajalec se obveže, da bo upošteval veljavno zakonodajo, ki ureja graditev objektov v Republiki Sloveniji, vključno s povezanimi podzakonskimi akti, predpisi, tehničnimi smernicami, standardi, pravili stroke in dobro gradbeno prakso. Prav tako mora izvajalec upoštevati vse zahteve izdanega integralnega gradbenega dovoljenja in vsa dela izvesti skladno s projektno dokumentacijo ter ostalimi pogoji, objavljenimi v razpisni dokumentaciji. | The Contractor undertakes to comply with the applicable legislation governing the construction of buildings in the Republic of Slovenia, including related by-laws, regulations, technical guidelines, standards, professional rules and good construction practice. The Contractor shall also comply with all the requirements of the integral building permit issued and shall carry out all works in accordance with the project documentation and other conditions published in the tender documentation.
0.1.2 | Dela lahko izvaja samo izvajalec, ki je registriran za opravljanje gradbene dejavnosti in ima za tovrstna dela ustrezno zavarovanje za škodo, certifikate, tehnično izobražen kader, sredstva ter je usposobljen za samostojno pripravo in izvedbo del. | The work may only be carried out by a contractor who is registered to carry out construction work and who has the appropriate insurance for such work, certificates, technically trained staff, resources and is qualified to prepare and carry out the work independently.
0.1.3 | Izvajalec odgovarja za kakovost izvedbe vseh del. | The Contractor shall be responsible for the quality of the execution of all works.
0.1.4 | Izvajalec nosi vso odgovornost za nesreče in škodo, ki nastane na objektu ali v okolici zaradi njegovega dela. | The Contractor shall bear all liability for accidents and damage to the installation or the surrounding area caused by his work.
0.1.5 | Pred oddajo ponudbe se je izvajalec dolžan seznaniti z območjem predvidenim za gradnjo in temu prilagoditi vsa potrebna dela, kar mora biti zajeto v ponudbi. V neposredni bližini predvidene gradnje se nahajajo stavbe, v katerih potekajo izobraževalni in raziskovalni procesi. Zato bo izvajalec moral izvajati kontrolo hrupa in kontrolo vibracij. Dela, ki so hrupna in dela, ki povzročajo vibracije bo izvajalec moral preprečiti oziroma jih izvesti na način, da povzročajo minimalne vplive. Tehnologijo rušenja, pilotiranja in tehnologijo izvedbe ostalih del bo izvajalec moral prilagoditi tako, da bo vpliv minimalen. Izvajalec mora preprečiti in zmanjšati emisije delcev iz gradbišča na najmanjšo možno mero. | Before submitting a tender, the contractor is obliged to familiarise himself with the area to be constructed and to adapt any necessary works accordingly, which must be included in the tender. In the immediate vicinity of the proposed construction, there are buildings in which educational and research processes take place. The contractor will therefore be required to carry out noise and vibration control. Noise and vibration works will have to be avoided or carried out in such a way as to minimise the impact. Demolition, piling and other works will have to be adapted to minimise the impact. The contractor must avoid and minimise the emission of particulates emitted from the construction site as far as is reasonably practicable.
0.1.6 | Izvajalec je pred oddajo ponudbe dolžan pregledati projektno dokumentacijo in ostale pogoje, ki so del razpisne dokumentacije V primeru morebitnih napak in neskladij je izvajalec dolžan na to opozoriti naročnika pred oddajo ponudbe. | The Contractor is obliged to review the project documentation and other conditions forming part of the tender documentation before submitting the tender In case of any errors or inconsistencies, the Contractor is obliged to bring these to the attention of the Contracting Authority before submitting the tender.
0.1.7 | Pred oddajo ponudbe je izvajalec dolžan preveriti ustreznost popisov del in količin v teh popisih ter njihovo skladnost z ostalimi dokumenti projektne dokumentacije, ki so del razpisne dokumentacije. Prav tako je izvajalec dolžan preveriti vse detajle in sheme. Vse izmere je potrebno preveriti po posameznih projektih oz. načrtih, ki sestavljajo razpisno dokumentacijo. V primeru ugotovljenih neskladij je v času priprave ponudbe obvezan o tem obvestiti naročnika. | Before submitting a tender, the Contractor shall check the adequacy of the inventories of works and quantities in these Bills of Quantities and their conformity with the other documents of the project documentation forming part of the tender documentation. The Contractor shall also check all details and diagrams. All measurements shall be checked against the individual projects or plans forming part of the tender documentation. In the event of any discrepancies, the Contractor shall inform the Contracting Authority at the time of preparing the tender.
0.1.8 | Pred oddajo ponudbe je izvajalec dolžan v tem popisu preveriti zmnožke in seštevke ter prenose le-teh v rekapitulacijo. Izvajalec se s pripravo ponudbe obvezuje, da je prebral vse celice in elemente celotnega popisa, vključno z vsemi postavkami in splošnimi navodili ali določili in je preveril pravilnost preračuna ter s tem zagotavlja ponudbeno vrednost. | Before submitting a tender, the Contractor is required to check the products and totals in this Bill of Quantities (BoQ) and their transfer to the recapitulation. The Contractor undertakes, by preparing a tender, to have read all the cells and elements of the complete BoQ, including all headings and general instructions or provisions, and to have checked the correctness of the conversion, thereby guaranteeing the value of the tender.
0.1.9 | Dela bo izvajalec moral izvajati po predloženi projektni dokumentaciji, detajlih in z upoštevanjem navodil in potrditev projektanta, nadzornika in investitorja. Vso potrebno delavniško dokumentacijo zagotovi izvajalec del v okviru ponujene cene. | The Contractor shall carry out the works in accordance with the submitted design documents, details and subject to the instructions and approvals of the Designer, the Supervisor and the Investor. All necessary workshop documentation shall be provided by the Contractor within the scope of the price quoted.
0.1.10 | Pred izvedbo posameznih del je izvajalec dolžan pregledati projektno dokumentacijo za izvedbo gradnje (PZI) in elaborate. Na morebitne napake v dokumentaciji ali neskladja med posameznimi načrti ali deli načrtov (popisi del, tehnična poročila, lokacijski in tehnični prikazi) izvajalec opozori nadzornika in projektanta, in se z njima pravočasno uskladi. | The Contractor shall review the Detailed Design documentation (PZI) and the studies before carrying out the individual works. The Contractor shall draw the attention of the Supervisor and the Designer to any errors in the documentation or discrepancies between the individual designs or parts of designs (BoQ, technical reports, location and technical drawings) and shall coordinate with them in good time.
0.1.11 | Tehnični opisi, prikazi, detajli, sheme ter ostali dokumenti v PZI dokumentaciji predstavljajo dodaten opis popisnih postavk gradbeno obrtniških in inštalacijskih del ter jih je potrebno dosledno upoštevati skupaj s popisom del. | The technical descriptions, illustrations, details, diagrams and other documents in the Detailed Design documentation (PZI) are additional descriptions of the BoQ inventory items of the building, construction and installation works and must be strictly followed together with the BoQ.
0.1.12 | Specifikacije in zahteve, navedene v popisu, se ne smejo upoštevati kot edine zahteve. Izvajalec je dolžan v ceni zajeti in dobaviti vse elemente opreme ter opraviti dela in storitve, ki niso eksplicitno navedeni, a so bistvenega pomena za funkcionalnost, skladnost s predpisi ter kontinuirano, zanesljivo in varno obratovanje opreme. | The specifications and requirements set out in the BoQ shall not be taken as the only requirements. The Contractor shall be obliged to include in the price and supply all items of equipment and to carry out works and services which are not expressly mentioned but which are essential for the functionality, regulatory compliance and continuous, reliable and safe operation of the equipment.
0.1.13 | Vsa dela morajo biti izvedena kvalitetno in iz materialov z zahtevanimi lastnostmi, izvedena skladno z veljavno zakonodajo in z upoštevanjem navodil za vgradnjo za izbrane materiale in opremo, s predložitvijo predpisanih izjav o lastnostih in/ali certifikatov. Vsi gradbeni proizvodi (GP) morajo biti označeni s CE oznako. | All work shall be of good quality and be executed with materials of the required characteristics, in accordance with the applicable legislation and in compliance with the installation instructions for the materials and equipment selected, and shall be accompanied by the prescribed declarations of performance and/or certificates. All construction products (GP) shall bear the CE marking.
0.1.14 | Za vsako opisano delo v popisu je potrebno upoštevati celotno potrebno delo, ves osnovni in pomožni material, prevoz materiala in orodja na objekt, notranje transporte, delovne in pomožne odre, zaključno čiščenje in odstranitev odpadkov po dovršenem delu. | For each work described in the inventory, the total work required, all basic and ancillary materials, the transport of materials and tools to the site, internal transports, working and ancillary scaffolding, final cleaning and the disposal of waste after the work has been completed must be taken into account.
0.1.15 | Vsa delovna sredstva, organizacija in koordinacija del, pripravljalna, spremljajoča in zaključna dela, potrebni montažni in tesnilni materiali ter podkonstrukcije so sestavni del posameznih postavk. | All labour, organisation and coordination of the works, preparatory, accompanying and finishing works, necessary prefabrication and sealing materials and substructures are part of the individual items.
0.1.16 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - načrt organizacije gradbišča s podrobnim terminskim planom in izvedba vseh pripravljalnih del, postavitev, organizacija, zaščita in prijava gradbišča, gradbiščnih objektov, ureditev začasnih deponij, tekoče vzdrževanje, skupaj s plačilom splošnih stroškov pristojbin in davkov upravnih organov, pridobivanju raznih dovoljenj in soglasij za izvedbo, ograditev gradbišča in postavitev gradbene table in prometne signalizacije, zagotavljanje ustrezne varnosti na gradbišču, tekoče vzdrževanje in končna odstranitev gradbišča; - zagotovitev potrebnih začasnih površin za transportne poti in gradnjo izven območja gradbišča s plačilom stroškov za sanacijo in vzpostavitev okoliških zemljišč in objektov v prvotno stanje (soglasja, odškodnine, itd.); - začasni odvoz, deponiranje in vračanje izkopanega materiala, ki ga ne bo možno deponirati na gradbišču; - odvoz in zagotovitev odstranjevanja odpadnega gradbenega materiala skladno z zakonodajo na področju ravnanja z odpadki (odvoz na urejene deponije s plačilom komunalnih prispevkov in taks itd.); - oteženi izkop v mokrem terenu, izkop v vodi, odvod meteorne vode iz gradbene jame in vode, ki se izceja iz bočnih strani izkopov; - ustrezno varovanje izkopa gradbene jame za objekt in ostalih manjših posameznih izkopov za izvedbo komunalne infrastrukture brez posegov na sosednja zemljišča; - ustrezno varovanje obstoječih objektov, infrastrukture in okolice v času gradnje ter dokumentiranje vseh morebitnih škodnih dogodkov; - pripravljalna, spremljajoča in zaključna dela (zakoličbe, zagotovitev potrebnih komunalnih priključkov za potrebe izvajanja gradnje, izvedba začasnih inštalacij, označevanje podzemnih vodov, postavljanje in vzdrževanje zakoličbenih profilov, izvedba in označevanje novih in starih križanj ter morebitna zaščita križanj komunalnih vodov, geodetski posnetki in izdajanje vmesnih posnetkov izvedene infrastrukture naročniku, izdelava zbirnih kart, itd.), v kolikor ni to drugače določeno; - pridobivanje soglasij in izvedba morebitnih zapor na vseh cestah s plačilom stroškov, nadomestil in pristojbin; - zagotovitev oz. postavitev in končna odstranitev po zaključku gradnje začasnih skladišč in začasnega pisarniškega kontejnerskega objekta vključno z opremo za dve delovni mesti in za skupne operativne sestanke vel. ca. 40 m2 za potrebe naročnika, s tekočim vzdrževanjem in čiščenjem. | The following must also be included or taken into account in the uniform prices for individual items: - a construction site organisation plan with a detailed timetable and the execution of all preparatory works, the setting-up, organisation, protection and registration of the construction site, site facilities, the arrangement of temporary storage facilities, ongoing maintenance, including the payment of general costs of fees and taxes of the administrative authorities, the obtaining of various permits and consents for the execution, the fencing of the site and the erection of construction signs and traffic signals, the provision of adequate security on the site, ongoing maintenance and the final dismantling of the construction site; - provision of the necessary temporary areas for transport routes and off-site construction, with costs for restoration and reinstatement of surrounding land and buildings (consents, compensation, etc.); - temporary removal, storage and return of excavated material that cannot be stored on site; - removing and disposing of waste building materials in accordance with waste management legislation (removal to regulated landfill sites with payment of municipal fees and charges, etc.); - difficult excavation in wet ground, excavation in water, drainage of rainwater from the construction pit and water draining from the sides of excavations; - adequate protection of the excavation of the construction pit for the building and other small individual excavations for the implementation of the utility infrastructure without encroaching on neighbouring land; - adequate protection of existing facilities, infrastructure and the surrounding area during construction, and documentation of any damage incidents; - preparatory, accompanying and finishing works (stake-out, provision of the necessary utility connections for the needs of construction, execution of temporary installations, marking of underground lines, installation and maintenance of stake-out profiles, execution and marking of new and old crossings and possible protection of crossings of utility lines, geodetic surveys and issuing of intermediate images of the completed infrastructure to the client, production of summary maps, etc.), unless otherwise specified; - obtaining consents and implementing any road closures, with costs, compensation and fees; - provision or erection and final removal on completion of construction of temporary storage and temporary office container building including equipment for two workstations and for joint operational meetings of approx. 40 m2 for the needs of the client, with ongoing maintenance and cleaning.
0.1.17 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - izdelava montažne tehnične dokumentacije, detajlov izvedbe in vse druge potrebne delavniške dokumentacije (s področja arhitekture, gradbeništva, elektrotehnike, strojništva in zunanje ter krajinske ureditve) ter pridobitev obvezne potrditve s strani projektanta, nadzornika in investitorja; - odprava vseh vrst inštalacijskih kolizij z izvajanjem potrebnih premikov inštalacij in njihovim usklajevanjem na mestu montaže, vse v obsegu, ki ne vpliva na projektirano rešitev ali tip inštalacij oz. opreme; - zagotavljanje kompletnosti elektro-instalacijskih sistemov s področja avtomatike za doseganje njihove popolne funkcionalnosti delovanja; - stroški za nadzor in koordinacijo izvedbe vseh elektro napeljav, ki so predmet končne instalacije proizvoda (senčila, vrata, okna,…); - izdelava montažnih skic in detajlov za izvedbo v dogovoru z vodjo gradnje in nadzornikom; - izdelava in predstavitev vzorcev v ustrezni velikosti za potrditev projektanta, nadzornika in investitorja; - zagotavljanje varnosti in zdravja pri delu, zlasti izvajanje vseh del, ki izhajajo in ukrepov, ki izhajajo iz določil veljavnih predpisov varstva pri delu in zahtev Varnostnega načrta;- stroški garancij, ki jih mora izvajalec predložiti naročniku. | The following must also be included or taken into account in the uniform prices for individual items: - preparation of prefabricated technical documentation, construction details and all other necessary workshop documentation (architectural, civil, electrical, mechanical, exterior and landscaping) and obtaining the mandatory approval of the designer, the supervisor and the investor; - elimination of all types of installation conflicts by carrying out the necessary relocation of installations and their coordination at the installation site, all to the extent that it does not affect the design solution or the type of installation or equipment; - ensuring the completeness of electrical installation systems in the automation sector to achieve their full operational functionality; - the cost of supervising and coordinating the installation of all the electrical installations that are the subject of the final installation of the product (blinds, doors, windows, etc.); - preparation of erection drawings and details for implementation in agreement with the construction manager and supervisor; - production and presentation of samples in appropriate sizes for the approval of the designer, the supervisor and the investor; - ensuring health and safety at work, in particular the implementation of all the works arising from and the measures resulting from the provisions of the applicable occupational safety regulations and the requirements of the Safety Plan; - the cost of the guarantees to be provided by the contractor to the client.
0.1.18 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - strošek vodje del glavnega izvajalca, ki bo izvajal tudi koordinacijo s podizvajalci in z drugimi izvajalci, ki jih bo izbral naročnik in bo opravljal delo vodje gradbišča; - koordinacija del z ostalimi izvajalci oz. podizvajalci del, projektantom, nadzornikom in investitorjem pri medsebojnem usklajevanju organizacije gradbišča in časovnega načrta del ter pri usklajevanju izdelave plana montaže, potrjenih s strani vseh udeležencev gradnje; - stroški koordinacije, sodelovanja in usklajevanja z dobavitelji tehnološke, laboratorijske, eksperimentalne in vse ostale pohištvene ter multimedijske opreme ter z vsemi ostalimi dobavitelji oz. podizvajalci na objektu; - stroški izdelave situacij; - stroški zavarovanja objekta v času izvedbe del in delavcev ter materiala na gradbišču v času izvajanja del, od začetka del do pridobitve uporabnega dovoljenja za objekt. Zavarovanje mora biti sklenjeno pri ustrezni zavarovalni družbi najmanj v višini pogodbene vrednosti ali v zakonsko predpisani vrednosti (v kolikor zavarovanje v višini pogodbene vrednosti presega zakonsko dovoljeno), za ves čas trajanja izvedbe del do uspešne primopredaje objekta; - preizkušanje kvalitete materiala, ki se vgrajuje in dokazovanje kvalitete s certifikati oz. tehničnimi soglasji; - izvedba vseh zahtevanih testov in preizkusov (npr. tlačni preizkusi, termografski pregledi, meritve elektromagnetnega sevanja, hrupa, itd.), poskusnega obratovanja celotnega objekta s poudarkom na vseh inštalacijah ter izvajanje predpisanega monitoringa v skladu s Poročilom o vplivih na okolje (pred gradnjo, med gradnjo in po končani gradnji); - izdelava izkaza požarne varnosti, vključno s sprotnim spremljanjem gradnje in izvajanjem požarnovarnostnih zahtev ter izdelava Požarnega reda z obveznimi prilogami; - izdelava Izkaza zaščite pred hrupom v stavbah; - izdelava Izkaza energijskih lastnosti stavbe in energetske izkaznice; - sodelovanje z izvajalci gradbenega in projektantskega nadzora in investitorjem za izvedbo tehničnega pregleda in priprava primopredaje, ki mora vsebovati vso zahtevano dokumentacijo, predvsem pa: izjave o skladnosti, požarni izkaz in ostale izkaze ter obvezne tabele, dokazilo o zanesljivosti objekta (DZO), certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo in vzdrževanje ter vse ostale dokumente v skladu s predpisi in pogodbenimi določili. | The following must also be included or taken into account in the uniform prices of the individual items: - the cost of a works manager for the main contractor, who will also coordinate with subcontractors and other contractors selected by the client and act as site manager; - coordination of the works with other contractors or subcontractors, the designer, the supervisor and the investor in coordinating the organisation of the construction site and the timetable for the works, and in coordinating the production of an installation plan approved by all the participants in the construction; - the costs of coordination, cooperation and coordination with suppliers of technological, laboratory, experimental and all other furniture and multimedia equipment, as well as with all other suppliers or subcontractors on the site; - the cost of drawing up situations; - the cost of insuring the building during the execution of the works and the workers and materials on site during the execution of the works, from the start of the works until the building has been licensed for occupation. The insurance must be taken out with a suitable insurance company for at least the contract value or the legal value (if the insurance for the contract value exceeds the legal value), for the entire duration of the works until the successful handover of the building; - testing the quality of the material to be installed and proving it with certificates or technical approvals; - carrying out all required tests and trials (e.g. pressure tests, thermographic inspections, electromagnetic radiation measurements, noise measurements, etc.), trial operation of the entire building, with emphasis on all installations, and carrying out the required monitoring in accordance with the Environmental Impact Assessment Report (before, during and after construction); - preparation of a fire safety statement, including ongoing monitoring of construction and implementation of fire safety requirements, and preparation of a Fire Safety Order with mandatory annexes; - preparation of a Noise Protection Statement for buildings; - preparation of the Building Energy Performance Report and Energy Performance Certificate; - cooperation with the construction and design supervision contractors and the investor to carry out the technical inspection and prepare the handover, which must include all the required documentation, in particular: declarations of conformity, fire and other statements and mandatory tables, proof of reliability of the building (DZO), certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use and maintenance, and all other documents in accordance with the regulations and the contractual provisions.
0.1.19 | V enotnih cenah posameznih postavk, ki se nanašajo na opremo in posamezne sisteme, mora biti zajeto oz. upoštevano tudi naslednje: - dobava oz. transport, - stroški za vse delovne stroje za dvigovanje bremen in delovne košare za dostope do delovišč; - morebitni stroški povzročeni upravljavcem GJI, ki bi nastali v zvezi s predmetno gradnjo; - montaža, vključno s pomožnim montažnim materialom (vezni, tesnilni in pritrdilni material, sidra, nosilni profili, podkonstrukcije in podobno) in navodili proizvajalca, - odprava vseh kolizij sistemov s stenami in med sistemi, - izvedba vseh potrebnih tesnjenj, - priključitev in nastavitve, vključno z morebitnim kalibriranjem, - zagon, testiranje in meritve, vključno s poročili, - šolanje uporabnikov oz. vzdrževalnega osebja za uporabo in vzdrževanje sistemov, - navodila za obratovanje in vzdrževanje, - vsi potrebni certifikati, izjave o skladnosti oz. potrdila ter - vsa druga pomožna dela in material, da se zagotovi funkcionalnost posamezne postavke popisa. | The following must also be included or taken into account in the uniform prices for individual items relating to equipment and individual systems: - delivery/transport, - the cost of all lifting machines and work baskets for access to work sites; - any costs incurred to the operators of utility infrastructure (GJI) in connection with the subject construction; - installation, including ancillary installation materials (bonding, sealing and fixing materials, anchors, support profiles, substructures, etc.) and manufacturer's instructions, - eliminating all system-to-wall and system-to-system collisions, - all necessary sealing work, - connection and set-up, including calibration if necessary, - commissioning, testing and measurements, including reports, - training users or maintenance staff in the use and maintenance of the systems, - operating and maintenance instructions, - any necessary certificates, declarations of conformity or attestations; and - all other ancillary works and materials to ensure the functionality of each inventory item.
0.1.20 | Vsi odri morajo biti upoštevani v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All scaffolding must be included in the uniform prices of the items listed, except where specifically mentioned.
0.1.21 | Vsi delovni in pomožni odri, lestve in ostala potrebna pomožna sredstva, kot tudi čiščenje vseh elementov po končanih delih, mora biti upoštevano v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All working and auxiliary scaffolding, ladders and other necessary ancillaries, as well as the cleaning of all elements after completion of the works, shall be included in the uniform prices of the items listed, except those specifically mentioned.
0.1.22 | Delavniško dokumentacijo za vse nosilne jeklene konstrukcije in podkonstrukcije izdela izvajalec, strošek izdelave delavniške dokumentacije se upošteva v ponujenih cenah in se ne obračuna posebej. | The cost of the shop drawings for all steelwork and substructures shall be included in the prices quoted and shall not be charged separately.
0.1.23 | V enotnih cenah postavk mora biti vključeno tudi vgrajevanje vseh instalacijskih razvodov v opaže armirano betonskih elementov in izdelava prehodov inštalacij ter dodatno izrezovanje utorov in prebojev v kamnite, zidane ali armirano-betonske stene, ponovno demontiranje in montiranje vseh vrst montažnih sten, vsa dodatna dela za zagotavljanje primernih križanj med posameznimi instalacijskimi vodi, izdelava vseh vrst ojačitev konstrukcij in podobna dela, ki zagotavljajo kakovostno vgradnjo vseh vrst instalacijskih vodov in niso posebej navedena v popisu GOI del. V ponudbi morajo biti upoštevana vsa drobna strojna in elektro instalacijska dela in transporti. | The installation of all installation ducts in the formwork of reinforced concrete elements and the construction of installation penetrations, as well as the additional cutting of grooves and penetrations in stone, masonry or reinforced concrete walls, the reassembly and reinstallation of all types of prefabricated walls, all additional work to ensure adequate crossings between individual installation ducts, the construction of all types of structural reinforcement and similar work to ensure the quality installation of all types of installation ducts and not specifically mentioned in the BoQ of the Construction, installation and finishing works (GOI) shall also be included in the uniform prices of the items. The tender shall take into account all minor mechanical and electrical installation work and transport.
0.1.24 | Vsi kovinski elementi in konstrukcije, ki bi lahko bili izpostavljeni atmosferskim in ostalim korozijskim vplivom, morajo biti ustrezno protikorozijsko zaščiteni. | All metallic elements and structures that could be exposed to atmospheric and other corrosive influences must be adequately protected against corrosion.
0.1.25 | Za vse večje jeklene dele se skladno s predpisi, izdelajo ustrezne ozemljitve, nevidno pritrjene in speljane na splošno ozemljitev objekta. | For all major steel parts, appropriate earth connections shall be made in accordance with the regulations, invisibly attached and connected to the general earth of the building.
0.1.26 | Za vse vidne elemente in serijske elemente je obvezna predhodna uskladitev obdelav, barv in materialov s projektantom na podlagi dostavljenih vzorcev v ustrezni velikosti. Obvezna je preveritev dejanskih mer na licu mesta in posledična prilagoditev elementov in njihove montaže. | For all visible elements and serial elements, it is mandatory to coordinate the finishes, colours and materials with the designer beforehand on the basis of the supplied samples in the appropriate size. It is mandatory to check the actual dimensions on site and to adjust the elements and their installation accordingly.
0.1.27 | Dimenzije obrtniških izdelkov in količine je potrebno pred naročanjem preveriti na objektu. Potrebna je uskladitev vseh elementov (kljuke, okovje, detajlne konstrukcije in obdelave, itd.) s projektantom, nadzornikom in investitorjem. Izvajalec je dolžan pred izdelavo predložiti projektantu v potrditev ustrezne delavniške načrte in detajle. | The dimensions of the workmanship and quantities must be checked on site before ordering. All elements (hooks, fittings, detailed construction and finishes, etc.) must be coordinated with the designer, the supervisor and the investor. The contractor is obliged to submit the relevant workshop plans and details to the designer for approval before manufacture.
0.1.28 | V posameznih postavkah popisa so navedeni proizvajalci in/ali tipi posameznih sistemov, materialov ali opreme, s čimer so zgolj natančno opredeljene zahtevane tehnične lastnosti. Izvajalec del lahko ponudi nadomesten sistem, material ali opremo drugega proizvajalca in tipa, pri čemer morajo biti tehnične lastnosti ponujenega sistema, materiala ali opreme enakovredne ali boljše od opredeljenih v popisu, dimenzijsko pa ne smejo presegati projektiranih dimenzij. Vse funkcijske in tehnične karakteristike nadomestnih sistemov, materialov ali opreme mora izvajalec dokazati z ustrezno dokumentacijo. Vse morebitne posledice zaradi spremembe sistemov, materialov ali opreme vključno z morebitnimi spremembami oz. dopolnitvami BIM modelov in projektne dokumentacije, stroškovno in časovno bremenijo izvajalca. | The individual items of the Inventory shall specify the manufacturers and/or types of the individual systems, materials or equipment, thereby merely specifying the required technical characteristics. The Contractor may offer a substitute system, material or equipment of a different manufacturer and type, provided that the technical characteristics of the offered system, material or equipment shall be equivalent to or better than those specified in the BoQ, and shall not exceed the design dimensions. All functional and technical characteristics of the substitute systems, materials or equipment shall be demonstrated by the Contractor with appropriate documentation. Any consequences resulting from changes to systems, materials or equipment, including any changes or additions to the BIM models and project documentation, shall be borne by the Contractor in terms of cost and time.
0.1.29 | Vsako zamenjavo, uporabo in končni izbor nadomestnih sistemov, materialov, proizvodov in opreme morajo obvezno in pravočasno (pred dobavo in vgradnjo) pisno potrditi projektant (vseh sodelujočih strok), nadzornik in investitor. | Any replacement, use and final selection of alternative systems, materials, products and equipment must be approved in writing by the designer (of all disciplines involved), the supervisor and the investor in a timely manner (prior to delivery and installation).
0.1.30 | Izvajalec mora v ponudbeno ceno vključiti tudi: - ves čas gradnje sprotno beleženje sprememb oz. odstopanj od PZI dokumentacije, vključno z izdelavo tekstualnega opisa sprememb, - pripravo podlog na nivoju PZI, ki so potrebne za posodobitev oz. uskladitev BIM modela z izvedenim stanjem (LOD 500) in izdelavo projektne dokumentacije izvedenih del (PID), - mesečno predajanje potrjenih sprememb opreme in materiala, ki vplivajo na BIM model, v formatu IFC, - vzdrževanje in uporabljanje pri izvedbi zadnje veljavne revizije PZI dokumentacije, vključno z dopolnitvami PZI načrtov, ki so nastali zaradi sprememb med gradnjo. | The contractor must also include in the tender price: - keeping a record of changes or deviations from the construction documentation (PZI) throughout construction, including a textual description of the changes, - preparation of the Detailed Design (PZI) level documents required to update or align the BIM model with the as-built condition (LOD 500) and the preparation of the as-built project documentation for the works (PID), - monthly submission of approved equipment and material changes affecting the BIM model in IFC format, - maintenance and use in the execution of the last valid revision of the construction documentation (PZI), including additions to the construction design documentation (PZI) resulting from changes during construction.

## 0.2_Uvod-DGNB
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
0.2 | SPLOŠNI TEHNIČNI POGOJI ZA PODROČJE DGNB CERTIFICIRANJA | GENERAL TECHNICAL CONDITIONS FOR DGNB CERTIFICATION
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic entity with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
| Splošni pogoji za področje DGNB certificiranja predstavljajo dopolnilo splošnim tehničnim pogojem in ne odpravljajo drugih obveznosti in odgovornosti, ki jih ima izvajalec v skladu s predpisi in pogodbo. | The General Conditions for DGNB Certification are complementary to the General Technical Conditions and do not exclude other obligations and responsibilities that the Contractor has under the Regulations and the Contract.
0.2.1 | Izvajalec mora v svojih ponudbah upoštevati, da se bo objekt certificiral v skladu z zahtevami DGNB sistema certificiranja trajnostne gradnje, ter pravočasno (vsaj 60 dni pred vgradnjo posameznega produkta) dostaviti vso ustrezno dokumentacijo za vse v ponudbi zajete materiale, elemente in opremo. Zahtevana je uporaba materialov, elementov ali opreme, ki so okolju in ljudem prijazni, energetsko učinkoviti in obenem ustrezajo zahtevam DGNB sistema. Zahtevan nivo certifikata je: ZLATI CERTIFIKAT | The Contractor shall take into account in its tenders that the building will be certified in accordance with the requirements of the DGNB Sustainable Building Certification Scheme and shall deliver all relevant documentation for all materials, elements and equipment included in the tender in a timely manner (at least 60 days before the installation of each product). The use of materials, elements or equipment that are environmentally and human friendly, energy efficient and at the same time meet the requirements of the DGNB system is required. The required level of certification is: GOLD CERTIFICATE
0.2.2 | Podrobnejši opis DGNB sistema in navodila za posamezne kriterije so dostopna v dokumentu"DGNB Criteria Set New Construction Buildings, Version 2020 International", ki je na voljo na DGNB spletni strani https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria | A more detailed description of the DGNB system and guidance on the individual criteria is available in the document "DGNB Criteria Set New Construction Buildings, Version 2020 International", available on the DGNB website https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria
0.2.3 | Izvajalec mora v svojih ponudbah upoštevati, da je potrebno skladno z določili DGNB certifikacijskega sistema, pravočasno (pred pričetkom gradnje) dostaviti vso ustrezno dokumentacijo, za vse v ponudbi zajete materiale, elemente in opremo (tehnični list, varnostni list, izjava o lastnostih, tehnična navodila za ravnanje, servisiranje, vzdrževanje,...) v slovenskem jeziku. Vgradnja kakršnihkoli materialov, elementov ali opreme, se izvede zgolj na podlagi predhodne preveritve posredovane dokumentacije in obenem potrditve s strani nadzornika. | The Contractor must take into account in its tenders that, in accordance with the provisions of the DGNB certification system, all relevant documentation for all materials, elements and equipment included in the tender (technical data sheet, safety data sheet, declaration of properties, technical instructions for handling, servicing, maintenance,...) must be delivered on time (prior to the start of construction) in the Slovene language (in accordance with the provisions of the DGNB certification system). The installation of any materials, elements or equipment shall be subject to prior checking of the submitted documentation and, at the same time, to the approval of the Supervisor.
0.2.4 | Izbrani materiali, elementi, naprave, sistemi in oprema morajo prispevati k večji trajnosti stavbe v smeri zagotavljanja energetske učinkovitosti, ekonomičnega in enostavnega vzdrževanja ter čiščenja, dolge življenjske dobe, uporabe okolju prijaznih materialov ipd. | The materials, elements, appliances, systems and equipment chosen must contribute to the sustainability of the building in terms of energy efficiency, economic and easy maintenance and cleaning, long lifetime, use of environmentally friendly materials, etc.
0.2.5 | Predloženi dokumenti za vse uporabljene materiale, elemente in opremo morajo izpolnjevati zahteve najmanj kakovostne stopnje QS3 (zaželeno QS4), iz dokumenta: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001) | The documents submitted for all materials, components and equipment used shall meet the requirements of at least quality level QS3 (preferably QS4) of the document DGNB Quality Grades for Materials, Components and Equipment (JULFS--7X9001)
0.2.6 | V kolikor izbrani materiali oz. elementi, navedeni v posameznih postavkah, ne ustrezajo vsaj kakovostni stopnji QS3 iz seznama: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), je izvajalec dolžan na to opozoriti projektanta, nadzor in investitorja ter podati predlog ustreznega materiala oz. elementa. | If the selected materials or elements listed in the individual items do not meet at least quality level QS3 of the list of DGNB quality classes for materials, elements and equipment (JULFS--7X9001), the Contractor shall draw this to the attention of the Designer, the Supervisor and the Investor, and shall make a proposal for a suitable material or element.
0.2.7 | Izvajalec lahko v svoji ponudbi predlaga alternativne produkte in rešitve glede na predvidene s projektom, pod pogojem, da le-te prav tako izpolnjujejo vse navedene zahteve. Pri morebitnih predlaganih alternativnih produktih oz. rešitvah je potrebno upoštevati najmanj enake ali boljše lastnosti v smislu življenjske dobe, obstojnosti, ter enostavnosti in stroška čiščenja ter vzdrževanja v primerjavi s projektom predpisanimi rešitvami. Za alternativne rešitve izvajalec pridobi soglasje projektanta, nadzornika in investitorja pred pričetkom gradnje. | The Contractor may propose alternative products and solutions to those envisaged by the project in its tender, provided that they also meet all the requirements set out above. Any alternative products or solutions proposed shall have at least the same or better characteristics in terms of service life, durability, and ease and cost of cleaning and maintenance compared to the solutions envisaged by the project. For alternative solutions, the contractor shall obtain the agreement of the designer, the supervisor and the investor before starting construction.
0.2.8 | Izvajalec med gradnjo dnevno beleži vsa eventualna odstopanja od PZI projektne dokumentacije ter podatke pravočasno posreduje naročniku, nadzoru in projektantu. Potrjene spremembe vnese v podlage za izdelavo PID in posodobitev BIM modelov. | During construction, the Contractor shall record on a daily basis any deviations from the Detailed Design documentation (PZI) and shall provide the information to the Client, Supervision and the Designer in a timely manner. Confirmed changes shall be entered into the basis for the As-built documentation (PID) and BIM model updates.
0.2.9 | Izvajalec med gradnjo sproti izpolnjuje Seznam vseh konstrukcijskih sestav s pripadajočimi vgrajenimi gradbenimi materiali in dokumentira naslednje podatke o vgrajenih materialih (v slovenskem jeziku): - Varnostni list - Tehnični list - Izjavo o lastnostih (če je relevantno) - Izkazovanje morebiti obstoječega okoljskega certifikata (Tip I - okoljski znak ali Tip III - okoljska produktna deklaracija /EPD) - Izjavo proizvajalca ali dobavitelja, da produkt ustreza zahtevam ENV1.2 - Tehnična navodila za ravnanje, servisiranje, vzdrževanje oziroma ostale, z zakonom predpisane dokumente in dokumentacijo. | During construction, the Contractor shall keep a List of all structural assemblies with their associated construction materials and document the following information on the materials installed (in Slovene language): - Safety Data Sheet - Technical Data Sheet - Declaration of performance (if applicable) - Demonstration of any existing environmental certification (Type I - Ecolabel or Type III - Environmental Product Declaration /EPD) - A declaration by the manufacturer or supplier that the product complies with the requirements of ENV1.2 - Technical instructions for handling, servicing, maintenance or other documents and documentation required by law.
0.2.10 | Za vse vgrajene bistvene tehnične sisteme mora izvajalec zagotoviti obstoj pooblaščenega servisa, ki deluje na območju Republike Slovenije, da ima investitor možnost skleniti ustrezno pogodbo o vzdrževanju. Med bistvene tehnične sisteme sodijo npr.: sistemi ogrevanja in hlajenja, priprava tehnoloških medijev, prezračevanje in klimatizacija, sistemi detekcije in gašenja požara, sistemi tehničnega varovanja, BMS in CNS sistemi upravljanja stavbe, razsvetljava, komunikacijski in WI-FI sistemi,... | For all installed essential technical systems, the contractor must ensure the existence of an authorised service centre operating in the territory of the Republic of Slovenia, so that the investor has the possibility of concluding an appropriate maintenance contract. The essential technical systems include, for example: heating and cooling systems, technological media preparation, ventilation and air conditioning, fire detection and extinguishing systems, technical security systems, BMS and CNS building management systems, lighting, communication and WI-FI systems,...
0.2.11 | Zaželeno je, da imajo uporabljeni elementi in materiali okoljsko oznako Tip I. (kot npr. ENCODE, BLUE ANGEL, ipd...). | It is preferable that the elements and materials used have a Type I environmental label (such as ENCODE, BLUE ANGEL, etc...).
0.2.12 | Izvajalec bo za elemente iz lesa moral dokazovati izvor z navedbo izvorne države in tipa lesa, FSC / PEFC certifikat z dodatnim pripadajočim potrdilom Chain of custody-trgovski certifikat dobavitelja - ta se dokazuje z dobavnicami, računi ali enakovredno. Za izdelke iz naravnega kamna iz EU držav je potrebna deklaracija, da je izvor in procesiranje teh izdelkov v celoti v EU državah. Za izdelke iz naravnega kamna, ki prihajajo iz držav izven EU, je potrebno predložiti dokazilo o izpolnjevanju ILO konvencije 182, ki vključuje neodvisna inšpekcijska poročila. | For wood elements, the contractor will be required to provide proof of origin, indicating the country of origin and the type of wood, FSC/PEFC certification with an additional Chain of Custody certificate - the supplier's trade certificate - this shall be evidenced by delivery notes, invoices or equivalent. For natural stone products from EU countries, a declaration that the sourcing and processing of these products is entirely in EU countries is required. For natural stone products from non-EU countries, proof of compliance with ILO Convention 182, including independent inspection reports, is required.
0.2.13 | Izobraževanje udeležencev pri gradnji Izvajalec je dolžan vse udeležence pri gradnji podrobneje seznaniti tudi z relevantnimi koncepti, študijami, elaborati, ki opredelujejo trajnostni način gradnje za naslednja področja: - zaščita pred hrupom (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)) - zaščita pred prašenjem - zaščita tal in podzemne vode (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)), Analiza tveganja za onesnaženje vodnega telesa podzemne vode št. 0346-023/2023, maj 2023 (Geološko projektiranje d.o.o.)) - ravnanje z gradbenimi odpadki (Načrt gospodarjenja z gradbenimi odpadki) Izobraževanja se izvajajo skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.1 1.2, 2.2, 3.2 in 4.2 Training for the parties implementing the construction work | Training of construction participants The contractor is also obliged to inform all construction participants in detail about relevant concepts, studies, elaborations defining sustainable construction methods for the following areas: - noise protection (Environmental Impact Assessment Report No 100123-11523, dated 11.5.2023, supplemented on 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.)) - dust protection - protection of soil and groundwater (Environmental Impact Assessment Report No. 100123-11523, dated 11.5.2023, supplemented 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.), Risk analysis for contamination of the groundwater No. 0346-023/2023, May 2023 (Geološko projektiranje d.o.o.)) - construction waste management (Construction Waste Management Plan) The training shall be carried out in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.1 1.2, 2.2, 3.2 and 4.2 Training for the parties implementing the construction work
0.2.14 | Navodila za obratovanje in vzdrževanje objekta Izvajalec pripravi Navodila za obratovanje in vzdrževanje objekta skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilih: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual | Instructions for the operation and maintenance of the facility The Contractor shall prepare the Operation and Maintenance Instructions for the Facility in accordance with the applicable Slovenian legislation and the DGNB System Instructions specified in the Criteria: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual
0.2.15 | Meritve kontrole kakovosti gradnje Izvajalec mora upoštevati, da se bodo po koncu gradnje izvedle naslednje meritve: - meritve zrakotesnosti - meritve s termokamero (termografija) - meritve akustike - meritve zvočne zaščite ovoja stavbe - meritve zvočne zaščite ločilnih elementov med posameznimi prostori različnih namembnosti - meritve udarnega zvoka - meritve vlažnosti vgrajenih elementov, pred vgradnjo finalnih tlakov - test odvoda dima in toplote Meritve morajo opraviti ustrezno usposobljeni preskusni organi ali strokovnjaki ter rezultate oceniti in primerjati z zahtevami. Obseg opravljenih meritev mora biti sorazmeren z velikostjo zgradbe in mora ustrezno odražati cilj preverjanja kakovosti zgradbe. Smiselno je, da izvajalec del tekom gradnje za sprotno kontrolo kakovosti vgrajenih materialov, elementov in opreme, sam izvaja meritve. Končne meritve (ob primopredaji) izvede tretja oseba kot neodvisna potrditev doseganja zahtev. Meritve se izvajajo skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 2. Quality control measurements | Construction quality control measurements The contractor must take into account that the following measurements will be carried out after completion of the construction: - airtightness measurements - thermal camera measurements (thermography) - acoustics measurements - measurements of the sound insulation of the building envelope - measurements of the sound insulation of the separating elements between different rooms of different uses - impact sound measurements - moisture measurements of the installed elements, prior to the installation of the final flooring - smoke and heat extraction test The measurements shall be carried out by suitably qualified test bodies or experts and the results evaluated and compared with the requirements. The extent of the measurements carried out shall be proportionate to the size of the building and shall adequately reflect the objective of the building quality verification. It is reasonable for the contractor to carry out his own measurements during construction to check the quality of the materials, elements and equipment installed. Final measurements (at handover) are carried out by a third party as an independent confirmation of compliance with the requirements. The measurements shall be carried out in accordance with the applicable Slovenian legislation and the DGNB system instructions specified in the benchmark: PRO 2.2 2. Quality control measurements
0.2.16 | Zagotavljanje kakovosti za uporabljene gradbene proizvode Izvajalec mora zagotavljati izvajanje primerjav med definiranim in dejansko uporabljenim materialom, elementom ali opremo skladno seznamom: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), vključno z dokazno dokumentacijo ugotovitev primerjav ter skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 3.1 Quality assurance for the used construction products | Quality assurance for the construction products used The Contractor shall ensure that comparisons are made between the defined and the actual material, element or equipment used in accordance with the list: DGNB Quality Grades of Installed Materials, Elements and Equipment (JULFS--7X9001), including supporting documentation of the findings of the comparisons, and in accordance with the DGNB system instructions defined in the Criterion: PRO 2.2 3.1 Quality assurance for the used construction products
0.2.17 | Zaščita pred vlago Izvajalec predloži dokumentacijo, ki dokazuje, da je bil izveden program prezračevanja, prilagojen stavbi, s čimer se zagotovi pogoje, da so vgrajeni gradbeni elementi ustrezno suhi, skladno z navodili DGNB opredeljenimi v merilu: PRO 2.2 4.1 Mould prevention | Protection against moisture The Contractor shall provide documentation demonstrating that a building-specific ventilation programme has been implemented to ensure that the building elements installed are adequately dry, in accordance with the DGNB guidelines specified in the criteria: PRO 2.2 4.1 Mould prevention
0.2.18 | Preizkusi delovanja sistemov Izvajalec sodeluje pri izvedbi predhodnega in končnega preizkusa delovanja vseh bistvenih tehničnih komponent stavbe in pripravi ustrezne dokazne dokumentacije ter pri usposabljanju vzdrževalcev/upravljalcev stavbe, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators | System performance tests The Contractor shall be involved in the performance of the preliminary and final performance tests of all essential technical components of the building and the preparation of the relevant supporting documentation, as well as in the training of the maintenance/management staff of the building, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators
0.2.19 | Poročilo o zagonu objekta Izvajalec sodeluje pri pripravi končnega poročila o zagonu objekta, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 5.1 Creation of a detailed final report | Commissioning report The Contractor shall be involved in the preparation of the final commissioning report, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 5.1 Creation of a detailed final report
0.2.20 | Koncept celovitega delovanja sistemov v stavbi Izvajalec sodeluje pri procesu implementiranja stalnega nadzora in nastavitev delovanja stavbe ter usposabljanju vzdrževalcev/upravljalcev stavbe. Navedeno se izvede v skladu z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 6.1 Creation and handover of an integral operating concept | The concept of integrated building systems The contractor is involved in the process of implementing the building's continuous monitoring and settings and training the building's maintenance/management staff. This shall be done in accordance with the DGNB system instructions defined in the benchmark: PRO 2.3 6.1 Creation and handover of an integral operating concept
0.2.21 | Prilagoditev nastavitev sistemov po začetni fazi uporabe objekta Izvajalec sodeluje pri ponovnem pregledu delovanja vseh bistvenih tehničnih sistemov ter eventualni ponovni prilagoditvi teh sistemov s strani strokovnjaka oz. (neodvisne) tretje osebe. Postopek se izvede po približno 10–14 mesecih po zaključku gradnje, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 7.1 Readjustment of the system following initial operating phase | Adjusting system settings after the initial phase of use of the building The Contractor shall be involved in the re-examination of the functioning of all essential technical systems and the possible re-adjustment of these systems by an expert or (independent) third party. The procedure shall be carried out approximately 10-14 months after completion of construction, in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.3 7.1 Readjustment of the system following initial operating phase

## 4.7.0_Rekapitulacija
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
| REKAPITULACIJA STROŠKOV STROJNIH DEL | COST SUMMARY OF MECHANICAL WORKS
| 4 NAČRT S PODROČJA STROJNIŠTVA | 4 DOCUMENTATION IN THE FIELD OF MECHANICAL ENGINEERING
| 4/7 Ogrevanje in hlajenje | 4/7 Heating and Cooling
4.7 | STROJNA DELA | MECHANICAL WORKS
4.7.1 | OGREVANJE | HEATING | 0
4.7.2 | HLAJENJE | REFRIGERATION | 0
4.7.3 | GLIKOLNI MEDIJ SSE | GLYCOL MEDIUM SSE | 0
4.7.4 | GLIKOLNI MEDIJ KLIMATIZACIJA | GLYCOL MEDIUM AIR CONDITIONING | 0
0
0 | NEPREDVIDENA DELA | UNFORSEEN WORKS | 0
| SKUPAJ STROJNA DELA: | TOTAL MECHANICAL WORKS: | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT

## 4.7.1_Ogrevanje
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.7 | STROJNA DELA | MECHANICAL WORKS
4.7.1 | OGREVANJE | HEATING |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
1 | OGREVANJE | HEATING
| Vse postavke v nadalevanju zajemajo dobavo in montažo (razen tam kjer je to posebej navedeno). | All items below include delivery and installation (except where specifically indicated).
1.1 | Toplotna črpalka / hladilni agregat, večnamenska naprava z možnostjo hkratne priprave ogrevne in hladilne vode, naprava toplotne viške (grelne ali hladilne) kompenzira preko tretjega integriranega prenosnika toplote posredno na sistem geosond. Kompaktna naprava, tiha izvedba z dvema hladilnima krogoma ter z večimi spiralnimi "scroll" kompresorji, z okoljevarstvenim hladilnim sredstvom HFC, z opremo za zvezno regulacijo delovanja in krmilno električno omaro s povezlivo na CNS, RS-485 Modbus., Ethernet, z varnostnimo opremo za kontrolo delovanja pretokov na vseh treh vodnih straneh, skladnost z Eurovent, CE in evropskimi direktivami, vključno s protivibracijskimi podstavki in montažnim materialom; | Heat pump / chiller, multifunctional unit with the possibility of simultaneous heating and cooling water production, the unit compensates for heat peaks (heating or cooling) via a third integrated heat exchanger indirectly to the geoprobe system. Compact unit, quiet design with two refrigeration circuits and multiple scroll compressors, with HFC refrigerant, with continuous operation control equipment and electrical control cabinet with connection to CNS, RS-485 Modbus, Ethernet, with safety equipment to control the operation of the flows on all three water sides, compliance with Eurovent, CE and European directives, including anti-vibration mats and mounting material;
| Trije obratovalni režimi: | Three operating modes:
| 1. Priprava ogrevne vode, režim delovanja kot toplotna črpalka: | 1. Hot water production, heat pump mode:
| - ogrevna moč 404,6 kW pri temp. ogrevne vode 45/50°C, pretok 70,5 m3/h, padec tlaka 26 kPa | - heating output 404,6 kW at heating water temperature 45/50°C, flow 70,5 m3/h, pressure drop 26 kPa
| - glikolni medij (25% propilen glikol, 75% vode) iz sistema geosond Δt= 4°C, pretok 67,9 m3/h, padec tlaka 29 kPa; | - glycol medium (25% propylene glycol, 75% water) from geoprobe system Δt= 4°C, flow 67.9 m3/h, pressure drop 29 kPa;
| 2. Priprava hladilne vode, režim delovanja kot hladilni agregat: | 2. Chilled water production, operation as a chiller:
| - hladilna moč 439,4 kW pri temp. hladilne vode 14/9°C, pretok 75,6 m3/h, padec tlaka 33 kPa | - cooling power 439.4 kW at cooling water temperature 14/9°C, flow rate 75.6 m3/h, pressure drop 33 kPa
| - glikolni medij (25% propilen glikol, 75% vode) iz sistema geosond Δt= 4°C, pretok 113,5 m3/h, padec tlaka 79 kPa; | - glycol medium (25% propylene glycol, 75% water) from geoprobe system Δt= 4°C, flow rate 113,5 m3/h, pressure drop 79 kPa;
| 3. Priprava ogrevne vode in hladilne vode hkrati, režim simultanega delovanja kot toplotna črpalka + hladilni agregat: | 3. Simultaneous operation as heat pump + chiller, simultaneous heating and cooling water production:
| - ogrevna moč 439,1 kW pri temp. ogrevne vode 44,6/50°C, pretok 70,5 m3/h, padec tlaka 28 kPa | - heating output 439,1 kW at a heating water temperature of 44,6/50°C, flow rate 70,5 m3/h, pressure drop 28 kPa
| - hladilna moč 335,7 kW pri temp. hladilne vode 12,8/9°C, pretok 75,6 m3/h, padec tlaka 33 kPa | - cooling power 335.7 kW at cooling water temperature 12.8/9°C, flow 75.6 m3/h, pressure drop 33 kPa
| Ostali tehnični podatki: | Other technical data:
| - število hladilnih krogov: 2, število kompresorjev: 4, okoljevarstveno hladilno sredstvo HFC, ustreza R410A, regulacija moči 10 - 100 % | - number of refrigeration circuits: 2, number of compressors: 4, environmentally friendly HFC refrigerant, R410A equivalent, power control 10 - 100%
| - kontrola delovanja temperatur in pretokov na vseh treh vodnih straneh | - monitoring the operation of temperatures and flows on all three water sides
| - učinkovitosti delovanja TER > 8,0 / EER > 5,0 / COP > 4,1 | - tER > 8.0 / EER > 5.0 / COP > 4.1
| - električni podatki: Pel = 108,7 kW, Imax = 237 A, 400V / 3 / 50Hz; | - electrical data: Pel = 108.7 kW, Imax = 237 A, 400V / 3 / 50Hz;
| - krmiljenje in regulacija naprave z možnostjo nastavitve vseh parametrov v različnih režimih delovanja, možnostjo avtomatskega preklopi med režimi, ter komunikacija z obtočnimi črplkami na vseh treh vodnih straneh | - control and regulation of the plant with the possibility of setting all parameters in different operating modes, automatic switching between modes, and communication with the circulators on all three water sides
| - komunikacija štirimi napravami TCHA med seboj (vodilna, sledljiva, ...), kot na primer Aernet | - communication between four TCHA devices (lead, follow, ...), such as Aernet
| - komunikacije na CNS: RS-485 Modbus, Ethernet | - cNS communications: RS-485 Modbus, Ethernet
| - dimenzije do: dolžina L x širina W x višina H = 2600 x 1300 x 2200 mm | - dimensions up to: length L x width W x height H = 2600 x 1300 x 2200 mm
| - obratovalna teža do 2000 kg | - operating weight up to 2000 kg
| - tiha izvedba, zvočna moč do 84 dB(A), tlačna moč na razdalji 2m: do 63 dB(A) | - quiet design, sound power up to 84 dB(A), pressure power at 2 m: up to 63 dB(A)
| - priključki na cevovode 6x DN100 | - pipeline connections 6x DN100
| - vključno z protivibracijskimi podstavki, prirobnicami za cevne priključke, vijačnim, pritrdilnim in tesnilnim materialom; | - including anti-vibration mats, flanges for pipe connections, screwing, fastening and sealing materials;
| -ustreza proizvod AERMEC tip NXP1400°4L°°° z dodatno opremo ali enakovredno | -corresponds to AERMEC product type NXP1400°4L°°° with accessories or equivalent
| Oznaka: TCHA40.1, TCHA40.2, TCHA40.3, TCHA40.4 | Code: TCHA40.1, TCHA40.2, TCHA40.3, TCHA40.4 | kpl | 4 |  | 0
1.2 | Hidravlična kretnica, jeklena tlačna posoda PN10, skladno z direktivo o tlačni opremi PED, pokončne izvedbe, material ogljikovo jeklo P235TR1 (St37.0), ustrezne debeline jekla (min 10mm), skladnost z direktivo PED, komplet z vsemi priključki, izdelano po delavniški risbi dobavitelja, skladno s shemo in v načrtu, vključno s potiprirobnicami, varilnim, pritrdilnim, tesnilnim materialom. Tehnični podatki: | Hydraulic pressure switch, steel pressure vessel PN10, PED compliant, upright design, material carbon steel P235TR1 (St37.0), appropriate steel thickness (min 10mm), PED compliant, complete with all connections, manufactured according to supplier's shop drawing, as per schematic diagram and as per plan, including sub-plates, welding, fixing, sealing material. Technical data:
| - ogrevna voda 50/40°C | - heating water 50/40°C
| - prostornina hidravlične kretnice: V = 16 m3 | - hydraulic switching volume: V = 16 m3
| - dimenzije posode: premer D x višina H = ø2300 x 4500 mm, postavljeno na jeklenih nogah 500 mm od tal, skupna višina 5000 mm | - dimensions of the container: diameter D x height H = ø2300 x 4500 mm, raised on steel legs 500 mm from the floor, total height 5000 mm
| - z pregradno ploščo horizontalno na sredini v kretnici z odrtino ø500 mm | - with a horizontal barrier plate in the centre in a switch with a ø500 mm opening
| - s prirobničnimi priključki PN10: 4x DN300 (glavni priključki od tega 2x zg.prekat, 2x sp.pekat), 1x DN50 (spodaj na dnu); z navojnimi priključki 1x DN25 (zgoraj na vrhu) ter 7x DN15 priključki za tipala in prikazovalnike | - with PN10 flanged connections: 4x DN300 (main connections of which 2x upper chamber, 2x lower chamber), 1x DN50 (bottom); with 1x DN25 threaded connections (top) and 7x DN15 connections for sensors and displays
| - prirobnična revizijska odprtina PN10: DN500 s slepo protiprirobnico, pritrdilnim in tesnilnim materialom | - pN10 flanged inspection opening: DN500 with blind counter flange, fixing and sealing material
| - antikorozijska zaščita; dvakratni premaz s temeljnim temperaturno odpornim antikorozijskim premazom ter dvakratnio premaz s prekrivno barvo, antikorozijska zaščita s temeljnimi in prekrivnimi barvami mora biti obstojna na temperature v območju od -20 do +80°C in se mora izvesti v skladu z EN ISO 12944 z življenjsko dobo: visoko trajanje H (več kot 15 let). | - anti-corrosion protection; two coats of temperature-resistant anti-corrosion primer and two coats of overcoat, the anti-corrosion protection with primers and overcoats must be resistant to temperatures in the range -20 to +80°C and must be carried out in accordance with EN ISO 12944 with a service life of: high durability H (more than 15 years).
| - obratovalna teža 18.000 kg | - operating weight 18.000 kg
| - toplotna parozaporno izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z naslednjimi lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, požarna klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +110°C, lepljeno na rezervoar z originalnim lepilom proizvajalca, vključno s trakovi za šive, debelina 50 mm; | - thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, fire classification B-s3-d0 according to EN13501-1, for temperatures from -50 to +110°C, bonded to the tank with the original manufacturer's adhesive, including seam tapes, 50 mm thick;
| Oznaka: HKA41.10 | Code: HKA41.10 | kpl | 1 |  | 0
1.3 | Razdelilnik / zbiralnik izdelan iz jeklene cevi DN300 ø323,9x7,1 po EN 10216-1 (DIN2448), iz materiala P235TR2 (St37.0), PN10, ležeče izvedbe, z prirobničnima zaključkoma DN300 in eno slepo prirobnico DN300, skladnost z direktivo PED, komplet z vsemi priključki, izdelano po delavniški risbi dobavitelja, skladno s shemo in v načrtu, vključno s potiprirobnicami, varilnim, pritrdilnim, tesnilnim materialom; | Manifold / manifold made of steel pipe DN300 ø323,9x7,1 according to EN 10216-1 (DIN2448), made of material P235TR2 (St37.0), PN10, of creep design, with flanged ends DN300 and one blind flange DN300, PED compliance, complete with all connections, made according to the supplier's shop drawing, according to the scheme and in the plan, including sub-fittings, welding, fixing, sealing material;
| - ogrevna voda 50/40°C | - heating water 50/40°C
| - dimenzije: premer D x dolžina L = DN300 x 2000 mm, z konstrukcijo za pritrditev na tla oziroma obešanje na strop | - dimensions: diameter D x length L = DN300 x 2000 mm, with floor or ceiling mounting structure
| - s prirobničnimi priključki PN10: 4x DN125 in navojnimi priključki: 1x DN32, 2x DN15 | - with PN10 flange connections: 4x DN125 and threaded connections: 1x DN32, 2x DN15
| - čiščenje in barvanje, odstranitev rje do kovinskega sijaja, dvakratni premaz s temeljnim antikorozijskim barvami ter dvakratni premaz s prekrivno barvo: obstojnost na temperature v območju od +5 do +80°C, skladno z EN ISO 12944 z življenjsko dobo: visoko trajanje H (več kot 15 let) | - cleaning and painting, rust removal to metallic gloss, double coating with anti-corrosion primer and double coating with overcoat: temperature resistance in the range +5 to +80°C, in accordance with EN ISO 12944 with service life: high durability H (more than 15 years)
| - komplet s toplotna parozaporna izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +105°C, debelina 40mm | - complete with thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, classification B-s3-d0 according to EN13501-1, for temperatures -50 to +105°C, thickness 40mm
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and pipe clamps with noise damping lining, suitable for HILTI or SIKLA, or equivalent;
| Oznaka: pri HKA41.10 | Code: at HKA41.10 | kpl | 2 |  | 0
1.4 | Razdelilnik / zbiralnik izdelan iz jeklene cevi DN300 ø323,9x7,1 po EN 10216-1 (DIN2448), iz materiala P235TR2 (St37.0), PN10, ležeče izvedbe, z prirobničnima zaključkoma DN300 in eno slepo prirobnico DN300, skladnost z direktivo PED, komplet z vsemi priključki, izdelano po delavniški risbi dobavitelja, skladno s shemo in v načrtu, vključno s potiprirobnicami, varilnim, pritrdilnim, tesnilnim materialom; | Manifold / manifold made of steel pipe DN300 ø323,9x7,1 according to EN 10216-1 (DIN2448), made of material P235TR2 (St37.0), PN10, of creep design, with flanged ends DN300 and one blind flange DN300, PED compliance, complete with all connections, made according to the supplier's shop drawing, according to the scheme and in the plan, including sub-fittings, welding, fixing, sealing material;
| - ogrevna voda 50/40°C | - heating water 50/40°C
| - dimenzije: premer D x dolžina L = DN300 x 1500 mm, s konstrukcijo za pritrditev na tla / strop | - dimensions: diameter D x length L = DN300 x 1500 mm, with floor/ceiling mounting structure
| - s prirobničnimi priključki PN10: 2x DN200 in navojnimi priključki: 1x DN32, 2x DN15 | - with PN10 flange connections: 2x DN200 and threaded connections: 1x DN32, 2x DN15
| - čiščenje in barvanje, odstranitev rje do kovinskega sijaja, dvakratni premaz s temeljnim antikorozijskim barvami ter dvakratni premaz s prekrivno barvo: obstojnost na temperature v območju od +5 do +80°C, skladno z EN ISO 12944 z življenjsko dobo: visoko trajanje H (več kot 15 let) | - cleaning and painting, rust removal to metallic gloss, double coating with anti-corrosion primer and double coating with overcoat: temperature resistance in the range +5 to +80°C, in accordance with EN ISO 12944 with service life: high durability H (more than 15 years)
| - komplet s toplotna parozaporna izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +105°C, debelina 40mm | - complete with thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, classification B-s3-d0 according to EN13501-1, for temperatures -50 to +105°C, thickness 40mm
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and pipe clamps with noise damping lining, suitable for HILTI or SIKLA, or equivalent;
| Oznaka: pri HKA41.10 | Code: at HKA41.10 | kpl | 2 |  | 0
1.5 | Ekspanzijska naprava za kompenzacijo temperaturnih raztezkov v sistemu ogrevne vode skladno z EN12828, naprava za vzdrževanje tlaka z dvema kompresorjema ter kompaktno regulacijsko enoto z vsemi funkcijskimi elementi in komunikacijo s CNS, RS485 / Modbus RTU ter možnostjo povezave večih naprav kot Master / Slave, vključno s pritrdilnim in tesnilnim materialom; | Expansion device for temperature expansion compensation in heating water system according to EN12828, pressure maintenance device with two compressors and compact control unit with all functional elements and communication with CNS, RS485 / Modbus RTU and possibility of connection of several devices as Master / Slave, including fixing and sealing material;
| - natančnost vzdrževanja tlaka ± 0,1 bar z dvema kompresorema (eden delovni, drugi je rezerva), sklop z dvema prelivnima ventiloma in varnostnim ventilom, preklapljanje je odvisno od časa in obremenitve | - pressure maintenance accuracy ± 0.1 bar with two compressors (one working, one reserve), two overflow valves and safety valve assembly, time and load dependent switching
| - primarna posoda V= 3000 l, podnožje s senzorjem za merjenje količine vode | - primary tank V= 3000 l, base with sensor for measuring water quantity
| - električna priključna moč 2x 1,2 kW pri 230 V / 1 / 50 Hz | - electrical connection power 2x 1,2 kW at 230 V / 1 / 50 Hz
| - PN10, CE skladno s PED | - PN10, CE according to PED
| - nivo hrupa kompresorja do 62 dB(A) | - compressor noise level up to 62 dB(A)
| - ustreza proizvod PNEVMATEX tip C10.2-5.0 + CG3000.6 ali enakovredno | - corresponds to PNEVMATEX product type C10.2-5.0 + CG3000.6 or equivalent
| Oznaka: EPK41.21 | Code: EPK41.21 | kpl | 1 |  | 0
1.6 | Varnostni ventil po TRD 721, PN16, varnostna funkcija izpusta medija zaradi toplotnih raztezkov v sistemu, vzmetno delovanje, možnost ročnega odzračenja, prostor vzmeti zaščiten z membrano, prirobnična izvedba, vključno s pritrdilnim in tesnilnim materialom; | Safety valve according to TRD 721, PN16, safety function of medium discharge due to thermal expansion in the system, spring operation, manual venting possible, spring space protected by diaphragm, flanged version, including fixing and sealing material;
| - za sistem ogrevne vode v temperaturnem območju od 5 do 80°C | - for heating water systems in the temperature range 5 to 80°C
| - tlak odpiranja 5,0 barg, | - opening pressure 5,0 barg,
| - s prirobničnim priključkoma DN 50 / 80, komplet z ventilom s ključavnico 2" (DN50) | - with flange connection DN 50/80, complete with valve with 2" lock (DN50)
| - ustreza proizvod IMI PNEUMATEX tip DSV 50 - 5.0 DGH + ... ali enakovredno | - iMI PNEUMATEX product type DSV 50 - 5.0 DGH + ... or equivalent
| Oznaka: VV41.23 | Code: VV41.23 | kpl | 1 |  | 0
1.7 | Naprava za odplinjevanje sistema ogrevne vode skladno z EN12828 in dopolnjevanje z mehčano vodo z hidravlično ločitvijo tip AB po EN1717 komplet z kompaktno regulacijsko enoto z vsemi funkcijskimi elementi in komunikacijo s CNS, RS485 / Modbus RT ter možnostjo povezave večih naprav kot Master / Slave, vključno s pritrdilnim in tesnilnim materialom; | Device for degassing of the heating water system according to EN12828 and supplementing with softened water with hydraulic separation type AB according to EN1717 complete with compact control unit with all functional elements and communication with CNS, RS485 / Modbus RT and possibility of connection of several devices as Master / Slave, including fixing and sealing material;
| - za dopolnjevanje delovnega tlaka v sistemu do 4,5 bar | - for replenishing the system working pressure up to 4,5 bar
| - električna priključna moč 1,4 kW pri 230 V / 1 / 50 Hz | - electrical connection power 1,4 kW at 230 V / 1 / 50 Hz
| - PN10, CE skladno z evropskimi direktivami 2004/108/EC, 2006/95/EC | - PN10, CE compliant with European Directives 2004/108/EC, 2006/95/EC
| - nivo hrupa pri dopolnjevanju do 62 dB(A) | - replenishment noise level up to 62 dB(A)
| - ustreza proizvod PNEVMATEX tip V Connect V 8.1 E + Pleno P AB5 ali enakovredno | - corresponds to PNEVMATEX product type V Connect V 8.1 E + Pleno P AB5 or equivalent
| Oznaka: NOD41.22 | Code: NOD41.22 | kpl | 1 |  | 0
1.8 | Varnostni ventil po TRD 721, PN16, varnostna funkcija izpusta medija zaradi toplotnih raztezkov v sistemu, vzmetno delovanje, možnost ročnega odzračenja, prostor vzmeti zaščiten z membrano, prirobnična izvedba, vključno s pritrdilnim in tesnilnim materialom; | Safety valve according to TRD 721, PN16, safety function of medium discharge due to thermal expansion in the system, spring operation, manual venting possible, spring space protected by diaphragm, flanged version, including fixing and sealing material;
| - za sistem ogrevne vode / hladilne vode v temperaturnem območju od 5 do 80°C | - for heating water/cooling water systems in the temperature range 5 to 80°C
| - tlak odpiranja 6,0 barg, | - opening pressure 6,0 barg,
| - s prirobničnim priključkoma DN 32 / 50, komplet z ventilom s ključavnico 1 1/4" (DN32) | - with flange connection DN 32/50, complete with 1 1/4" (DN32) ratchet valve
| - ustreza proizvod IMI PNEUMATEX tip DSV 32 - 6.0 DGH + ... ali enakovredno | - corresponds to IMI PNEUMATEX product type DSV 32 - 6.0 DGH + ... or equivalent
| Oznaka: VV41.31, VV41.32, VV40.33. VV40.34 | Code: VV41.31, VV41.32, VV40.33. VV40.34 | kpl | 4 |  | 0
1.9 | Varnostni ventil po TRD 721, PN16, varnostna funkcija izpusta medija zaradi toplotnih raztezkov v sistemu, vzmetno delovanje, možnost ročnega odzračenja, prostor vzmeti zaščiten z membrano, prirobnična izvedba, vključno s pritrdilnim in tesnilnim materialom; | Safety valve according to TRD 721, PN16, safety function of medium discharge due to thermal expansion in the system, spring operation, manual venting possible, spring space protected by diaphragm, flanged version, including fixing and sealing material;
| - za sistem ogrevne vode (dogrevanje s SSE) v temperaturnem območju od 5 do 80°C | - for heating water systems (heating with SSE) in the temperature range 5 to 80°C
| - tlak odpiranja 6,0 barg, | - opening pressure 6,0 barg,
| - s prirobničnim priključkoma DN 20 / 32, komplet z ventilom s ključavnico 3/4" (DN20) | - with flange connection DN 20 / 32, complete with 3/4" (DN20) ratchet valve
| - ustreza proizvod IMI PNEUMATEX tip DSV 20 - 6.0 DGH + ... ali enakovredno | - corresponds to IMI PNEUMATEX product type DSV 20 - 6.0 DGH + ... or equivalent
| Oznaka: VV42.13 | Code: VV42.13 | kpl | 1 |  | 0
1.10 | Akumulacijska toplotne energije SSE, jeklena tlačna posoda PN10, skladno z direktivo o tlačni opremi PED, pokončne izvedbe, material ogljikovo jeklo P235TR1 (St37.0), ustrezne debeline jekla (min 10mm), skladnost z direktivo PED, komplet z vsemi priključki, izdelano po delavniški risbi dobavitelja, skladno s shemo in v načrtu, vključno s potiprirobnicami, varilnim, pritrdilnim, tesnilnim materialom. Tehnični podatki: | Thermal energy storage SSE, steel pressure vessel PN10, PED compliant, upright design, material carbon steel P235TR1 (St37.0), appropriate steel thickness (min 10mm), PED compliant, complete with all connections, manufactured according to supplier's shop drawing, as per schematic diagram and as per plan, including sub-fittings, welding, fixing, sealing materials. Technical data:
| - za ogrevno vodo 55°C (do 70°C) | - for heating water 55°C (up to 70°C)
| - prostornina hidravlične kretnice: V = 8 m3 | - hydraulic switching volume: V = 8 m3
| - dimenzije posode: premer D x višina H = ø2000 x 3000 mm, postavljeno na jeklenih nogah 500 mm od tal, skupna višina 3500 mm | - dimensions of the container: diameter D x height H = ø2000 x 3000 mm, raised on steel legs 500 mm from the floor, total height 3500 mm
| - s priključki PN10: 6x DN32 (glavni priključki od tega 2x zg.prekat, 2x sredina, 2x sp.pekat), 1x DN25 (spodaj na dnu) 1x DN25 (zgoraj na vrhu) ter 6x DN15 priključki za tipala in prikazovalnike | - with PN10 connections: 6x DN32 (main connections of which 2x upper chamber, 2x middle, 2x lower chamber), 1x DN25 (bottom) 1x DN25 (top) and 6x DN15 connections for sensors and displays
| - prirobnična revizijska odprtina PN10: DN500 s slepo protiprirobnico, pritrdilnim in tesnilnim materialom | - pN10 flanged inspection opening: DN500 with blind counter flange, fixing and sealing material
| - antikorozijska zaščita; dvakratni premaz s temeljnim temperaturno odpornim antikorozijskim premazom ter dvakratnio premaz s prekrivno barvo, antikorozijska zaščita s temeljnimi in prekrivnimi barvami mora biti obstojna na temperature v območju od -20 do +80°C in se mora izvesti v skladu z EN ISO 12944 z življenjsko dobo: visoko trajanje H (več kot 15 let). | - anti-corrosion protection; two coats of temperature-resistant anti-corrosion primer and two coats of overcoat, the anti-corrosion protection with primers and overcoats must be resistant to temperatures in the range -20 to +80°C and must be carried out in accordance with EN ISO 12944 with a service life of: high durability H (more than 15 years).
| - obratovalna teža 9.200 kg | - operating weight 9,200 kg
| - toplotna parozaporno izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z naslednjimi lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, požarna klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +110°C, lepljeno na rezervoar z originalnim lepilom proizvajalca, vključno s trakovi za šive, debelina 50 mm; | - thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, fire classification B-s3-d0 according to EN13501-1, for temperatures from -50 to +110°C, bonded to the tank with the original manufacturer's adhesive, including seam tapes, 50 mm thick;
| Oznaka: ATE42.30 | Code: ATE42.30 | kpl | 1 |  | 0
1.11 | Plinski kondenzacijski kotel, talna izvedba, skladen s EN303, za zaprte ogrevalne sisteme po EN 12828, gorivo zemeljski plin ZP, s filtrom za zgorevalni zrak iz prostora, z ventilatorjem zgorevalnega zraka in zvočno izoliranim sesalnim ustjem; - ogrevalna moč modularno regulirana od 60 do 600 kW pri 40/55°C, tlačna stopnja PN6, - normiran izkoristki do 98% (Hs) / 105% (Hi) pri 30°C, - teža ca 400 kg, dimenzije Š x V x G = 680 x 1520 x 1600 mm, priključek dimovoda DN250, - nizke emisije in dušikovi oksidi NOx razred 3 po EN 676, - ustreza proizvod WEISHAUPT tip kotla WTC-GB 620-A ali enakovredno; | Gas-fired condensing boiler, floor-standing, EN303 compliant, for closed heating systems according to EN 12828, fuel natural gas ZP, with combustion air filter, combustion air fan and acoustically insulated inlet; - heating power modularly regulated from 60 to 600 kW at 40/55°C, pressure level PN6, - normalised efficiencies up to 98% (Hs) / 105% (Hi) at 30°C, - weight approx. 400 kg, dimensions W x H x D = 680 x 1520 x 1600 mm, flue connection DN250, - low emissions and NOx class 3 according to EN 676, - corresponds to WEISHAUPT boiler type WTC-GB 620-A or equivalent;
| Gorilnik plinskega kotla za zemeljski plin ZP z modulno regulacijo, skladen z EN 676, komplet s plinsko progo: regulator plina od 33 do 150 mbar, dvojni magnetni ventil, plinski filter in krogelni plinski ventil s termičnim varovalom, - ustreza proizvod WEISHAUPT tip gorilnika WG40N-A ZM-PLN U6TAE s pripadajočo plinsko progo ali enakovredno; | Natural gas boiler burner ZP with modular control, in compliance with EN 676, complete with gas line: gas regulator from 33 to 150 mbar, double solenoid valve, gas filter and gas ball valve with thermal fuse, - corresponds to WEISHAUPT burner type WG40N-A ZM-PLN U6TAE with associated gas line or equivalent;
| Varnostni set kotla za ogrevalne sisteme po EN 12828 z omejevalniki tlaka sestavljen iz: razdelilnik, avtomatski hitri odzračevalnik, manometer, varnostni ventil kotla 5,0 barg ter: - omejevalnika minimalnega tlaka od 0,5 do 6 barg (nastavljen na 1,0 barg), - dva omejevalnika maksimalnega tlaka od 0,5 do 6 barg (oba nastavljena na 4,5 barg); - ustreza proizvod WEISHAUPT za predvideni kotel ali enakovredno; | Boiler safety set for heating systems according to EN 12828 with pressure relief valves consisting of: manifold, automatic quick vent, pressure gauge, boiler safety valve 5.0 barg and: - minimum pressure limiter from 0.5 to 6 barg (set to 1.0 barg), - two maximum pressure limiters from 0.5 to 6 barg (both set to 4.5 barg); - the WEISHAUPT product for the intended boiler or equivalent;
| Nevtralizacijska naprava kondenzata kotla, za plinski kotel na ZP, z zračnim rahlanjem granulata in nevtralizacijskim granulatom ca 18 kg, dimenzije ca D x Š x V = 1090 x 160 x 230 mm, komplet z adapter setom za kotel in dimovodni sistem; - ustreza proizvod WEISHAUPT za predvideni kotel ali enakovredno; | Boiler condensate neutraliser, for LP-gas boiler, with air-assisted granulate rake and neutralisation granulate approx. 18 kg, dimensions approx. L x W x H = 1090 x 160 x 230 mm, complete with adapter set for boiler and flue system; - the WEISHAUPT product for the intended boiler or equivalent;
| Oznaka: K43.11, K43.12 | Code: K43.11, K43.12 | kpl | 2 |  | 0
1.12 | Hidravlični set za dva kotla s hidravlično kretnico in dvema kotlovskima obtočnima črpalkama: hidravlična kretnica s priklučki DN150 z odzračevalnim ventilom, dve temperaturni tipali s tulkama, zbiralnik magnetita, konzola oziroma stojalo za kretnico, dve elektronsko regulirani obtočni črpalki Grundfos Magna 65-120F, dva povezovalna seta, cevni deli DN100, štiri redukcije na DN65, štiri fleksibilnr spojkr DN100, štiri zaporne lopute DN100, dve konzoli za prirobnico DN65, dva razdelilnika DN150, vsak z dvema odcepoma DN100 komplet s toplotno izolacijo; razporeditev desnoa li levo (vrtljivo), pretok do 40 m3/h, priključki na kretnici prirobnični 4x DN100, mere komore ca 160 x 200 mm, mere kretnice ca V x Š x G = 1050 x 550 x 160 mm; - ustreza proizvod WEISHAUPT za predvideno povezavo dveh kotelov z dodatno opremo ali enakovredno; | Hidravlični set za dva kotla s hidravlično kretnico in dvema kotlovskima obtočnima črpalkama: hidravlična kretnica s priklučki DN150 z odzračevalnim ventilom, dve temperaturni tipali s tulkama, zbiralnik magnetita, konzola oziroma stojalo za kretnico, dve elektronsko regulirani obtočni črpalki Grundfos Magna 65-120F, dva povezovalna seta, cevni deli DN100, štiri redukcije na DN65, štiri fleksibilnr spojkr DN100, štiri zaporne lopute DN100, dve konzoli za prirobnico DN65, dva razdelilnika DN150, vsak z dvema odcepoma DN100 komplet s toplotno izolacijo; razporeditev desnoa li levo (vrtljivo), pretok do 40 m3/h, priključki na kretnici prirobnični 4x DN100, mere komore ca 160 x 200 mm, mere kretnice ca V x Š x G = 1050 x 550 x 160 mm; - the WEISHAUPT product is suitable for the intended connection of two boilers with accessories or equivalent;
| Oznaka: HK43.10 | Code: HK43.10 | kpl | 2 |  | 0
1.13 | Kotlovska regulacija za upravljanje dveh kotlov ter regulacijski sistem z varovali in tipali, razširjena za upravljanje kotlovskega hidravličnega kroga v odvisnosti od zunanje temperature ali s konstantno temperaturo ogrevne vode iz dveh kotlov; elektronsko krmiljenje in upravljanje za modulitran način obratovanja od 12 do 100%, digitalna mikroprocesorska avtomatika z integrirano kontrolo tesnosti in LCD prikazovalnikom ter izhodi za motnje oziroma napake, prikazovalnik obratovalnih ur in startov gorilnika, dvojni nadzor plamena, kot dodatna varnost, elektronska regulacija plin-zrak z ločenimi koračnimi servo pogoni, ožičenje komponent s kodirnim vtikačem, komplet z zunanjim temperaturnim z tipalom ter elektro kabelskimi povezavami za opisan regulacijski sistem; - možnostjo upravljanja na daljavo ob soglasju uporabnika, s podporo proizvajalca opreme 5 let; - komunikacija na CNS: RS485 / Modbus RTU; - ustreza proizvod WEISHAUPT za predvidena dva kotla in hidravlični set z dodatno opremo ali enakovredno; | Boiler control for control of two boilers and control system with guards and sensors, extended for control of the boiler hydraulic circuit depending on the external temperature or with constant heating water temperature from two boilers; electronic control and management for modulating operation from 12 to 100%, digital microprocessor automation with integrated leakage control and LCD display and outputs for disturbances or faults, display of operating hours and burner starts, dual flame control as additional safety, electronic gas-air control with separate step servo drives, wiring of the components with coding plug, complete with external temperature sensor and electrical cable connections for the described control system; - remote control with user consent, backed by the equipment manufacturer for 5 years; - communication to CNS: RS485 / Modbus RTU; - the WEISHAUPT product for the intended two boilers and hydraulic set with accessories or equivalent;
| Oznaka: za K43.11, K43.12, HK43.10 | Code: for K43.11, K43.12, HK43.10 | kpl | 1 |  | 0
1.14 | Dimovodni sistema dveh plinskih kondenzacijskih kotlov nazivne moči 2x 600 kW iz zgornjih postavk, za vgradnjo v jašku objekta, voden na streho, višina od tal postavitve kotlov do zaključka dimnika ca 28m, absolutna kota postavitve kotla ca 300m, dimniški sistem dimenzioniran po EN 13384, predvidena dimenzija dimnika DN315, nerjavno jeklo AISI316L (lahko tudi temperaturno odporni PP, če kotlovska regulacija preprečuje preseganje dopustne temperature), dimniški priklučki za dva kotla DN250 z motorno vodenima dimnima loputama, priključni kosi na DN315, komplet s čistilnimi odprtinami dimnika, sifonom za odvod kondenzata, strešno dimniško obrobo, rešetko za prezračevanje dimnika, izolacija iz mineralne volne z zaščitnim plaščem, vključno z montažnim, obešalnim in pritrdilnim materialom; | Dimovodni sistema dveh plinskih kondenzacijskih kotlov nazivne moči 2x 600 kW iz zgornjih postavk, za vgradnjo v jašku objekta, voden na streho, višina od tal postavitve kotlov do zaključka dimnika ca 28m, absolutna kota postavitve kotla ca 300m, dimniški sistem dimenzioniran po EN 13384, predvidena dimenzija dimnika DN315, nerjavno jeklo AISI316L (lahko tudi temperaturno odporni PP, če kotlovska regulacija preprečuje preseganje dopustne temperature), dimniški priklučki za dva kotla DN250 z motorno vodenima dimnima loputama, priključni kosi na DN315, komplet s čistilnimi odprtinami dimnika, sifonom za odvod kondenzata, strešno dimniško obrobo, rešetko za prezračevanje dimnika, izolacija iz mineralne volne z zaščitnim plaščem, vključno z montažnim, obešalnim in pritrdilnim materialom;
| Oznaka: za K43.11, K43.12 | Code: for K43.11, K43.12 | kpl | 1 |  | 0
1.15 | Razdelilnik / zbiralnik izdelan iz jeklene cevi DN250 ø323,9x7,1 po EN 10216-1 (DIN2448), iz materiala P235TR2 (St37.0), PN10, ležeče izvedbe, z prirobničnima zaključkoma DN250 in dvema slepima prirobnicama DN250, skladnost z direktivo PED, komplet z vsemi priključki, izdelano po delavniški risbi dobavitelja, skladno s shemo in v načrtu, vključno s potiprirobnicami, varilnim, pritrdilnim, tesnilnim materialom; | Manifold / manifold made of steel pipe DN250 ø323,9x7,1 according to EN 10216-1 (DIN2448), made of material P235TR2 (St37.0), PN10, bearing version, with flanged ends DN250 and two blind flanges DN250, PED compliance, complete with all connections, made according to the supplier's shop drawing, according to the scheme and in the plan, including sub-fittings, welding, fixing, sealing material;
| - ogrevna voda 50/40°C | - heating water 50/40°C
| - dimenzije: premer D x dolžina L = DN250 x 1200 mm, s konstrukcijo za pritrditev na tla / strop | - dimensions: diameter D x length L = DN250 x 1200 mm, with floor/ceiling mounting structure
| - s prirobničnimi priključki PN10: 4x DN200 in navojnimi priključki: 1x DN32, 2x DN15 | - with PN10 flange connections: 4x DN200 and threaded connections: 1x DN32, 2x DN15
| - čiščenje in barvanje, odstranitev rje do kovinskega sijaja, dvakratni premaz s temeljnim antikorozijskim barvami ter dvakratni premaz s prekrivno barvo: obstojnost na temperature v območju od +5 do +80°C, skladno z EN ISO 12944 z življenjsko dobo: visoko trajanje H (več kot 15 let) | - cleaning and painting, rust removal to metallic gloss, double coating with anti-corrosion primer and double coating with overcoat: temperature resistance in the range +5 to +80°C, in accordance with EN ISO 12944 with service life: high durability H (more than 15 years)
| - komplet s toplotna parozaporna izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +105°C, debelina 40mm | - complete with thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, classification B-s3-d0 according to EN13501-1, for temperatures -50 to +105°C, thickness 40mm
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and hose clamps with noise damping lining, suitable for HILTI or SIKLA, or equivalent;
| Oznaka: pred HK43.10 | Mark: before HK43.10 | kpl | 1 |  | 0
1.16 | Razdelilnik / zbiralnik izdelan iz jeklene cevi DN400 ø406,4x8,8 po EN 10216-1 (DIN2448), iz materiala P235TR1 (St37.0), PN10, ležeče izvedbe, z bombiranima ali prirobničnima zaključkoma, skladnost z direktivo PED, komplet z vsemi priključki, izdelano po delavniški risbi dobavitelja, skladno s shemo in v načrtu, vključno s potiprirobnicami, varilnim, pritrdilnim, tesnilnim materialom; | Manifold / manifold made of steel pipe DN400 ø406,4x8,8 according to EN 10216-1 (DIN2448), made of P235TR1 (St37.0), PN10, flat design, with bomb-coated or flanged ends, PED compliance, complete with all connections, made according to the supplier's shop drawing, according to the scheme and in the plan, including sub-plates, welding, fixing, sealing material;
| - ogrevna voda 50/40°C | - heating water 50/40°C
| - dimenzije: premer D x dolžina L = DN250 x 4000 mm, s konstrukcijo za pritrditev na tla / strop | - dimensions: diameter D x length L = DN250 x 4000 mm, with floor/ceiling mounting structure
| - s prirobničnimi priključki PN10: 1x DN200, 1x DN150, 1x DN125, 2x DN80 ter z navojnimi priključki: 1x DN20 | - with PN10 flanged connections: 1x DN200, 1x DN150, 1x DN125, 2x DN80 and with threaded connections: 1x DN20
| - čiščenje in barvanje, odstranitev rje do kovinskega sijaja, dvakratni premaz s temeljnim antikorozijskim barvami ter dvakratni premaz s prekrivno barvo: obstojnost na temperature v območju od +5 do +80°C, skladno z EN ISO 12944 z življenjsko dobo: visoko trajanje H (več kot 15 let) | - cleaning and painting, rust removal to metallic gloss, double coating with anti-corrosion primer and double coating with overcoat: temperature resistance in the range +5 to +80°C, in accordance with EN ISO 12944 with service life: high durability H (more than 15 years)
| - komplet s toplotna parozaporna izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +105°C, debelina 40mm | - complete with thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, classification B-s3-d0 according to EN13501-1, for temperatures -50 to +105°C, thickness 40mm
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and hose clamps with noise damping lining, suitable for HILTI or SIKLA, or equivalent;
| Oznaka: RZ44.10 | Code: RZ44.10 | kpl | 2 |  | 0
1.17 | Obtočna črpalka, centrifugalna inline, s suhim rotorjem, PN16, skladnost z ErP, elektronsko regulirana z integriranim frekvenčnim pretvornikom, s tipalom diferenčnega tlaka, upravljalnikom nastavitev s prikazovalnikom parametrov, internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, centrifugal inline, dry-running, PN16, ErP-compliant, electronically controlled with integrated frequency converter, differential pressure sensor, setting control with parameter display, internal hydraulic, electrical and communication connections, pump material grey cast iron with suitable medium seal, flanged design, including counter flanges, fixing and sealing material. Technical data:
| - ogrevna voda 50/45°C | - heating water 50/45°C
| - pretok V= 70,5m3/h, tlačna višina H= 90kPa | - flow rate V= 70,5m3/h, pressure head H= 90kPa
| - možnost izbire delovanja črpalke na proporcionalni tlak ter optimizacijo delovne točke z avtomatsko nastavitvijo pretoka ali glede na trenutne potrebe obratovanja | - option to choose proportional pressure operation and optimise the operating point by automatically adjusting the flow rate or according to the current operating needs
| - komunikacija s CNS: RS485 / Modbus RTU | - communication with CNS: RS485 / Modbus RTU
| - elektro podatki Pel= 2,2 kW, 400V /3/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 2,2 kW, 400V /3/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip TPE3 100-130 ali enakovredno | - corresponds to GRUNDFOS product type TPE3 100-130 or equivalent
| Oznaka: P41.081, P41.082, P41.083, P41.084 | Code: P41.081, P41.082, P41.083, P41.084 | kpl | 4 |  | 0
1.18 | Obtočna črpalka, PN10, z mokrim rotorjem, skladnost z ErP, elektronsko regulirana s PM motorjem in integrairanim frekvenčnim pretvornikom, inegrirano tipalo diferenčnega tlaka in temperature, upravljalnik nastavitev s prikazovalnikom parametrov, z internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, PN10, wet-rotor, ErP-compliant, electronically controlled with PM motor and integrated frequency converter, integrated differential pressure and temperature sensor, setting controller with parameter display, with internal hydraulic, electrical and communication connections, pump material grey cast iron with appropriate sealing for the medium, flanged design, including counter-flanges, fixing and sealing material. Technical data:
| - ogrevna voda 50/40°C | - heating water 50/40°C
| - pretok V= 2,04 m3/h, tlačna višina H= 30kPa, | - flow rate V= 2,04 m3/h, pressure head H= 30kPa,
| - komunikacija s CNS: RS485 / Modbus RTU | - communication with CNS: RS485 / Modbus RTU
| - elektro podatki Pel= 0,050kW, 230V /1/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 0,050kW, 230V /1/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip MAGNA3 25-40 | - corresponds to GRUNDFOS product type MAGNA3 25-40
| Oznaka: P42.082 | Code: P42.082 | kpl | 1 |  | 0
1.19 | Obtočna črpalka, centrifugalna inline, s suhim rotorjem, PN16, skladnost z ErP, elektronsko regulirana z integriranim frekvenčnim pretvornikom, s tipalom diferenčnega tlaka, upravljalnikom nastavitev s prikazovalnikom parametrov, internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, centrifugal inline, dry-running, PN16, ErP-compliant, electronically controlled with integrated frequency converter, differential pressure sensor, setting control with parameter display, internal hydraulic, electrical and communication connections, pump material grey cast iron with suitable medium seal, flanged design, including counter flanges, fixing and sealing material. Technical data:
| - ogrevna voda 50/40°C | - heating water 50/40°C
| - pretok V= 119m3/h, tlačna višina H= 160kPa | - flow rate V= 119m3/h, pressure head H= 160kPa
| - možnost izbire delovanja črpalke na proporcionalni tlak ter optimizacijo delovne točke z avtomatsko nastavitvijo, glede na trenutne potrebe obratovanja | - option to select proportional pressure operation and optimise the operating point by automatic adjustment, depending on the current operating requirements
| - komunikacija s CNS: RS485 / Modbus RTU | - communication with CNS: RS485 / Modbus RTU
| - elektro podatki Pel= 7,5 kW, 400V /3/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 7,5 kW, 400V /3/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip TPE3 100-260 ali enakovredno | - corresponds to GRUNDFOS product type TPE3 100-260 or equivalent
| Oznaka: P44.081 | Code: P44.081 | kpl | 1 |  | 0
1.20 | Obtočna črpalka, centrifugalna inline, s suhim rotorjem, PN16, skladnost z ErP, elektronsko regulirana z integriranim frekvenčnim pretvornikom, s tipalom diferenčnega tlaka, upravljalnikom nastavitev s prikazovalnikom parametrov, internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, centrifugal inline, dry-running, PN16, ErP-compliant, electronically controlled with integrated frequency converter, differential pressure sensor, setting control with parameter display, internal hydraulic, electrical and communication connections, pump material grey cast iron with suitable medium seal, flanged design, including counter flanges, fixing and sealing material. Technical data:
| - ogrevna voda 50/40°C | - heating water 50/40°C
| - pretok V= 39,1m3/h, tlačna višina H= 160kPa | - flow rate V= 39,1m3/h, pressure head H= 160kPa
| - možnost izbire delovanja črpalke na proporcionalni tlak ter optimizacijo delovne točke z avtomatsko nastavitvijo, glede na trenutne potrebe obratovanja | - option to select proportional pressure operation and optimise the operating point by automatic adjustment, depending on the current operating requirements
| - komunikacija s CNS: RS485 / Modbus RTU | - communication with CNS: RS485 / Modbus RTU
| - elektro podatki Pel= 2,2 kW, 400V /3/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 2,2 kW, 400V /3/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip TPE3 65-220 ali enakovredno | - corresponds to GRUNDFOS product type TPE3 65-220 or equivalent
| Oznaka: P44.082 | Code: P44.082 | kpl | 1 |  | 0
1.21 | Obtočna črpalka, centrifugalna inline, s suhim rotorjem, PN16, skladnost z ErP, elektronsko regulirana z integriranim frekvenčnim pretvornikom, s tipalom diferenčnega tlaka, upravljalnikom nastavitev s prikazovalnikom parametrov, internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, centrifugal inline, dry-running, PN16, ErP-compliant, electronically controlled with integrated frequency converter, differential pressure sensor, setting control with parameter display, internal hydraulic, electrical and communication connections, pump material grey cast iron with suitable medium seal, flanged design, including counter flanges, fixing and sealing material. Technical data:
| - ogrevna voda 50/40°C | - heating water 50/40°C
| - pretok V= 26,6m3/h, tlačna višina H= 110kPa | - flow rate V= 26,6m3/h, pressure head H= 110kPa
| - možnost izbire delovanja črpalke na proporcionalni tlak ter optimizacijo delovne točke z avtomatsko nastavitvijo, glede na trenutne potrebe obratovanja | - option to select proportional pressure operation and optimise the operating point by automatic adjustment, depending on the current operating requirements
| - komunikacija s CNS: RS485 / Modbus RTU | - communication with CNS: RS485 / Modbus RTU
| - elektro podatki Pel= 1,1 kW, 400V /3/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 1,1 kW, 400V /3/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip TPE3 50-180 ali enakovredno | - corresponds to GRUNDFOS product type TPE3 50-180 or equivalent
| Oznaka: P44.083 | Code: P44.083 | kpl | 1 |  | 0
1.22 | Zaporna loputa z elektromotornim pogonom ON/OFF, 24V, IP66 in stikali končne lege odrto in zaprto, PN16, material lopute nodularna litina / EPDM, za vgradnjo med prirobnice, komplet s protiprirobnicama, vijačnim in tesnilnim materialom; | Butterfly valve with ON/OFF electric motor drive, 24V, IP66 and open and closed end position switches, PN16, butterfly valve material ductile iron / EPDM, for mounting between flanges, complete with counter flanges, screw and sealing material;
| - ogrevna voda 50/40°C | - heating water 50/40°C
| DN 80 - ustreza proizvod BELIMO tip D680N +GR24A-5 +S2A ali enakovredno Oznaka: DV44.075, DV44.076 | DN 80 - corresponds to BELIMO product type D680N +GR24A-5 +S2A or equivalent Code: DV44.075, DV44.076 | kpl | 2 |  | 0
| DN 100 - ustreza proizvod BELIMO tip D6100W +JRCA-S2-T +S2A ali enakovredno Oznaka: DV44.073, DV44.074 | DN 100 - fits BELIMO product type D6100W +JRCA-S2-T +S2A or equivalent Code: DV44.073, DV44.074 | kpl | 2 |  | 0
| DN 125 - ustreza proizvod BELIMO tip D6125W +JRCA-S2-T +S2A ali enakovredno Oznaka: VX41.061, VX41.062, VX41.063, VX41.064, VX41.065, VX41.066, VX41.067, VX41.068 | DN 125 - fits BELIMO product type D6125W +JRCA-S2-T +S2A or equivalent Code: VX41.061, VX41.062, VX41.063, VX41.064, VX41.065, VX41.066, VX41.067, VX41.068 | kpl | 8 |  | 0
| DN 150 - ustreza proizvod BELIMO tip D6150W +JRCA-S2-T +S2A ali enakovredno Oznaka: DV44.071, DV44.072 | DN 150 - fits BELIMO product type D6150W +JRCA-S2-T +S2A or equivalent Code: DV44.071, DV44.072 | kpl | 2 |  | 0
1.23 | Regulacijski ventil, tropotni mešalni, z elektromotornim zveznim pogonom, 24V, IP54, PN16, material ventila siva litina, nerjavno jeklo / EPDM, prirobnična izvedba, komplet s protiprirobnicami, vijačnim in tesnilnim materialom; | Control valve, tropical mixing, with electric motor continuous drive, 24V, IP54, PN16, valve material grey cast iron, stainless steel / EPDM, flanged version, complete with counter flanges, screwing and sealing material;
| - ogrevna voda 50/40°C, mešanje pred TCHA40.1, TCHA40.2, TCHA40.3, TCHA40.4 | - heating water 50/40°C, mixing before TCHA40.1, TCHA40.2, TCHA40.3, TCHA40.4
| - DN100, kvs = 145 m3/h | - DN100, kvs = 145 m3/h
| - ustreza proizvod BELIMO tip H7100N, tip pogona RV24A-SR ali enakovredno | - corresponds to BELIMO product type H7100N, actuator type RV24A-SR or equivalent
| Oznaka: VY41.051, VY41.052, VY41.053, VY41.054 | Code: VY41.051, VY41.052, VY41.053, VY41.054 | kpl | 4 |  | 0
1.24 | Tipalo tlaka s pretvornikom, za mertev tlaka v območju od 0 do 6 barg (relativno) ter nastavljivim alarmnim tlakom, navojni priključek 1/2" (DN15), material nerjavno jeklo, električni podatki: napajanje 24V, izhod 4-20mA, kompletno z ventilom za tipalo tlaka 1/2" (DN15) ter tesnilnim in pritrdilnim materialom; | Pressure sensor with transducer, for pressure measurement in the range from 0 to 6 barg (relative) and adjustable alarm pressure, threaded connection 1/2" (DN15), material stainless steel, electrical data: power supply 24V, output 4-20mA, complete with pressure sensor valve 1/2" (DN15) and sealing and fixing material;
| - ogrevna voda 50/40°C | - heating water 50/40°C
| - alarm, če je tlak p < 3,5 barg (nastavitev na tipalu ali programska nastavitev) | - alarm if pressure p < 3.5 barg (sensor setting or software setting)
| - ustreza proizvod ENDRESS+HAUSER tip PTC31B + PZAV ali enakovredno | - corresponds to ENDRESS+HAUSER product type PTC31B + PZAV or equivalent
| Oznaka: PIA41.019 | Code: PIA41.019 | kpl | 1 |  | 0
1.25 | Temperaturno tipalo, potopno, za merilno območje od -10 do +100°C, potopna dolžina L=250mm, v tulki iz nerjavnega materiala z navojnim priključkom 1/2" (DN15), električni podatki: napajanje 24V, izhod 4-20mA, komplet s pritrdilnim in tesnilnim materialom; | Temperature sensor, immersion, for measuring range -10 to +100°C, immersion length L=250mm, in stainless steel sleeve with threaded connection 1/2" (DN15), electrical data: power supply 24V, output 4-20mA, complete with fixing and sealing material;
| - ogrevna voda 50/40°C | - heating water 50/40°C
| - ustreza proizvod ELEKTRONIKA PAHOR, tip CVB ali enakovredno | - corresponds to the product ELEKTRONIKA PAHOR, type CVB or equivalent
| Oznaka: TIC41.006, TIC41.007, TIC41.008, TIC41.009, TIC42.004, TIC42.005, TIC42.006 | Code: TIC41.006, TIC41.007, TIC41.008, TIC41.009, TIC42.004, TIC42.005, TIC42.006 | kpl | 7 |  | 0
1.26 | Temperaturno tipalo, potopno, za merilno območje od -10 do +100°C, potopna dolžina L=100mm, v tulki iz nerjavnega materiala z navojnim priključkom 1/2" (DN15), električni podatki: napajanje 24V, izhod 4-20mA, komplet s pritrdilnim in tesnilnim materialom; | Temperature sensor, immersion, for measuring range -10 to +100°C, immersion length L=100mm, in stainless steel sleeve with threaded connection 1/2" (DN15), electrical data: power supply 24V, output 4-20mA, complete with fixing and sealing material;
| - ogrevna voda 50/40°C | - heating water 50/40°C
| - ustreza proizvod ELEKTRONIKA PAHOR, tip CVB ali enakovredno | - corresponds to the product ELEKTRONIKA PAHOR, type CVB or equivalent
| Oznaka: TIC41.001, TIC41.002, TIC40.003, TIC41.004, TIC41.011, TIC41.012, TIC41.013, TIC41.014, TIC42.003, TIC43.001, TI44.001, TI44.002, TI44.003, TI44.004, TI44.005, TI44.006 | Code: TIC41.001, TIC41.002, TIC40.003, TIC41.004, TIC41.011, TIC41.012, TIC41.013, TIC41.014, TIC42.003, TIC43.001, TI44.001, TI44.002, TI44.003, TI44.004, TI44.005, TI44.006 | kpl | 16 |  | 0
1.27 | Krogelni ventil s priklučkom za praznenje oz. polnenje, navojna izvedba, PN16, z ročico, material nerjavno jeklo / PTFE, vključno s pritrdilnim in tesnilnim materialom: | Ball valve with union for emptying or filling, threaded version, PN16, with handle, material stainless steel/PTFE, incl. fitting and sealing material:
| - ogrevna voda 50/40°C | - heating water 50/40°C
| - ustreza proizvod END ARMATUREN ali enakovredno | - eND ARMATUREN or equivalent
| DN 15 | DN 15 | kos | 148 |  | 0
| DN 20 | DN 20 | kos | 8 |  | 0
| DN 25 | DN 25 | kos | 8 |  | 0
1.28 | Krogelni ventil, navojna izvedba, PN16, z ročico, material nerjavno jeklo / PTFE, vključno s pritrdilnim in tesnilnim materialom: | Ball valve, threaded version, PN16, with handle, material stainless steel/PTFE, incl. fitting and sealing material:
| - ogrevna voda 50/40°C | - heating water 50/40°C
| - ustreza proizvod END ARMATUREN ali enakovredno | - eND ARMATUREN or equivalent
| DN 15 | DN 15 | kos | 140 |  | 0
| DN 20 | DN 20 | kos | 24 |  | 0
| DN 25 | DN 25 | kos | 12 |  | 0
| DN 32 | DN 32 | kos | 48 |  | 0
| DN 40 | DN 40 | kos | 10 |  | 0
| DN 50 | DN 50 | kos | 18 |  | 0
1.29 | Zaporna loputa, prirobnična izvedba, mehko tesnenje, PN16, z ročnim pogonom z ročico do vključno DN100 oziroma z ročnim polžnim pogonom nad vključno DN125, material nodularna litina / EPDM, za vgradnjo med prirobnice, komplet s protiprirobnicama, vijačnim in tesnilnim materialom; | Butterfly valve, flanged version, soft sealing, PN16, with manual lever actuator up to and including DN100 or with manual screw actuator up to and including DN125, material ductile iron / EPDM, for installation between flanges, complete with two anti-seize plates, screw and sealing material;
| - ogrevna voda 50/40°C | - heating water 50/40°C
| - ustreza proizvod IMP ARMATURE ali enakovredno | - iMP ARMATURE or equivalent
| DN 65 | DN 65 | kpl | 22 |  | 0
| DN 80 | DN 80 | kpl | 10 |  | 0
| DN 100 | DN 100 | kpl | 28 |  | 0
| DN 125 | DN 125 | kpl | 12 |  | 0
| DN 150 | DN 150 | kpl | 8 |  | 0
| DN 200 | DN 200 | kpl | 18 |  | 0
1.30 | Nepovratni ventil, z vmetjo, navojna izvedba, PN16 material nerjavno jeklo, EPDM, vključno z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Non-return valve, with spout, threaded version, PN16 material stainless steel, EPDM, incl. threaded Dutch, fastening and sealing material;
| - ogrevna voda 50/40°C | - heating water 50/40°C
| - ustreza proizvod END ARMATUREN ali enakovredno | - eND ARMATUREN or equivalent
| DN 25 | DN 25 | kpl | 4 |  | 0
| DN 32 | DN 32 | kpl | 10 |  | 0
| DN 40 | DN 40 | kpl | 2 |  | 0
| DN 50 | DN 50 | kpl | 6 |  | 0
1.31 | Nepovratna loputa, z vmetjo, prirobnična izvedba, material nodularna litina / EPDM, vzmet nerjavno jeklo, za vgradnjo med prirobnice, komplet s protiprirobnicama, vijačnim in tesnilnim materialom; | Non-return hatch, with spout, flanged version, material ductile iron / EPDM, spring stainless steel, for installation between flanges, complete with two counter flanges, screwing and sealing material;
| - ogrevna voda 50/40°C | - heating water 50/40°C
| - ustreza proizvod END ARMATUREN ali enakovredno | - eND ARMATUREN or equivalent
| DN 65 | DN 65 | kpl | 2 |  | 0
| DN 80 | DN 80 | kpl | 3 |  | 0
| DN 100 | DN 100 | kpl | 2 |  | 0
| DN 125 | DN 125 | kpl | 4 |  | 0
| DN 150 | DN 150 | kpl | 1 |  | 0
| DN 200 | DN 200 | kpl | 2 |  | 0
1.32 | Lovilnik nesnage, navojna izvedba, z normalnim sitom, PN16, material siva litina, sito nerjavno jeklo, komplet s krogelnim ventilom DN15 za praznenje in izpiranje, vključno z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Debris trap, threaded version, with normal sieve, PN16, material grey cast iron, sieve stainless steel, complete with ball valve DN15 for emptying and flushing, incl. two threaded Hollanders, fixing and sealing material;
| - ogrevna voda 50/40°C | - heating water 50/40°C
| - ustreza proizvod IMP ARMATURE ali enakovredno | - iMP ARMATURE or equivalent
| DN 15 | DN 15 | kos | 6 |  | 0
| DN 20 | DN 20 | kos | 4 |  | 0
| DN 25 | DN 25 | kos | 4 |  | 0
| DN 32 | DN 32 | kos | 16 |  | 0
| DN 40 | DN 40 | kos | 5 |  | 0
| DN 50 | DN 50 | kos | 5 |  | 0
1.33 | Lovilnik nesnage, prirobnična izvedba, z normalnim sitom, PN16, material siva litina, sito nerjavno jeklo, komplet s krogelnim ventilom DN15 za praznenje in izpiranje, vključno s protiprirobnicama, vijačnim in tesnilnim materialom; | Debris trap, flanged version, with normal sieve, PN16, material grey cast iron, sieve stainless steel, complete with ball valve DN15 for emptying and flushing, incl. counter flanges, screwing and sealing material;
| - ogrevna voda 50/40°C | - heating water 50/40°C
| - ustreza proizvod IMP ARMATURE ali enakovredno | - iMP ARMATURE or equivalent
| DN 65 | DN 65 | kpl | 6 |  | 0
| DN 80 | DN 80 | kpl | 1 |  | 0
| DN 100 | DN 100 | kpl | 2 |  | 0
| DN 125 | DN 125 | kpl | 4 |  | 0
1.34 | Izločevalnika nečistoč, magnetita in mikro mehurčkov, ciklonsko izločanje, PN16, skladno s PED, material medenina, EPDM, navojni priključki, z ventilom za izpust nečistoč ter avtomatskim odzračevalnim ventilom, vključno z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Impurity, magnetite and microbubble eliminators, cyclonic elimination, PN16, PED-compliant, material brass, EPDM, threaded connections, with impurity discharge valve and automatic vent valve, incl. threaded dutch, fixing and sealing material;
| - ogrevna voda 50/40°C | - heating water 50/40°C
| - ustreza proizvod IMI PMEUMATEX tip Zeparo ZUKM ali enakovredno | - corresponds to IMI PMEUMATEX product type Zeparo ZUKM or equivalent
| DN 32 | DN 32 | kpl | 1 |  | 0
1.35 | Izločevalnika nečistoč, magnetita in mikro mehurčkov, ciklonsko izločanje, PN16, skladno s PED, material jeklo, prirobnični priključki, z dvema krogelnim ventilom DN15 za izpust nečistoč in odzračevanje ter avtomatskim odzračevalnim ventilom, vključno s protiprirobnicama, vijačnim in tesnilnim materialom; | Impurity, magnetite and micro-bubble eliminators, cyclonic elimination, PN16, PED-compliant, material steel, flanged connections, with two DN15 ball valves for impurity discharge and venting and an automatic vent valve, incl. counter flanges, screwing and sealing material;
| - ogrevna voda 50/40°C | - heating water 50/40°C
| - ustreza proizvod IMI PMEUMATEX tip Zeparo G-Force ZG ... + ZUTX 25 ali enakovredno | - iMI PMEUMATEX product type Zeparo G-Force ZG ... + ZUTX 25 or equivalent
| DN 200 | DN 200 | kpl | 3 |  | 0
1.36 | Ventil za hidravlično uravnoteženje, nastavitev pretoka, navojna izvedba, PN16, s priključkoma za priklop naprave za merjenje pretoka, z zaporno funkcijo brez prenastavitve pretoka, material siva litina, nerjavno jeklo, EPDM, PTFE, vključno z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Hydraulic balancing valve, flow adjustment, threaded version, PN16, with two connections for connection of flow measuring device, with shut-off function without flow reset, material grey cast iron, stainless steel, EPDM, PTFE, incl. threaded plugs, fastening and sealing material;
| - ogrevna voda 50/40°C | - heating water 50/40°C
| - ustreza proizvod IMI TA tip STAD ali enakovredno | - the product conforms to IMI TA type STAD or equivalent
| DN 15 | DN 15 | kos | 20 |  | 0
| DN 20 | DN 20 | kos | 4 |  | 0
| DN 25 | DN 25 | kos | 4 |  | 0
| DN 32 | DN 32 | kos | 14 |  | 0
| DN 40 | DN 40 | kos | 6 |  | 0
| DN 50 | DN 50 | kos | 6 |  | 0
1.37 | Ventil za hidravlično uravnoteženje, nastavitev pretoka, prirobnična izvedba, PN16, s priključkoma za priklop naprave za merjenje pretoka, z zaporno funkcijo brez prenastavitve pretoka, material siva litina, nerjavno jeklo, EPDM, PTFE, vključno s protiprirobnicama, vijačnim in tesnilnim materialom; | Hydraulic balancing valve, flow adjustable, flanged version, PN16, with two connections for connection to a flow measuring device, with shut-off function without flow reset, material grey cast iron, stainless steel, EPDM, PTFE, incl. anti-seize, screwing and sealing material;
| - ogrevna voda 50/40°C | - heating water 50/40°C
| - ustreza proizvod IMI TA tip STAF ali enakovredno | - corresponds to IMI TA type STAF or equivalent
| DN 65 | DN 65 | kpl | 5 |  | 0
| DN 80 | DN 80 | kpl | 2 |  | 0
| DN 100 | DN 100 | kpl | 1 |  | 0
1.38 | Kompenzator vibracij in prenosa hrupa iz strojne opreme na cevovod ali iz hrupnega prostora po cevovodu v sosednji prostor, navojna izvedba, PN16, material nerjavno jeklo, EPDM, vključno z nerjavnima navojnima holandcema, pritrdilnim in tesnilnim materialom; | Vibration and noise compensator for noise transmission from machinery to pipeline or from noise room through pipeline to adjacent room, threaded version, PN16, material stainless steel, EPDM, incl. stainless steel threaded dutch, fastening and sealing material;
| - ogrevna voda 50/40°C | - heating water 50/40°C
| - ustreza proizvod END ARMATUREN tip KP ali enakovredno | - corresponds to END ARMATUREN type KP or equivalent
| DN 15 | DN 15 | kos | 8 |  | 0
| DN 20 | DN 20 | kpl | 6 |  | 0
| DN 25 | DN 25 | kpl | 24 |  | 0
| DN 32 | DN 32 | kpl | 8 |  | 0
| DN 40 | DN 40 | kpl | 8 |  | 0
1.39 | Kompenzator vibracij in prenosa hrupa iz strojne opreme na cevovod ali iz hrupnega prostora po cevovodu v sosednji prostor, prirobnična izvedba, PN16, material pocinkano jeklo, EPDM, vključno s protiprirobnicama, vijačnim in tesnilnim materialom; | Vibration and noise compensator for transmission of noise from machinery to pipeline or from noise room through pipeline to adjacent room, flanged version, PN16, material galvanised steel, EPDM, incl. counter flanges, screw and gasket material;
| - ogrevna voda 50/40°C | - heating water 50/40°C
| - ustreza proizvod END ARMATUREN tip KP ali enakovredno | - corresponds to END ARMATUREN type KP or equivalent
| DN 50 | DN 50 | kos | 4 |  | 0
| DN 65 | DN 65 | kpl | 4 |  | 0
| DN 80 | DN 80 | kpl | 2 |  | 0
| DN 100 | DN 100 | kpl | 20 |  | 0
1.40 | Termometer, tekočinski, dolžina skale 100mm, kotni 90°, potopna dolžina 40mm, v zaščitni cevi - tulki, klasa točnosti 1%, navojni priključek 1/2" (DN15), material medenina, aluminij, steklo, nerjavno jeklo, vključno s pritrdilnim in tesnilnim materialom; | Thermometer, liquid, scale length 100mm, angle 90°, immersion length 40mm, in protective tube - sleeves, accuracy class 1%, threaded connection 1/2" (DN15), material brass, aluminium, glass, stainless steel, incl. fixing and sealing material;
| - ogrevna voda 50/40°C | - heating water 50/40°C
| - ustreza proizvod INOL ali enakovredno | - corresponds to INOL or equivalent
| - območjem merjenja: 0 do 100°C | - measuring range: 0 to 100°C | kpl | 112 |  | 0
1.41 | Manometer ø 68 mm, klasa točnosti 1,6% po EN837-1, navojni radialni priključek, material medenina, nerjavno jeklo, steklo / EPDM, komplet z manometrskim ventilom DN15 (1/2"), vključno s pritrdilnim in tesnilnim materialom; | Pressure gauge ø 68 mm, accuracy class 1.6% according to EN837-1, threaded radial connection, material brass, stainless steel, glass / EPDM, complete with pressure gauge valve DN15 (1/2"), incl. mounting and sealing material;
| - ogrevna voda 50/40°C | - heating water 50/40°C
| - ustreza proizvod INOL ali enakovredno | - corresponds to INOL or equivalent
| - območjem merjenja: 0 do 6 bar | - measuring range: 0 to 6 bar | kpl | 112 |  | 0
1.42 | Avtomatski odzračevalnik, z zapornim in ročno odzračevalnim ventilom PN10 material medenina / PTFE, vključno z navojnim holandcem in tesnilnim materialom; | Automatic venting valve, with shut-off and manual venting valve PN10 material brass/PTFE, including threaded Dutchman and sealing material;
| - ogrevna voda 50/40°C | - heating water 50/40°C
| DN25 - ustreza proizvod IMI PNEUMATEX tip ZUTX 25 ali enakovredno | DN25 - corresponds to IMI PNEUMATEX product type ZUTX 25 or equivalent | kpl | 72 |  | 0
1.43 | Odzračitveni lonček, volumen V ≥ 2 litra, izdelan iz cevi DN100, ø114x2,3 mm po EN ISO1127, dolžina L=300mm, z bombiranima zaključkoma, material AISI304, vključno z varilnim materialom; | Refrigerated crucible, volume V ≥ 2 litres, made of DN100 pipe, ø114x2,3 mm according to EN ISO1127, length L=300mm, with bomb-coated ends, material AISI304, incl. welding consumables;
| - ogrevna voda 50/40°C | - heating water 50/40°C | kpl | 96 |  | 0
1.44 | Kasetni ventilatorski konvektor štiricevne izvedbe za ogrevanje in hlajenje, vgradnja v dvojni strop z masko na stropu, izdelano iz jeklene pocinkane pločevine, lamelna prenosnika toplote, zbiralnik za kondenzat s črpalko za prečrpavanje kondenzata, radialni ventilator z inverter elektromotorjem, maska z možnostjo usmerjanja vpiha zraka na štiri strani, barva bela RAL9010, odzračevalni in izpustni ventil, delovni tlak do 6 bar, gibke cevne povezave nerjavne izvedbe, dva regulacijska ventila z elektromotornim pogonom s funkcijo hidravličnega uravnoteženja, zaporni ventili za ogrevno in hladilno vodo, vključno z obešalnim, pritrdilnim in tesnilnim materialom; Eurovent certifikat; Tehnični podatki: | Four-pipe cassette fan coil unit for heating and cooling, double ceiling installation with ceiling mask, made of galvanised sheet steel, laminated heat exchangers, condensate collector with condensate pump, radial fan with inverter electric motor, mask with possibility of directing the air inlet on four sides, colour white RAL9010, vent and discharge valve, working pressure up to 6 bar, flexible stainless steel pipe connections, two control valves with electric motor drive with hydraulic balancing function, shut-off valves for heating and cooling water, including hanging, fixing and sealing material; Eurovent certificate; Technical data:
| - hrup v največji hitrosti do 50 dB(A) | - noise at maximum speed up to 50 dB(A)
| - inverter motor ventilatorja za nastavitev zvezne hitrosti | - inverter fan motor for continuous speed adjustment
| - črpalka za prečrpavanje kondenzata | - condensate pump
| - elektro podatki: do 100 W, 230V/ 1/ 50Hz | - electrical data: up to 100 W, 230V/ 1/ 50Hz
| - dimenzije: dolžina L x širina W x višina H = 600 x 600 x 300 mm, teža 30 kg | - dimensions: length L x width W x height H = 600 x 600 x 300 mm, weight 30 kg
| - gibke cevne povezave iz nerjavnega jekla DN20 - ustreza proizvod CATS | - flexible hose connections in stainless steel DN20 - corresponds to CATS product
| - prehodni regulacijska ventil ogrevanje, tlačno neodvisni za hidravlično uravnoteženje z elektro motornim ali elektro termičnim on/off pogonom, vključno z navojnima holandcema, pretok 65 ÷ 650 l/h - ustreza proizvod DANFOSS tip ventila AB-QM 15, tip pogona TWA-Q, NZ | - heating control valve, pressure independent for hydraulic balancing with electric motor or electric thermal on/off actuator, incl. threaded Dutch, flow 65 ÷ 650 l/h - corresponds to DANFOSS product valve type AB-QM 15, actuator type TWA-Q, NZ
| - prehodni regulacijska ventil hlajenje, tlačno neodvisni za hidravlično uravnoteženje z elektro motornim ali elektro termičnim on/off pogonom, vključno z navojnima holandcema, pretok 110 ÷ 1100 l/h - ustreza proizvod DANFOSS tip ventila AB-QM 20, tip pogona TWA-Q, NZ | - transient cooling control valve, pressure independent for hydraulic balancing with electric motor or electric thermal on/off actuator, incl. threaded Dutch, flow 110 ÷ 1100 l/h - corresponds to DANFOSS product valve type AB-QM 20, actuator type TWA-Q, NZ
| - štirje zaporni krogelni ventili DN20 za ogrevno in za hladilno vodo - ustreza proizvod KOVINA | - four DN20 stop ball valves for heating and cooling water - corresponds to product METAL
| Kasetni ventilatorski konvektor ustreza proizvod AERMEC tip FCLI z dodatno opremo ali enakovredno: | The cassette fan coil unit corresponds to the AERMEC product type FCLI with accessories or equivalent:
| - ogrevna moč za 50/40-20°C: 1140 W, hladilna moč za 9/14-26°C: 1540 W, ustreza tip FCLI34 | - heating power for 50/40-20°C: 1140 W, cooling power for 9/14-26°C: 1540 W, corresponds to type FCLI34 | kpl | 34 |  | 0
| - ogrevna moč za 50/40-20°C: 1260 W, hladilna moč za 9/14-26°C: 2250 W, ustreza tip FCLI44 | - heating power for 50/40-20°C: 1260 W, cooling power for 9/14-26°C: 2250 W, corresponds to type FCLI44 | kpl | 319 |  | 0
| - ogrevna moč za 50/40-20°C: 2250 W, hladilna moč za 9/14-26°C: 2930 W, ustreza tip FCLI124 | - heating power for 50/40-20°C: 2250 W, cooling power for 9/14-26°C: 2930 W, corresponds to type FCLI124 | kpl | 22 |  | 0
1.45 | Kanalski ventilatorski konvektor štiricevne izvedbe za ogrevanje in hlajenje, vgradnja pod strop, izdelano iz jeklene pocinkane pločevine, lamelna prenosnika toplote, zbiralnik za kondenzat s črpalko za prečrpavanje kondenzata, radialni ventilator z inverterskim elektromotorjem, odzračevalni in izpustni ventil, delovni tlak do 6 bar, gibke cevne povezave nerjavne izvedbe, dva regulacijska ventila z elektromotornim pogonom s funkcijo hidravličnega uravnoteženja, zaporni ventili za ogrevno in hladilno vodo, vključno z obešalnim, pritrdilnim in tesnilnim materialom; Eurovent certifikat; Tehnični podatki: | Four-pipe ducted fan-coil unit for heating and cooling, ceiling mounting, made of galvanised sheet steel, laminated heat exchangers, condensate collector with condensate pump, radial fan with inverter electric motor, vent and discharge valve, operating pressure up to 6 bar, flexible stainless steel pipe connections, two electric motor-operated control valves with hydraulic balancing function, shut-off valves for heating and cooling water, incl. hanging, fixing and sealing material; Eurovent certificate; Technical data:
| - filter za zajem prostorskega zraka G3 z zaščitno mrežico | - g3 room air filter with protective mesh
| - plenum z dvema priključkoma iztočnega zraka 2x Ø250 mm | - plenum with two outlet air connections 2x Ø250 mm
| - hrup v največji hitrosti do 55 dB(A) | - noise at maximum speed up to 55 dB(A)
| - inverter motor ventilatorja za nastavitev zvezne hitrosti | - inverter fan motor for continuous speed adjustment
| - črpalka za prečrpavanje kondenzata | - condensate pump
| - elektro podatki: do 280 W, 230V/ 1/ 50Hz | - electrical data: up to 280 W, 230V/ 1/ 50Hz
| - dimenzije: dolžina L x širina W x višina H = 800÷1200 x 600 x 300 mm, teža do 50 kg | - dimensions: length L x width W x height H = 800÷1200 x 600 x 300 mm, weight up to 50 kg
| - gibke cevne povezave iz nerjavnega jekla DN20 - ustreza proizvod CATS | - flexible hose connections in stainless steel DN20 - corresponds to CATS product
| - prehodni regulacijska ventil ogrevanje, tlačno neodvisni za hidravlično uravnoteženje z elektro motornim ali elektro termičnim on/off pogonom, vključno z navojnima holandcema, pretok 65 ÷ 650 l/h - ustreza proizvod DANFOSS tip ventila AB-QM 15, tip pogona TWA-Q, NZ | - heating control valve, pressure independent for hydraulic balancing with electric motor or electric thermal on/off actuator, incl. threaded Dutch, flow 65 ÷ 650 l/h - corresponds to DANFOSS product valve type AB-QM 15, actuator type TWA-Q, NZ
| - prehodni regulacijska ventil hlajenje, tlačno neodvisni za hidravlično uravnoteženje z elektro motornim ali elektro termičnim on/off pogonom, vključno z navojnima holandcema, pretok 110 ÷ 1100 l/h - ustreza proizvod DANFOSS tip ventila AB-QM 20, tip pogona TWA-Q, NZ | - transient cooling control valve, pressure independent for hydraulic balancing with electric motor or electric thermal on/off actuator, including threaded Dutchman, flow 110 ÷ 1100 l/h - corresponds to DANFOSS product valve type AB-QM 20, actuator type TWA-Q, NZ
| - štirje zaporni krogelni ventili DN20 za ogrevno in za hladilno vodo - ustreza proizvod KOVINA | - four DN20 stop ball valves for heating and cooling water - corresponds to product METAL
| Kanalski ventilatorski konvektor ustreza proizvod AERMEC tip FCZI-P z dodatno opremo ali enakovredno: | The ducted fan coil unit corresponds to the AERMEC product type FCZI-P with accessories or equivalent:
| - ogrevna moč za 50/40-20°C: 1140 W, hladilna moč za 9/14-26°C: 1540 W, ustreza tip FCZI-P202 | - heating power for 50/40-20°C: 1140 W, cooling power for 9/14-26°C: 1540 W, corresponds to type FCZI-P202 | kpl | 17 |  | 0
| - ogrevna moč za 50/40-20°C: 1260 W, hladilna moč za 9/14-26°C: 2250 W, ustreza tip FCZI-P302 | - heating power for 50/40-20°C: 1260 W, cooling power for 9/14-26°C: 2250 W, corresponds to type FCZI-P302 | kpl | 84 |  | 0
| - ogrevna moč za 50/40-20°C: 2250 W, hladilna moč za 9/14-26°C: 2930 W, ustreza tip FCZI-P402 | - heating power for 50/40-20°C: 2250 W, cooling power for 9/14-26°C: 2930 W, corresponds to type FCZI-P402 | kpl | 152 |  | 0
1.46 | Kanalski ventilatorski konvektor štiricevne izvedbe za ogrevanje in hlajenje, vgradnja v parapet, izdelano iz jeklene pocinkane pločevine, lamelna prenosnika toplote, zbiralnik za kondenzat s črpalko za prečrpavanje kondenzata, radialni ventilator z inverterskim elektromotorjem, odzračevalni in izpustni ventil, delovni tlak do 6 bar, gibke cevne povezave nerjavne izvedbe, dva regulacijska ventila z elektromotornim pogonom s funkcijo hidravličnega uravnoteženja, zaporni ventili za ogrevno in hladilno vodo, vključno z obešalnim, pritrdilnim in tesnilnim materialom; Eurovent certifikat; Tehnični podatki: | Four-pipe ducted fan convector for heating and cooling, installation in parapet, made of galvanised sheet steel, laminated heat exchangers, condensate collector with condensate pump, radial fan with inverter electric motor, vent and discharge valve, operating pressure up to 6 bar, flexible stainless steel pipe connections, two electric motor-operated control valves with hydraulic balancing function, shut-off valves for heating and cooling water, incl. hanging, fixing and sealing material; Eurovent certificate; Technical data:
| - filter za zajem prostorskega zraka G3 z zaščitno mrežico | - g3 room air filter with protective mesh
| - hrup v največji hitrosti do 55 dB(A) | - noise at maximum speed up to 55 dB(A)
| - inverter motor ventilatorja za nastavitev zvezne hitrosti | - inverter fan motor for continuous speed adjustment
| - črpalka za prečrpavanje kondenzata | - condensate pump
| - elektro podatki: do 280 W, 230V/ 1/ 50Hz | - electrical data: up to 280 W, 230V/ 1/ 50Hz
| - dimenzije: dolžina L x širina W x višina H = 800÷1200 x 600 x 300 mm, teža do 50 kg | - dimensions: length L x width W x height H = 800÷1200 x 600 x 300 mm, weight up to 50 kg
| - gibke cevne povezave iz nerjavnega jekla DN20 - ustreza proizvod CATS | - flexible hose connections in stainless steel DN20 - corresponds to CATS product
| - prehodni regulacijska ventil ogrevanje, tlačno neodvisni za hidravlično uravnoteženje z elektro motornim ali elektro termičnim on/off pogonom, vključno z navojnima holandcema, pretok 110 ÷ 1100 l/h - ustreza proizvod DANFOSS tip ventila AB-QM 20, tip pogona TWA-Q, NZ | - heating control valve, pressure independent for hydraulic balancing with electric motor or electric thermal on/off actuator, incl. threaded Dutch, flow 110 ÷ 1100 l/h - corresponds to DANFOSS product valve type AB-QM 20, actuator type TWA-Q, NZ
| - prehodni regulacijska ventil ogrevanje, tlačno neodvisni za hidravlično uravnoteženje z elektro motornim ali elektro termičnim on/off pogonom, vključno z navojnima holandcema, pretok 65 ÷ 650 l/h - ustreza proizvod DANFOSS tip ventila AB-QM 15, tip pogona TWA-Q, NZ | - heating control valve, pressure independent for hydraulic balancing with electric motor or electric thermal on/off actuator, incl. threaded Dutch, flow 65 ÷ 650 l/h - corresponds to DANFOSS product valve type AB-QM 15, actuator type TWA-Q, NZ
| - štirje zaporni krogelni ventili DN20 za ogrevno in za hladilno vodo - ustreza proizvod KOVINA | - four DN20 stop ball valves for heating and cooling water - corresponds to product METAL
| Kanalski ventilatorski konvektor ustreza proizvod AERMEC tip FCZI-P z dodatno opremo ali enakovredno: | The ducted fan coil unit corresponds to the AERMEC product type FCZI-P with accessories or equivalent:
| - ogrevna moč za 50/40-20°C: 1140 W, hladilna moč za 9/14-26°C: 1540 W, ustreza tip FCZI-P201 | - heating power for 50/40-20°C: 1140 W, cooling power for 9/14-26°C: 1540 W, corresponds to type FCZI-P201 | kpl | 1 |  | 0
| - ogrevna moč za 50/40-20°C: 1260 W, hladilna moč za 9/14-26°C: 2250 W, ustreza tip FCZI-P301 | - heating power for 50/40-20°C: 1260 W, cooling power for 9/14-26°C: 2250 W, corresponds to type FCZI-P301 | kpl | 43 |  | 0
| - ogrevna moč za 50/40-20°C: 2250 W, hladilna moč za 9/14-26°C: 2930 W, ustreza tip FCZI-P401 | - heating power for 50/40-20°C: 2250 W, cooling power for 9/14-26°C: 2930 W, corresponds to type FCZI-P401 | kpl | 40 |  | 0
1.47 | Jeklene srednje težke šivne cevi izdelane po EN10255 (DIN2440), material S195T (St33.2), vključno z oblikovnimi kosi (loki, redukcije, T kosi, ...) in varilnim materialom, | Medium-weight seamed steel tubes manufactured to EN10255 (DIN2440), material S195T (St33.2), including forming pieces (bows, reducers, T-pieces, etc.) and welding consumables,
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and hose clamps with noise damping lining, suitable for HILTI or SIKLA, or equivalent;
| DN 15, ø 21,3 x 2,65 | DN 15, ø 21,3 x 2,65 | m | 240 |  | 0
| DN 20, ø 26,9 x 2,65 | DN 20, ø 26,9 x 2,65 | m | 210 |  | 0
| DN 25, ø 33,7 x 3,25 | DN 25, ø 33,7 x 3,25 | m | 270 |  | 0
| DN 32, ø 42,4 x 3,25 | DN 32, ø 42,4 x 3,25 | m | 360 |  | 0
| DN 40, ø 48,3 x 3,25 | DN 40, ø 48,3 x 3,25 | m | 270 |  | 0
| DN 50, ø 60,3 x 3,65 | DN 50, ø 60,3 x 3,65 | m | 240 |  | 0
| 90°lok DN 15, ø 21,3 x 2,65 | 90°lok DN 15, ø 21,3 x 2,65 | kos | 40 |  | 0
| 90°lok DN 20, ø 26,9 x 2,65 | 90°lok DN 20, ø 26,9 x 2,65 | kos | 40 |  | 0
| 90°lok DN 25, ø 33,7 x 3,25 | 90°lok DN 25, ø 33,7 x 3,25 | kos | 50 |  | 0
| 90°lok DN 32, ø 42,4 x 3,25 | 90°lok DN 32, ø 42,4 x 3,25 | kos | 60 |  | 0
| 90°lok DN 40, ø 48,3 x 3,25 | 90°lok DN 40, ø 48,3 x 3,25 | kos | 50 |  | 0
| 90°lok DN 50, ø 60,3 x 3,65 | 90°lok DN 50, ø 60,3 x 3,65 | kos | 40 |  | 0
| T kos DN 25 / odcep DN 15 | T piece DN 25 / branch DN 15 | kos | 40 |  | 0
| T kos DN 25 / odcep DN 20 | T piece DN 25 / branch DN 20 | kos | 40 |  | 0
| T kos DN 32 / odcep DN 20 | T piece DN 32 / branch DN 20 | kos | 50 |  | 0
| T kos DN 32 / odcep DN 25 | T piece DN 32 / branch DN 25 | kos | 60 |  | 0
| T kos DN 40 / odcep DN 15 | T piece DN 40 / branch DN 15 | kos | 50 |  | 0
| T kos DN 40 / odcep DN 20 | T piece DN 40 / branch DN 20 | kos | 40 |  | 0
| T kos DN 50 / odcep DN 15 | T piece DN 50 / branch DN 15 | kos | 30 |  | 0
| T kos DN 40 / odcep DN 40 | T piece DN 40 / branch DN 40 | kos | 30 |  | 0
| T kos DN 50 / odcep DN 50 | T piece DN 50 / branch DN 50 | kos | 20 |  | 0
| redukcija DN 20 / DN 15 | reduction DN 20 / DN 15 | kos | 40 |  | 0
| redukcija DN 25 / DN 20 | dN 25 / DN 20 reduction | kos | 40 |  | 0
| redukcija DN 32 / DN 25 | dN 32 / DN 25 reduction | kos | 50 |  | 0
| redukcija DN 40 / DN 32 | dN 40 / DN 32 reduction | kos | 60 |  | 0
| redukcija DN 50 / DN 32 | dN 50 / DN 32 reduction | kos | 50 |  | 0
| redukcija DN 50 / DN 40 | dN 50 / DN 40 reduction | kos | 40 |  | 0
| prirobnica DN 50 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 50 to EN1092, PN16, including bolting and sealing material | kpl | 10 |  | 0
1.48 | Jeklene brezšivne cevi izdelane po EN10216-1 (DIN2448), iz materiala P235TR2 (St37), vključno z oblikovnimi kosi (loki, redukcije, T kosi, ...) in varilnim materialom, | Seamless steel tubes manufactured to EN10216-1 (DIN2448), in P235TR2 (St37), including forming pieces (bends, reducers, T-pieces, etc.) and welding consumables,
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and hose clamps with noise damping lining, suitable for HILTI or SIKLA, or equivalent;
| DN 65, ø 76,1 x 2,9 | DN 65, ø 76,1 x 2,9 | m | 240 |  | 0
| DN 80, ø 88,9 x 3,2 | DN 80, ø 88,9 x 3,2 | m | 270 |  | 0
| DN 100, ø 114,3 x 3,6 | DN 100, ø 114,3 x 3,6 | m | 330 |  | 0
| DN 125, ø 139,7 x 4,0 | DN 125, ø 139,7 x 4,0 | m | 480 |  | 0
| DN 150, ø 168,3 x 4,5 | DN 150, ø 168,3 x 4,5 | m | 240 |  | 0
| DN 200, ø 219,1 x 5,9 | DN 200, ø 219.1 x 5.9 | m | 120 |  | 0
| 90°lok DN 65, ø 76,1 x 2,9 | 90°lok DN 65, ø 76,1 x 2,9 | kos | 70 |  | 0
| 90°lok DN 80, ø 88,9 x 3,2 | 90°lok DN 80, ø 88,9 x 3,2 | kos | 80 |  | 0
| 90°lok DN 100, ø 114,3 x 3,6 | 90°lok DN 100, ø 114,3 x 3,6 | kos | 90 |  | 0
| 90°lok DN 125, ø 139,7 x 4,0 | 90°block DN 125, ø 139.7 x 4.0 | kos | 70 |  | 0
| 90°lok DN 150, ø 168,3 x 4,5 | 90°lok DN 150, ø 168,3 x 4,5 | kos | 50 |  | 0
| 90°lok DN 200, ø 219,1 x 5,9 | 90°lok DN 200, ø 219.1 x 5.9 | kos | 30 |  | 0
| T kos DN 65 / odcep DN 50 | T piece DN 65 / branch DN 50 | kos | 20 |  | 0
| T kos DN 65 / odcep DN 65 | T piece DN 65 / branch DN 65 | kos | 20 |  | 0
| T kos DN 80 / odcep DN 65 | T piece DN 80 / branch DN 65 | kos | 20 |  | 0
| T kos DN 80 / odcep DN 80 | T piece DN 80 / branch DN 80 | kos | 20 |  | 0
| T kos DN 100 / odcep DN 80 | T piece DN 100 / branch DN 80 | kos | 20 |  | 0
| T kos DN 125 / odcep DN 100 | T piece DN 125 / branch DN 100 | kos | 20 |  | 0
| T kos DN 150 / odcep DN 125 | T piece DN 150 / branch DN 125 | kos | 20 |  | 0
| T kos DN 200 / odcep DN 150 | T piece DN 200 / branch DN 150 | kos | 20 |  | 0
| T kos DN 200 / odcep DN 200 | T piece DN 200 / branch DN 200 | kos | 20 |  | 0
| redukcija DN 65 / DN 50 | dN 65 / DN 50 reduction | kos | 20 |  | 0
| redukcija DN 80 / DN 65 | dN 80 / DN 65 reduction | kos | 20 |  | 0
| redukcija DN 100 / DN 80 | dN 100 / DN 80 reduction | kos | 20 |  | 0
| redukcija DN 125 / DN 100 | dN 125 / DN 100 reduction | kos | 20 |  | 0
| redukcija DN 150 / DN 125 | reduction DN 150 / DN 125 | kos | 20 |  | 0
| redukcija DN 200 / DN 150 | reduction DN 200 / DN 150 | kos | 20 |  | 0
| prirobnica DN 65 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 65 to EN1092, PN16, including bolting and sealing material | kpl | 20 |  | 0
| prirobnica DN 80 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 80 to EN1092, PN16, including bolting and sealing material | kpl | 20 |  | 0
| prirobnica DN 100 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 100 to EN1092, PN16, including bolting and sealing material | kpl | 20 |  | 0
| prirobnica DN 125 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 125 to EN1092, PN16, including bolting and sealing material | kpl | 20 |  | 0
| prirobnica DN 150 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 150 to EN1092, PN16, including bolting and sealing material | kpl | 20 |  | 0
| prirobnica DN 200 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 200 to EN1092, PN16, including bolting and sealing material | kpl | 20 |  | 0
1.49 | Čiščenje in barvanje jeklenih cevovodov iz ogljikovega jekla, odstranitev rje do kovinskega sijaja, dvakratni premaz s temeljnim antikorozijskim barvami ter dvakratni premaz s prekrivno barvo: antikorozijska zaščita s temeljnimi in prekrivnimi barvami mora biti obstojna na temperature v območju od -20 do +80°C in se mora izvesti v skladu z EN ISO 12944 z življenjsko dobo: visoko trajanje H (več kot 15 let). | Cleaning and painting of carbon steel pipelines, rust removal to metallic gloss, two coats of anticorrosion primer and two coats of overcoat: the anticorrosion protection with primer and overcoat must be resistant to temperatures in the range -20 to +80°C and must be carried out in accordance with EN ISO 12944 with a service life: high durability H (more than 15 years).
| - ogrevna voda 50/40°C | - heating water 50/40°C | m2 | 1800 |  | 0
1.50 | Jeklene nerjavne cevi za precizno uporabo, zatisni press sistem, PN10 ali več, izdelava in skladnost po EN10088, EN10312, material nerjavno jeklo 1.4520 ali 1.4404 ali boljši, vključno s spojnimi in oblikovnimi zatisnimi press kosi (90°loki, T kosi, redukcije, ...), spojnim in tesnilnim materialom, zatiskanje z originalnim press orodjem proizvajalca, komplet s prehodnimi navojnimi in prirobnični oblikovnimi kosi, ustreza proizvod VIEGA ali KANTHERM ali enakovredno; | Stainless steel tubes for precision applications, press fitting system, PN10 or higher, manufacture and conformity to EN10088, EN10312, material stainless steel 1.4520 or 1.4404 or better, including coupling and press fitting shapes (90°bends, T-pieces, reducers, etc.), coupling and sealing material, press fitting with original manufacturer's press tool, complete with threaded and flanged transition shapes, corresponding to VIEGA or KANTHERM product or equivalent;
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and hose clamps with noise damping lining, suitable for HILTI or SIKLA, or equivalent;
| DN 15, ø 18 x 1,2 | DN 15, ø 18 x 1,2 | m | 4220 |  | 0
| DN 20, ø 22 x 1,5 | DN 20, ø 22 x 1,5 | m | 3350 |  | 0
| DN 25, ø 28 x 1,5 | DN 25, ø 28 x 1,5 | m | 1890 |  | 0
| DN 32, ø 35 x 1,5 | DN 32, ø 35 x 1,5 | m | 1350 |  | 0
| DN 40, ø 42 x 1,5 | DN 40, ø 42 x 1,5 | m | 1230 |  | 0
| DN 50, ø 54 x 1,5 | DN 50, ø 54 x 1,5 | m | 1290 |  | 0
| DN 65, ø 76,1 x 2 | DN 65, ø 76,1 x 2 | m | 720 |  | 0
| DN 80, ø 88,9 x 2 | DN 80, ø 88,9 x 2 | m | 360 |  | 0
| DN 100, ø 108 x 2 | DN 100, ø 108 x 2 | m | 270 |  | 0
| 90°lok DN 15, ø 18 x 1,2 | 90°lok DN 15, ø 18 x 1,2 | kos | 780 |  | 0
| 90°lok DN 20, ø 22 x 1,5 | 90°lok DN 20, ø 22 x 1,5 | kos | 450 |  | 0
| 90°lok DN 25, ø 28 x 1,5 | 90°lok DN 25, ø 28 x 1,5 | kos | 320 |  | 0
| 90°lok DN 32, ø 35 x 1,5 | 90°lok DN 32, ø 35 x 1,5 | kos | 250 |  | 0
| 90°lok DN 40, ø 42 x 1,5 | 90°lok DN 40, ø 42 x 1,5 | kos | 210 |  | 0
| 90°lok DN 50, ø 54 x 1,5 | 90°lok DN 50, ø 54 x 1,5 | kos | 200 |  | 0
| 90°lok DN 65, ø 76,1 x 2 | 90°lok DN 65, ø 76,1 x 2 | kos | 140 |  | 0
| 90°lok DN 80, ø 88,9 x 2 | 90°lok DN 80, ø 88,9 x 2 | kos | 80 |  | 0
| 90°lok DN 100, ø 108 x 2 | 90°lok DN 100, ø 108 x 2 | kos | 60 |  | 0
| T kos DN 25 / odcep DN 15 | T piece DN 25 / branch DN 15 | kos | 400 |  | 0
| T kos DN 25 / odcep DN 20 | T piece DN 25 / branch DN 20 | kos | 200 |  | 0
| T kos DN 32 / odcep DN 25 | T piece DN 32 / branch DN 25 | kos | 200 |  | 0
| T kos DN 40 / odcep DN 15 | T piece DN 40 / branch DN 15 | kos | 200 |  | 0
| T kos DN 40 / odcep DN 32 | T piece DN 40 / branch DN 32 | kos | 200 |  | 0
| T kos DN 50 / odcep DN 15 | T piece DN 50 / branch DN 15 | kos | 200 |  | 0
| T kos DN 50 / odcep DN 25 | T piece DN 50 / branch DN 25 | kos | 200 |  | 0
| T kos DN 50 / odcep DN 40 | T piece DN 50 / branch DN 40 | kos | 100 |  | 0
| T kos DN 65 / odcep DN 50 | T piece DN 65 / branch DN 50 | kos | 100 |  | 0
| T kos DN 100 / odcep DN 80 | T piece DN 100 / branch DN 80 | kos | 100 |  | 0
| redukcija DN 20 / DN 15 | reduction DN 20 / DN 15 | kos | 200 |  | 0
| redukcija DN 25 / DN 20 | dN 25 / DN 20 reduction | kos | 100 |  | 0
| redukcija DN 32 / DN 15 | dN 32 / DN 15 reduction | kos | 100 |  | 0
| redukcija DN 32 / DN 25 | dN 32 / DN 25 reduction | kos | 100 |  | 0
| redukcija DN 40 / DN 32 | dN 40 / DN 32 reduction | kos | 100 |  | 0
| redukcija DN 50 / DN 32 | dN 50 / DN 32 reduction | kos | 60 |  | 0
| redukcija DN 50 / DN 20 | dN 50 / DN 20 reduction | kos | 60 |  | 0
| redukcija DN 50 / DN 40 | dN 50 / DN 40 reduction | kos | 60 |  | 0
| redukcija DN 65 / DN 20 | dN 65 / DN 20 reduction | kos | 30 |  | 0
| redukcija DN 65 / DN 40 | dN 65 / DN 40 reduction | kos | 30 |  | 0
| redukcija DN 100 / DN 25 | dN 100 / DN 25 reduction | kos | 30 |  | 0
| redukcija DN 100 / DN 80 | dN 100 / DN 80 reduction | kos | 30 |  | 0
| prirobnica DN 32 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 32 to EN1092, PN16, including bolting and sealing material | kpl | 20 |  | 0
| prirobnica DN 40 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 40 to EN1092, PN16, including bolting and sealing material | kpl | 20 |  | 0
| prirobnica DN 50 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 50 to EN1092, PN16, including bolting and sealing material | kpl | 20 |  | 0
| prirobnica DN 65 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 65 to EN1092, PN16, including bolting and sealing material | kpl | 20 |  | 0
| prirobnica DN 80 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 80 to EN1092, PN16, including bolting and sealing material | kpl | 20 |  | 0
| prirobnica DN 100 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 100 to EN1092, PN16, including bolting and sealing material | kpl | 20 |  | 0
1.51 | Toplotna izolacija cevovodov in cevnih armatur s parozaporno izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z naslednjimi lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, požarna klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +110°C, lepljeno na cevovode in armature z originalnim lepilom proizvajalca, vključno s trakovi za šive; | Thermal insulation of pipelines and pipe fittings with vapour barrier insulation made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, fire classification B-s3-d0 according to EN13501-1, for temperatures from -50 to +110°C, bonded to pipelines and fittings with the original manufacturer's adhesive, including seam tapes;
| - barva izolacije črna | - insulation colour black
| - ustreza proizvod ARMACELL tip Armaflex ACE Plus ali enakovredno | - corresponds to ARMACELL product type Armaflex ACE Plus or equivalent
| DN 15 ; debelina 13 mm | DN 15 ; thickness 13 mm | m | 6690 |  | 0
| DN 20 ; debelina 19 mm | DN 20 ; thickness 19 mm | m | 5340 |  | 0
| DN 25 ; debelina 19 mm | DN 25 ; thickness 19 mm | m | 3240 |  | 0
| DN 32 ; debelina 25 mm | DN 32 ; thickness 25 mm | m | 2580 |  | 0
| DN 40 ; debelina 25 mm | DN 40 ; thickness 25 mm | m | 2250 |  | 0
| DN 50 ; debelina 40 mm | DN 50 ; thickness 40 mm | m | 2320 |  | 0
| DN 65 ; debelina 40 mm | DN 65 ; thickness 40 mm | m | 1450 |  | 0
| DN 80 ; debelina 40 mm | DN 80 ; thickness 40 mm | m | 950 |  | 0
| DN 100 ; debelina 40 mm | DN 100 ; thickness 40 mm | m | 920 |  | 0
| DN 125 ; debelina 40 mm | DN 125 ; thickness 40 mm | m | 1890 |  | 0
| DN 150 ; debelina 40 mm | DN 150 ; thickness 40 mm | m | 1040 |  | 0
| DN 200 ; debelina 40 mm | DN 200 ; thickness 40 mm | m | 660 |  | 0
| v ploščah ; debelina 40 mm | in panels ; thickness 40 mm | m2 | 600 |  | 0
1.52 | Tlačni preskus trdnosti in tesnenja sistema cevovodov, skladeno z opisom v "IZS Priročnik tlačnih preizkusov strojnih inštalacij", vključno s potrebnim materialom za izvedbo preizkusa, ter izdelavo pisnega poročila o uspešno opravljenem tlačnem preizkusu; | Pressure test of the strength and tightness of the piping system, as described in the "IZS Manual for Pressure Testing of Mechanical Installations", including the necessary materials for the test, and the production of a written report on the successful completion of the pressure test;
| preskusni tlak = 1,3 x najvišji delovni tlak = 6,5 barg | test pressure = 1,3 x maximum working pressure = 6,5 barg | kpl | 1 |  | 0
1.53 | Izpiranje cevovodov s sanitarno hladno vodo v celotnem sistemu novoinstaliranih razvodov z namenom odstranjevanja nečistoč v sistemu cevovodov, vključno s čiščenjem lovilnikov nesnage in drugih elementov; | Flushing of sanitary cold water piping throughout the newly installed piping system to remove impurities in the piping system, including cleaning of debris traps and other elements; | kpl | 1 |  | 0
1.54 | Kvalifikacija zvarov ter izdelava dokumentacije o zvarih: | Weld qualification and documentation of welds:
| - zvare lahko izvajajo samo varilci s certifikatom pooblaščenih organizacij, | - welding can only be carried out by welders certified by approved organisations,
| - postopek vizualne kontrole zvarov, kontrolirajo se vsi zvari - 100% zvarov, | - visual weld inspection procedure, all welds are inspected - 100% of welds,
| - postopek kontrole s snemanja zvarov - 10% zvarov, kjer so enakomerno zastopani vsi premeri, | - weld stripping inspection procedure - 10% of welds where all diameters are equally represented,
| - označevanje zvarov, izdelava dokumentacije z dokazili o ustreznosti ter slikovnim materialom; | - marking welds, producing documentation with proof of conformity and pictorial material; | kpl | 1 |  | 0
1.55 | Ognjeodporna tesnilna masa, vgradnja na prehodu cevovodov skozi zid med požarnima sektortjema, požarna odpornost 90 minut, ustreza proizvod HILTI ali enakovredno. | Fire-resistant sealant, for installation at the transition of pipelines through the wall between the two fire sectors, fire resistance 90 minutes, equivalent to HILTI or equivalent.
| Vsak prehod mora biti označen z nalepko ali tablico z osnovnimi požarnimi podatki; | Each passageway must be marked with a sticker or placard with basic fire information; | kpl | 1 |  | 0
1.56 | Preizkusno obratovanje delovanja sistema v obsegu: | Operational test of the system in scope:
| - pregled instalacije, armatur in opreme, | - inspection of plumbing, fixtures and fittings,
| - pregled delovanja naprav, elementov regulacije in nastavitve parametrov, | - overview of the operation of the devices, control elements and parameter settings,
| - pregled cirkulacije ogrevnega medija, | - checking the circulation of the heating medium,
| - ogrevanje vode na predpisane parametre; | - heating water to the prescribed parameters;
| Preizkusno obratovanje traja neprekinjeno 72 ur. | The test operation shall be continuous for 72 hours. | kpl | 1 |  | 0
1.57 | Napisne ploščice iz nerjavne pločevine z vgravirano oznako po shemi za opremo in armature, kompletno z jekleno pritrdilno žico ali visoko kvalitetne nalepke; visoko trajanje H (več kot 15 let) | Stainless steel nameplates with engraved marking according to the scheme for fittings and fixtures, complete with steel fixing wire or high quality stickers; high durability H (more than 15 years) | kpl | 1 |  | 0
1.58 | Samolepilne puščice za označitev smeri pretoka ter z napisom vrste medija: visoko trajanje H (več kot 15 let) | Self-adhesive arrows to indicate the direction of flow and the type of media: high durability H (more than 15 years) | kpl | 1 |  | 0
1.59 | Izdelava montažnih risb za izvedbo inštalacij med gradnjo objekta, kot so: detajli priključkov, montažne skice, montažni detajli, ipd. | Preparation of assembly drawings for the installation of services during the construction of the building, such as: connection details, assembly sketches, assembly details, etc. | kpl | 1 |  | 0
1.60 | Kvalifikacije montaže IQ-pregledi (instalation qualification) po GEP Commissioning protokolu in dokumentiranje kvalifikacije montaže, vključno z odpravo prvotnih napak montaže; | Installation qualification IQ-checks (installation qualification) according to the GEP Commissioning Protocol and documentation of installation qualification, including correction of original installation faults; | kpl | 1 |  | 0
1.61 | Meritve delovanja OQ-kvalifikacija (operation qualification) ter dokumentiranje meritev delovanja, vključno z nastavitvijo parametrov; | OQ (operation qualification) measurements and documentation of performance measurements, including parameter settings; | kpl | 1 |  | 0
1.62 | Posnetki izvedenega stanja, sprotno beleženje vseh sprememb nastalih med izvedbo, vrisovanje in vpisovanje v PZI projektno dokumentacijo; | Recording of the as-built condition, keeping a running record of any changes made during the execution, plotting and recording in the PZI project documentation; | kpl | 1 |  | 0
1.63 | Stenska shema sistema, vloženo v zaščitni okvir s prosojnim umetnim steklom (plastika) ali plastificirano, vključno s pritrditvijo na notranjo steno v strojnici objekta; | A wall diagram of the system, encased in a protective frame with transparent plastic or plasticised glass, including fixing to an internal wall in the mechanical room of the building; | kpl | 1 |  | 0
1.64 | Primopredajna dokumentacija, ki mora vsebovati: izjave, dokazilo o zanesljivosti objekta, certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo, obratovanje in vzdrževanje ter ostalo primopredajno dokumantacijo. Predaja se v dveh mapiranih izvodih ter en izvod v elektronski obliki; | The handover documentation, which shall include: declarations, proof of the reliability of the facility, certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use, operation and maintenance, and other handover documentation. It shall be handed over in two mapped copies and one copy in electronic form; | kpl | 1 |  | 0
| OGREVANJE | HEATING |  |  |  | 0

## 4.7.2_Hlajenje
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.7 | STROJNA DELA | MECHANICAL WORKS
4.7.2 | HLAJENJE | REFRIGERATION |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
2 | HLAJENJE | REFRIGERATION
| Vse postavke v nadalevanju zajemajo dobavo in montažo (razen tam kjer je to posebej navedeno). | All items below include delivery and installation (except where specifically indicated).
2.1 | Hidravlična kretnica, jeklena tlačna posoda PN10, skladno z direktivo o tlačni opremi PED, pokončne izvedbe, material ogljikovo jeklo P235TR1 (St37.0), ustrezne debeline jekla (min 10mm), skladnost z direktivo PED, komplet z vsemi priključki, izdelano po delavniški risbi dobavitelja, skladno s shemo in v načrtu, vključno s potiprirobnicami, varilnim, pritrdilnim, tesnilnim materialom. Tehnični podatki: | Hydraulic pressure switch, steel pressure vessel PN10, PED compliant, upright design, material carbon steel P235TR1 (St37.0), appropriate steel thickness (min 10mm), PED compliance, complete with all connections, manufactured according to supplier's shop drawing, as per schematic diagram and as per plan, including sub-fittings, welding, fixing, sealing material. Technical data:
| - hladilna voda 9/14°C | - cooling water 9/14°C
| - prostornina hidravlične kretnice: V = 16 m3 | - hydraulic switching volume: V = 16 m3
| - dimenzije posode: premer D x višina H = ø2300 x 4500 mm, postavljeno na jeklenih nogah 500 mm od tal, skupna višina 5000 mm | - dimensions of the container: diameter D x height H = ø2300 x 4500 mm, raised on steel legs 500 mm from the floor, total height 5000 mm
| - z pregradno ploščo horizontalno na sredini v kretnici z odrtino ø500 mm | - with a horizontal barrier plate in the centre in a switch with a ø500 mm opening
| - s prirobničnimi priključki PN10: 4x DN300 (glavni priključki od tega 2x zg.prekat, 2x sp.pekat), 1x DN50 (spodaj na dnu); z navojnimi priključki 1x DN25 (zgoraj na vrhu) ter 7x DN15 priključki za tipala in prikazovalnike | - with PN10 flanged connections: 4x DN300 (main connections of which 2x upper chamber, 2x lower chamber), 1x DN50 (bottom); with 1x DN25 threaded connections (top) and 7x DN15 connections for sensors and displays
| - prirobnična revizijska odprtina PN10: DN500 s slepo protiprirobnico, pritrdilnim in tesnilnim materialom | - pN10 flanged inspection opening: DN500 with blind counter flange, fixing and sealing material
| - antikorozijska zaščita; dvakratni premaz s temeljnim temperaturno odpornim antikorozijskim premazom ter dvakratnio premaz s prekrivno barvo, antikorozijska zaščita s temeljnimi in prekrivnimi barvami mora biti obstojna na temperature v območju od -20 do +80°C in se mora izvesti v skladu z EN ISO 12944 z življenjsko dobo: visoko trajanje H (več kot 15 let). | - anti-corrosion protection; two coats of temperature-resistant anti-corrosion primer and two coats of overcoat, the anti-corrosion protection with primers and overcoats must be resistant to temperatures in the range -20 to +80°C and must be carried out in accordance with EN ISO 12944 with a service life of: high durability H (more than 15 years).
| - obratovalna teža 18.000 kg | - operating weight 18.000 kg
| - toplotna parozaporno izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z naslednjimi lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, požarna klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +110°C, lepljeno na rezervoar z originalnim lepilom proizvajalca, vključno s trakovi za šive, debelina 50 mm; | - thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, fire classification B-s3-d0 according to EN13501-1, for temperatures from -50 to +110°C, bonded to the tank with the original manufacturer's adhesive, including seam tapes, 50 mm thick;
| Oznaka: HKA46.10 | Code: HKA46.10 | kpl | 1 |  | 0
2.2 | Razdelilnik / zbiralnik izdelan iz jeklene cevi DN300 ø323,9x7,1 po EN 10216-1 (DIN2448), iz materiala P235TR2 (St37.0), PN10, ležeče izvedbe, z prirobničnima zaključkoma DN300 in eno slepo prirobnico DN300, skladnost z direktivo PED, komplet z vsemi priključki, izdelano po delavniški risbi dobavitelja, skladno s shemo in v načrtu, vključno s potiprirobnicami, varilnim, pritrdilnim, tesnilnim materialom; | Manifold / manifold made of steel pipe DN300 ø323,9x7,1 according to EN 10216-1 (DIN2448), made of material P235TR2 (St37.0), PN10, of creep design, with flanged ends DN300 and one blind flange DN300, PED compliance, complete with all connections, made according to the supplier's shop drawing, according to the scheme and in the plan, including sub-fittings, welding, fixing, sealing material;
| - hladilna voda 9/14°C | - cooling water 9/14°C
| - dimenzije: premer D x dolžina L = DN300 x 2000 mm, z konstrukcijo za pritrditev na tla oziroma obešanje na strop | - dimensions: diameter D x length L = DN300 x 2000 mm, with floor or ceiling mounting structure
| - s prirobničnimi priključki PN10: 4x DN125 in navojnimi priključki: 1x DN32, 2x DN15 | - with PN10 flange connections: 4x DN125 and threaded connections: 1x DN32, 2x DN15
| - čiščenje in barvanje, odstranitev rje do kovinskega sijaja, dvakratni premaz s temeljnim antikorozijskim barvami ter dvakratni premaz s prekrivno barvo: obstojnost na temperature v območju od +5 do +80°C, skladno z EN ISO 12944 z življenjsko dobo: visoko trajanje H (več kot 15 let) | - cleaning and painting, rust removal to metallic gloss, double coating with anti-corrosion primer and double coating with overcoat: temperature resistance in the range +5 to +80°C, in accordance with EN ISO 12944 with service life: high durability H (more than 15 years)
| - komplet s toplotna parozaporna izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +105°C, debelina 40mm | - complete with thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, classification B-s3-d0 according to EN13501-1, for temperatures -50 to +105°C, thickness 40mm
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and pipe clamps with noise damping lining, suitable for HILTI or SIKLA, or equivalent;
| Oznaka: pri HKA46.10 | Code: at HKA46.10 | kpl | 2 |  | 0
2.3 | Razdelilnik / zbiralnik izdelan iz jeklene cevi DN300 ø323,9x7,1 po EN 10216-1 (DIN2448), iz materiala P235TR2 (St37.0), PN10, ležeče izvedbe, z prirobničnima zaključkoma DN300 in eno slepo prirobnico DN300, skladnost z direktivo PED, komplet z vsemi priključki, izdelano po delavniški risbi dobavitelja, skladno s shemo in v načrtu, vključno s potiprirobnicami, varilnim, pritrdilnim, tesnilnim materialom; | Manifold / manifold made of steel pipe DN300 ø323,9x7,1 according to EN 10216-1 (DIN2448), made of material P235TR2 (St37.0), PN10, of creep design, with flanged ends DN300 and one blind flange DN300, PED compliance, complete with all connections, made according to the supplier's shop drawing, according to the scheme and in the plan, including sub-fittings, welding, fixing, sealing material;
| - hladilna voda 9/14°C | - cooling water 9/14°C
| - dimenzije: premer D x dolžina L = DN300 x 1500 mm, s konstrukcijo za pritrditev na tla / strop | - dimensions: diameter D x length L = DN300 x 1500 mm, with floor/ceiling mounting structure
| - s prirobničnimi priključki PN10: 2x DN200 in navojnimi priključki: 2x DN15 | - with PN10 flange connections: 2x DN200 and threaded connections: 2x DN15
| - čiščenje in barvanje, odstranitev rje do kovinskega sijaja, dvakratni premaz s temeljnim antikorozijskim barvami ter dvakratni premaz s prekrivno barvo: obstojnost na temperature v območju od +5 do +80°C, skladno z EN ISO 12944 z življenjsko dobo: visoko trajanje H (več kot 15 let) | - cleaning and painting, rust removal to metallic gloss, double coating with anti-corrosion primer and double coating with overcoat: temperature resistance in the range +5 to +80°C, in accordance with EN ISO 12944 with service life: high durability H (more than 15 years)
| - komplet s toplotna parozaporna izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +105°C, debelina 40mm | - complete with thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, classification B-s3-d0 according to EN13501-1, for temperatures -50 to +105°C, thickness 40mm
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and pipe clamps with noise damping lining, suitable for HILTI or SIKLA, or equivalent;
| Oznaka: pri HKA46.10 | Code: at HKA46.10 | kpl | 2 |  | 0
2.4 | Ekspanzijska naprava za kompenzacijo temperaturnih raztezkov v sistemu hladilne vode skladno z EN12828, naprava za vzdrževanje tlaka z dvema kompresorjema ter kompaktno regulacijsko enoto z vsemi funkcijskimi elementi in komunikacijo s CNS, RS485 / Modbus RTU ter možnostjo povezave večih naprav kot Master / Slave, vključno s pritrdilnim in tesnilnim materialom; | Expansion device for temperature expansion compensation in cooling water system according to EN12828, pressure maintenance device with two compressors and compact control unit with all functional elements and communication with CNS, RS485 / Modbus RTU and possibility of connection of several devices as Master / Slave, including fastening and sealing material;
| - natančnost vzdrževanja tlaka ± 0,1 bar z dvema kompresorema (eden delovni, drugi je rezerva), sklop z dvema prelivnima ventiloma in varnostnim ventilom, preklapljanje je odvisno od časa in obremenitve | - pressure maintenance accuracy ± 0.1 bar with two compressors (one working, one reserve), two overflow valves and safety valve assembly, time and load dependent switching
| - primarna posoda V= 1500 l, podnožje s senzorjem za merjenje količine vode | - primary tank V= 1500 l, base with sensor for measuring water quantity
| - električna priključna moč 2x 1,2 kW pri 230 V / 1 / 50 Hz | - electrical connection power 2x 1,2 kW at 230 V / 1 / 50 Hz
| - PN10, CE skladno s PED | - PN10, CE according to PED
| - nivo hrupa kompresorja do 62 dB(A) | - compressor noise level up to 62 dB(A)
| - ustreza proizvod PNEVMATEX tip C10.2-5.0 + CG1500.6 ali enakovredno | - corresponds to PNEVMATEX product type C10.2-5.0 + CG1500.6 or equivalent
| Oznaka: EPK46.21 | Code: EPK46.21 | kpl | 1 |  | 0
2.5 | Varnostni ventil po TRD 721, PN16, varnostna funkcija izpusta medija zaradi toplotnih raztezkov v sistemu, vzmetno delovanje, možnost ročnega odzračenja, prostor vzmeti zaščiten z membrano, prirobnična izvedba, vključno s pritrdilnim in tesnilnim materialom; | Safety valve according to TRD 721, PN16, safety function of medium discharge due to thermal expansion in the system, spring operation, manual venting possible, spring space protected by diaphragm, flanged version, including fastening and sealing material;
| - za sistem ogrevne vode v temperaturnem območju od 5 do 50°C | - for heating water systems in the temperature range 5 to 50°C
| - tlak odpiranja 5,0 barg, | - opening pressure 5,0 barg,
| - s prirobničnim priključkoma DN 50 / 80, komplet z ventilom s ključavnico 2" (DN50) | - with flange connection DN 50/80, complete with valve with 2" lock (DN50)
| - ustreza proizvod IMI PNEUMATEX tip DSV 50 - 5.0 DGH + ... ali enakovredno | - iMI PNEUMATEX product type DSV 50 - 5.0 DGH + ... or equivalent
| Oznaka: VV46.23 | Code: VV46.23 | kpl | 1 |  | 0
2.6 | Naprava za odplinjevanje sistema hladilne vode skladno z EN12828 in dopolnjevanje z mehčano vodo z hidravlično ločitvijo tip AB po EN1717 komplet z kompaktno regulacijsko enoto z vsemi funkcijskimi elementi in komunikacijo s CNS, RS485 / Modbus RT ter možnostjo povezave večih naprav kot Master / Slave, vključno s pritrdilnim in tesnilnim materialom; | Device for degassing of the cooling water system according to EN12828 and make-up of softened water with hydraulic separation type AB according to EN1717 complete with compact control unit with all functional elements and communication with CNS, RS485 / Modbus RT and possibility of connection of several devices as Master / Slave, including fixing and sealing material;
| - za dopolnjevanje delovnega tlaka v sistemu do 4,5 bar | - for replenishing the system working pressure up to 4,5 bar
| - električna priključna moč 1,4 kW pri 230 V / 1 / 50 Hz | - electrical connection power 1,4 kW at 230 V / 1 / 50 Hz
| - PN10, CE skladno z evropskimi direktivami 2004/108/EC, 2006/95/EC | - PN10, CE compliant with European Directives 2004/108/EC, 2006/95/EC
| - nivo hrupa pri dopolnjevanju do 62 dB(A) | - replenishment noise level up to 62 dB(A)
| - ustreza proizvod PNEVMATEX tip V Connect V 8.1 E + Pleno P AB5 ali enakovredno | - corresponds to PNEVMATEX product type V Connect V 8.1 E + Pleno P AB5 or equivalent
| Oznaka: NOD46.22 | Code: NOD46.22 | kpl | 1 |  | 0
2.7 | Razdelilnik / zbiralnik izdelan iz jeklene cevi DN400 ø406,4x8,8 po EN 10216-1 (DIN2448), iz materiala P235TR1 (St37.0), PN10, ležeče izvedbe, z bombiranima ali prirobničnima zaključkoma, skladnost z direktivo PED, komplet z vsemi priključki, izdelano po delavniški risbi dobavitelja, skladno s shemo in v načrtu, vključno s potiprirobnicami, varilnim, pritrdilnim, tesnilnim materialom; | Manifold / manifold made of steel pipe DN400 ø406,4x8,8 according to EN 10216-1 (DIN2448), made of P235TR1 (St37.0), PN10, flat design, with bomb-coated or flanged ends, PED compliance, complete with all connections, made according to the supplier's shop drawing, according to the scheme and in the plan, including sub-plates, welding, fixing, sealing material;
| - hladilna voda 9/14°C | - cooling water 9/14°C
| - dimenzije: premer D x dolžina L = DN300 x 4500 mm, s konstrukcijo za pritrditev na tla / strop | - dimensions: diameter D x length L = DN300 x 4500 mm, with floor/ceiling mounting structure
| - s prirobničnimi priključki PN10: 3x DN200, 2x DN150, 1x DN100 ter z navojnimi priključki: 1x DN20 | - with PN10 flange connections: 3x DN200, 2x DN150, 1x DN100 and with threaded connections: 1x DN20
| - čiščenje in barvanje, odstranitev rje do kovinskega sijaja, dvakratni premaz s temeljnim antikorozijskim barvami ter dvakratni premaz s prekrivno barvo: obstojnost na temperature v območju od +5 do +80°C, skladno z EN ISO 12944 z življenjsko dobo: visoko trajanje H (več kot 15 let) | - cleaning and painting, rust removal to metallic gloss, double coating with anti-corrosion primer and double coating with overcoat: temperature resistance in the range +5 to +80°C, in accordance with EN ISO 12944 with service life: high durability H (more than 15 years)
| - komplet s toplotna parozaporna izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +105°C, debelina 40mm | - complete with thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, classification B-s3-d0 according to EN13501-1, for temperatures -50 to +105°C, thickness 40mm
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and pipe clamps with noise damping lining, suitable for HILTI or SIKLA, or equivalent;
| Oznaka: RZ47.10 | Code: RZ47.10 | kpl | 2 |  | 0
2.8 | Obtočna črpalka, centrifugalna inline, s suhim rotorjem, PN16, skladnost z ErP, elektronsko regulirana z integriranim frekvenčnim pretvornikom, s tipalom diferenčnega tlaka, upravljalnikom nastavitev s prikazovalnikom parametrov, internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, centrifugal inline, dry-running, PN16, ErP-compliant, electronically controlled with integrated frequency converter, differential pressure sensor, setting control with parameter display, internal hydraulic, electrical and communication connections, pump material grey cast iron with suitable medium seal, flanged design, including counter flanges, fixing and sealing material. Technical data:
| - hladilna voda 9/14°C | - cooling water 9/14°C
| - pretok V= 75,6m3/h, tlačna višina H= 80kPa | - flow rate V= 75,6m3/h, pressure head H= 80kPa
| - možnost izbire delovanja črpalke na proporcionalni tlak ter optimizacijo delovne točke z avtomatsko nastavitvijo pretoka ali glede na trenutne potrebe obratovanja | - option to choose proportional pressure operation and optimise the operating point by automatically adjusting the flow rate or according to the current operating requirements
| - komunikacija s CNS: RS485 / Modbus RTU | - communication with CNS: RS485 / Modbus RTU
| - elektro podatki Pel= 2,2 kW, 400V /3/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 2,2 kW, 400V /3/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip TPE3 100-130 ali enakovredno | - corresponds to GRUNDFOS product type TPE3 100-130 or equivalent
| Oznaka: P46.081, P46.082, P46.083, P46.084 | Code: P46.081, P46.082, P46.083, P46.084 | kpl | 4 |  | 0
2.9 | Obtočna črpalka, centrifugalna inline, s suhim rotorjem, PN16, skladnost z ErP, elektronsko regulirana z integriranim frekvenčnim pretvornikom, s tipalom diferenčnega tlaka, upravljalnikom nastavitev s prikazovalnikom parametrov, internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, centrifugal inline, dry-running, PN16, ErP-compliant, electronically controlled with integrated frequency converter, differential pressure sensor, setting control with parameter display, internal hydraulic, electrical and communication connections, pump material grey cast iron with suitable medium seal, flanged design, including counter flanges, fixing and sealing material. Technical data:
| - hladilna voda 9/14°C | - cooling water 9/14°C
| - pretok V= 182m3/h, tlačna višina H= 160kPa | - flow rate V= 182m3/h, pressure head H= 160kPa
| - možnost izbire delovanja črpalke na proporcionalni tlak ter optimizacijo delovne točke z avtomatsko nastavitvijo pretoka ali glede na trenutne potrebe obratovanja | - option to choose proportional pressure operation and optimise the operating point by automatically adjusting the flow rate or according to the current operating needs
| - komunikacija s CNS: RS485 / Modbus RTU | - communication with CNS: RS485 / Modbus RTU
| - elektro podatki Pel= 11 kW, 400V /3/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 11 kW, 400V /3/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip TPE3 125-290 ali enakovredno | - corresponds to GRUNDFOS product type TPE3 125-290 or equivalent
| Oznaka: P47.081 | Code: P47.081 | kpl | 1 |  | 0
2.10 | Obtočna črpalka, centrifugalna inline, s suhim rotorjem, PN16, skladnost z ErP, elektronsko regulirana z integriranim frekvenčnim pretvornikom, s tipalom diferenčnega tlaka, upravljalnikom nastavitev s prikazovalnikom parametrov, internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, centrifugal inline, dry-running, PN16, ErP-compliant, electronically controlled with integrated frequency converter, differential pressure sensor, setting control with parameter display, internal hydraulic, electrical and communication connections, pump material grey cast iron with suitable medium seal, flanged design, including counter flanges, fixing and sealing material. Technical data:
| - hladilna voda 9/14°C | - cooling water 9/14°C
| - pretok V= 100m3/h, tlačna višina H= 160kPa | - flow rate V= 100m3/h, pressure head H= 160kPa
| - možnost izbire delovanja črpalke na proporcionalni tlak ter optimizacijo delovne točke z avtomatsko nastavitvijo pretoka ali glede na trenutne potrebe obratovanja | - option to choose proportional pressure operation and optimise the operating point by automatically adjusting the flow rate or according to the current operating needs
| - komunikacija s CNS: RS485 / Modbus RTU | - communication with CNS: RS485 / Modbus RTU
| - elektro podatki Pel= 5,5 kW, 400V /3/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 5,5 kW, 400V /3/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip TPE3 100-230 ali enakovredno | - corresponds to GRUNDFOS product type TPE3 100-230 or equivalent
| Oznaka: P47.082 | Code: P47.082 | kpl | 1 |  | 0
2.11 | Obtočna črpalka, centrifugalna inline, s suhim rotorjem, PN16, skladnost z ErP, elektronsko regulirana z integriranim frekvenčnim pretvornikom, s tipalom diferenčnega tlaka, upravljalnikom nastavitev s prikazovalnikom parametrov, internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, centrifugal inline, dry-running, PN16, ErP-compliant, electronically controlled with integrated frequency converter, differential pressure sensor, setting control with parameter display, internal hydraulic, electrical and communication connections, pump material grey cast iron with suitable medium seal, flanged design, including counter flanges, fixing and sealing material. Technical data:
| - hladilna voda 9/14°C | - cooling water 9/14°C
| - pretok V= 98m3/h, tlačna višina H= 120kPa | - flow rate V= 98m3/h, pressure head H= 120kPa
| - možnost izbire delovanja črpalke na proporcionalni tlak ter optimizacijo delovne točke z avtomatsko nastavitvijo pretoka ali glede na trenutne potrebe obratovanja | - option to choose proportional pressure operation and optimise the operating point by automatically adjusting the flow rate or according to the current operating requirements
| - komunikacija s CNS: RS485 / Modbus RTU | - communication with CNS: RS485 / Modbus RTU
| - elektro podatki Pel= 4 kW, 400V /3/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 4 kW, 400V /3/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip TPE3 100-170 ali enakovredno | - corresponds to GRUNDFOS product type TPE3 100-170 or equivalent
| Oznaka: P47.083 | Code: P47.083 | kpl | 1 |  | 0
2.12 | Obtočna črpalka, PN10, z mokrim rotorjem, skladnost z ErP, elektronsko regulirana s PM motorjem in integrairanim frekvenčnim pretvornikom, inegrirano tipalo diferenčnega tlaka in temperature, upravljalnik nastavitev s prikazovalnikom parametrov, z internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, PN10, wet-rotor, ErP-compliant, electronically controlled with PM motor and integrated frequency converter, integrated differential pressure and temperature sensor, setting control with parameter display, with internal hydraulic, electrical and communication connections, pump material grey cast iron with appropriate sealing for the medium, flanged design, including counter flanges, fixing and sealing material. Technical data:
| - hladilna voda 15/19°C | - cooling water 15/19°C
| - pretok V= 2,61 m3/h, tlačna višina H= 35kPa, | - flow rate V= 2,61 m3/h, pressure head H= 35kPa,
| - komunikacija s CNS: RS485 / Modbus RTU | - communication with CNS: RS485 / Modbus RTU
| - elektro podatki Pel= 50W, 230V /1/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 50W, 230V /1/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip MAGNA3 25-40 | - corresponds to GRUNDFOS product type MAGNA3 25-40
| Oznaka: P12.421 | Code: P12.421 | kpl | 1 |  | 0
2.13 | Obtočna črpalka, PN10, z mokrim rotorjem, skladnost z ErP, elektronsko regulirana s PM motorjem in integrairanim frekvenčnim pretvornikom, inegrirano tipalo diferenčnega tlaka in temperature, upravljalnik nastavitev s prikazovalnikom parametrov, z internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, PN10, wet-rotor, ErP-compliant, electronically controlled with PM motor and integrated frequency converter, integrated differential pressure and temperature sensor, setting control with parameter display, with internal hydraulic, electrical and communication connections, pump material grey cast iron with appropriate sealing for the medium, flanged design, including counter flanges, fixing and sealing material. Technical data:
| - hladilna voda 15/19°C | - cooling water 15/19°C
| - pretok V= 0,49 m3/h, tlačna višina H= 30 kPa, oz. | - flow rate V = 0.49 m3/h, pressure head H = 30 kPa, or
| - pretok V= 0,56 m3/h, tlačna višina H= 30 kPa, oz. | - flow rate V = 0.56 m3/h, pressure head H = 30 kPa, or
| - pretok V= 0,64 m3/h, tlačna višina H= 30 kPa | - flow rate V = 0,64 m3/h, pressure head H = 30 kPa
| - komunikacija s CNS: RS485 / Modbus RTU | - communication with CNS: RS485 / Modbus RTU
| - elektro podatki Pel= 50W, 230V /1/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 50W, 230V /1/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip ALPHA2 25-40 N 130 | - corresponds to GRUNDFOS product type ALPHA2 25-40 N 130
| Oznaka: P12.411, P13.411, P13.421 | Code: P12.411, P13.411, P13.421 | kpl | 3 |  | 0
2.14 | Regulacijski ventil, prehodni, tlačno neodvisni za hidravlično uravnoteženje z elektromotornim zveznim pogonom, 24V, IP54, PN16, material ventila nikljana medenina, nerjavno jeklo / EPDM, navojna izvedba, komplet z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Control valve, intermediate, pressure independent for hydraulic balancing with electromotor continuous actuator, 24V, IP54, PN16, valve material nickel-plated brass, stainless steel / EPDM, threaded version, complete with threaded Dutch, fixing and sealing material;
| - hladilna voda 9/19°C | - cooling water 9/19°C
| DN25, Vv = 0,22 ÷ 2,2 m3/h - ustreza proizvod DANFOSS tip ventila AB-QM 25, tip pogona AME 110/24V NL ali enakovredno | DN25, Vv = 0,22 ÷ 2,2 m3/h - corresponds to DANFOSS product valve type AB-QM 25, actuator type AME 110/24V NL or equivalent
| Oznaka: VA12.422 | Code: VA12.422 | kpl | 1 |  | 0
2.15 | Regulacijski ventil, prehodni, tlačno neodvisni za hidravlično uravnoteženje z elektromotornim zveznim pogonom, 24V, IP54, PN16, material ventila nikljana medenina, nerjavno jeklo / EPDM, navojna izvedba, komplet z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Control valve, intermediate, pressure independent for hydraulic balancing with electromotor continuous actuator, 24V, IP54, PN16, valve material nickel-plated brass, stainless steel / EPDM, threaded version, complete with threaded Dutch, fixing and sealing material;
| - hladilna voda 9/19°C | - cooling water 9/19°C
| DN15, Vv = 0,065 ÷ 0,65 m3/h - ustreza proizvod DANFOSS tip ventila AB-QM 15, tip pogona AME 110/24V NL ali enakovredno | DN15, Vv = 0,065 ÷ 0,65 m3/h - corresponds to DANFOSS product valve type AB-QM 15, actuator type AME 110/24V NL or equivalent
| Oznaka: VA12.412, VA13.412, VA13.422 | Code: VA12.412, VA13.412, VA13.422 | kpl | 3 |  | 0
2.16 | Zaporna loputa z elektromotornim pogonom ON/OFF, 24V, IP66 in stikali končne lege odrto in zaprto, PN16, material lopute nodularna litina / EPDM, za vgradnjo med prirobnice, komplet s protiprirobnicama, vijačnim in tesnilnim materialom; | Butterfly valve with ON/OFF electric motor drive, 24V, IP66 and open and closed end position switches, PN16, butterfly valve material ductile iron / EPDM, for mounting between flanges, complete with counter flanges, screw and sealing material;
| - hladilna voda 9/14°C | - cooling water 9/14°C
| DN 125 - ustreza proizvod BELIMO tip D6125W +JRCA-S2-T +S2A ali enakovredno Oznaka: VX46.061, VX46.062, VX46.063, VX46.064, VX46.065, VX46.066, VX46.067, VX46.068 | DN 125 - fits BELIMO product type D6125W +JRCA-S2-T +S2A or equivalent Code: VX46.061, VX46.062, VX46.063, VX46.064, VX46.065, VX46.066, VX46.067, VX46.068 | kpl | 8 |  | 0
| DN 150 - ustreza proizvod BELIMO tip D6150W +JRCA-S2-T +S2A ali enakovredno Oznaka: DV47.073, DV47.074, DV47.075, DV47.076 | DN 150 - fits BELIMO product type D6150W +JRCA-S2-T +S2A or equivalent Code: DV47.073, DV47.074, DV47.075, DV47.076 | kpl | 4 |  | 0
| DN 200 - ustreza proizvod BELIMO tip D6200W +PRCA-S2-T-200 +S2A ali enakovredno Oznaka: DV47.071, DV47.072 | DN 200 - corresponds to BELIMO product type D6200W +PRCA-S2-T-200 +S2A or equivalent Code: DV47.071, DV47.072 | kpl | 2 |  | 0
2.17 | Tipalo tlaka s pretvornikom, za mertev tlaka v območju od 0 do 6 barg (relativno) ter nastavljivim alarmnim tlakom, navojni priključek 1/2" (DN15), material nerjavno jeklo, električni podatki: napajanje 24V, izhod 4-20mA, kompletno z ventilom za tipalo tlaka 1/2" (DN15) ter tesnilnim in pritrdilnim materialom; | Pressure sensor with transducer, for pressure measurement in the range from 0 to 6 barg (relative) and adjustable alarm pressure, threaded connection 1/2" (DN15), material stainless steel, electrical data: power supply 24V, output 4-20mA, complete with pressure sensor valve 1/2" (DN15) and sealing and fixing material;
| - hladilna voda 9/14°C | - cooling water 9/14°C
| - alarm, če je tlak p < 3,5 barg (nastavitev na tipalu ali programska nastavitev) | - alarm if pressure p < 3.5 barg (sensor setting or software setting)
| - ustreza proizvod ENDRESS+HAUSER tip PTC31B + PZAV ali enakovredno | - corresponds to ENDRESS+HAUSER product type PTC31B + PZAV or equivalent
| Oznaka: PIA46.019 | Code: PIA46.019 | kpl | 1 |  | 0
2.18 | Temperaturno tipalo, potopno, za merilno območje od -10 do +100°C, potopna dolžina L=250mm, v tulki iz nerjavnega materiala z navojnim priključkom 1/2" (DN15), električni podatki: napajanje 24V, izhod 4-20mA, komplet s pritrdilnim in tesnilnim materialom; | Temperature sensor, immersion, for measuring range -10 to +100°C, immersion length L=250mm, in stainless steel sleeve with threaded connection 1/2" (DN15), electrical data: power supply 24V, output 4-20mA, complete with fixing and sealing material;
| - hladilna voda 9/14°C | - cooling water 9/14°C
| - ustreza proizvod ELEKTRONIKA PAHOR, tip CVB ali enakovredno | - corresponds to the product ELEKTRONIKA PAHOR, type CVB or equivalent
| Oznaka: TIC46.003, TIC46.004, TIC46.005, TIC46.006 | Code: TIC46.003, TIC46.004, TIC46.005, TIC46.006 | kpl | 4 |  | 0
2.19 | Temperaturno tipalo, potopno, za merilno območje od -10 do +100°C, potopna dolžina L=100mm, v tulki iz nerjavnega materiala z navojnim priključkom 1/2" (DN15), električni podatki: napajanje 24V, izhod 4-20mA, komplet s pritrdilnim in tesnilnim materialom; | Temperature sensor, immersion, for measuring range -10 to +100°C, immersion length L=100mm, in stainless steel sleeve with threaded connection 1/2" (DN15), electrical data: power supply 24V, output 4-20mA, complete with fixing and sealing material;
| - hladilna voda 9/14°C | - cooling water 9/14°C
| - ustreza proizvod ELEKTRONIKA PAHOR, tip CVB ali enakovredno | - corresponds to the product ELEKTRONIKA PAHOR, type CVB or equivalent
| Oznaka: TIC46.001, TIC46.002, TIC46.003, TIC46.004, TI47.001, TI47.002, TI47.003, TI47.004, TI47.005, TI47.006, TIC12.413, TIC12.423, TIC13.413, TIC13.423 | Code: TIC46.001, TIC46.002, TIC46.003, TIC46.004, TI47.001, TI47.002, TI47.003, TI47.004, TI47.005, TI47.006, TIC12.413, TIC12.423, TIC13.413, TIC13.423 | kpl | 14 |  | 0
2.20 | Krogelni ventil s priklučkom za praznenje oz. polnenje, navojna izvedba, PN16, z ročico, material nerjavno jeklo / PTFE, vključno s pritrdilnim in tesnilnim materialom: | Ball valve with union for emptying or filling, threaded version, PN16, with handle, material stainless steel/PTFE, incl. fitting and sealing material:
| - hladilna voda 9/14°C | - cooling water 9/14°C
| - ustreza proizvod END ARMATUREN ali enakovredno | - eND ARMATUREN or equivalent
| DN 15 | DN 15 | kos | 148 |  | 0
| DN 20 | DN 20 | kos | 8 |  | 0
| DN 25 | DN 25 | kos | 8 |  | 0
2.21 | Krogelni ventil, navojna izvedba, PN16, z ročico, material nerjavno jeklo / PTFE, vključno s pritrdilnim in tesnilnim materialom: | Ball valve, threaded version, PN16, with handle, material stainless steel/PTFE, incl. fitting and sealing material:
| - hladilna voda 9/14°C | - cooling water 9/14°C
| - ustreza proizvod END ARMATUREN ali enakovredno | - eND ARMATUREN or equivalent
| DN 15 | DN 15 | kos | 120 |  | 0
| DN 20 | DN 20 | kos | 18 |  | 0
| DN 25 | DN 25 | kos | 18 |  | 0
| DN 32 | DN 32 | kos | 20 |  | 0
| DN 40 | DN 40 | kos | 24 |  | 0
| DN 50 | DN 50 | kos | 12 |  | 0
2.22 | Zaporna loputa, prirobnična izvedba, mehko tesnenje, PN16, z ročnim pogonom z ročico do vključno DN100 oziroma z ročnim polžnim pogonom nad vključno DN125, material nodularna litina / EPDM, za vgradnjo med prirobnice, komplet s protiprirobnicama, vijačnim in tesnilnim materialom; | Butterfly valve, flanged version, soft sealing, PN16, with manual lever actuator up to and including DN100 or with manual screw actuator up to and including DN125, material ductile iron / EPDM, for installation between flanges, complete with two anti-seize plates, screw and sealing material;
| - hladilna voda 9/14°C | - cooling water 9/14°C
| - ustreza proizvod IMP ARMATURE ali enakovredno | - iMP ARMATURE or equivalent
| DN 65 | DN 65 | kpl | 14 |  | 0
| DN 80 | DN 80 | kpl | 8 |  | 0
| DN 100 | DN 100 | kpl | 6 |  | 0
| DN 125 | DN 125 | kpl | 22 |  | 0
| DN 150 | DN 150 | kpl | 10 |  | 0
| DN 200 | DN 200 | kpl | 16 |  | 0
2.23 | Nepovratni ventil, z vmetjo, navojna izvedba, PN16 material nerjavno jeklo, EPDM, vključno z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Non-return valve, with spout, threaded version, PN16 material stainless steel, EPDM, incl. threaded Dutch, fastening and sealing material;
| - hladilna voda 9/14°C | - cooling water 9/14°C
| - ustreza proizvod END ARMATUREN ali enakovredno | - eND ARMATUREN or equivalent
| DN 25 | DN 25 | kpl | 3 |  | 0
| DN 32 | DN 32 | kpl | 2 |  | 0
| DN 40 | DN 40 | kpl | 1 |  | 0
2.24 | Nepovratna loputa, z vmetjo, prirobnična izvedba, PN16 material nodularna litina, EPDM, vzmet nerjavno jeklo, za vgradnjo med prirobnice, komplet s protiprirobnicama, vijačnim in tesnilnim materialom; | Non-return butterfly valve, with spigot, flanged version, PN16 material ductile iron, EPDM, stainless steel spring, for mounting between flanges, complete with counter flanges, screwing and sealing material;
| - hladilna voda 9/14°C | - cooling water 9/14°C
| - ustreza proizvod END ARMATUREN ali enakovredno | - eND ARMATUREN or equivalent
| DN 125 | DN 125 | kpl | 4 |  | 0
| DN 150 | DN 150 | kpl | 2 |  | 0
| DN 200 | DN 200 | kpl | 1 |  | 0
2.25 | Lovilnik nesnage, navojna izvedba, z normalnim sitom, PN16, material siva litina, sito nerjavno jeklo, komplet s krogelnim ventilom DN15 za praznenje in izpiranje, vključno z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Debris trap, threaded version, with normal sieve, PN16, material grey cast iron, sieve stainless steel, complete with ball valve DN15 for emptying and flushing, incl. two threaded Hollanders, fixing and sealing material;
| - hladilna voda 9/14°C | - cooling water 9/14°C
| - ustreza proizvod IMP ARMATURE ali enakovredno | - iMP ARMATURE or equivalent
| DN 15 | DN 15 | kos | 4 |  | 0
| DN 20 | DN 20 | kos | 6 |  | 0
| DN 25 | DN 25 | kos | 2 |  | 0
| DN 32 | DN 32 | kos | 6 |  | 0
| DN 40 | DN 40 | kos | 8 |  | 0
| DN 50 | DN 50 | kos | 4 |  | 0
2.26 | Lovilnik nesnage, prirobnična izvedba, z normalnim sitom, PN16, material siva litina, sito nerjavno jeklo, komplet s krogelnim ventilom DN15 za praznenje in izpiranje, vključno s protiprirobnicama, vijačnim in tesnilnim materialom; | Debris trap, flanged version, with normal sieve, PN16, material grey cast iron, sieve stainless steel, complete with ball valve DN15 for emptying and flushing, incl. counter flanges, screwing and sealing material;
| - hladilna voda 9/14°C | - cooling water 9/14°C
| - ustreza proizvod IMP ARMATURE ali enakovredno | - iMP ARMATURE or equivalent
| DN 65 | DN 65 | kpl | 6 |  | 0
| DN 80 | DN 80 | kpl | 4 |  | 0
| DN 100 | DN 100 | kpl | 6 |  | 0
| DN 125 | DN 125 | kpl | 6 |  | 0
| DN 150 | DN 150 | kpl | 2 |  | 0
| DN 200 | DN 200 | kpl | 1 |  | 0
2.27 | Izločevalnika nečistoč, magnetita in mikro mehurčkov, ciklonsko izločanje, PN16, skladno s PED, material jeklo, prirobnični priključki, z dvema krogelnim ventilom DN15 za izpust nečistoč in odzračevanje ter avtomatskim odzračevalnim ventilom, vključno s protiprirobnicama, vijačnim in tesnilnim materialom; | Impurity, magnetite and micro-bubble eliminators, cyclonic elimination, PN16, PED compliant, material steel, flanged connections, with two DN15 ball valves for impurity discharge and venting and automatic vent valve, incl. counter flanges, screw and gasket material;
| - hladilna voda 9/14°C | - cooling water 9/14°C
| - ustreza proizvod IMI PMEUMATEX tip Zeparo G-Force ZG ... + ZUTX 25 ali enakovredno | - iMI PMEUMATEX product type Zeparo G-Force ZG ... + ZUTX 25 or equivalent
| DN 200 | DN 200 | kpl | 2 |  | 0
2.28 | Ventil za hidravlično uravnoteženje, nastavitev pretoka, navojna izvedba, PN16, s priključkoma za priklop naprave za merjenje pretoka, z zaporno funkcijo brez prenastavitve pretoka, material siva litina, nerjavno jeklo, EPDM, PTFE, vključno z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Hydraulic balancing valve, flow adjustment, threaded version, PN16, with two connections for connection of flow measuring device, with shut-off function without flow reset, material grey cast iron, stainless steel, EPDM, PTFE, incl. threaded plugs, fastening and sealing material;
| - hladilna voda 9/14°C | - cooling water 9/14°C
| - ustreza proizvod IMI TA tip STAD ali enakovredno | - the product conforms to IMI TA type STAD or equivalent
| DN 15 | DN 15 | kos | 24 |  | 0
| DN 20 | DN 20 | kos | 8 |  | 0
| DN 25 | DN 25 | kos | 4 |  | 0
| DN 32 | DN 32 | kos | 8 |  | 0
| DN 40 | DN 40 | kos | 8 |  | 0
| DN 50 | DN 50 | kos | 4 |  | 0
2.29 | Ventil za hidravlično uravnoteženje, nastavitev pretoka, prirobnična izvedba, PN16, s priključkoma za priklop naprave za merjenje pretoka, z zaporno funkcijo brez prenastavitve pretoka, material siva litina, nerjavno jeklo, EPDM, PTFE, vključno s protiprirobnicama, vijačnim in tesnilnim materialom; | Hydraulic balancing valve, flow adjustable, flanged version, PN16, with two connections for connection to a flow measuring device, with shut-off function without flow reset, material grey cast iron, stainless steel, EPDM, PTFE, incl. anti-seize, screwing and sealing material;
| - hladilna voda 9/14°C | - cooling water 9/14°C
| - ustreza proizvod IMI TA tip STAF ali enakovredno | - corresponds to IMI TA type STAF or equivalent
| DN 65 | DN 65 | kpl | 6 |  | 0
| DN 80 | DN 80 | kpl | 2 |  | 0
| DN 100 | DN 100 | kpl | 1 |  | 0
| DN 125 | DN 125 | kpl | 2 |  | 0
2.30 | Kompenzator vibracij in prenosa hrupa iz strojne opreme na cevovod ali iz hrupnega prostora po cevovodu v sosednji prostor, navojna izvedba, PN16, material nerjavno jeklo, EPDM, vključno z nerjavnima navojnima holandcema, pritrdilnim in tesnilnim materialom; | Vibration and noise compensator for noise transmission from machinery to pipeline or from noise room through pipeline to adjacent room, threaded version, PN16, material stainless steel, EPDM, incl. stainless steel threaded dutch, fastening and sealing material;
| - hladilna voda 9/14°C | - cooling water 9/14°C
| - ustreza proizvod END ARMATUREN tip KP ali enakovredno | - corresponds to END ARMATUREN type KP or equivalent
| DN 15 | DN 15 | kos | 8 |  | 0
| DN 20 | DN 20 | kpl | 12 |  | 0
| DN 25 | DN 25 | kpl | 16 |  | 0
| DN 32 | DN 32 | kpl | 8 |  | 0
| DN 40 | DN 40 | kpl | 14 |  | 0
2.31 | Kompenzator vibracij in prenosa hrupa iz strojne opreme na cevovod ali iz hrupnega prostora po cevovodu v sosednji prostor, prirobnična izvedba, PN16, material nerjavno jeklo, EPDM, vključno z nerjavnima protiprirobnicama, vijačnim in tesnilnim materialom; | Vibration and noise compensator for noise transmission from machinery to pipeline or from noise room through pipeline to adjacent room, flanged version, PN16, material stainless steel, EPDM, incl. stainless steel counter flanges, screwing and sealing material;
| - hladilna voda 9/14°C | - cooling water 9/14°C
| - ustreza proizvod END ARMATUREN tip KP ali enakovredno | - corresponds to END ARMATUREN type KP or equivalent
| DN 50 | DN 50 | kpl | 8 |  | 0
| DN 65 | DN 65 | kpl | 8 |  | 0
| DN 80 | DN 80 | kpl | 2 |  | 0
| DN 100 | DN 100 | kpl | 20 |  | 0
| DN 125 | DN 125 | kpl | 2 |  | 0
2.32 | Termometer, tekočinski, dolžina skale 100mm, kotni 90°, potopna dolžina 40mm, v zaščitni cevi - tulki, klasa točnosti 1%, navojni priključek 1/2" (DN15), material medenina, aluminij, steklo, nerjavno jeklo, vključno s pritrdilnim in tesnilnim materialom; | Thermometer, liquid, scale length 100mm, angle 90°, immersion length 40mm, in protective tube - sleeves, accuracy class 1%, threaded connection 1/2" (DN15), material brass, aluminium, glass, stainless steel, incl. fixing and sealing material;
| - hladilna voda 9/14°C | - cooling water 9/14°C
| - ustreza proizvod INOL ali enakovredno | - corresponds to INOL or equivalent
| - območjem merjenja: 0 do 100°C | - measuring range: 0 to 100°C | kpl | 92 |  | 0
2.33 | Manometer ø 68 mm, klasa točnosti 1,6% po EN837-1, navojni radialni priključek, material medenina, nerjavno jeklo, steklo / EPDM, komplet z manometrskim ventilom DN15 (1/2"), vključno s pritrdilnim in tesnilnim materialom; | Pressure gauge ø 68 mm, accuracy class 1.6% according to EN837-1, threaded radial connection, material brass, stainless steel, glass / EPDM, complete with pressure gauge valve DN15 (1/2"), incl. mounting and sealing material;
| - hladilna voda 9/14°C | - cooling water 9/14°C
| - ustreza proizvod INOL ali enakovredno | - corresponds to INOL or equivalent
| - območjem merjenja: 0 do 6 bar | - measuring range: 0 to 6 bar | kpl | 92 |  | 0
2.34 | Avtomatski odzračevalnik, z zapornim in ročno odzračevalnim ventilom PN10 material medenina / PTFE, vključno z navojnim holandcem in tesnilnim materialom; | Automatic venting valve, with shut-off and manual venting valve PN10 material brass/PTFE, including threaded Dutchman and sealing material;
| - hladilna voda 9/14°C | - cooling water 9/14°C
| DN25 - ustreza proizvod IMI PNEUMATEX tip ZUTX 25 ali enakovredno | DN25 - corresponds to IMI PNEUMATEX product type ZUTX 25 or equivalent | kpl | 78 |  | 0
2.35 | Odzračitveni lonček, volumen V ≥ 2 litra, izdelan iz cevi DN100, ø114x2,3 mm po EN ISO1127, dolžina L=300mm, z bombiranima zaključkoma, material AISI304, vključno z varilnim materialom; | Refrigerated crucible, volume V ≥ 2 litres, made of DN100 pipe, ø114x2,3 mm according to EN ISO1127, length L=300mm, with bomb-coated ends, material AISI304, incl. welding consumables;
| - hladilna voda 9/14°C | - cooling water 9/14°C | kpl | 88 |  | 0
2.36 | Jeklene srednje težke šivne cevi izdelane po EN10255 (DIN2440), material S195T (St33.2), vključno z oblikovnimi kosi (loki, redukcije, T kosi, ...) in varilnim materialom, | Medium-weight seamed steel tubes manufactured to EN10255 (DIN2440), material S195T (St33.2), including forming pieces (bows, reducers, T-pieces, etc.) and welding consumables,
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and pipe clamps with noise damping lining, suitable for HILTI or SIKLA, or equivalent;
| DN 15, ø 21,3 x 2,65 | DN 15, ø 21,3 x 2,65 | m | 240 |  | 0
| DN 20, ø 26,9 x 2,65 | DN 20, ø 26,9 x 2,65 | m | 210 |  | 0
| DN 25, ø 33,7 x 3,25 | DN 25, ø 33,7 x 3,25 | m | 270 |  | 0
| DN 32, ø 42,4 x 3,25 | DN 32, ø 42,4 x 3,25 | m | 360 |  | 0
| DN 40, ø 48,3 x 3,25 | DN 40, ø 48,3 x 3,25 | m | 270 |  | 0
| DN 50, ø 60,3 x 3,65 | DN 50, ø 60,3 x 3,65 | m | 240 |  | 0
| 90°lok DN 15, ø 21,3 x 2,65 | 90°lok DN 15, ø 21,3 x 2,65 | kos | 40 |  | 0
| 90°lok DN 20, ø 26,9 x 2,65 | 90°lok DN 20, ø 26,9 x 2,65 | kos | 40 |  | 0
| 90°lok DN 25, ø 33,7 x 3,25 | 90°lok DN 25, ø 33,7 x 3,25 | kos | 50 |  | 0
| 90°lok DN 32, ø 42,4 x 3,25 | 90°lok DN 32, ø 42,4 x 3,25 | kos | 60 |  | 0
| 90°lok DN 40, ø 48,3 x 3,25 | 90°lok DN 40, ø 48,3 x 3,25 | kos | 50 |  | 0
| 90°lok DN 50, ø 60,3 x 3,65 | 90°lok DN 50, ø 60,3 x 3,65 | kos | 40 |  | 0
| T kos DN 25 / odcep DN 15 | T piece DN 25 / branch DN 15 | kos | 40 |  | 0
| T kos DN 25 / odcep DN 20 | T piece DN 25 / branch DN 20 | kos | 40 |  | 0
| T kos DN 32 / odcep DN 20 | T piece DN 32 / branch DN 20 | kos | 50 |  | 0
| T kos DN 32 / odcep DN 25 | T piece DN 32 / branch DN 25 | kos | 60 |  | 0
| T kos DN 40 / odcep DN 15 | T piece DN 40 / branch DN 15 | kos | 50 |  | 0
| T kos DN 40 / odcep DN 20 | T piece DN 40 / branch DN 20 | kos | 40 |  | 0
| T kos DN 50 / odcep DN 15 | T piece DN 50 / branch DN 15 | kos | 30 |  | 0
| T kos DN 40 / odcep DN 40 | T piece DN 40 / branch DN 40 | kos | 30 |  | 0
| T kos DN 50 / odcep DN 50 | T piece DN 50 / branch DN 50 | kos | 20 |  | 0
| redukcija DN 20 / DN 15 | reduction DN 20 / DN 15 | kos | 40 |  | 0
| redukcija DN 25 / DN 20 | dN 25 / DN 20 reduction | kos | 40 |  | 0
| redukcija DN 32 / DN 25 | dN 32 / DN 25 reduction | kos | 50 |  | 0
| redukcija DN 40 / DN 32 | dN 40 / DN 32 reduction | kos | 60 |  | 0
| redukcija DN 50 / DN 32 | dN 50 / DN 32 reduction | kos | 50 |  | 0
| redukcija DN 50 / DN 40 | dN 50 / DN 40 reduction | kos | 40 |  | 0
| prirobnica DN 50 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 50 to EN1092, PN16, including bolting and sealing material | kpl | 10 |  | 0
2.37 | Jeklene brezšivne cevi izdelane po EN10216-1 (DIN2448), iz materiala P235TR2 (St37), vključno z oblikovnimi kosi (loki, redukcije, T kosi, ...) in varilnim materialom, | Seamless steel tubes manufactured to EN10216-1 (DIN2448), in P235TR2 (St37), including forming pieces (bends, reducers, T-pieces, etc.) and welding consumables,
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and hose clamps with noise damping lining, suitable for HILTI or SIKLA, or equivalent;
| DN 65, ø 76,1 x 2,9 | DN 65, ø 76,1 x 2,9 | m | 180 |  | 0
| DN 80, ø 88,9 x 3,2 | DN 80, ø 88,9 x 3,2 | m | 390 |  | 0
| DN 100, ø 114,3 x 3,6 | DN 100, ø 114,3 x 3,6 | m | 120 |  | 0
| DN 125, ø 139,7 x 4,0 | DN 125, ø 139,7 x 4,0 | m | 390 |  | 0
| DN 150, ø 168,3 x 4,5 | DN 150, ø 168,3 x 4,5 | m | 480 |  | 0
| DN 200, ø 219,1 x 5,9 | DN 200, ø 219.1 x 5.9 | m | 390 |  | 0
| 90°lok DN 65, ø 76,1 x 2,9 | 90°block DN 65, ø 76,1 x 2,9 | kos | 30 |  | 0
| 90°lok DN 80, ø 88,9 x 3,2 | 90°lok DN 80, ø 88,9 x 3,2 | kos | 60 |  | 0
| 90°lok DN 100, ø 114,3 x 3,6 | 90°lok DN 100, ø 114,3 x 3,6 | kos | 20 |  | 0
| 90°lok DN 125, ø 139,7 x 4,0 | 90°lok DN 125, ø 139.7 x 4.0 | kos | 60 |  | 0
| 90°lok DN 150, ø 168,3 x 4,5 | 90°lok DN 150, ø 168,3 x 4,5 | kos | 80 |  | 0
| 90°lok DN 200, ø 219,1 x 5,9 | 90°lok DN 200, ø 219.1 x 5.9 | kos | 60 |  | 0
| T kos DN 65 / odcep DN 50 | T piece DN 65 / branch DN 50 | kos | 20 |  | 0
| T kos DN 65 / odcep DN 65 | T piece DN 65 / branch DN 65 | kos | 20 |  | 0
| T kos DN 80 / odcep DN 65 | T piece DN 80 / branch DN 65 | kos | 20 |  | 0
| T kos DN 80 / odcep DN 80 | T piece DN 80 / branch DN 80 | kos | 20 |  | 0
| T kos DN 100 / odcep DN 80 | T piece DN 100 / branch DN 80 | kos | 20 |  | 0
| T kos DN 125 / odcep DN 100 | T piece DN 125 / branch DN 100 | kos | 20 |  | 0
| T kos DN 150 / odcep DN 125 | T piece DN 150 / branch DN 125 | kos | 20 |  | 0
| T kos DN 200 / odcep DN 150 | T piece DN 200 / branch DN 150 | kos | 20 |  | 0
| T kos DN 200 / odcep DN 200 | T piece DN 200 / branch DN 200 | kos | 20 |  | 0
| redukcija DN 65 / DN 50 | dN 65 / DN 50 reduction | kos | 20 |  | 0
| redukcija DN 80 / DN 65 | dN 80 / DN 65 reduction | kos | 20 |  | 0
| redukcija DN 100 / DN 80 | dN 100 / DN 80 reduction | kos | 20 |  | 0
| redukcija DN 125 / DN 100 | dN 125 / DN 100 reduction | kos | 20 |  | 0
| redukcija DN 150 / DN 125 | reduction DN 150 / DN 125 | kos | 20 |  | 0
| redukcija DN 200 / DN 150 | reduction DN 200 / DN 150 | kos | 20 |  | 0
| prirobnica DN 65 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 65 to EN1092, PN16, including bolting and sealing material | kpl | 20 |  | 0
| prirobnica DN 80 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 80 to EN1092, PN16, including bolting and sealing material | kpl | 20 |  | 0
| prirobnica DN 100 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 100 to EN1092, PN16, including bolting and sealing material | kpl | 20 |  | 0
| prirobnica DN 125 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 125 to EN1092, PN16, including bolting and sealing material | kpl | 20 |  | 0
| prirobnica DN 150 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 150 to EN1092, PN16, including bolting and sealing material | kpl | 20 |  | 0
| prirobnica DN 200 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 200 to EN1092, PN16, including bolting and sealing material | kpl | 20 |  | 0
2.38 | Čiščenje in barvanje jeklenih cevovodov iz ogljikovega jekla, odstranitev rje do kovinskega sijaja, dvakratni premaz s temeljnim antikorozijskim barvami ter dvakratni premaz s prekrivno barvo: antikorozijska zaščita s temeljnimi in prekrivnimi barvami mora biti obstojna na temperature v območju od -20 do +80°C in se mora izvesti v skladu z EN ISO 12944 z življenjsko dobo: visoko trajanje H (več kot 15 let). | Cleaning and painting of carbon steel pipelines, rust removal to metallic gloss, two coats of anticorrosion primer and two coats of overcoat: the anticorrosion protection with primer and overcoat must be resistant to temperatures in the range -20 to +80°C and must be carried out in accordance with EN ISO 12944 with a service life: high durability H (more than 15 years).
| - hladilna voda 9/14°C | - cooling water 9/14°C | m2 | 2400 |  | 0
2.39 | Jeklene nerjavne cevi za precizno uporabo, zatisni press sistem, PN10 ali več, izdelava in skladnost po EN10088, EN10312, material nerjavno jeklo 1.4520 ali 1.4404 ali boljši, vključno s spojnimi in oblikovnimi zatisnimi press kosi (90°loki, T kosi, redukcije, ...), spojnim in tesnilnim materialom, zatiskanje z originalnim press orodjem proizvajalca, komplet s prehodnimi navojnimi in prirobnični oblikovnimi kosi, ustreza proizvod VIEGA ali KANTHERM ali enakovredno; | Stainless steel tubes for precision applications, press fitting system, PN10 or higher, manufacture and conformity to EN10088, EN10312, material stainless steel 1.4520 or 1.4404 or better, including coupling and press fitting shapes (90°bends, T-pieces, reducers, etc.), coupling and sealing material, press fitting with original manufacturer's press tool, complete with threaded and flanged transition shapes, corresponding to VIEGA or KANTHERM product or equivalent;
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and hose clamps with noise damping lining, suitable for HILTI or SIKLA, or equivalent;
| DN 15, ø 18 x 1,2 | DN 15, ø 18 x 1,2 | m | 1200 |  | 0
| DN 20, ø 22 x 1,5 | DN 20, ø 22 x 1,5 | m | 3320 |  | 0
| DN 25, ø 28 x 1,5 | DN 25, ø 28 x 1,5 | m | 3780 |  | 0
| DN 32, ø 35 x 1,5 | DN 32, ø 35 x 1,5 | m | 1680 |  | 0
| DN 40, ø 42 x 1,5 | DN 40, ø 42 x 1,5 | m | 1320 |  | 0
| DN 50, ø 54 x 1,5 | DN 50, ø 54 x 1,5 | m | 1920 |  | 0
| DN 65, ø 76,1 x 2 | DN 65, ø 76,1 x 2 | m | 1450 |  | 0
| DN 80, ø 88,9 x 2 | DN 80, ø 88,9 x 2 | m | 300 |  | 0
| DN 100, ø 108 x 2 | DN 100, ø 108 x 2 | m | 360 |  | 0
| 90°lok DN 15, ø 18 x 1,2 | 90°lok DN 15, ø 18 x 1,2 | kos | 420 |  | 0
| 90°lok DN 20, ø 22 x 1,5 | 90°lok DN 20, ø 22 x 1,5 | kos | 790 |  | 0
| 90°lok DN 25, ø 28 x 1,5 | 90°lok DN 25, ø 28 x 1,5 | kos | 630 |  | 0
| 90°lok DN 32, ø 35 x 1,5 | 90°lok DN 32, ø 35 x 1,5 | kos | 250 |  | 0
| 90°lok DN 40, ø 42 x 1,5 | 90°lok DN 40, ø 42 x 1,5 | kos | 200 |  | 0
| 90°lok DN 50, ø 54 x 1,5 | 90°lok DN 50, ø 54 x 1,5 | kos | 300 |  | 0
| 90°lok DN 65, ø 76,1 x 2 | 90°lok DN 65, ø 76,1 x 2 | kos | 220 |  | 0
| 90°lok DN 80, ø 88,9 x 2 | 90°lok DN 80, ø 88,9 x 2 | kos | 60 |  | 0
| 90°lok DN 100, ø 108 x 2 | 90°lok DN 100, ø 108 x 2 | kos | 60 |  | 0
| T kos DN 25 / odcep DN 15 | T piece DN 25 / branch DN 15 | kos | 420 |  | 0
| T kos DN 25 / odcep DN 20 | T piece DN 25 / branch DN 20 | kos | 790 |  | 0
| T kos DN 32 / odcep DN 25 | T piece DN 32 / branch DN 25 | kos | 105 |  | 0
| T kos DN 40 / odcep DN 15 | T piece DN 40 / branch DN 15 | kos | 250 |  | 0
| T kos DN 40 / odcep DN 32 | T piece DN 40 / branch DN 32 | kos | 200 |  | 0
| T kos DN 50 / odcep DN 15 | T piece DN 50 / branch DN 15 | kos | 300 |  | 0
| T kos DN 50 / odcep DN 25 | T piece DN 50 / branch DN 25 | kos | 220 |  | 0
| T kos DN 50 / odcep DN 40 | T piece DN 50 / branch DN 40 | kos | 50 |  | 0
| T kos DN 65 / odcep DN 50 | T piece DN 65 / branch DN 50 | kos | 60 |  | 0
| T kos DN 100 / odcep DN 80 | T piece DN 100 / branch DN 80 | kos | 20 |  | 0
| redukcija DN 20 / DN 15 | reduction DN 20 / DN 15 | kos | 200 |  | 0
| redukcija DN 25 / DN 20 | dN 25 / DN 20 reduction | kos | 420 |  | 0
| redukcija DN 32 / DN 15 | dN 32 / DN 15 reduction | kos | 790 |  | 0
| redukcija DN 32 / DN 25 | dN 32 / DN 25 reduction | kos | 320 |  | 0
| redukcija DN 40 / DN 32 | dN 40 / DN 32 reduction | kos | 250 |  | 0
| redukcija DN 50 / DN 32 | dN 50 / DN 32 reduction | kos | 200 |  | 0
| redukcija DN 50 / DN 20 | dN 50 / DN 20 reduction | kos | 300 |  | 0
| redukcija DN 50 / DN 40 | dN 50 / DN 40 reduction | kos | 220 |  | 0
| redukcija DN 65 / DN 20 | dN 65 / DN 20 reduction | kos | 50 |  | 0
| redukcija DN 65 / DN 40 | dN 65 / DN 40 reduction | kos | 60 |  | 0
| redukcija DN 100 / DN 65 | dN 100 / DN 65 reduction | kos | 20 |  | 0
| redukcija DN 100 / DN 80 | dN 100 / DN 80 reduction | kos | 20 |  | 0
| prirobnica DN 32 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 32 to EN1092, PN16, including bolting and sealing material | kpl | 20 |  | 0
| prirobnica DN 40 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 40 to EN1092, PN16, including bolting and sealing material | kpl | 20 |  | 0
| prirobnica DN 50 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 50 to EN1092, PN16, including bolting and sealing material | kpl | 20 |  | 0
| prirobnica DN 65 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 65 to EN1092, PN16, including bolting and sealing material | kpl | 20 |  | 0
| prirobnica DN 80 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 80 to EN1092, PN16, including bolting and sealing material | kpl | 20 |  | 0
| prirobnica DN 100 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 100 to EN1092, PN16, including bolting and sealing material | kpl | 20 |  | 0
2.40 | Bakrene cevi, zatisni press sistem, izdelane po EN1057, material baker, vključno s spojnimi in oblikovnimi zatisnimi press kosi (90°loki, T kosi, redukcije, ...), spojnim in tesnilnim materialom, zatiskanje z originalnim press orodjem proizvajalca, komplet s prehodnimi navojnimi oblikovnimi kosi, ustreza proizvod VIEGA ali enakovredno, | Copper tubes, press fitting system, manufactured to EN1057, material copper, including joining and forming press fittings (90°bends, T-fittings, reducers, etc.), joining and sealing material, press fitting with original manufacturer's press tool, complete with threaded transition fittings, corresponding to VIEGA product or equivalent,
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and pipe clamps with noise damping lining, suitable for HILTI or SIKLA, or equivalent;
| - odtok kondenztata od hladilnih teles in naprav | - condensate drainage from refrigeration units and appliances
| DN 20, ø 22 x 1 | DN 20, ø 22 x 1 | m | 2680 |  | 0
| DN 25, ø 28 x 1 | DN 25, ø 28 x 1 | m | 1600 |  | 0
| DN 32, ø 35 x 1,5 | DN 32, ø 35 x 1,5 | m | 960 |  | 0
| DN 40, ø 42 x 1,5 | DN 40, ø 42 x 1,5 | m | 150 |  | 0
| 45°lok DN 20, ø 22 x 1,5 | 45°lok DN 20, ø 22 x 1,5 | kos | 450 |  | 0
| 45°lok DN 25, ø 28 x 1,5 | 45°block DN 25, ø 28 x 1,5 | kos | 260 |  | 0
| 45°lok DN 32, ø 35 x 1,5 | 45°lok DN 32, ø 35 x 1,5 | kos | 140 |  | 0
| 45°lok DN 40, ø 42 x 1,5 | 45°arc DN 40, ø 42 x 1,5 | kos | 20 |  | 0
| 90°lok DN 20, ø 22 x 1,5 | 90°lok DN 20, ø 22 x 1,5 | kos | 450 |  | 0
| 90°lok DN 25, ø 28 x 1,5 | 90°lok DN 25, ø 28 x 1,5 | kos | 260 |  | 0
| 90°lok DN 32, ø 35 x 1,5 | 90°lok DN 32, ø 35 x 1,5 | kos | 140 |  | 0
| 90°lok DN 40, ø 42 x 1,5 | 90°lok DN 40, ø 42 x 1,5 | kos | 20 |  | 0
| Y kos DN 25 / odcep DN 20 | Y piece DN 25 / branch DN 20 | kos | 240 |  | 0
| Y kos DN 32 / odcep DN 25 | Y piece DN 32 / branch DN 25 | kos | 180 |  | 0
| Y kos DN 40 / odcep DN 32 | Y piece DN 40 / branch DN 32 | kos | 60 |  | 0
| redukcija DN 25 / DN 20 | dN 25 / DN 20 reduction | kos | 120 |  | 0
| redukcija DN 32 / DN 20 | dN 32 / DN 20 reduction | kos | 90 |  | 0
| redukcija DN 32 / DN 25 | dN 32 / DN 25 reduction | kos | 60 |  | 0
| redukcija DN 40 / DN 32 | dN 40 / DN 32 reduction | kos | 60 |  | 0
| DN 32 prehodni kos za priklop na sifon | DN 32 transition piece for connection to siphon | kos | 40 |  | 0
| DN 40 prehodni kos za priklop na sifon | DN 40 transition piece for connection to siphon | kos | 8 |  | 0
2.41 | Sifon za kondenzat odvodni priključek DN40, dovodni priključkom 5/4' (DN32 - stisnjen spoj) oz. d 12 - 18 mm (za gladke cevne nastavke) vertikalno ali vodoravno, z vodno smradno zaporo (60 mm) in mehansko smradno zaporo s kroglico ter čistilnim vložkom, predviden za klimatske naprave, material PP, skladnost z EN12056, vključno s spojnim in tesnilnim materialom; | Condensate trap outlet connection DN40, inlet connection 5/4' (DN32 - compression joint) or d 12 - 18 mm (for plain pipe fittings) vertically or horizontally, with water odour stop (60 mm) and mechanical odour stop with ball and cleaning insert, intended for air-conditioning systems, material PP, compliance with EN12056, incl. jointing and sealing material;
| - ustreza proizvod Hutterer & Lechner tip HL136.N oziroma .3 ali enakovredno | - corresponds to Hutterer & Lechner product type HL136.N or .3 or equivalent | kpl | 48 |  | 0
2.42 | Toplotna izolacija cevovodov in cevnih armatur s parozaporno izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z naslednjimi lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, požarna klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +110°C, lepljeno na cevovode in armature z originalnim lepilom proizvajalca, vključno s trakovi za šive; | Thermal insulation of pipelines and pipe fittings with vapour barrier insulation made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, fire classification B-s3-d0 according to EN13501-1, for temperatures from -50 to +110°C, bonded to pipelines and fittings with the original manufacturer's adhesive, including seam tapes;
| - barva izolacije črna | - insulation colour black
| - ustreza proizvod ARMACELL tip Armaflex ACE Plus ali enakovredno | - corresponds to ARMACELL product type Armaflex ACE Plus or equivalent
| DN 15 ; debelina 13 mm | DN 15 ; thickness 13 mm | m | 2160 |  | 0
| DN 20 ; debelina 19 mm | DN 20 ; thickness 19 mm | m | 9320 |  | 0
| DN 25 ; debelina 19 mm | DN 25 ; thickness 19 mm | m | 8480 |  | 0
| DN 32 ; debelina 25 mm | DN 32 ; thickness 25 mm | m | 4520 |  | 0
| DN 40 ; debelina 25 mm | DN 40 ; thickness 25 mm | m | 2610 |  | 0
| DN 50 ; debelina 40 mm | DN 50 ; thickness 40 mm | m | 3240 |  | 0
| DN 65 ; debelina 40 mm | DN 65 ; thickness 40 mm | m | 2450 |  | 0
| DN 80 ; debelina 40 mm | DN 80 ; thickness 40 mm | m | 1040 |  | 0
| DN 100 ; debelina 40 mm | DN 100 ; thickness 40 mm | m | 960 |  | 0
| DN 125 ; debelina 40 mm | DN 125 ; thickness 40 mm | m | 780 |  | 0
| DN 150 ; debelina 40 mm | DN 150 ; thickness 40 mm | m | 960 |  | 0
| DN 200 ; debelina 40 mm | DN 200 ; thickness 40 mm | m | 780 |  | 0
| v ploščah ; debelina 40 mm | in panels ; thickness 40 mm | m2 | 600 |  | 0
2.43 | Tlačni preskus trdnosti in tesnenja sistema cevovodov, skladeno z opisom v "IZS Priročnik tlačnih preizkusov strojnih inštalacij", vključno s potrebnim materialom za izvedbo preizkusa, ter izdelavo pisnega poročila o uspešno opravljenem tlačnem preizkusu; | Pressure test of the strength and tightness of the piping system, as described in the "IZS Manual for Pressure Testing of Mechanical Installations", including the necessary materials for the test, and the production of a written report on the successful completion of the pressure test;
| preskusni tlak = 1,3 x najvišji delovni tlak = 6,5 barg | test pressure = 1,3 x maximum working pressure = 6,5 barg | kpl | 1 |  | 0
2.44 | Izpiranje cevovodov s sanitarno hladno vodo v celotnem sistemu novoinstaliranih razvodov z namenom odstranjevanja nečistoč v sistemu cevovodov, vključno s čiščenjem lovilnikov nesnage in drugih elementov; | Flushing of sanitary cold water piping throughout the newly installed piping system to remove impurities in the piping system, including cleaning of debris traps and other elements; | kpl | 1 |  | 0
2.45 | Kvalifikacija zvarov ter izdelava dokumentacije o zvarih: | Weld qualification and documentation of welds:
| - zvare lahko izvajajo samo varilci s certifikatom pooblaščenih organizacij, | - welds can only be carried out by welders certified by approved organisations,
| - postopek vizualne kontrole zvarov, kontrolirajo se vsi zvari - 100% zvarov, | - visual weld inspection procedure, all welds are inspected - 100% of welds,
| - postopek kontrole s snemanja zvarov - 10% zvarov, kjer so enakomerno zastopani vsi premeri, | - weld stripping inspection procedure - 10% of welds where all diameters are equally represented,
| - označevanje zvarov, izdelava dokumentacije z dokazili o ustreznosti ter slikovnim materialom; | - marking welds, producing documentation with proof of conformity and pictorial material; | kpl | 1 |  | 0
2.46 | Ognjeodporna tesnilna masa, vgradnja na prehodu cevovodov skozi zid med požarnima sektortjema, požarna odpornost 90 minut, ustreza proizvod HILTI ali enakovredno. | Fire-resistant sealant, for installation at the transition of pipelines through the wall between the two fire sectors, fire resistance 90 minutes, equivalent to HILTI or equivalent.
| Vsak prehod mora biti označen z nalepko ali tablico z osnovnimi požarnimi podatki; | Each passageway must be marked with a sticker or placard with basic fire information; | kpl | 1 |  | 0
2.47 | Preizkusno obratovanje delovanja sistema v obsegu: | Operational test of the system in scope:
| - pregled instalacije, armatur in opreme, | - inspection of plumbing, fixtures and fittings,
| - pregled delovanja naprav, elementov regulacije in nastavitve parametrov, | - overview of the operation of the devices, control elements and parameter settings,
| - pregled cirkulacije hladilnega medija, | - checking the circulation of the cooling medium,
| - ogrevanje vode na predpisane parametre; | - heating water to the prescribed parameters;
| Preizkusno obratovanje traja neprekinjeno 72 ur. | The test operation shall be continuous for 72 hours. | kpl | 1 |  | 0
2.48 | Napisne ploščice iz nerjavne pločevine z vgravirano oznako po shemi za opremo in armature, kompletno z jekleno pritrdilno žico ali visoko kvalitetne nalepke; visoko trajanje H (več kot 15 let) | Stainless steel nameplates with engraved marking according to the scheme for fittings and fixtures, complete with steel fixing wire or high quality stickers; high durability H (more than 15 years) | kpl | 1 |  | 0
2.49 | Samolepilne puščice za označitev smeri pretoka ter z napisom vrste medija: visoko trajanje H (več kot 15 let) | Self-adhesive arrows to indicate the direction of flow and the type of media: high durability H (more than 15 years) | kpl | 1 |  | 0
2.50 | Izdelava montažnih risb za izvedbo inštalacij med gradnjo objekta, kot so: detajli priključkov, montažne skice, montažni detajli, ipd. | Preparation of assembly drawings for the installation of services during the construction of the building, such as: connection details, assembly sketches, assembly details, etc. | kpl | 1 |  | 0
2.51 | Kvalifikacije montaže IQ-pregledi (instalation qualification) po GEP Commissioning protokolu in dokumentiranje kvalifikacije montaže, vključno z odpravo prvotnih napak montaže; | Installation qualification IQ checks (installation qualification) according to the GEP Commissioning Protocol and documentation of installation qualification, including correction of original installation faults; | kpl | 1 |  | 0
2.52 | Meritve delovanja OQ-kvalifikacija (operation qualification) ter dokumentiranje meritev delovanja, vključno z nastavitvijo parametrov; | OQ (operation qualification) measurements and documentation of performance measurements, including parameter setting; | kpl | 1 |  | 0
2.53 | Posnetki izvedenega stanja, sprotno beleženje vseh sprememb nastalih med izvedbo, vrisovanje in vpisovanje v PZI projektno dokumentacijo; | Recording of the as-built condition, keeping a running record of any changes made during execution, plotting and entering into the PZI project documentation; | kpl | 1 |  | 0
2.54 | Stenska shema sistema, vloženo v zaščitni okvir s prosojnim umetnim steklom (plastika) ali plastificirano, vključno s pritrditvijo na notranjo steno v strojnici objekta; | A wall diagram of the system, enclosed in a protective frame with transparent plastic or plasticised glass, including fixing to an internal wall in the mechanical room of the building; | kpl | 1 |  | 0
2.55 | Primopredajna dokumentacija, ki mora vsebovati: izjave, dokazilo o zanesljivosti objekta, certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo, obratovanje in vzdrževanje ter ostalo primopredajno dokumantacijo. Predaja se v dveh mapiranih izvodih ter en izvod v elektronski obliki; | The handover documentation, which shall include: declarations, proof of the reliability of the facility, certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use, operation and maintenance, and other handover documentation. It shall be handed over in two mapped copies and one copy in electronic form; | kpl | 1 |  | 0
| HLAJENJE | REFRIGERATION |  |  |  | 0

## 4.7.3_GM-SSE
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.7 | STROJNA DELA | MECHANICAL WORKS
4.7.3 | GLIKOLNI MEDIJ SSE | GLYCOL MEDIUM SSE |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
3 | GLIKOLNI MEDIJ SSE | GLYCOL MEDIUM SSE
| Vse postavke v nadalevanju zajemajo dobavo in montažo (razen tam kjer je to posebej navedeno). | All items below include delivery and installation (except where specifically indicated).
3.1 | Vakuumski sprelemnik sončne energije SSE za podporo ogrevalnemu sistemu, komplet z vso pripadajočo opremo za vgradnjo na streho: | SSE vacuum solar energy spreader to support the heating system, complete with all accessories for installation on the roof:
| - površina 1x SSE 3m2, skupna površina 15x SSE 45 m2 moč proizvedene pare 100 W/m2, izkoristek do 80%, toplotna moč SSE do 520 W/m2, skupaj toplona moč 23,4 kW | - area 1x SSE 3m2, total area 15x SSE 45 m2 steam output 100 W/m2, efficiency up to 80%, heat output of SSE up to 520 W/m2, total heat output 23,4 kW
| - postavitev 15x SSE: 5 vrst, 3x SSE v vsako vrsto, hidravlične vezava Tiechelman za izenačitev tlačnih uporov skozi sistem SSE, komplet s tesnilnim in pritrdilnim materialom primernim za glikolni medij in temperature do 150°C | - 15x SSE installation: 5 rows, 3x SSE in each row, Tiechelman hydraulic coupling to equalise the pressure resistance through the SSE system, complete with sealing and fixing material suitable for glycol medium and temperatures up to 150°C
| - nagibni kot vgradnje sprejemnikov SSE: 25° | - sSE receiver installation angle: 25°
| - komplet z jekleno pocinkano podkonstrukcijo za vgradnjo na ravno streho, utežmi ali integrirana pritrditev v strešno konstrukcijao, vključno s pritrdilnim materalom SSE na podkonstrukcijo; | - complete with galvanised steel substructure for installation on flat roof, weights or integrated fixing in the roof structure, including SSE fixing material to the substructure;
| - ustreza proizvod VIESSMANN tip Vitosol 300-T, SP3B - kpl 15 z pripadjočo dodatno opremo | - corresponds to VIESSMANN product type Vitosol 300-T, SP3B - kpl 15 with accessories
| Oznaka: SSE42.20 | Code: SSE42.20 | kpl | 1 |  | 0
3.2 | Ploščni izmenjevalnik toplote, sestavljena vijačena izvedba, PN16, material AISI316 (ali boljši), debeline plošč 0,6mm, tesnila EPDM do 150°C trajne obremenitve, skladnost s PED. Tehnični podatki: | Plate heat exchanger, bolted composite design, PN16, material AISI316 (or better), plate thickness 0,6mm, EPDM seals up to 150°C permanent load, PED compliant. Technical data:
| - prenos toplote iz sistema sprejemnikov sončne energije SSE na ogrevno vodo | - heat transfer from the SSE solar energy receiver system to the heating water
| - glikolni medij SSE (35% propilen glikol) | - sSE glycol medium (35% propylene glycol)
| - izmenjana toplota 23,4 kW - ogrevanje | - heat exchanged 23,4 kW - heating
| - primar hladna stran P: glikolni medij (35% propilen glikol in 65% voda), temp. vstopa 63C, temp. izstopa 48°C, pretok 1,43m3/h, padec tlaka do 20kPa | - primary cold side P: glycol medium (35% propylene glycol and 65% water), inlet temp 63C, outlet temp 48°C, flow 1.43m3/h, pressure drop up to 20kPa
| - sekundar topla stran S: ogrevna voda, temp. vstopa 50°C, temp. izstopa 60°C, pretok 2,04m3/h, padec tlaka do 20kPa | - secondary hot side S: heating water, inlet temp. 50°C, outlet temp. 60°C, flow rate 2,04m3/h, pressure drop up to 20kPa
| - vsi priključki prirobnični PN10, primar P DN25, sekundar S DN25 | - all connections flanged PN10, primary P DN25, secondary S DN25
| - vključno s podstavkom prenosnika, pritrdilnim in tesnilnim materialom; | - including the laptop base, fixing and sealing materials;
| - dimenzije do: dolžina L x širina W x višina H = 500 x 400 x 9000 mm | - dimensions up to: length L x width W x height H = 500 x 400 x 9000 mm
| - komplet s toplotna parozaporna izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +105°C, debelina 50mm | - complete with thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0.040W/mK according to EN ISO8497, classification B-s3-d0 according to EN13501-1, for temperatures -50 to +105°C, thickness 50mm
| - ustrezen proizvod ALFA LAVAL tip T5-BFG + toplotna izolacija ali enakovredno | - suitable product ALFA LAVAL type T5-BFG + thermal insulation or equivalent
| Oznaka: HE42.10 | Code: HE42.10 | kpl | 1 |  | 0
3.3 | Obtočna črpalka, PN10, z mokrim rotorjem, skladnost z ErP, elektronsko regulirana s PM motorjem in integrairanim frekvenčnim pretvornikom, inegrirano tipalo diferenčnega tlaka in temperature, upravljalnik nastavitev s prikazovalnikom parametrov, z internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, PN10, wet-rotor, ErP-compliant, electronically controlled with PM motor and integrated frequency converter, integrated differential pressure and temperature sensor, setting controller with parameter display, with internal hydraulic, electrical and communication connections, pump material grey cast iron with appropriate sealing for the medium, flanged design, including counter flanges, fixing and sealing material. Technical data:
| - glikolni medij SSE (35% propilen glikol) | - sSE glycol medium (35% propylene glycol)
| - pretok V= 1,43 m3/h, tlačna višina H= 45kPa, | - flow rate V= 1,43 m3/h, pressure head H= 45kPa,
| - komunikacija s CNS: RS485 / Modbus RTU | - communication with CNS: RS485 / Modbus RTU
| - elektro podatki Pel= 0,084kW, 230V /1/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 0,084kW, 230V /1/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip MAGNA3 25-60 | - corresponds to GRUNDFOS product type MAGNA3 25-60
| Oznaka: P42.081 | Code: P42.081 | kpl | 1 |  | 0
3.4 | Temperaturno tipalo, potopno, za merilno območje od -10 do +100°C, potopna dolžina L=100mm, v tulki iz nerjavnega materiala z navojnim priključkom 1/2" (DN15), električni podatki: napajanje 24V, izhod 4-20mA, komplet s pritrdilnim in tesnilnim materialom; | Temperature sensor, immersion, for measuring range -10 to +100°C, immersion length L=100mm, in stainless steel sleeve with threaded connection 1/2" (DN15), electrical data: power supply 24V, output 4-20mA, complete with fixing and sealing material;
| - glikolni medij SSE (35% propilen glikol) | - sSE glycol medium (35% propylene glycol)
| - ustreza proizvod ELEKTRONIKA PAHOR, tip CVB ali enakovredno | - corresponds to the product ELEKTRONIKA PAHOR, type CVB or equivalent
| Oznaka: TIC42.001. TI42.002 | Code: TIC42.001. TI42.002 | kpl | 2 |  | 0
3.5 | Tipalo tlaka s pretvornikom, za mertev tlaka v območju od 0 do 8 barg (relativno) ter nastavljivim alarmnim tlakom, navojni priključek 1/2" (DN15), material nerjavno jeklo, električni podatki: napajanje 24V, izhod 4-20mA, kompletno z ventilom za tipalo tlaka 1/2" (DN15) ter tesnilnim in pritrdilnim materialom; | Pressure sensor with transducer, for pressure measurement in the range from 0 to 8 barg (relative) and adjustable alarm pressure, threaded connection 1/2" (DN15), material stainless steel, electrical data: power supply 24V, output 4-20mA, complete with pressure sensor valve 1/2" (DN15) and sealing and fixing material;
| - glikolni medij SSE (35% propilen glikol) | - sSE glycol medium (35% propylene glycol)
| - alarm, če je tlak p < 3,5 barg (nastavitev na tipalu ali programska nastavitev) | - alarm if pressure p < 3.5 barg (sensor setting or software setting)
| - ustreza proizvod ENDRESS+HAUSER tip PTC31B + PZAV ali enakovredno | - corresponds to ENDRESS+HAUSER product type PTC31B + PZAV or equivalent
| Oznaka: PIA42.009 | Code: PIA42.009 | kpl | 1 |  | 0
3.6 | Ekspanzijska posoda za kompenzacijo toplotnih raztezkov medija v sistemu, PN10, skladno z direktivo EU o tlačni opremi PED, pokončna izvedba v obliki valja, membrana po DIN 4807, tlaki do 10 bar, temperature na membrani od 5 do 70°C, vključno s pritrdilnim in tesnilnim materialom; | Expansion vessel for compensating thermal expansion of the medium in the system, PN10, in compliance with the EU Pressure Equipment Directive PED, upright cylindrical design, diaphragm according to DIN 4807, pressures up to 10 bar, diaphragm temperatures from 5 to 70°C, including fixing and sealing material;
| - glikolni medij SSE (35% propilen glikol) | - sSE glycol medium (35% propylene glycol)
| - prostornina ekspanzijske posode 400 litrov | - expansion tank capacity 400 litres
| - dimenzije: premer D x višina H = ø620 x 1500mm | - dimensions: diameter D x height H = ø620 x 1500mm
| - z navojnim priključkom 3/4" (DN20), komplet z ventilom s ključavnico 3/4" (DN20) | - with 3/4" (DN20) threaded connection, complete with 3/4" (DN20) keyed valve
| - ustreza proizvod IMI PNEUMATEX tip PNEUMATEX tip SU 400.10 + DLV 20 ali enakovredno | - corresponds to IMI PNEUMATEX product type PNEUMATEX type SU 400.10 + DLV 20 or equivalent
| Oznaka: EP42.11 | Code: EP42.11 | kpl | 1 |  | 0
3.7 | Varnostni ventil po TRD 721, PN16, varnostna funkcija izpusta medija zaradi toplotnih raztezkov v sistemu, vzmetno delovanje, možnost ročnega odzračenja, prostor vzmeti zaščiten z membrano, prirobnična izvedba, vključno s pritrdilnim in tesnilnim materialom; | Safety valve according to TRD 721, PN16, safety function of medium discharge due to thermal expansion in the system, spring operation, manual venting possible, spring space protected by diaphragm, flanged version, including fixing and sealing material;
| - glikolni medij SSE (35% propilen glikol) | - sSE glycol medium (35% propylene glycol)
| - tlak odpiranja 8,0 barg, | - opening pressure 8,0 barg,
| - z navojnim priključkom 1" (DN25), komplet z ventilom s ključavnico 1" (DN25) | - with 1" (DN25) threaded connection, complete with 1" (DN25) keyed valve
| - ustreza proizvod IMI PNEUMATEX tip DSV 25 - 8.0 SOL + DLV 25 ali enakovredno | - iMI PNEUMATEX product type DSV 25 - 8.0 SOL + DLV 25 or equivalent
| Oznaka: VV42.12 | Code: VV42.12 | kpl | 1 |  | 0
3.8 | Krogelni ventil s priklučkom za praznenje oz. polnenje, navojna izvedba, PN16, z ročico, material medenina / PTFE, vključno s pritrdilnim in tesnilnim materialom: | Ball valve with union for emptying or filling, threaded version, PN16, with handle, material brass/PTFE, incl. fitting and sealing material:
| - glikolni medij SSE (35% propilen glikol) | - sSE glycol medium (35% propylene glycol)
| - ustreza proizvod END ARMATUREN ali enakovredno | - eND ARMATUREN or equivalent
| DN 15 | DN 15 | kos | 8 |  | 0
| DN 20 | DN 20 | kos | 1 |  | 0
3.9 | Krogelni ventil, navojna izvedba, PN16, z ročico, material medenina / PTFE, vključno s pritrdilnim in tesnilnim materialom: | Ball valve, threaded version, PN16, with lever, material brass/PTFE, incl. mounting and sealing material:
| - glikolni medij SSE (35% propilen glikol) | - sSE glycol medium (35% propylene glycol)
| - ustreza proizvod END ARMATUREN ali enakovredno | - eND ARMATUREN or equivalent
| DN 15 | DN 15 | kos | 8 |  | 0
| DN 25 | DN 25 | kos | 10 |  | 0
| DN 32 | DN 32 | kos | 6 |  | 0
3.10 | Izločevalnika nečistoč, magnetita in mikro mehurčkov, ciklonsko izločanje, PN16, skladno s PED, material medenina, EPDM, navojni priključki, z ventilom za izpust nečistoč ter avtomatskim odzračevalnim ventilom, vključno z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Impurity, magnetite and microbubble eliminators, cyclonic elimination, PN16, PED-compliant, material brass, EPDM, threaded connections, with impurity discharge valve and automatic vent valve, incl. threaded dutch, fixing and sealing material;
| - glikolni medij SSE (35% propilen glikol) | - sSE glycol medium (35% propylene glycol)
| - ustreza proizvod IMI PMEUMATEX tip Zeparo ZUKM ali enakovredno | - corresponds to IMI PMEUMATEX product type Zeparo ZUKM or equivalent
| DN 32 | DN 32 | kpl | 1 |  | 0
3.11 | Ventil za hidravlično uravnoteženje, nastavitev pretoka, navojna izvedba, PN16, s priključkoma za priklop naprave za merjenje pretoka, z zaporno funkcijo brez prenastavitve pretoka, material siva litina, nerjavno jeklo, EPDM, PTFE, vključno z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Hydraulic balancing valve, flow adjustment, threaded version, PN16, with two connections for connection of flow measuring device, with shut-off function without flow reset, material grey cast iron, stainless steel, EPDM, PTFE, incl. threaded plugs, fastening and sealing material;
| - glikolni medij SSE (35% propilen glikol) | - sSE glycol medium (35% propylene glycol)
| - ustreza proizvod IMI TA tip STAD ali enakovredno | - the product conforms to IMI TA type STAD or equivalent
| DN 32 | DN 32 | kos | 5 |  | 0
3.12 | Kompenzator vibracij iz strojne opreme na cevovod, navojna izvedba, PN16, material pocinkano jeklo, EPDM, vključno s pritrdilnim in tesnilnim materialom; | Vibration compensator from hardware to pipeline, threaded version, PN16, material galvanised steel, EPDM, including fixing and sealing material;
| - glikolni medij SSE (35% propilen glikol) | - sSE glycol medium (35% propylene glycol)
| - ustreza proizvod END ARMATUREN tip KP ali enakovredno | - corresponds to END ARMATUREN type KP or equivalent
| DN 25 | DN 25 | kpl | 2 |  | 0
3.13 | Termometer, tekočinski, dolžina skale 100mm, kotni 90°, potopna dolžina 40mm, v zaščitni cevi - tulki, klasa točnosti 1%, navojni priključek 1/2" (DN15), material medenina, aluminij, steklo, nerjavno jeklo, vključno s pritrdilnim in tesnilnim materialom; | Thermometer, liquid, scale length 100mm, angle 90°, immersion length 40mm, in protective tube - sleeves, accuracy class 1%, threaded connection 1/2" (DN15), material brass, aluminium, glass, stainless steel, incl. fixing and sealing material;
| - glikolni medij SSE (35% propilen glikol) | - sSE glycol medium (35% propylene glycol)
| - ustreza proizvod INOL ali enakovredno | - corresponds to INOL or equivalent
| - območjem merjenja: 0 do 100°C | - measuring range: 0 to 100°C | kpl | 8 |  | 0
3.14 | Manometer ø 68 mm, klasa točnosti 1,6% po EN837-1, navojni radialni priključek, material medenina, nerjavno jeklo, steklo / EPDM, komplet z manometrskim ventilom DN15 (1/2"), vključno s pritrdilnim in tesnilnim materialom; | Pressure gauge ø 68 mm, accuracy class 1.6% according to EN837-1, threaded radial connection, material brass, stainless steel, glass / EPDM, complete with pressure gauge valve DN15 (1/2"), incl. mounting and sealing material;
| - glikolni medij SSE (35% propilen glikol) | - sSE glycol medium (35% propylene glycol)
| - ustreza proizvod INOL ali enakovredno | - corresponds to INOL or equivalent
| - območjem merjenja: 0 do 10 bar | - measuring range: 0 to 10 bar | kpl | 8 |  | 0
3.15 | Avtomatski odzračevalnik, z zapornim in ročno odzračevalnim ventilom PN10 material medenina / PTFE, vključno z navojnim holandcem in tesnilnim materialom; | Automatic venting valve, with stop and manual venting valve PN10 material brass/PTFE, incl. threaded dutch and sealing material;
| - glikolni medij SSE (35% propilen glikol) | - sSE glycol medium (35% propylene glycol)
| DN25 - ustreza proizvod IMI PNEUMATEX tip ZUTX 25 ali enakovredno | DN25 - corresponds to IMI PNEUMATEX product type ZUTX 25 or equivalent | kpl | 8 |  | 0
3.16 | Odzračitveni lonček, volumen V ≥ 2 litra, izdelan iz cevi DN100, ø114x3,6 mm po EN10216-1 (DIN2448), dolžina L=300mm, z bombiranima zaključkoma, material P235TR2 (St37), vključno z varilnim materialom; | Discharge cup, volume V ≥ 2 litres, made of DN100 pipe, ø114x3,6 mm according to EN10216-1 (DIN2448), length L=300mm, with bomb-lined ends, material P235TR2 (St37), incl. welding material;
| - glikolni medij SSE (35% propilen glikol) | - sSE glycol medium (35% propylene glycol) | kpl | 2 |  | 0
3.17 | Jeklene srednje težke šivne cevi izdelane po EN10255 (DIN2440), material S195T (St33.2), vključno z oblikovnimi kosi (loki, redukcije, T kosi, ...) in varilnim materialom, | Medium-weight seamed steel tubes manufactured to EN10255 (DIN2440), material S195T (St33.2), including forming pieces (bows, reducers, T-pieces, etc.) and welding consumables,
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and pipe clamps with noise damping lining, suitable for HILTI or SIKLA, or equivalent;
| DN 15, ø 21,3 x 2,65 | DN 15, ø 21,3 x 2,65 | m | 30 |  | 0
| DN 20, ø 26,9 x 2,65 | DN 20, ø 26,9 x 2,65 | m | 12 |  | 0
| DN 25, ø 33,7 x 3,25 | DN 25, ø 33,7 x 3,25 | m | 30 |  | 0
| DN 32, ø 42,4 x 3,25 | DN 32, ø 42,4 x 3,25 | m | 240 |  | 0
| 90°lok DN 15, ø 21,3 x 2,65 | 90°lok DN 15, ø 21,3 x 2,65 | kos | 12 |  | 0
| 90°lok DN 20, ø 26,9 x 2,65 | 90°lok DN 20, ø 26,9 x 2,65 | kos | 4 |  | 0
| 90°lok DN 25, ø 33,7 x 3,25 | 90°lok DN 25, ø 33,7 x 3,25 | kos | 8 |  | 0
| 90°lok DN 32, ø 42,4 x 3,25 | 90°lok DN 32, ø 42,4 x 3,25 | kos | 30 |  | 0
| T kos DN 15 / odcep DN 15 | T piece DN 15 / branch DN 15 | kos | 10 |  | 0
| T kos DN 25 / odcep DN 20 | T piece DN 25 / branch DN 20 | kos | 2 |  | 0
| T kos DN 32 / odcep DN 15 | T piece DN 32 / branch DN 15 | kos | 10 |  | 0
| T kos DN 32 / odcep DN 25 | T piece DN 32 / branch DN 25 | kos | 20 |  | 0
| redukcija DN 25 / DN 20 | dN 25 / DN 20 reduction | kos | 4 |  | 0
| redukcija DN 32 / DN 25 | dN 32 / DN 25 reduction | kos | 8 |  | 0
3.18 | Čiščenje in barvanje jeklenih cevovodov iz ogljikovega jekla, odstranitev rje do kovinskega sijaja, dvakratni premaz s temeljnim antikorozijskim barvami ter dvakratni premaz s prekrivno barvo: antikorozijska zaščita s temeljnimi in prekrivnimi barvami mora biti obstojna na temperature v območju od -20 do +80°C in se mora izvesti v skladu z EN ISO 12944 z življenjsko dobo: visoko trajanje H (več kot 15 let). | Cleaning and painting of carbon steel pipelines, rust removal to metallic gloss, two coats of anticorrosion primer and two coats of overcoat: the anticorrosion protection with primer and overcoat must be resistant to temperatures in the range -20 to +80°C and must be carried out in accordance with EN ISO 12944 with a service life: high durability H (more than 15 years).
| - glikolni medij SSE (35% propilen glikol) | - sSE glycol medium (35% propylene glycol) | m2 | 36 |  | 0
3.19 | Toplotna izolacija cevovodov in cevnih armatur s parozaporno izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z naslednjimi lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, požarna klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +110°C, lepljeno na cevovode in armature z originalnim lepilom proizvajalca, vključno s trakovi za šive; | Thermal insulation of pipelines and pipe fittings with vapour barrier insulation made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, fire classification B-s3-d0 according to EN13501-1, for temperatures from -50 to +110°C, bonded to pipelines and fittings with the original manufacturer's adhesive, including seam tapes;
| - ustreza proizvod ARMACELL tip Armaflex ACE Plus ali enakovredno | - corresponds to ARMACELL product type Armaflex ACE Plus or equivalent
| - z dodatno aluminijasto pločevino Alu 0,6 mm | - with additional aluminium sheet Alu 0,6 mm
| DN 15, ø 21,3 ; debelina 13 mm | DN 15, ø 21,3 ; thickness 13 mm | m | 50 |  | 0
| DN 20, ø 26,9 ; debelina 19 mm | DN 20, ø 26,9 ; thickness 19 mm | m | 20 |  | 0
| DN 25, ø 33,7 ; debelina 19 mm | DN 25, ø 33,7 ; thickness 19 mm | m | 50 |  | 0
| DN 32, ø 42,4 ; debelina 25 mm | DN 32, ø 42,4 ; thickness 25 mm | m | 360 |  | 0
| v ploščah ; debelina 25 mm | in panels ; thickness 25 mm | m2 | 20 |  | 0
3.20 | Tlačni preskus trdnosti in tesnenja sistema cevovodov, skladeno z opisom v "IZS Priročnik tlačnih preizkusov strojnih inštalacij", vključno s potrebnim materialom za izvedbo preizkusa, ter izdelavo pisnega poročila o uspešno opravljenem tlačnem preizkusu; | Pressure test of the strength and tightness of the piping system, as described in the "IZS Manual for Pressure Testing of Mechanical Installations", including the necessary materials for the test, and the production of a written report on the successful completion of the pressure test;
| preskusni tlak = 1,2 x najvišji delovni tlak = 9,6 barg | test pressure = 1,2 x maximum working pressure = 9,6 barg | kpl | 1 |  | 0
3.21 | Izpiranje cevovodov s sanitarno hladno vodo v celotnem sistemu novoinstaliranih razvodov z namenom odstranjevanja nečistoč v sistemu cevovodov, vključno s čiščenjem lovilnikov nesnage in drugih elementov; | Flushing of sanitary cold water piping throughout the newly installed piping system to remove impurities in the piping system, including cleaning of debris traps and other elements; | kpl | 1 |  | 0
3.22 | Glikolnega medija in polnenje sistema; glikolni medij je mešanica mehčane vode in glikola, pričetek zmrzovanja -18°C, glikol mora biti primeren za prenos toplote pri ogrevalnih in hladilnih procesih; glikolni medij je potrebno pred polnjenjem zmešati v homogeno mešanico in šele nato napolniti sistem; | Glycol medium and system charging; the glycol medium is a mixture of softened water and glycol, freezing point -18°C, the glycol must be suitable for heat transfer in heating and cooling processes; the glycol medium must be mixed to a homogeneous mixture before charging and only then the system must be charged;
| - glikolni medij SSE (35% propilen glikol) | - sSE glycol medium (35% propylene glycol)
| - predvidoma ustreza propilen glikol proizvod BASF tip Gythermin P44 ali enakovredno | - presumed to correspond to the propylene glycol product BASF type Gythermin P44 or equivalent
| - količina glikola cca 70 litrov | - quantity of glycol approx. 70 litres | kpl | 1 |  | 0
3.23 | Kvalifikacija zvarov ter izdelava dokumentacije o zvarih: | Weld qualification and documentation of welds:
| - zvare lahko izvajajo samo varilci s certifikatom pooblaščenih organizacij, | - welding can only be carried out by welders certified by approved organisations,
| - postopek vizualne kontrole zvarov, kontrolirajo se vsi zvari - 100% zvarov, | - visual weld inspection procedure, all welds are inspected - 100% of welds,
| - postopek kontrole s snemanja zvarov - 10% zvarov, kjer so enakomerno zastopani vsi premeri, | - weld stripping inspection procedure - 10% of welds where all diameters are equally represented,
| - označevanje zvarov, izdelava dokumentacije z dokazili o ustreznosti ter slikovnim materialom; | - marking welds, producing documentation with proof of conformity and pictorial material; | kpl | 1 |  | 0
3.24 | Ognjeodporna tesnilna masa, vgradnja na prehodu cevovodov skozi zid med požarnima sektortjema, požarna odpornost 90 minut, ustreza proizvod HILTI ali enakovredno. | Fire-resistant sealant, for installation at the transition of pipelines through the wall between the two fire sectors, fire resistance 90 minutes, equivalent to HILTI or equivalent.
| Vsak prehod mora biti označen z nalepko ali tablico z osnovnimi požarnimi podatki; | Each passageway must be marked with a sticker or placard with basic fire information; | kpl | 1 |  | 0
3.25 | Preizkusno obratovanje delovanja sistema v obsegu: | Operational test of the system in scope:
| - pregled instalacije, armatur in opreme, | - inspection of plumbing, fixtures and fittings,
| - pregled delovanja naprav, elementov regulacije in nastavitve parametrov, | - overview of the operation of the devices, control elements and parameter settings,
| - pregled cirkulacije glikolnega medija, | - checking the circulation of the glycol medium,
| - kontrola predpisanih parametrov glikolnega medija | - control of the prescribed parameters of the glycol medium
| Preizkusno obratovanje traja neprekinjeno 72 ur. | The test operation shall be continuous for 72 hours. | kpl | 1 |  | 0
3.26 | Napisne ploščice iz nerjavne pločevine z vgravirano oznako po shemi za opremo in armature, kompletno z jekleno pritrdilno žico ali visoko kvalotetne nalepke; visoko trajanje H (več kot 15 let) | Stainless steel nameplates with engraved marking according to the scheme for fittings and fixtures, complete with steel fixing wire or high quality labels; high durability H (more than 15 years) | kpl | 1 |  | 0
3.27 | Samolepilne puščice za označitev smeri pretoka ter z napisom vrste medija; visoko trajanje H (več kot 15 let) | Self-adhesive arrows to indicate direction of flow and type of media; high H lifetime (more than 15 years) | kpl | 1 |  | 0
3.28 | Izdelava montažnih risb za izvedbo inštalacij med gradnjo objekta, kot so: detajli priključkov, montažne skice, montažni detajli, ipd. | Preparation of assembly drawings for the installation of services during the construction of the building, such as: connection details, assembly sketches, assembly details, etc. | kpl | 1 |  | 0
3.29 | Kvalifikacije montaže IQ-pregledi (instalation qualification) po GEP Commissioning protokolu in dokumentiranje kvalifikacije montaže, vključno z odpravo prvotnih napak montaže; | Installation qualification IQ checks (installation qualification) according to the GEP Commissioning Protocol and documentation of installation qualification, including correction of original installation faults; | kpl | 1 |  | 0
3.30 | Meritve delovanja OQ-kvalifikacija (operation qualification) ter dokumentiranje meritev delovanja, vključno z nastavitvijo parametrov; | OQ (operation qualification) measurements and documentation of performance measurements, including parameter settings; | kpl | 1 |  | 0
3.31 | Posnetki izvedenega stanja, sprotno beleženje vseh sprememb nastalih med izvedbo, vrisovanje in vpisovanje v PZI projektno dokumentacijo; | Recording of the as-built condition, keeping a running record of any changes made during execution, plotting and entering into the PZI project documentation; | kpl | 1 |  | 0
3.32 | Stenska shema sistema, vloženo v zaščitni okvir s prosojnim umetnim steklomo (plastika) ali plastificirano, vključno s pritrditvijo na notranjo steno v strojnici objekta; | Wall diagram of the system, encased in a protective frame with transparent plastic or plasticised glass, including fixing to an internal wall in the mechanical room of the building; | kpl | 1 |  | 0
3.33 | Primopredajna dokumentacija, ki mora vsebovati: izjave, dokazilo o zanesljivosti objekta, certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo, obratovanje in vzdrževanje ter ostalo primopredajno dokumantacijo. Predaja se v dveh mapiranih izvodih ter en izvod v elektronski obliki; | The handover documentation, which shall include: declarations, proof of the reliability of the facility, certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use, operation and maintenance, and other handover documentation. It shall be handed over in two mapped copies and one copy in electronic form; | kpl | 1 |  | 0
| GLIKOLNI MEDIJ SSE | GLYCOL MEDIUM SSE |  |  |  | 0

## 4.7.4_GM-Klima
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.7 | STROJNA DELA | MECHANICAL WORKS
4.7.4 | GLIKOLNI MEDIJ KLIMATIZACIJA | GLYCOL MEDIUM AIR CONDITIONING |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
4 | GLIKOLNI MEDIJ KLIMATIZACIJA | GLYCOL MEDIUM AIR CONDITIONING
| Vse postavke v nadalevanju zajemajo dobavo in montažo (razen tam kjer je to posebej navedeno). | All items below include delivery and installation (except where specifically indicated).
4.1 | Ekspanzijska posoda za kompenzacijo toplotnih raztezkov medija v sistemu, PN10, skladno z direktivo EU o tlačni opremi PED, pokončna izvedba v obliki diska, membrana po DIN 4807, tlaki do 10 bar, temperature na membrani od 5 do 70°C, vključno s pritrdilnim in tesnilnim materialom; | Expansion vessel for compensation of thermal expansion of the medium in the system, PN10, in compliance with the EU Pressure Equipment Directive PED, upright disc design, diaphragm according to DIN 4807, pressures up to 10 bar, diaphragm temperatures from 5 to 70°C, incl. fixing and sealing material;
| - glikolni medij prezračevanje in klimatizacija (35% etilen glikol) | - glycol medium ventilation and air conditioning (35% ethylene glycol)
| - prostornina ekspanzijske posode 12 litrov | - expansion tank capacity 12 litres
| - dimenzije: premer D x debelina H = ø360 x 200 mm | - dimensions: diameter D x thickness H = ø360 x 200 mm
| - z navojnim priključkom 1/2" (DN15), komplet z ventilom s ključavnico 1/2" (DN15) | - with threaded connection 1/2" (DN15), complete with valve with lock 1/2" (DN15)
| - ustreza proizvod IMI PNEUMATEX tip SD 12.10 + DLV 15 ali enakovredno | - corresponds to IMI PNEUMATEX product type SD 12.10 + DLV 15 or equivalent
| Oznaka: EP09.501, EP16.501 | Code: EP09.501, EP16.501 | kpl | 2 |  | 0
4.2 | Ekspanzijska posoda za kompenzacijo toplotnih raztezkov medija v sistemu, PN10, skladno z direktivo EU o tlačni opremi PED, pokončna izvedba v obliki diska, membrana po DIN 4807, tlaki do 10 bar, temperature na membrani od 5 do 70°C, vključno s pritrdilnim in tesnilnim materialom; | Expansion vessel for compensation of thermal expansion of the medium in the system, PN10, in compliance with the EU Pressure Equipment Directive PED, upright disc design, diaphragm according to DIN 4807, pressures up to 10 bar, diaphragm temperatures from 5 to 70°C, incl. fixing and sealing material;
| - glikolni medij prezračevanje in klimatizacija (35% etilen glikol) | - glycol medium ventilation and air conditioning (35% ethylene glycol)
| - prostornina ekspanzijske posode 35 litrov | - expansion tank capacity 35 litres
| - dimenzije: premer D x debelina H = ø490 x 280 mm | - dimensions: diameter D x thickness H = ø490 x 280 mm
| - z navojnim priključkom 3/4" (DN20), komplet z ventilom s ključavnico 3/4" (DN20) | - with 3/4" (DN20) threaded connection, complete with 3/4" (DN20) keyed valve
| - ustreza proizvod IMI PNEUMATEX tip SD 35.10 + DLV 20 ali enakovredno | - corresponds to IMI PNEUMATEX product type SD 35.10 + DLV 20 or equivalent
| Oznaka: EP12.501, EP13.501 | Code: EP12.501, EP13.501 | kpl | 2 |  | 0
4.3 | Varnostni ventil po TRD 721, PN16, varnostna funkcija izpusta medija zaradi toplotnih raztezkov v sistemu, vzmetno delovanje, možnost ročnega odzračenja, prostor vzmeti zaščiten z membrano, prirobnična izvedba, vključno s pritrdilnim in tesnilnim materialom; | Safety valve according to TRD 721, PN16, safety function of medium discharge due to thermal expansion in the system, spring operation, manual venting possible, spring space protected by diaphragm, flanged version, including fixing and sealing material;
| - glikolni medij prezračevanje in klimatizacija (35% etilen glikol) | - glycol medium ventilation and air conditioning (35% ethylene glycol)
| - tlak odpiranja 5,0 barg, | - opening pressure 5,0 barg,
| - z navojnim priključkom 1/2" (DN15), komplet z ventilom s ključavnico 1/2" (DN15) | - with threaded connection 1/2" (DN15), complete with valve with lock 1/2" (DN15)
| - ustreza proizvod IMI PNEUMATEX tip DSV 15 - 5.0 F + DLV 15 ali enakovredno | - iMI PNEUMATEX product type DSV 15 - 5.0 F + DLV 15 or equivalent
| Oznaka: VV09.502, VV16.502 | Code: VV09.502, VV16.502 | kpl | 2 |  | 0
4.4 | Varnostni ventil po TRD 721, PN16, varnostna funkcija izpusta medija zaradi toplotnih raztezkov v sistemu, vzmetno delovanje, možnost ročnega odzračenja, prostor vzmeti zaščiten z membrano, prirobnična izvedba, vključno s pritrdilnim in tesnilnim materialom; | Safety valve according to TRD 721, PN16, safety function of medium discharge due to thermal expansion in the system, spring operation, manual venting possible, spring space protected by diaphragm, flanged version, including fixing and sealing material;
| - glikolni medij prezračevanje in klimatizacija (35% etilen glikol) | - glycol medium ventilation and air conditioning (35% ethylene glycol)
| - tlak odpiranja 5,0 barg, | - opening pressure 5,0 barg,
| - z navojnim priključkom 3/4" (DN20), komplet z ventilom s ključavnico 3/4" (DN20) | - with 3/4" (DN20) threaded connection, complete with 3/4" (DN20) keyed valve
| - ustreza proizvod IMI PNEUMATEX tip DSV 20 - 5.0 F + DLV 20 ali enakovredno | - iMI PNEUMATEX product type DSV 20 - 5.0 F + DLV 20 or equivalent
| Oznaka: VV12.502, VV13.502 | Code: VV12.502, VV13.502 | kpl | 2 |  | 0
4.5 | Tipalo tlaka s pretvornikom, za mertev tlaka v območju od 0 do 4 barg (relativno) ter nastavljivim alarmnim tlakom, navojni priključek 1/2" (DN15), material nerjavno jeklo, električni podatki: napajanje 24V, izhod 4-20mA, kompletno z ventilom za tipalo tlaka 1/2" (DN15) ter tesnilnim in pritrdilnim materialom; | Pressure sensor with transducer, for pressure measurement in the range from 0 to 4 barg (relative) and adjustable alarm pressure, threaded connection 1/2" (DN15), material stainless steel, electrical data: power supply 24V, output 4-20mA, complete with pressure sensor valve 1/2" (DN15) and sealing and fixing material;
| - glikolni medij prezračevanje in klimatizacija (35% etilen glikol) | - glycol medium ventilation and air conditioning (35% ethylene glycol)
| - alarm, če je tlak p < 2,0 barg (nastavitev na tipalu ali programska nastavitev) | - alarm if pressure p < 2.0 barg (sensor setting or software setting)
| - ustreza proizvod ENDRESS+HAUSER tip PTC31B + PZAV ali enakovredno (PIA) | - corresponds to ENDRESS+HAUSER product type PTC31B + PZAV or equivalent (PIA)
| Oznaka: PIA09.019, PIA12.019, PIA13.019, PIA16.019 | Code: PIA09.019, PIA12.019, PIA13.019, PIA16.019 | kpl | 4 |  | 0
4.6 | Krogelni ventil s priključkom za praznenje oz. polnenje, navojna izvedba, PN16, z ročico, material medenina / PTFE, vključno s pritrdilnim in tesnilnim materialom: | Ball valve with connection for emptying or filling, threaded version, PN16, with handle, material brass/PTFE, incl. fitting and sealing material:
| - glikolni medij prezračevanje in klimatizacija (35% etilen glikol) | - glycol medium ventilation and air conditioning (35% ethylene glycol)
| - ustreza proizvod END ARMATUREN ali enakovredno | - eND ARMATUREN or equivalent
| DN 15 | DN 15 | kos | 20 |  | 0
| DN 20 | DN 20 | kos | 4 |  | 0
4.7 | Krogelni ventil, navojna izvedba, PN16, z ročico, material medenina / PTFE, vključno s pritrdilnim in tesnilnim materialom: | Ball valve, threaded version, PN16, with handle, material brass/PTFE, incl. fitting and sealing material:
| - glikolni medij prezračevanje in klimatizacija (35% etilen glikol) | - glycol medium ventilation and air conditioning (35% ethylene glycol)
| - ustreza proizvod END ARMATUREN ali enakovredno | - eND ARMATUREN or equivalent
| DN 40 | DN 40 | kos | 4 |  | 0
| DN 50 | DN 50 | kos | 12 |  | 0
4.8 | Zaporna loputa, prirobnična izvedba, mehko tesnenje, PN16, z ročnim pogonom z ročico do vključno DN100 oziroma z ročnim polžnim pogonom nad vključno DN125, material nodularna litina / EPDM, za vgradnjo med prirobnice, komplet s protiprirobnicama, vijačnim in tesnilnim materialom; | Butterfly valve, flanged version, soft sealing, PN16, with manual lever actuator up to and including DN100 or with manual screw actuator up to and including DN125, material ductile iron / EPDM, for installation between flanges, complete with two anti-seize fittings, screwing and sealing material;
| - glikolni medij prezračevanje in klimatizacija (35% etilen glikol) | - glycol medium ventilation and air conditioning (35% ethylene glycol)
| - ustreza proizvod IMP ARMATURE ali enakovredno | - iMP ARMATURE or equivalent
| DN 80 | DN 80 | kpl | 8 |  | 0
4.9 | Lovilnik nesnage, navojna izvedba, z normalnim sitom, PN16, material siva litina, sito nerjavno jeklo, komplet s krogelnim ventilom DN15 za praznenje in izpiranje, vključno z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Debris trap, threaded version, with normal sieve, PN16, material grey cast iron, sieve stainless steel, complete with ball valve DN15 for emptying and flushing, incl. two threaded Hollanders, fixing and sealing material;
| - glikolni medij prezračevanje in klimatizacija (35% etilen glikol) | - glycol medium ventilation and air conditioning (35% ethylene glycol)
| - ustreza proizvod IMP ARMATURE ali enakovredno | - iMP ARMATURE or equivalent
| DN 50 | DN 50 | kos | 2 |  | 0
4.10 | Lovilnik nesnage, prirobnična izvedba, z normalnim sitom, PN16, material siva litina, sito nerjavno jeklo, komplet s krogelnim ventilom DN15 za praznenje in izpiranje, vključno s protiprirobnicama, vijačnim in tesnilnim materialom; | Debris trap, flanged version, with normal sieve, PN16, material grey cast iron, sieve stainless steel, complete with ball valve DN15 for emptying and flushing, incl. counter flanges, screwing and sealing material;
| - glikolni medij prezračevanje in klimatizacija (35% etilen glikol) | - glycol medium ventilation and air conditioning (35% ethylene glycol)
| - ustreza proizvod IMP ARMATURE ali enakovredno | - iMP ARMATURE or equivalent
| DN 80 | DN 80 | kpl | 2 |  | 0
4.11 | Ventil za hidravlično uravnoteženje, nastavitev pretoka, navojna izvedba, PN16, s priključkoma za priklop naprave za merjenje pretoka, z zaporno funkcijo brez prenastavitve pretoka, material siva litina, nerjavno jeklo, EPDM, PTFE, vključno z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Hydraulic balancing valve, flow adjustment, threaded version, PN16, with two connections for connection of flow measuring device, with shut-off function without flow reset, material grey cast iron, stainless steel, EPDM, PTFE, incl. threaded plugs, fastening and sealing material;
| - glikolni medij prezračevanje in klimatizacija (35% etilen glikol) | - glycol medium ventilation and air conditioning (35% ethylene glycol)
| - ustreza proizvod IMI TA tip STAD ali enakovredno | - the product conforms to IMI TA type STAD or equivalent
| DN 40 | DN 40 | kos | 1 |  | 0
| DN 50 | DN 50 | kos | 3 |  | 0
4.12 | Ventil za hidravlično uravnoteženje, nastavitev pretoka, prirobnična izvedba, PN16, s priključkoma za priklop naprave za merjenje pretoka, z zaporno funkcijo brez prenastavitve pretoka, material siva litina, nerjavno jeklo, EPDM, PTFE, vključno s protiprirobnicama, vijačnim in tesnilnim materialom; | Hydraulic balancing valve, flow adjustable, flanged version, PN16, with two connections for connection to a flow measuring device, with shut-off function without flow reset, material grey cast iron, stainless steel, EPDM, PTFE, incl. anti-seize, screwing and sealing material;
| - glikolni medij prezračevanje in klimatizacija (35% etilen glikol) | - glycol medium ventilation and air conditioning (35% ethylene glycol)
| - ustreza proizvod IMI TA tip STAF ali enakovredno | - corresponds to IMI TA type STAF or equivalent
| DN 80 | DN 80 | kpl | 2 |  | 0
4.13 | Kompenzator vibracij iz strojne opreme na cevovod, prirobnična izvedba, PN16, material pocinkano jeklo, EPDM, vključno s pritrdilnim in tesnilnim materialom; | Vibration compensator from hardware to pipeline, flanged version, PN16, material galvanised steel, EPDM, including fixing and sealing material;
| - glikolni medij prezračevanje in klimatizacija (35% etilen glikol) | - glycol medium ventilation and air conditioning (35% ethylene glycol)
| - ustreza proizvod END ARMATUREN tip KP ali enakovredno | - corresponds to END ARMATUREN type KP or equivalent
| DN 32 | DN 32 | kpl | 2 |  | 0
| DN 50 | DN 50 | kpl | 2 |  | 0
4.14 | Termometer, tekočinski, dolžina skale 100mm, kotni 90°, potopna dolžina 40mm, v zaščitni cevi - tulki, klasa točnosti 1%, navojni priključek 1/2" (DN15), material medenina, aluminij, steklo, nerjavno jeklo, vključno s pritrdilnim in tesnilnim materialom; | Thermometer, liquid, scale length 100mm, angle 90°, immersion length 40mm, in protective tube - sleeves, accuracy class 1%, threaded connection 1/2" (DN15), material brass, aluminium, glass, stainless steel, incl. fixing and sealing material;
| - glikolni medij prezračevanje in klimatizacija (35% etilen glikol) | - glycol medium ventilation and air conditioning (35% ethylene glycol)
| - ustreza proizvod INOL ali enakovredno | - corresponds to INOL or equivalent
| - območjem merjenja: 0 do 100°C | - measuring range: 0 to 100°C | kpl | 20 |  | 0
4.15 | Manometer ø 68 mm, klasa točnosti 1,6% po EN837-1, navojni radialni priključek, material medenina, nerjavno jeklo, steklo / EPDM, komplet z manometrskim ventilom DN15 (1/2"), vključno s pritrdilnim in tesnilnim materialom; | Pressure gauge ø 68 mm, accuracy class 1.6% according to EN837-1, threaded radial connection, material brass, stainless steel, glass / EPDM, complete with pressure gauge valve DN15 (1/2"), including fitting and sealing material;
| - glikolni medij prezračevanje in klimatizacija (35% etilen glikol) | - glycol medium ventilation and air conditioning (35% ethylene glycol)
| - ustreza proizvod INOL ali enakovredno | - corresponds to INOL or equivalent
| - območjem merjenja: 0 do 10 bar | - measuring range: 0 to 10 bar | kpl | 10 |  | 0
4.16 | Avtomatski odzračevalnik, z zapornim in ročno odzračevalnim ventilom PN10 material medenina / PTFE, vključno z navojnim holandcem in tesnilnim materialom; | Automatic vent, with stop and manual vent valve PN10 material brass/PTFE, incl. threaded dutch and sealing material;
| - glikolni medij prezračevanje in klimatizacija (35% etilen glikol) | - glycol medium ventilation and air conditioning (35% ethylene glycol)
| DN25 - ustreza proizvod IMI PNEUMATEX tip ZUTX 25 ali enakovredno | DN25 - corresponds to IMI PNEUMATEX product type ZUTX 25 or equivalent | kpl | 12 |  | 0
4.17 | Odzračitveni lonček, volumen V ≥ 2 litra, izdelan iz cevi DN100, ø114x3,6 mm po EN10216-1 (DIN2448), dolžina L=300mm, z bombiranima zaključkoma, material P235TR2 (St37), vključno z varilnim materialom; | Discharge cup, volume V ≥ 2 litres, made of DN100 pipe, ø114x3,6 mm according to EN10216-1 (DIN2448), length L=300mm, with bomb-coated ends, material P235TR2 (St37), incl. welding consumables;
| - glikolni medij prezračevanje in klimatizacija (35% etilen glikol) | - glycol medium ventilation and air conditioning (35% ethylene glycol) | kpl | 8 |  | 0
4.18 | Jeklene srednje težke šivne cevi izdelane po EN10255 (DIN2440), material S195T (St33.2), vključno z oblikovnimi kosi (loki, redukcije, T kosi, ...) in varilnim materialom, | Medium-weight seamed steel tubes manufactured to EN10255 (DIN2440), material S195T (St33.2), including forming pieces (bows, reducers, T-pieces, etc.) and welding consumables,
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and pipe clamps with noise damping lining, suitable for HILTI or SIKLA, or equivalent;
| - predizolirane obemke za hladen glikolni medij prezračevanja | - pre-insulated cold glycol medium ventilation perimeters
| DN 15, ø 21,3 x 2,65 | DN 15, ø 21,3 x 2,65 | m | 60 |  | 0
| DN 20, ø 26,9 x 2,65 | DN 20, ø 26,9 x 2,65 | m | 12 |  | 0
| DN 25, ø 33,7 x 3,25 | DN 25, ø 33,7 x 3,25 | m | 12 |  | 0
| DN 32, ø 42,4 x 3,25 | DN 32, ø 42,4 x 3,25 | m | 12 |  | 0
| DN 40, ø 48,3 x 3,25 | DN 40, ø 48,3 x 3,25 | m | 90 |  | 0
| DN 50, ø 60,3 x 3,65 | DN 50, ø 60,3 x 3,65 | m | 180 |  | 0
| 90°lok DN 15, ø 21,3 x 2,65 | 90°lok DN 15, ø 21,3 x 2,65 | kos | 12 |  | 0
| 90°lok DN 20, ø 26,9 x 2,65 | 90°lok DN 20, ø 26,9 x 2,65 | kos | 4 |  | 0
| 90°lok DN 25, ø 33,7 x 3,25 | 90°lok DN 25, ø 33,7 x 3,25 | kos | 4 |  | 0
| 90°lok DN 32, ø 42,4 x 3,25 | 90°lok DN 32, ø 42,4 x 3,25 | kos | 4 |  | 0
| 90°lok DN 40, ø 48,3 x 3,25 | 90°lok DN 40, ø 48,3 x 3,25 | kos | 20 |  | 0
| 90°lok DN 50, ø 60,3 x 3,65 | 90°lok DN 50, ø 60,3 x 3,65 | kos | 40 |  | 0
| T kos DN 20 / odcep DN 20 | T piece DN 20 / branch DN 20 | kos | 2 |  | 0
| T kos DN 25 / odcep DN 25 | T piece DN 25 / branch DN 25 | kos | 2 |  | 0
| T kos DN 50 / odcep DN 40 | T piece DN 50 / branch DN 40 | kos | 2 |  | 0
| redukcija DN 25 / DN 20 | dN 25 / DN 20 reduction | kos | 4 |  | 0
| redukcija DN 50 / DN 25 | dN 50 / DN 25 reduction | kos | 2 |  | 0
| redukcija DN 50 / DN 40 | dN 50 / DN 40 reduction | kos | 8 |  | 0
| prirobnica DN 40 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 40 to EN1092, PN16, including bolting and sealing material | kpl | 4 |  | 0
| prirobnica DN 50 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 50 to EN1092, PN16, including bolting and sealing material | kpl | 4 |  | 0
4.19 | Jeklene brezšivne cevi izdelane po EN10216-1 (DIN2448), iz materiala P235TR2 (St37), vključno z oblikovnimi kosi (loki, redukcije, T kosi, ...) in varilnim materialom, | Seamless steel tubes manufactured to EN10216-1 (DIN2448), in P235TR2 (St37), including forming pieces (bends, reducers, T-pieces, etc.) and welding consumables,
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and pipe clamps with noise damping lining, suitable for HILTI or SIKLA, or equivalent;
| - predizolirane obemke za hladen glikolni medij prezračevanja | - pre-insulated cold glycol medium ventilation perimeters
| DN 65, ø 76,1 x 2,9 | DN 65, ø 76,1 x 2,9 | m | 12 |  | 0
| DN 80, ø 88,9 x 3,2 | DN 80, ø 88,9 x 3,2 | m | 90 |  | 0
| 90°lok DN 65, ø 76,1 x 2,9 | 90°block DN 65, ø 76,1 x 2,9 | kos | 2 |  | 0
| 90°lok DN 80, ø 88,9 x 3,2 | 90°lok DN 80, ø 88,9 x 3,2 | kos | 30 |  | 0
| T kos DN 80 / odcep DN 50 | T piece DN 80 / branch DN 50 | kos | 2 |  | 0
| T kos DN 80 / odcep DN 65 | T piece DN 80 / branch DN 65 | kos | 2 |  | 0
| T kos DN 80 / odcep DN 80 | T piece DN 80 / branch DN 80 | kos | 2 |  | 0
| redukcija DN 65 / DN 40 | dN 65 / DN 40 reduction | kos | 1 |  | 0
| redukcija DN 80 / DN 50 | dN 80 / DN 50 reduction | kos | 4 |  | 0
4.20 | Čiščenje in barvanje jeklenih cevovodov iz ogljikovega jekla, odstranitev rje do kovinskega sijaja, dvakratni premaz s temeljnim antikorozijskim barvami ter dvakratni premaz s prekrivno barvo: antikorozijska zaščita s temeljnimi in prekrivnimi barvami mora biti obstojna na temperature v območju od -20 do +80°C in se mora izvesti v skladu z EN ISO 12944 z življenjsko dobo: visoko trajanje H (več kot 15 let). | Cleaning and painting of carbon steel pipelines, rust removal to metallic gloss, two coats of anticorrosion primer and two coats of overcoat: the anticorrosion protection with primer and overcoat must be resistant to temperatures in the range -20 to +80°C and must be carried out in accordance with EN ISO 12944 with a service life: high durability H (more than 15 years).
| - glikolni medij prezračevanje in klimatizacija (35% etilen glikol) | - glycol medium ventilation and air conditioning (35% ethylene glycol) | m2 | 200 |  | 0
4.21 | Bakrene cevi, zatisni press sistem, izdelane po EN1057, material baker, vključno s spojnimi in oblikovnimi zatisnimi press kosi (90°loki, T kosi, redukcije, ...), spojnim in tesnilnim materialom, zatiskanje z originalnim press orodjem proizvajalca, komplet s prehodnimi navojnimi oblikovnimi kosi, ustreza proizvod VIEGA ali enakovredno, | Copper tubes, press fitting system, manufactured to EN1057, material copper, including joining and forming press fittings (90°bends, T-fittings, reducers, etc.), joining and sealing material, press fitting with original manufacturer's press tool, complete with threaded transition fittings, corresponding to VIEGA product or equivalent,
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and pipe clamps with noise damping lining, suitable for HILTI or SIKLA, or equivalent;
| - odtok kondenztata od hladilnih teles in naprav | - condensate drainage from refrigeration units and appliances
| DN 40, ø 42 x 1,5 | DN 40, ø 42 x 1,5 | m | 30 |  | 0
| 45°lok DN 40, ø 42 x 1,5 | 45°arc DN 40, ø 42 x 1,5 | kos | 4 |  | 0
| 90°lok DN 40, ø 42 x 1,5 | 90°lok DN 40, ø 42 x 1,5 | kos | 10 |  | 0
| DN 40 prehodni kos za priklop na sifon | DN 40 transition piece for connection to siphon | kos | 4 |  | 0
4.22 | Sifon za kondenzat odvodni priključek DN40, dovodni priključkom 5/4' (DN32 - stisnjen spoj) oz. d 12 - 18 mm (za gladke cevne nastavke) vertikalno ali vodoravno, z vodno smradno zaporo (60 mm) in mehansko smradno zaporo s kroglico ter čistilnim vložkom, predviden za klimatske naprave, material PP, skladnost z EN12056, vključno s spojnim in tesnilnim materialom; | Condensate trap outlet connection DN40, inlet connection 5/4' (DN32 - compression joint) or d 12 - 18 mm (for plain pipe fittings) vertically or horizontally, with water odour stop (60 mm) and mechanical odour stop with ball and cleaning insert, intended for air-conditioning systems, material PP, compliance with EN12056, incl. jointing and sealing material;
| - ustreza proizvod Hutterer & Lechner tip HL136.N oziroma .3 ali enakovredno | - corresponds to Hutterer & Lechner product type HL136.N or .3 or equivalent | kpl | 4 |  | 0
4.23 | Toplotna izolacija cevovodov in cevnih armatur s parozaporno izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z naslednjimi lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, požarna klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +110°C, lepljeno na cevovode in armature z originalnim lepilom proizvajalca, vključno s trakovi za šive; | Thermal insulation of pipelines and pipe fittings with vapour barrier insulation made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, fire classification B-s3-d0 according to EN13501-1, for temperatures from -50 to +110°C, bonded to pipelines and fittings with the original manufacturer's adhesive, including seam tapes;
| - ustreza proizvod ARMACELL tip Armaflex ACE Plus ali enakovredno | - corresponds to ARMACELL product type Armaflex ACE Plus or equivalent
| - z dodatno aluminijasto pločevino Alu 0,6 mm | - with additional aluminium sheet Alu 0,6 mm
| DN 15, ø 21,3 ; debelina 13 mm | DN 15, ø 21,3 ; thickness 13 mm | m | 90 |  | 0
| DN 20, ø 26,9 ; debelina 19 mm | DN 20, ø 26,9 ; thickness 19 mm | m | 20 |  | 0
| DN 25, ø 33,7 ; debelina 19 mm | DN 25, ø 33,7 ; thickness 19 mm | m | 20 |  | 0
| DN 32, ø 42,4 ; debelina 25 mm | DN 32, ø 42,4 ; thickness 25 mm | m | 20 |  | 0
| DN 40, ø 48,3 debelina 25 mm | DN 40, ø 48,3 thickness 25 mm | m | 140 |  | 0
| DN 50, ø 60,3 ; debelina 40 mm | DN 50, ø 60,3 ; thickness 40 mm | m | 270 |  | 0
| DN 65, ø 76,1 ; debelina 40 mm | DN 65, ø 76,1 ; thickness 40 mm | m | 20 |  | 0
| DN 80, ø 88,9 ; debelina 40 mm | DN 80, ø 88,9 ; thickness 40 mm | m | 140 |  | 0
| v ploščah ; debelina 40 mm | in panels ; thickness 40 mm | m2 | 20 |  | 0
4.24 | Tlačni preskus trdnosti in tesnenja sistema cevovodov, skladeno z opisom v "IZS Priročnik tlačnih preizkusov strojnih inštalacij", vključno s potrebnim materialom za izvedbo preizkusa, ter izdelavo pisnega poročila o uspešno opravljenem tlačnem preizkusu; | Pressure test of the strength and tightness of the piping system, as described in the "IZS Manual for Pressure Testing of Mechanical Installations", including the necessary materials for the test, and the production of a written report on the successful completion of the pressure test;
| preskusni tlak = 1,3 x najvišji delovni tlak = 6,5 barg | test pressure = 1,3 x maximum working pressure = 6,5 barg | kpl | 1 |  | 0
4.25 | Izpiranje cevovodov s sanitarno hladno vodo v celotnem sistemu novoinstaliranih razvodov z namenom odstranjevanja nečistoč v sistemu cevovodov, vključno s čiščenjem lovilnikov nesnage in drugih elementov; | Flushing of sanitary cold water piping throughout the newly installed piping system to remove impurities in the piping system, including cleaning of debris traps and other elements; | kpl | 1 |  | 0
4.26 | Glikolnega medija in polnenje sistema; glikolni medij je mešanica mehčane vode in glikola, pričetek zmrzovanja -16°C, glikol mora biti primeren za prenos toplote pri ogrevalnih in hladilnih procesih; glikolni medij je potrebno pred polnjenjem zmešati v homogeno mešanico in šele nato napolniti sistem; | Glycol medium and system charging; the glycol medium is a mixture of softened water and glycol, freezing point -16°C, the glycol must be suitable for heat transfer in heating and cooling processes; the glycol medium must be mixed to a homogeneous mixture before charging and only then the system must be charged;
| - glikolni medij prezračevanje (30% etilen glikol) | - glycol medium aeration (30% ethylene glycol)
| - predvidoma ustreza propilen glikol proizvod BASF tip Gythermin NF ali enakovredno oziroma | - presumably corresponding to the propylene glycol product BASF type Gythermin NF or equivalent, or
| - količina glikola cca 400 litrov za vse prezračevalno klimatske sisteme | - glycol quantity approx. 400 litres for all ventilation and air conditioning systems | kpl | 1 |  | 0
4.27 | Kvalifikacija zvarov ter izdelava dokumentacije o zvarih: | Weld qualification and documentation of welds:
| - zvare lahko izvajajo samo varilci s certifikatom pooblaščenih organizacij, | - welds can only be carried out by welders certified by approved organisations,
| - postopek vizualne kontrole zvarov, kontrolirajo se vsi zvari - 100% zvarov, | - visual weld inspection procedure, all welds are inspected - 100% of welds,
| - postopek kontrole s snemanja zvarov - 10% zvarov, kjer so enakomerno zastopani vsi premeri, | - weld stripping inspection procedure - 10% of welds where all diameters are equally represented,
| - označevanje zvarov, izdelava dokumentacije z dokazili o ustreznosti ter slikovnim materialom; | - marking welds, producing documentation with proof of conformity and pictorial material; | kpl | 1 |  | 0
4.28 | Ognjeodporna tesnilna masa, vgradnja na prehodu cevovodov skozi zid med požarnima sektortjema, požarna odpornost 90 minut, ustreza proizvod HILTI ali enakovredno. | Fire-resistant sealant, for installation at the transition of pipelines through the wall between the two fire sectors, fire resistance 90 minutes, equivalent to HILTI or equivalent.
| Vsak prehod mora biti označen z nalepko ali tablico z osnovnimi požarnimi podatki; | Each passageway must be marked with a sticker or placard with basic fire information; | kpl | 1 |  | 0
4.29 | Preizkusno obratovanje delovanja sistema v obsegu: | Operational test of the system in scope:
| - pregled instalacije, armatur in opreme, | - inspection of plumbing, fixtures and fittings,
| - pregled delovanja naprav, elementov regulacije in nastavitve parametrov, | - overview of the operation of the devices, control elements and parameter settings,
| - pregled cirkulacije glikolnega medija, | - checking the circulation of the glycol medium,
| - kontrola predpisanih parametrov glikolnega medija | - control of the prescribed parameters of the glycol medium
| Preizkusno obratovanje traja neprekinjeno 72 ur. | The test operation shall be continuous for 72 hours. | kpl | 1 |  | 0
4.30 | Napisne ploščice iz nerjavne pločevine z vgravirano oznako po shemi za opremo in armature, kompletno z jekleno pritrdilno žico ali visoko kvalotetne nalepke; visoko trajanje H (več kot 15 let) | Stainless steel nameplates with engraved marking according to the scheme for fittings and fixtures, complete with steel fixing wire or high quality labels; high durability H (more than 15 years) | kpl | 1 |  | 0
4.31 | Samolepilne puščice za označitev smeri pretoka ter z napisom vrste medija; visoko trajanje H (več kot 15 let) | Self-adhesive arrows to indicate direction of flow and type of media; high H lifetime (more than 15 years) | kpl | 1 |  | 0
4.32 | Izdelava montažnih risb za izvedbo inštalacij med gradnjo objekta, kot so: detajli priključkov, montažne skice, montažni detajli, ipd. | Preparation of assembly drawings for the installation of services during the construction of the building, such as: connection details, assembly sketches, assembly details, etc. | kpl | 1 |  | 0
4.33 | Kvalifikacije montaže IQ-pregledi (instalation qualification) po GEP Commissioning protokolu in dokumentiranje kvalifikacije montaže, vključno z odpravo prvotnih napak montaže; | Installation qualification IQ-checks (installation qualification) according to the GEP Commissioning Protocol and documentation of installation qualification, including correction of original installation faults; | kpl | 1 |  | 0
4.34 | Meritve delovanja OQ-kvalifikacija (operation qualification) ter dokumentiranje meritev delovanja, vključno z nastavitvijo parametrov; | OQ (operation qualification) measurements and documentation of performance measurements, including parameter settings; | kpl | 1 |  | 0
4.35 | Posnetki izvedenega stanja, sprotno beleženje vseh sprememb nastalih med izvedbo, vrisovanje in vpisovanje v PZI projektno dokumentacijo; | Recording of the as-built condition, keeping a running record of any changes made during execution, plotting and entering into the PZI project documentation; | kpl | 1 |  | 0
4.36 | Stenska shema sistema, vloženo v zaščitni okvir s prosojnim umetnim steklomo (plastika) ali plastificirano, vključno s pritrditvijo na notranjo steno v strojnici objekta; | Wall diagram of the system, enclosed in a protective frame with transparent plastic or plasticised glass, including fixing to an internal wall in the mechanical room of the building; | kpl | 1 |  | 0
4.37 | Primopredajna dokumentacija, ki mora vsebovati: izjave, dokazilo o zanesljivosti objekta, certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo, obratovanje in vzdrževanje ter ostalo primopredajno dokumantacijo. Predaja se v dveh mapiranih izvodih ter en izvod v elektronski obliki; | The handover documentation, which shall include: declarations, proof of the reliability of the facility, certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use, operation and maintenance, and other handover documentation. It shall be handed over in two mapped copies and one copy in electronic form; | kpl | 1 |  | 0
| GLIKOLNI MEDIJ KLIMATIZACIJA | GLYCOL MEDIUM AIR CONDITIONING |  |  |  | 0