## 0_Naslovnica
OPOZORILO! Vsi prevodi v angleščino so strojno izdelani in zgolj informativne narave. V primeru kakršnekoli nejasnosti ali dvoma izključno velja izvirno besedilo v slovenščini. WARNING! All translations into English have been produced by machine translation and are provided for informational purposes only. In the event of any ambiguity or uncertainty, the original Slovenian text shall prevail exclusively.
| / | / | [5 empty] | /
| Sprem./Rev.: | Opis spremembe/Description of Changes: | [5 empty] | Datum/Date: | Podpis/Signature:
| Investitor/Investor: |  |  |  |  | Gradnja/Facility
|  |  | Univerza v Ljubljani Kongresni trg 12 1000 Ljubljana, Slovenija |  |  | Fakulteta za strojništvo/Faculty of Mechanical Engineering
| Projektant/Design Engineer: |  |  |  |  | Del objekta/sistem/Building/System:
|  |  | IBE, svetovanje, projektiranje in inženiring Ljubljana, Slovenija |  |  | STAVBA FAKULTETE/FACULTY BUILDING
| Projektant/Design Engineer: |  |  |  |  | Vrsta načrta/Documentation:
4 NAČRT S PODROČJA STROJNIŠTVA/ DOC. IN THE FIELD OF MECHANICAL ENGINEERING
|  | Ime in priimek/Name and Surname: |  |  | Id. št./Id. No: | Vsebina risbe (dokumenta)/Document Title:
| Vodja proj./ Des. Manager: | Boštjan Vuga, univ. dipl. inž. arh., grad. dip. (AA) |  |  | ZAPS 0035 PA PPN | PR. POPIS STROJNIH DEL/BOQ OF MECH. WORKS 4/8 Vodovod in kanalizacija/Water Supply and Sewerage
| Poobl. strok./ Cert. Profess.: | Sašo Ocvirk, univ. dipl. inž. str. |  |  | IZS S-0717
| Poobl. strok./ Cert. Profess.: |  |  |  |  | Št. proj./ Proj. No.: | 362-19 |  | Vrsta dokument./ Document. Type: | DZR
| Izdelal/ Creator: | Sašo Ocvirk, univ. dipl. inž. str. |  |  | IZS S-0717 | Klas. ozn./ Class. No.: | -- |  | Stran/ Page: | 1/*
| Datum/ Date: | maj/May 2026 |  | Merilo/ Scale: | / | Ident. ozn./ Id. No: | JULFS--6S0802P

## 0_Osebe
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
POOBLAŠČENI STROKOVNJAKI, ODGOVORNI ZA IZDELAVO PROJEKTANTSKEGA POPISA:
Id. št. ZAPS/IZS | Pooblaščeni strokovnjak | Strokovno področje
IZS S-0717 | Sašo Ocvirk, univ. dipl. inž. str. | Vodovod in kanalizacija
SODELAVCI PRI IZDELAVI PROJEKTANTSKEGA POPISA:
CERTIFIED EXPERTS RESPONSIBLE FOR ELABORATING THE BILL OF QUANTITIES:
Id. No ZAPS/IZS | Certified Expert | Area of Expertise
IZS S-0717 | Sašo Ocvirk, univ. dipl. inž. str. | Water supply and sewerage
COLABORATORS IN THE ELABORATING THE BILL OF QUANTITIES:

## 0.1_Uvod-STP
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
0.1 | SPLOŠNI TEHNIČNI POGOJI | GENERAL TECHNICAL CONDITIONS
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic operator with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
0.1.1 | Izvajalec se obveže, da bo upošteval veljavno zakonodajo, ki ureja graditev objektov v Republiki Sloveniji, vključno s povezanimi podzakonskimi akti, predpisi, tehničnimi smernicami, standardi, pravili stroke in dobro gradbeno prakso. Prav tako mora izvajalec upoštevati vse zahteve izdanega integralnega gradbenega dovoljenja in vsa dela izvesti skladno s projektno dokumentacijo ter ostalimi pogoji, objavljenimi v razpisni dokumentaciji. | The Contractor undertakes to comply with the applicable legislation governing the construction of buildings in the Republic of Slovenia, including related by-laws, regulations, technical guidelines, standards, professional rules and good construction practice. The Contractor shall also comply with all the requirements of the integral building permit issued and shall carry out all works in accordance with the project documentation and other conditions published in the tender documentation.
0.1.2 | Dela lahko izvaja samo izvajalec, ki je registriran za opravljanje gradbene dejavnosti in ima za tovrstna dela ustrezno zavarovanje za škodo, certifikate, tehnično izobražen kader, sredstva ter je usposobljen za samostojno pripravo in izvedbo del. | The work may only be carried out by a contractor who is registered to carry out construction work and who has the appropriate insurance for such work, certificates, technically trained staff, resources and is qualified to prepare and carry out the work independently.
0.1.3 | Izvajalec odgovarja za kakovost izvedbe vseh del. | The Contractor shall be responsible for the quality of the execution of all works.
0.1.4 | Izvajalec nosi vso odgovornost za nesreče in škodo, ki nastane na objektu ali v okolici zaradi njegovega dela. | The Contractor shall bear all liability for accidents and damage to the installation or the surrounding area caused by his work.
0.1.5 | Pred oddajo ponudbe se je izvajalec dolžan seznaniti z območjem predvidenim za gradnjo in temu prilagoditi vsa potrebna dela, kar mora biti zajeto v ponudbi. V neposredni bližini predvidene gradnje se nahajajo stavbe, v katerih potekajo izobraževalni in raziskovalni procesi. Zato bo izvajalec moral izvajati kontrolo hrupa in kontrolo vibracij. Dela, ki so hrupna in dela, ki povzročajo vibracije bo izvajalec moral preprečiti oziroma jih izvesti na način, da povzročajo minimalne vplive. Tehnologijo rušenja, pilotiranja in tehnologijo izvedbe ostalih del bo izvajalec moral prilagoditi tako, da bo vpliv minimalen. Izvajalec mora preprečiti in zmanjšati emisije delcev iz gradbišča na najmanjšo možno mero. | Before submitting a tender, the contractor is obliged to familiarise himself with the area to be constructed and to adapt any necessary works accordingly, which must be included in the tender. In the immediate vicinity of the proposed construction, there are buildings in which educational and research processes take place. The contractor will therefore be required to carry out noise and vibration control. Noise and vibration works will have to be avoided or carried out in such a way as to minimise the impact. Demolition, piling and other works will have to be adapted to minimise the impact. The contractor must avoid and minimise the emission of particulates emitted from the construction site as far as is reasonably practicable.
0.1.6 | Izvajalec je pred oddajo ponudbe dolžan pregledati projektno dokumentacijo in ostale pogoje, ki so del razpisne dokumentacije V primeru morebitnih napak in neskladij je izvajalec dolžan na to opozoriti naročnika pred oddajo ponudbe. | The Contractor is obliged to review the project documentation and other conditions forming part of the tender documentation before submitting the tender In case of any errors or inconsistencies, the Contractor is obliged to bring these to the attention of the Contracting Authority before submitting the tender.
0.1.7 | Pred oddajo ponudbe je izvajalec dolžan preveriti ustreznost popisov del in količin v teh popisih ter njihovo skladnost z ostalimi dokumenti projektne dokumentacije, ki so del razpisne dokumentacije. Prav tako je izvajalec dolžan preveriti vse detajle in sheme. Vse izmere je potrebno preveriti po posameznih projektih oz. načrtih, ki sestavljajo razpisno dokumentacijo. V primeru ugotovljenih neskladij je v času priprave ponudbe obvezan o tem obvestiti naročnika. | Before submitting a tender, the Contractor shall check the adequacy of the inventories of works and quantities in these Bills of Quantities and their conformity with the other documents of the project documentation forming part of the tender documentation. The Contractor shall also check all details and diagrams. All measurements shall be checked against the individual projects or plans forming part of the tender documentation. In the event of any discrepancies, the Contractor shall inform the Contracting Authority at the time of preparing the tender.
0.1.8 | Pred oddajo ponudbe je izvajalec dolžan v tem popisu preveriti zmnožke in seštevke ter prenose le-teh v rekapitulacijo. Izvajalec se s pripravo ponudbe obvezuje, da je prebral vse celice in elemente celotnega popisa, vključno z vsemi postavkami in splošnimi navodili ali določili in je preveril pravilnost preračuna ter s tem zagotavlja ponudbeno vrednost. | Before submitting a tender, the Contractor is required to check the products and totals in this Bill of Quantities (BoQ) and their transfer to the recapitulation. The Contractor undertakes, by preparing a tender, to have read all the cells and elements of the complete BoQ, including all headings and general instructions or provisions, and to have checked the correctness of the conversion, thereby guaranteeing the value of the tender.
0.1.9 | Dela bo izvajalec moral izvajati po predloženi projektni dokumentaciji, detajlih in z upoštevanjem navodil in potrditev projektanta, nadzornika in investitorja. Vso potrebno delavniško dokumentacijo zagotovi izvajalec del v okviru ponujene cene. | The Contractor shall carry out the works in accordance with the submitted design documents, details and subject to the instructions and approvals of the Designer, the Supervisor and the Investor. All necessary workshop documentation shall be provided by the Contractor within the scope of the price quoted.
0.1.10 | Pred izvedbo posameznih del je izvajalec dolžan pregledati projektno dokumentacijo za izvedbo gradnje (PZI) in elaborate. Na morebitne napake v dokumentaciji ali neskladja med posameznimi načrti ali deli načrtov (popisi del, tehnična poročila, lokacijski in tehnični prikazi) izvajalec opozori nadzornika in projektanta, in se z njima pravočasno uskladi. | The Contractor shall review the Detailed Design documentation (PZI) and the studies before carrying out the individual works. The Contractor shall draw the attention of the Supervisor and the Designer to any errors in the documentation or discrepancies between the individual designs or parts of designs (BoQ, technical reports, location and technical drawings) and shall coordinate with them in good time.
0.1.11 | Tehnični opisi, prikazi, detajli, sheme ter ostali dokumenti v PZI dokumentaciji predstavljajo dodaten opis popisnih postavk gradbeno obrtniških in inštalacijskih del ter jih je potrebno dosledno upoštevati skupaj s popisom del. | The technical descriptions, illustrations, details, diagrams and other documents in the Detailed Design documentation (PZI) are additional descriptions of the BoQ inventory items of the building, construction and installation works and must be strictly followed together with the BoQ.
0.1.12 | Specifikacije in zahteve, navedene v popisu, se ne smejo upoštevati kot edine zahteve. Izvajalec je dolžan v ceni zajeti in dobaviti vse elemente opreme ter opraviti dela in storitve, ki niso eksplicitno navedeni, a so bistvenega pomena za funkcionalnost, skladnost s predpisi ter kontinuirano, zanesljivo in varno obratovanje opreme. | The specifications and requirements set out in the BoQ shall not be taken as the only requirements. The Contractor shall be obliged to include in the price and supply all items of equipment and to carry out works and services which are not expressly mentioned but which are essential for the functionality, regulatory compliance and continuous, reliable and safe operation of the equipment.
0.1.13 | Vsa dela morajo biti izvedena kvalitetno in iz materialov z zahtevanimi lastnostmi, izvedena skladno z veljavno zakonodajo in z upoštevanjem navodil za vgradnjo za izbrane materiale in opremo, s predložitvijo predpisanih izjav o lastnostih in/ali certifikatov. Vsi gradbeni proizvodi (GP) morajo biti označeni s CE oznako. | All work shall be of good quality and be executed with materials of the required characteristics, in accordance with the applicable legislation and in compliance with the installation instructions for the materials and equipment selected, and shall be accompanied by the prescribed declarations of performance and/or certificates. All construction products (GP) shall bear the CE marking.
0.1.14 | Za vsako opisano delo v popisu je potrebno upoštevati celotno potrebno delo, ves osnovni in pomožni material, prevoz materiala in orodja na objekt, notranje transporte, delovne in pomožne odre, zaključno čiščenje in odstranitev odpadkov po dovršenem delu. | For each work described in the inventory, the total work required, all basic and ancillary materials, the transport of materials and tools to the site, internal transports, working and ancillary scaffolding, final cleaning and the disposal of waste after the work has been completed must be taken into account.
0.1.15 | Vsa delovna sredstva, organizacija in koordinacija del, pripravljalna, spremljajoča in zaključna dela, potrebni montažni in tesnilni materiali ter podkonstrukcije so sestavni del posameznih postavk. | All labour, organisation and coordination of the works, preparatory, accompanying and finishing works, necessary prefabrication and sealing materials and substructures are part of the individual items.
0.1.16 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - načrt organizacije gradbišča s podrobnim terminskim planom in izvedba vseh pripravljalnih del, postavitev, organizacija, zaščita in prijava gradbišča, gradbiščnih objektov, ureditev začasnih deponij, tekoče vzdrževanje, skupaj s plačilom splošnih stroškov pristojbin in davkov upravnih organov, pridobivanju raznih dovoljenj in soglasij za izvedbo, ograditev gradbišča in postavitev gradbene table in prometne signalizacije, zagotavljanje ustrezne varnosti na gradbišču, tekoče vzdrževanje in končna odstranitev gradbišča; - zagotovitev potrebnih začasnih površin za transportne poti in gradnjo izven območja gradbišča s plačilom stroškov za sanacijo in vzpostavitev okoliških zemljišč in objektov v prvotno stanje (soglasja, odškodnine, itd.); - začasni odvoz, deponiranje in vračanje izkopanega materiala, ki ga ne bo možno deponirati na gradbišču; - odvoz in zagotovitev odstranjevanja odpadnega gradbenega materiala skladno z zakonodajo na področju ravnanja z odpadki (odvoz na urejene deponije s plačilom komunalnih prispevkov in taks itd.); - oteženi izkop v mokrem terenu, izkop v vodi, odvod meteorne vode iz gradbene jame in vode, ki se izceja iz bočnih strani izkopov; - ustrezno varovanje izkopa gradbene jame za objekt in ostalih manjših posameznih izkopov za izvedbo komunalne infrastrukture brez posegov na sosednja zemljišča; - ustrezno varovanje obstoječih objektov, infrastrukture in okolice v času gradnje ter dokumentiranje vseh morebitnih škodnih dogodkov; - pripravljalna, spremljajoča in zaključna dela (zakoličbe, zagotovitev potrebnih komunalnih priključkov za potrebe izvajanja gradnje, izvedba začasnih inštalacij, označevanje podzemnih vodov, postavljanje in vzdrževanje zakoličbenih profilov, izvedba in označevanje novih in starih križanj ter morebitna zaščita križanj komunalnih vodov, geodetski posnetki in izdajanje vmesnih posnetkov izvedene infrastrukture naročniku, izdelava zbirnih kart, itd.), v kolikor ni to drugače določeno; - pridobivanje soglasij in izvedba morebitnih zapor na vseh cestah s plačilom stroškov, nadomestil in pristojbin; - zagotovitev oz. postavitev in končna odstranitev po zaključku gradnje začasnih skladišč in začasnega pisarniškega kontejnerskega objekta vključno z opremo za dve delovni mesti in za skupne operativne sestanke vel. ca. 40 m2 za potrebe naročnika, s tekočim vzdrževanjem in čiščenjem. | The following must also be included or taken into account in the uniform prices for individual items: - a construction site organisation plan with a detailed timetable and the execution of all preparatory works, the setting-up, organisation, protection and registration of the construction site, site facilities, the arrangement of temporary storage facilities, ongoing maintenance, including the payment of general costs of fees and taxes of the administrative authorities, the obtaining of various permits and consents for the execution, the fencing of the site and the erection of construction signs and traffic signals, the provision of adequate security on the site, ongoing maintenance and the final dismantling of the construction site; - provision of the necessary temporary areas for transport routes and off-site construction, with costs for restoration and reinstatement of surrounding land and buildings (consents, compensation, etc.); - temporary removal, storage and return of excavated material that cannot be stored on site; - removing and disposing of waste building materials in accordance with waste management legislation (removal to regulated landfill sites with payment of municipal fees and charges, etc.); - difficult excavation in wet ground, excavation in water, drainage of rainwater from the construction pit and water draining from the sides of excavations; - adequate protection of the excavation of the construction pit for the building and other small individual excavations for the implementation of the utility infrastructure without encroaching on neighbouring land; - adequate protection of existing facilities, infrastructure and the surrounding area during construction, and documentation of any damage incidents; - preparatory, accompanying and finishing works (stake-out, provision of the necessary utility connections for the needs of construction, execution of temporary installations, marking of underground lines, installation and maintenance of stake-out profiles, execution and marking of new and old crossings and possible protection of crossings of utility lines, geodetic surveys and issuing of intermediate images of the completed infrastructure to the client, production of summary maps, etc.), unless otherwise specified; - obtaining consents and implementing any road closures, with costs, compensation and fees; - provision or erection and final removal on completion of construction of temporary storage and temporary office container building including equipment for two workstations and for joint operational meetings of approx. 40 m2 for the needs of the client, with ongoing maintenance and cleaning.
0.1.17 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - izdelava montažne tehnične dokumentacije, detajlov izvedbe in vse druge potrebne delavniške dokumentacije (s področja arhitekture, gradbeništva, elektrotehnike, strojništva in zunanje ter krajinske ureditve) ter pridobitev obvezne potrditve s strani projektanta, nadzornika in investitorja; - odprava vseh vrst inštalacijskih kolizij z izvajanjem potrebnih premikov inštalacij in njihovim usklajevanjem na mestu montaže, vse v obsegu, ki ne vpliva na projektirano rešitev ali tip inštalacij oz. opreme; - zagotavljanje kompletnosti elektro-instalacijskih sistemov s področja avtomatike za doseganje njihove popolne funkcionalnosti delovanja; - stroški za nadzor in koordinacijo izvedbe vseh elektro napeljav, ki so predmet končne instalacije proizvoda (senčila, vrata, okna,…); - izdelava montažnih skic in detajlov za izvedbo v dogovoru z vodjo gradnje in nadzornikom; - izdelava in predstavitev vzorcev v ustrezni velikosti za potrditev projektanta, nadzornika in investitorja; - zagotavljanje varnosti in zdravja pri delu, zlasti izvajanje vseh del, ki izhajajo in ukrepov, ki izhajajo iz določil veljavnih predpisov varstva pri delu in zahtev Varnostnega načrta;- stroški garancij, ki jih mora izvajalec predložiti naročniku. | The following must also be included or taken into account in the uniform prices for individual items: - preparation of prefabricated technical documentation, construction details and all other necessary workshop documentation (architectural, civil, electrical, mechanical, exterior and landscaping) and obtaining the mandatory approval of the designer, the supervisor and the investor; - elimination of all types of installation conflicts by carrying out the necessary relocation of installations and their coordination at the installation site, all to the extent that it does not affect the design solution or the type of installation or equipment; - ensuring the completeness of electrical installation systems in the automation sector to achieve their full operational functionality; - the cost of supervising and coordinating the installation of all the electrical installations that are the subject of the final installation of the product (blinds, doors, windows, etc.); - preparation of erection drawings and details for implementation in agreement with the construction manager and supervisor; - production and presentation of samples in appropriate sizes for the approval of the designer, the supervisor and the investor; - ensuring health and safety at work, in particular the implementation of all the works arising from and the measures resulting from the provisions of the applicable occupational safety regulations and the requirements of the Safety Plan; - the cost of the guarantees to be provided by the contractor to the client.
0.1.18 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - strošek vodje del glavnega izvajalca, ki bo izvajal tudi koordinacijo s podizvajalci in z drugimi izvajalci, ki jih bo izbral naročnik in bo opravljal delo vodje gradbišča; - koordinacija del z ostalimi izvajalci oz. podizvajalci del, projektantom, nadzornikom in investitorjem pri medsebojnem usklajevanju organizacije gradbišča in časovnega načrta del ter pri usklajevanju izdelave plana montaže, potrjenih s strani vseh udeležencev gradnje; - stroški koordinacije, sodelovanja in usklajevanja z dobavitelji tehnološke, laboratorijske, eksperimentalne in vse ostale pohištvene ter multimedijske opreme ter z vsemi ostalimi dobavitelji oz. podizvajalci na objektu; - stroški izdelave situacij; - stroški zavarovanja objekta v času izvedbe del in delavcev ter materiala na gradbišču v času izvajanja del, od začetka del do pridobitve uporabnega dovoljenja za objekt. Zavarovanje mora biti sklenjeno pri ustrezni zavarovalni družbi najmanj v višini pogodbene vrednosti ali v zakonsko predpisani vrednosti (v kolikor zavarovanje v višini pogodbene vrednosti presega zakonsko dovoljeno), za ves čas trajanja izvedbe del do uspešne primopredaje objekta; - preizkušanje kvalitete materiala, ki se vgrajuje in dokazovanje kvalitete s certifikati oz. tehničnimi soglasji; - izvedba vseh zahtevanih testov in preizkusov (npr. tlačni preizkusi, termografski pregledi, meritve elektromagnetnega sevanja, hrupa, itd.), poskusnega obratovanja celotnega objekta s poudarkom na vseh inštalacijah ter izvajanje predpisanega monitoringa v skladu s Poročilom o vplivih na okolje (pred gradnjo, med gradnjo in po končani gradnji); - izdelava izkaza požarne varnosti, vključno s sprotnim spremljanjem gradnje in izvajanjem požarnovarnostnih zahtev ter izdelava Požarnega reda z obveznimi prilogami; - izdelava Izkaza zaščite pred hrupom v stavbah; - izdelava Izkaza energijskih lastnosti stavbe in energetske izkaznice; - sodelovanje z izvajalci gradbenega in projektantskega nadzora in investitorjem za izvedbo tehničnega pregleda in priprava primopredaje, ki mora vsebovati vso zahtevano dokumentacijo, predvsem pa: izjave o skladnosti, požarni izkaz in ostale izkaze ter obvezne tabele, dokazilo o zanesljivosti objekta (DZO), certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo in vzdrževanje ter vse ostale dokumente v skladu s predpisi in pogodbenimi določili. | The following must also be included or taken into account in the uniform prices of the individual items: - the cost of a works manager for the main contractor, who will also coordinate with subcontractors and other contractors selected by the client and act as site manager; - coordination of the works with other contractors or subcontractors, the designer, the supervisor and the investor in coordinating the organisation of the construction site and the timetable for the works, and in coordinating the production of an installation plan approved by all the participants in the construction; - the costs of coordination, cooperation and coordination with suppliers of technological, laboratory, experimental and all other furniture and multimedia equipment, as well as with all other suppliers or subcontractors on the site; - the cost of drawing up situations; - the cost of insuring the building during the execution of the works and the workers and materials on site during the execution of the works, from the start of the works until the building has been licensed for occupation. The insurance must be taken out with a suitable insurance company for at least the contract value or the legal value (if the insurance for the contract value exceeds the legal value), for the entire duration of the works until the successful handover of the building; - testing the quality of the material to be installed and proving it with certificates or technical approvals; - carrying out all required tests and trials (e.g. pressure tests, thermographic inspections, electromagnetic radiation measurements, noise measurements, etc.), trial operation of the entire building, with emphasis on all installations, and carrying out the required monitoring in accordance with the Environmental Impact Assessment Report (before, during and after construction); - preparation of a fire safety statement, including ongoing monitoring of construction and implementation of fire safety requirements, and preparation of a Fire Safety Order with mandatory annexes; - preparation of a Noise Protection Statement for buildings; - preparation of the Building Energy Performance Report and Energy Performance Certificate; - cooperation with the construction and design supervision contractors and the investor to carry out the technical inspection and prepare the handover, which must include all the required documentation, in particular: declarations of conformity, fire and other statements and mandatory tables, proof of reliability of the building (DZO), certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use and maintenance, and all other documents in accordance with the regulations and the contractual provisions.
0.1.19 | V enotnih cenah posameznih postavk, ki se nanašajo na opremo in posamezne sisteme, mora biti zajeto oz. upoštevano tudi naslednje: - dobava oz. transport, - stroški za vse delovne stroje za dvigovanje bremen in delovne košare za dostope do delovišč; - morebitni stroški povzročeni upravljavcem GJI, ki bi nastali v zvezi s predmetno gradnjo; - montaža, vključno s pomožnim montažnim materialom (vezni, tesnilni in pritrdilni material, sidra, nosilni profili, podkonstrukcije in podobno) in navodili proizvajalca, - odprava vseh kolizij sistemov s stenami in med sistemi, - izvedba vseh potrebnih tesnjenj, - priključitev in nastavitve, vključno z morebitnim kalibriranjem, - zagon, testiranje in meritve, vključno s poročili, - šolanje uporabnikov oz. vzdrževalnega osebja za uporabo in vzdrževanje sistemov, - navodila za obratovanje in vzdrževanje, - vsi potrebni certifikati, izjave o skladnosti oz. potrdila ter - vsa druga pomožna dela in material, da se zagotovi funkcionalnost posamezne postavke popisa. | The following must also be included or taken into account in the uniform prices for individual items relating to equipment and individual systems: - delivery/transport, - the cost of all lifting machines and work baskets for access to work sites; - any costs incurred to the operators of utility infrastructure (GJI) in connection with the subject construction; - installation, including ancillary installation materials (bonding, sealing and fixing materials, anchors, support profiles, substructures, etc.) and manufacturer's instructions, - eliminating all system-to-wall and system-to-system collisions, - all necessary sealing work, - connection and set-up, including calibration if necessary, - commissioning, testing and measurements, including reports, - training users or maintenance staff in the use and maintenance of the systems, - operating and maintenance instructions, - any necessary certificates, declarations of conformity or attestations; and - all other ancillary works and materials to ensure the functionality of each inventory item.
0.1.20 | Vsi odri morajo biti upoštevani v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All scaffolding must be included in the uniform prices of the items listed, except where specifically mentioned.
0.1.21 | Vsi delovni in pomožni odri, lestve in ostala potrebna pomožna sredstva, kot tudi čiščenje vseh elementov po končanih delih, mora biti upoštevano v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All working and auxiliary scaffolding, ladders and other necessary ancillaries, as well as the cleaning of all elements after completion of the works, shall be included in the uniform prices of the items listed, except those specifically mentioned.
0.1.22 | Delavniško dokumentacijo za vse nosilne jeklene konstrukcije in podkonstrukcije izdela izvajalec, strošek izdelave delavniške dokumentacije se upošteva v ponujenih cenah in se ne obračuna posebej. | The cost of the shop drawings for all steelwork and substructures shall be included in the prices quoted and shall not be charged separately.
0.1.23 | V enotnih cenah postavk mora biti vključeno tudi vgrajevanje vseh instalacijskih razvodov v opaže armirano betonskih elementov in izdelava prehodov inštalacij ter dodatno izrezovanje utorov in prebojev v kamnite, zidane ali armirano-betonske stene, ponovno demontiranje in montiranje vseh vrst montažnih sten, vsa dodatna dela za zagotavljanje primernih križanj med posameznimi instalacijskimi vodi, izdelava vseh vrst ojačitev konstrukcij in podobna dela, ki zagotavljajo kakovostno vgradnjo vseh vrst instalacijskih vodov in niso posebej navedena v popisu GOI del. V ponudbi morajo biti upoštevana vsa drobna strojna in elektro instalacijska dela in transporti. | The installation of all installation ducts in the formwork of reinforced concrete elements and the construction of installation penetrations, as well as the additional cutting of grooves and penetrations in stone, masonry or reinforced concrete walls, the reassembly and reinstallation of all types of prefabricated walls, all additional work to ensure adequate crossings between individual installation ducts, the construction of all types of structural reinforcement and similar work to ensure the quality installation of all types of installation ducts and not specifically mentioned in the BoQ of the Construction, installation and finishing works (GOI) shall also be included in the uniform prices of the items. The tender shall take into account all minor mechanical and electrical installation work and transport.
0.1.24 | Vsi kovinski elementi in konstrukcije, ki bi lahko bili izpostavljeni atmosferskim in ostalim korozijskim vplivom, morajo biti ustrezno protikorozijsko zaščiteni. | All metallic elements and structures that could be exposed to atmospheric and other corrosive influences must be adequately protected against corrosion.
0.1.25 | Za vse večje jeklene dele se skladno s predpisi, izdelajo ustrezne ozemljitve, nevidno pritrjene in speljane na splošno ozemljitev objekta. | For all major steel parts, appropriate earth connections shall be made in accordance with the regulations, invisibly attached and connected to the general earth of the building.
0.1.26 | Za vse vidne elemente in serijske elemente je obvezna predhodna uskladitev obdelav, barv in materialov s projektantom na podlagi dostavljenih vzorcev v ustrezni velikosti. Obvezna je preveritev dejanskih mer na licu mesta in posledična prilagoditev elementov in njihove montaže. | For all visible elements and serial elements, it is mandatory to coordinate the finishes, colours and materials with the designer beforehand on the basis of the supplied samples in the appropriate size. It is mandatory to check the actual dimensions on site and to adjust the elements and their installation accordingly.
0.1.27 | Dimenzije obrtniških izdelkov in količine je potrebno pred naročanjem preveriti na objektu. Potrebna je uskladitev vseh elementov (kljuke, okovje, detajlne konstrukcije in obdelave, itd.) s projektantom, nadzornikom in investitorjem. Izvajalec je dolžan pred izdelavo predložiti projektantu v potrditev ustrezne delavniške načrte in detajle. | The dimensions of the workmanship and quantities must be checked on site before ordering. All elements (hooks, fittings, detailed construction and finishes, etc.) must be coordinated with the designer, the supervisor and the investor. The contractor is obliged to submit the relevant workshop plans and details to the designer for approval before manufacture.
0.1.28 | V posameznih postavkah popisa so navedeni proizvajalci in/ali tipi posameznih sistemov, materialov ali opreme, s čimer so zgolj natančno opredeljene zahtevane tehnične lastnosti. Izvajalec del lahko ponudi nadomesten sistem, material ali opremo drugega proizvajalca in tipa, pri čemer morajo biti tehnične lastnosti ponujenega sistema, materiala ali opreme enakovredne ali boljše od opredeljenih v popisu, dimenzijsko pa ne smejo presegati projektiranih dimenzij. Vse funkcijske in tehnične karakteristike nadomestnih sistemov, materialov ali opreme mora izvajalec dokazati z ustrezno dokumentacijo. Vse morebitne posledice zaradi spremembe sistemov, materialov ali opreme vključno z morebitnimi spremembami oz. dopolnitvami BIM modelov in projektne dokumentacije, stroškovno in časovno bremenijo izvajalca. | The individual items of the Inventory shall specify the manufacturers and/or types of the individual systems, materials or equipment, thereby merely specifying the required technical characteristics. The Contractor may offer a substitute system, material or equipment of a different manufacturer and type, provided that the technical characteristics of the offered system, material or equipment shall be equivalent to or better than those specified in the BoQ, and shall not exceed the design dimensions. All functional and technical characteristics of the substitute systems, materials or equipment shall be demonstrated by the Contractor with appropriate documentation. Any consequences resulting from changes to systems, materials or equipment, including any changes or additions to the BIM models and project documentation, shall be borne by the Contractor in terms of cost and time.
0.1.29 | Vsako zamenjavo, uporabo in končni izbor nadomestnih sistemov, materialov, proizvodov in opreme morajo obvezno in pravočasno (pred dobavo in vgradnjo) pisno potrditi projektant (vseh sodelujočih strok), nadzornik in investitor. | Any replacement, use and final selection of alternative systems, materials, products and equipment must be approved in writing by the designer (of all disciplines involved), the supervisor and the investor in a timely manner (prior to delivery and installation).
0.1.30 | Izvajalec mora v ponudbeno ceno vključiti tudi: - ves čas gradnje sprotno beleženje sprememb oz. odstopanj od PZI dokumentacije, vključno z izdelavo tekstualnega opisa sprememb, - pripravo podlog na nivoju PZI, ki so potrebne za posodobitev oz. uskladitev BIM modela z izvedenim stanjem (LOD 500) in izdelavo projektne dokumentacije izvedenih del (PID), - mesečno predajanje potrjenih sprememb opreme in materiala, ki vplivajo na BIM model, v formatu IFC, - vzdrževanje in uporabljanje pri izvedbi zadnje veljavne revizije PZI dokumentacije, vključno z dopolnitvami PZI načrtov, ki so nastali zaradi sprememb med gradnjo. | The contractor must also include in the tender price: - keeping a record of changes or deviations from the construction documentation (PZI) throughout construction, including a textual description of the changes, - preparation of the Detailed Design (PZI) level documents required to update or align the BIM model with the as-built condition (LOD 500) and the preparation of the as-built project documentation for the works (PID), - monthly submission of approved equipment and material changes affecting the BIM model in IFC format, - maintenance and use in the execution of the last valid revision of the construction documentation (PZI), including additions to the construction design documentation (PZI) resulting from changes during construction.

## 0.2_Uvod-DGNB
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
0.2 | SPLOŠNI TEHNIČNI POGOJI ZA PODROČJE DGNB CERTIFICIRANJA | GENERAL TECHNICAL CONDITIONS FOR DGNB CERTIFICATION
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic entity with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
| Splošni pogoji za področje DGNB certificiranja predstavljajo dopolnilo splošnim tehničnim pogojem in ne odpravljajo drugih obveznosti in odgovornosti, ki jih ima izvajalec v skladu s predpisi in pogodbo. | The General Conditions for DGNB Certification are complementary to the General Technical Conditions and do not exclude other obligations and responsibilities that the Contractor has under the Regulations and the Contract.
0.2.1 | Izvajalec mora v svojih ponudbah upoštevati, da se bo objekt certificiral v skladu z zahtevami DGNB sistema certificiranja trajnostne gradnje, ter pravočasno (vsaj 60 dni pred vgradnjo posameznega produkta) dostaviti vso ustrezno dokumentacijo za vse v ponudbi zajete materiale, elemente in opremo. Zahtevana je uporaba materialov, elementov ali opreme, ki so okolju in ljudem prijazni, energetsko učinkoviti in obenem ustrezajo zahtevam DGNB sistema. Zahtevan nivo certifikata je: ZLATI CERTIFIKAT | The Contractor shall take into account in its tenders that the building will be certified in accordance with the requirements of the DGNB Sustainable Building Certification Scheme and shall deliver all relevant documentation for all materials, elements and equipment included in the tender in a timely manner (at least 60 days before the installation of each product). The use of materials, elements or equipment that are environmentally and human friendly, energy efficient and at the same time meet the requirements of the DGNB system is required. The required level of certification is: GOLD CERTIFICATE
0.2.2 | Podrobnejši opis DGNB sistema in navodila za posamezne kriterije so dostopna v dokumentu"DGNB Criteria Set New Construction Buildings, Version 2020 International", ki je na voljo na DGNB spletni strani https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria | A more detailed description of the DGNB system and guidance on the individual criteria is available in the document "DGNB Criteria Set New Construction Buildings, Version 2020 International", available on the DGNB website https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria
0.2.3 | Izvajalec mora v svojih ponudbah upoštevati, da je potrebno skladno z določili DGNB certifikacijskega sistema, pravočasno (pred pričetkom gradnje) dostaviti vso ustrezno dokumentacijo, za vse v ponudbi zajete materiale, elemente in opremo (tehnični list, varnostni list, izjava o lastnostih, tehnična navodila za ravnanje, servisiranje, vzdrževanje,...) v slovenskem jeziku. Vgradnja kakršnihkoli materialov, elementov ali opreme, se izvede zgolj na podlagi predhodne preveritve posredovane dokumentacije in obenem potrditve s strani nadzornika. | The Contractor must take into account in its tenders that, in accordance with the provisions of the DGNB certification system, all relevant documentation for all materials, elements and equipment included in the tender (technical data sheet, safety data sheet, declaration of properties, technical instructions for handling, servicing, maintenance,...) must be delivered on time (prior to the start of construction) in the Slovene language (in accordance with the provisions of the DGNB certification system). The installation of any materials, elements or equipment shall be subject to prior checking of the submitted documentation and, at the same time, to the approval of the Supervisor.
0.2.4 | Izbrani materiali, elementi, naprave, sistemi in oprema morajo prispevati k večji trajnosti stavbe v smeri zagotavljanja energetske učinkovitosti, ekonomičnega in enostavnega vzdrževanja ter čiščenja, dolge življenjske dobe, uporabe okolju prijaznih materialov ipd. | The materials, elements, appliances, systems and equipment chosen must contribute to the sustainability of the building in terms of energy efficiency, economic and easy maintenance and cleaning, long lifetime, use of environmentally friendly materials, etc.
0.2.5 | Predloženi dokumenti za vse uporabljene materiale, elemente in opremo morajo izpolnjevati zahteve najmanj kakovostne stopnje QS3 (zaželeno QS4), iz dokumenta: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001) | The documents submitted for all materials, components and equipment used shall meet the requirements of at least quality level QS3 (preferably QS4) of the document DGNB Quality Grades for Materials, Components and Equipment (JULFS--7X9001)
0.2.6 | V kolikor izbrani materiali oz. elementi, navedeni v posameznih postavkah, ne ustrezajo vsaj kakovostni stopnji QS3 iz seznama: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), je izvajalec dolžan na to opozoriti projektanta, nadzor in investitorja ter podati predlog ustreznega materiala oz. elementa. | If the selected materials or elements listed in the individual items do not meet at least quality level QS3 of the list of DGNB quality classes for materials, elements and equipment (JULFS--7X9001), the Contractor shall draw this to the attention of the Designer, the Supervisor and the Investor, and shall make a proposal for a suitable material or element.
0.2.7 | Izvajalec lahko v svoji ponudbi predlaga alternativne produkte in rešitve glede na predvidene s projektom, pod pogojem, da le-te prav tako izpolnjujejo vse navedene zahteve. Pri morebitnih predlaganih alternativnih produktih oz. rešitvah je potrebno upoštevati najmanj enake ali boljše lastnosti v smislu življenjske dobe, obstojnosti, ter enostavnosti in stroška čiščenja ter vzdrževanja v primerjavi s projektom predpisanimi rešitvami. Za alternativne rešitve izvajalec pridobi soglasje projektanta, nadzornika in investitorja pred pričetkom gradnje. | The Contractor may propose alternative products and solutions to those envisaged by the project in its tender, provided that they also meet all the requirements set out above. Any alternative products or solutions proposed shall have at least the same or better characteristics in terms of service life, durability, and ease and cost of cleaning and maintenance compared to the solutions envisaged by the project. For alternative solutions, the contractor shall obtain the agreement of the designer, the supervisor and the investor before starting construction.
0.2.8 | Izvajalec med gradnjo dnevno beleži vsa eventualna odstopanja od PZI projektne dokumentacije ter podatke pravočasno posreduje naročniku, nadzoru in projektantu. Potrjene spremembe vnese v podlage za izdelavo PID in posodobitev BIM modelov. | During construction, the Contractor shall record on a daily basis any deviations from the Detailed Design documentation (PZI) and shall provide the information to the Client, Supervision and the Designer in a timely manner. Confirmed changes shall be entered into the basis for the As-built documentation (PID) and BIM model updates.
0.2.9 | Izvajalec med gradnjo sproti izpolnjuje Seznam vseh konstrukcijskih sestav s pripadajočimi vgrajenimi gradbenimi materiali in dokumentira naslednje podatke o vgrajenih materialih (v slovenskem jeziku): - Varnostni list - Tehnični list - Izjavo o lastnostih (če je relevantno) - Izkazovanje morebiti obstoječega okoljskega certifikata (Tip I - okoljski znak ali Tip III - okoljska produktna deklaracija /EPD) - Izjavo proizvajalca ali dobavitelja, da produkt ustreza zahtevam ENV1.2 - Tehnična navodila za ravnanje, servisiranje, vzdrževanje oziroma ostale, z zakonom predpisane dokumente in dokumentacijo. | During construction, the Contractor shall keep a List of all structural assemblies with their associated construction materials and document the following information on the materials installed (in Slovene language): - Safety Data Sheet - Technical Data Sheet - Declaration of performance (if applicable) - Demonstration of any existing environmental certification (Type I - Ecolabel or Type III - Environmental Product Declaration /EPD) - A declaration by the manufacturer or supplier that the product complies with the requirements of ENV1.2 - Technical instructions for handling, servicing, maintenance or other documents and documentation required by law.
0.2.10 | Za vse vgrajene bistvene tehnične sisteme mora izvajalec zagotoviti obstoj pooblaščenega servisa, ki deluje na območju Republike Slovenije, da ima investitor možnost skleniti ustrezno pogodbo o vzdrževanju. Med bistvene tehnične sisteme sodijo npr.: sistemi ogrevanja in hlajenja, priprava tehnoloških medijev, prezračevanje in klimatizacija, sistemi detekcije in gašenja požara, sistemi tehničnega varovanja, BMS in CNS sistemi upravljanja stavbe, razsvetljava, komunikacijski in WI-FI sistemi,... | For all installed essential technical systems, the contractor must ensure the existence of an authorised service centre operating in the territory of the Republic of Slovenia, so that the investor has the possibility of concluding an appropriate maintenance contract. The essential technical systems include, for example: heating and cooling systems, technological media preparation, ventilation and air conditioning, fire detection and extinguishing systems, technical security systems, BMS and CNS building management systems, lighting, communication and WI-FI systems,...
0.2.11 | Zaželeno je, da imajo uporabljeni elementi in materiali okoljsko oznako Tip I. (kot npr. ENCODE, BLUE ANGEL, ipd...). | It is preferable that the elements and materials used have a Type I environmental label (such as ENCODE, BLUE ANGEL, etc...).
0.2.12 | Izvajalec bo za elemente iz lesa moral dokazovati izvor z navedbo izvorne države in tipa lesa, FSC / PEFC certifikat z dodatnim pripadajočim potrdilom Chain of custody-trgovski certifikat dobavitelja - ta se dokazuje z dobavnicami, računi ali enakovredno. Za izdelke iz naravnega kamna iz EU držav je potrebna deklaracija, da je izvor in procesiranje teh izdelkov v celoti v EU državah. Za izdelke iz naravnega kamna, ki prihajajo iz držav izven EU, je potrebno predložiti dokazilo o izpolnjevanju ILO konvencije 182, ki vključuje neodvisna inšpekcijska poročila. | For wood elements, the contractor will be required to provide proof of origin, indicating the country of origin and the type of wood, FSC/PEFC certification with an additional Chain of Custody certificate - the supplier's trade certificate - this shall be evidenced by delivery notes, invoices or equivalent. For natural stone products from EU countries, a declaration that the sourcing and processing of these products is entirely in EU countries is required. For natural stone products from non-EU countries, proof of compliance with ILO Convention 182, including independent inspection reports, is required.
0.2.13 | Izobraževanje udeležencev pri gradnji Izvajalec je dolžan vse udeležence pri gradnji podrobneje seznaniti tudi z relevantnimi koncepti, študijami, elaborati, ki opredelujejo trajnostni način gradnje za naslednja področja: - zaščita pred hrupom (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)) - zaščita pred prašenjem - zaščita tal in podzemne vode (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)), Analiza tveganja za onesnaženje vodnega telesa podzemne vode št. 0346-023/2023, maj 2023 (Geološko projektiranje d.o.o.)) - ravnanje z gradbenimi odpadki (Načrt gospodarjenja z gradbenimi odpadki) Izobraževanja se izvajajo skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.1 1.2, 2.2, 3.2 in 4.2 Training for the parties implementing the construction work | Training of construction participants The contractor is also obliged to inform all construction participants in detail about relevant concepts, studies, elaborations defining sustainable construction methods for the following areas: - noise protection (Environmental Impact Assessment Report No 100123-11523, dated 11.5.2023, supplemented on 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.)) - dust protection - protection of soil and groundwater (Environmental Impact Assessment Report No. 100123-11523, dated 11.5.2023, supplemented 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.), Risk analysis for contamination of the groundwater No. 0346-023/2023, May 2023 (Geološko projektiranje d.o.o.)) - construction waste management (Construction Waste Management Plan) The training shall be carried out in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.1 1.2, 2.2, 3.2 and 4.2 Training for the parties implementing the construction work
0.2.14 | Navodila za obratovanje in vzdrževanje objekta Izvajalec pripravi Navodila za obratovanje in vzdrževanje objekta skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilih: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual | Instructions for the operation and maintenance of the facility The Contractor shall prepare the Operation and Maintenance Instructions for the Facility in accordance with the applicable Slovenian legislation and the DGNB System Instructions specified in the Criteria: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual
0.2.15 | Meritve kontrole kakovosti gradnje Izvajalec mora upoštevati, da se bodo po koncu gradnje izvedle naslednje meritve: - meritve zrakotesnosti - meritve s termokamero (termografija) - meritve akustike - meritve zvočne zaščite ovoja stavbe - meritve zvočne zaščite ločilnih elementov med posameznimi prostori različnih namembnosti - meritve udarnega zvoka - meritve vlažnosti vgrajenih elementov, pred vgradnjo finalnih tlakov - test odvoda dima in toplote Meritve morajo opraviti ustrezno usposobljeni preskusni organi ali strokovnjaki ter rezultate oceniti in primerjati z zahtevami. Obseg opravljenih meritev mora biti sorazmeren z velikostjo zgradbe in mora ustrezno odražati cilj preverjanja kakovosti zgradbe. Smiselno je, da izvajalec del tekom gradnje za sprotno kontrolo kakovosti vgrajenih materialov, elementov in opreme, sam izvaja meritve. Končne meritve (ob primopredaji) izvede tretja oseba kot neodvisna potrditev doseganja zahtev. Meritve se izvajajo skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 2. Quality control measurements | Construction quality control measurements The contractor must take into account that the following measurements will be carried out after completion of the construction: - airtightness measurements - thermal camera measurements (thermography) - acoustics measurements - measurements of the sound insulation of the building envelope - measurements of the sound insulation of the separating elements between different rooms of different uses - impact sound measurements - moisture measurements of the installed elements, prior to the installation of the final flooring - smoke and heat extraction test The measurements shall be carried out by suitably qualified test bodies or experts and the results evaluated and compared with the requirements. The extent of the measurements carried out shall be proportionate to the size of the building and shall adequately reflect the objective of the building quality verification. It is reasonable for the contractor to carry out his own measurements during construction to check the quality of the materials, elements and equipment installed. Final measurements (at handover) are carried out by a third party as an independent confirmation of compliance with the requirements. The measurements shall be carried out in accordance with the applicable Slovenian legislation and the DGNB system instructions specified in the benchmark: PRO 2.2 2. Quality control measurements
0.2.16 | Zagotavljanje kakovosti za uporabljene gradbene proizvode Izvajalec mora zagotavljati izvajanje primerjav med definiranim in dejansko uporabljenim materialom, elementom ali opremo skladno seznamom: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), vključno z dokazno dokumentacijo ugotovitev primerjav ter skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 3.1 Quality assurance for the used construction products | Quality assurance for the construction products used The Contractor shall ensure that comparisons are made between the defined and the actual material, element or equipment used in accordance with the list: DGNB Quality Grades of Installed Materials, Elements and Equipment (JULFS--7X9001), including supporting documentation of the findings of the comparisons, and in accordance with the DGNB system instructions defined in the Criterion: PRO 2.2 3.1 Quality assurance for the used construction products
0.2.17 | Zaščita pred vlago Izvajalec predloži dokumentacijo, ki dokazuje, da je bil izveden program prezračevanja, prilagojen stavbi, s čimer se zagotovi pogoje, da so vgrajeni gradbeni elementi ustrezno suhi, skladno z navodili DGNB opredeljenimi v merilu: PRO 2.2 4.1 Mould prevention | Protection against moisture The Contractor shall provide documentation demonstrating that a building-specific ventilation programme has been implemented to ensure that the building elements installed are adequately dry, in accordance with the DGNB guidelines specified in the criteria: PRO 2.2 4.1 Mould prevention
0.2.18 | Preizkusi delovanja sistemov Izvajalec sodeluje pri izvedbi predhodnega in končnega preizkusa delovanja vseh bistvenih tehničnih komponent stavbe in pripravi ustrezne dokazne dokumentacije ter pri usposabljanju vzdrževalcev/upravljalcev stavbe, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators | System performance tests The Contractor shall be involved in the performance of the preliminary and final performance tests of all essential technical components of the building and the preparation of the relevant supporting documentation, as well as in the training of the maintenance/management staff of the building, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators
0.2.19 | Poročilo o zagonu objekta Izvajalec sodeluje pri pripravi končnega poročila o zagonu objekta, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 5.1 Creation of a detailed final report | Commissioning report The Contractor shall be involved in the preparation of the final commissioning report, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 5.1 Creation of a detailed final report
0.2.20 | Koncept celovitega delovanja sistemov v stavbi Izvajalec sodeluje pri procesu implementiranja stalnega nadzora in nastavitev delovanja stavbe ter usposabljanju vzdrževalcev/upravljalcev stavbe. Navedeno se izvede v skladu z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 6.1 Creation and handover of an integral operating concept | The concept of integrated building systems The contractor is involved in the process of implementing the building's continuous monitoring and settings and training the building's maintenance/management staff. This shall be done in accordance with the DGNB system instructions defined in the benchmark: PRO 2.3 6.1 Creation and handover of an integral operating concept
0.2.21 | Prilagoditev nastavitev sistemov po začetni fazi uporabe objekta Izvajalec sodeluje pri ponovnem pregledu delovanja vseh bistvenih tehničnih sistemov ter eventualni ponovni prilagoditvi teh sistemov s strani strokovnjaka oz. (neodvisne) tretje osebe. Postopek se izvede po približno 10–14 mesecih po zaključku gradnje, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 7.1 Readjustment of the system following initial operating phase | Adjusting system settings after the initial phase of use of the building The Contractor shall be involved in the re-examination of the functioning of all essential technical systems and the possible re-adjustment of these systems by an expert or (independent) third party. The procedure shall be carried out approximately 10-14 months after completion of construction, in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.3 7.1 Readjustment of the system following initial operating phase

## 4.8.0_Rekapitulacija
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
| REKAPITULACIJA STROŠKOV STROJNIH DEL | COST SUMMARY OF MECHANICAL WORKS
| 4 NAČRT S PODROČJA STROJNIŠTVA | 4 DOCUMENTATION IN THE FIELD OF MECHANICAL ENGINEERING
| 4/8 Vodovod in kanalizacija | 4/8 Water Supply and Sewerage
4.8 | STROJNA DELA | MECHANICAL WORKS
4.8.1 | VODOVOD, SANITARNA PITNA VODA | WATER SUPPLY, SANITARY DRINKING WATER | 0
4.8.2 | KANALIZACIJA | SEWER SYSTEM | 0
4.8.3 | ZALIVANJE | IRRIGATING | 0
0
0 | NEPREDVIDENA DELA | UNFORSEEN WORKS | 0
| SKUPAJ STROJNA DELA: | TOTAL MECHANICAL WORKS: | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT

## 4.8.1_Vodovod
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.8 | STROJNA DELA | MECHANICAL WORKS
4.8.1 | VODOVOD, SANITARNA PITNA VODA | WATER SUPPLY, SANITARY DRINKING WATER |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
1 | VODOVOD, SANITARNA PITNA VODA | WATER SUPPLY, SANITARY DRINKING WATER
| Vse postavke v nadalevanju zajemajo dobavo in montažo (razen tam kjer je to posebej navedeno). | All items below include delivery and installation (except where specifically indicated).
1.1 | Duktilne cevi za vodovod PN16 po EN545 / ISO2531 z notranjo zaščitno oblogo po ISO4179, zunanja zaščita z zlitino cinka in aluminija ter z epoksi zaščito, vključno z duktilnimi oblikovnimi fazonskimi kosi, skladnost z EN805 za pitno vodo, komplet s tesnilnim spojnim materialom VRS, polaganjem podzemnega voda v peščeni posteljici ter s PVC označevalnim trakom za vodovod; | PN16 ductile water pipes to EN545/ISO2531 with internal protective lining to ISO4179, external protection with zinc-aluminium alloy and epoxy protection, including ductile shaped bevel pieces, EN805 compliant for drinking water, complete with VRS sealing compound, underground water laying in sand bed and PVC water pipe marking tape;
| Vgradnja tudi v objektu do vodomerne niše oziroma vodomerne grupe, komplet s pocinkanim obešalnim materialom in cevnimi objemkami z oblogo za dušenje hrupa; | Installation also in the building up to the water meter niche or water meter cluster, complete with galvanised hanging material and hose clamps with noise attenuation lining;
| DN 80 | DN 80 | m | 12 |  | 0
| 90°lok DN 80 | 90°arc DN 80 | kos | 3 |  | 0
| prirobnica DN 80 | flange DN 80 | kos | 2 |  | 0
| označevalni trak vodovod | marker tape water supply | m | 2 |  | 0
1.2 | Vodotesno tesnilo za prehod cevi skozi betonsko steno zemlja / klet objekta, vodotesnost W2.1-E po DIN18533 za hidrostatični tlak do 3 m, sestavljeno iz: elastomernih tesnil EPDM ali NBR, z zategovalnimi korozijsko odpornimi prirobnicami in vijačnim materialom iz nerjavnega jekla; | Watertight seal for the passage of pipes through the concrete wall of a soil/basement building, watertightness W2.1-E according to DIN18533 for hydrostatic pressure up to 3 m, consisting of: elastomeric EPDM or NBR seals, with corrosion-resistant tightening flanges and stainless steel screw material;
| - zaščitna cev za vbetoniranje oziroma uvodnica in njena namestitev je del načrtov s področja arhitekture ter gradbeništva; | - the concrete protection pipe or introducer and its installation is part of the architectural and civil engineering plans;
| - ustreza proizvod HAUFF TECHNIK tip HSD ali enakovredno; | - corresponds to HAUFF TECHNIK product type HSD or equivalent;
| - prehod cevi NL DN80 Ø 98,7 mm | - pipe passage NL DN80 Ø 98.7 mm | kpl | 1 |  | 0
1.3 | Vodomer, vodovodne armature in oblikovni kosi v vodomerni niši, v skladu s standardi za pitno vodo EN805, EN806, material nodularna litina, EPDM, NBR, prirobnični priključki PN16, zunaj in znotraj epoksi premaz modre barve debeline min. 250 µm, vključno s tesnilnim in vijačnim materialom. Elementi vodomerne niše: | Water meter, water fittings and shaped pieces in water meter recess, in accordance with drinking water standards EN805, EN806, material ductile iron, EPDM, NBR, flange connections PN16, epoxy coating blue outside and inside, min. 250 µm thick, including sealing and screw material. Water meter recess elements EN805, EN806, material ductile iron, EPDM, NBR, PN16 flange connections, epoxy coating blue outside and inside, min. 250 µm thick, including sealing and screw material. Water meter recess elements:
| - E-KS DN 80 prehod na prirobnico PN16 | - E-KS DN 80 transition to PN16 flange
| - FFK-Q kos DN 80 / 90°, prirobnični PN16 | - FFK-Q piece DN 80 / 90°, flanged PN16
| - Zasun DN 80, prirobnični PN16 | - Gate valve DN 80, flanged PN16
| - Lovilnik nesnage DN 80, prirobnični PN16 | - Debris trap DN 80, flanged PN16
| - Vodomer kombiniran z impulznim izhodom Qn= 63 m3/h (od 0,025 do 78 m3/h), DN 80 / 20, prirobnični PN16, z opremo za daljinsko odčitavanje | - Water meter combined with pulse output Qn= 63 m3/h (from 0.025 to 78 m3/h), DN 80 / 20, flanged PN16, with remote reading equipment
| - MDK kos DN 80 / 164-211, prirobnični PN16 | - MDK piece DN 80 / 164-211, flanged PN16
| - Zasun DN 80, prirobnični PN16 | - Gate valve DN 80, flanged PN16
| - T kos DN 80 / 50, prirobnični PN16, z dodanim ventilom DN15 na slepi prirobnici (izpust, dezinfekcija) | - T piece DN 80/50, flanged PN16, with added valve DN15 on blind flange (drain, disinfection)
| - FFK-Q kos DN 80 / 90°, prirobnični PN16 | - FFK-Q piece DN 80 / 90°, flanged PN16 | kpl | 1 |  | 0
1.4 | Krogelni ventil iz nerjavnega jekla, navojna izvedba, PN16, material AISI316 / PTFE, z ročico in platformo po ISO5211 za prigraditev ključavnice, v skladu z EN806 za pitno vodo, vključno z nerjavnima protiprirobnicama AISI304, pritrdilnim in tesnilnim materialom. Ventilu se prigradi ključavnico zaradi onemogočenja zapiranja vodovoda nepooblaščeni osebi ! | Stainless steel ball valve, threaded version, PN16, material AISI316/PTFE, with handle and platform according to ISO5211 for fitting a lock, in accordance with EN806 for drinking water, including stainless counter flanges AISI304, fixing and sealing material. The valve shall be fitted with a lock to prevent unauthorised persons from closing the water supply!
| - komplet z ročico in ključavnico, ustreza proizvod END ARMATUREN ali enakovredno | - complete with handle and lock, corresponding product END ARMATUREN or equivalent
| - DN 50 | - DN 50 | kpl | 1 |  | 0
1.5 | Plovni ventil za polnenje bazena požarne vode, skladno s standardi za pitno vodo EN805, EN806, material nodularna litina, zunaj in znotraj epoksi premaz modre barve debeline min. 250 µm, tesnila EPDM, NBR, prirobnični priključki PN16, vključno s pritrdilnim in tesnilnim in materialom; | Float valve for filling fire water basin, according to drinking water standards EN805, EN806, material ductile iron, outside and inside epoxy coating blue, min. thickness 250 µm, seals EPDM, NBR, flange connections PN16, including fixing and sealing material;
| - plovni kotni ventil DN 50, prirobnični PN16, dvojni vzvod in krogla iz nerjavnega jekla, ustreza proizvood GALLUS, TYCO tip SV2 ali enakovredno | - float angle valve DN 50, flanged PN16, double lever and stainless steel ball, suitable for GALLUS, TYCO type SV2 or equivalent | kpl | 1 |  | 0
1.6 | Dvojna ionska mehčalna naprave za mehčanje vodovodne vode, prehrambena izvedba, ki ohranja kvaliteto pitne vode ter omogoča dezinfekcijo med regeneracijo, PN10 delovni tlaki do 6 bar, sestavljen iz: vstopni filter vode, dve tlačni patroni iz armiranega poliestra z ionsko smolo, večpotni krmilni ventil in impulzni vodomer, solnik s tabletirano soljo in solnim ventilom, tripotni hidravlični preklopni ventil ter krmilnik, dobavljeno kot kompaktna naprava vključno z kontrolo trdote vode na časovni interval, vključno s protiprirobnicama, vijačnim in tesnilnim materialom. Tehnični podatki: | Double ionic softener for softening tap water, food-grade version, preserving the quality of drinking water and allowing disinfection during regeneration, PN10 operating pressures up to 6 bar, consisting of: inlet water filter, two pressure cartridges made of reinforced polyester with ionic resin, multi-path control valve and pulse water meter, saline tank with salt tablet and salt valve, three-way hydraulic diverter valve and controller, supplied as a compact unit including water hardness control per time interval, including anti-seize, screwing and sealing material. Technical data:
| - kapaciteta naprave do 19,5 m3/h, trdota vode na vstopu 16°dH, na izstopu 0,5 do 5°dH, nastavljeno na 5°dH, priključki prirobnični, vstop vodovodne vode DN50, izstop mehčane vode DN50 | - capacity up to 19,5 m3/h, inlet water hardness 16°dH, outlet water hardness 0,5 to 5°dH, set to 5°dH, flanged connections, tap water inlet DN50, softened water outlet DN50
| - odvzem vzorca na časovni interval, nastavljeno na 60 minut | - sample collection at a time interval set to 60 minutes
| - električni podatki 500 W, 230V / 1 / 50Hz, IP 54 | - electrical data 500 W, 230V/1/50Hz, IP 54
| - krmilnik s komunikacijo CNS: RS485 / Modbus RTU oziroma Ethernet | - controller with CNS communication: RS485 / Modbus RTU or Ethernet
| - dimenzije cca dolžina L x širina B x višina H = 3100 x 1300 x 2470 mm | - dimensions approx. length L x width B x height H = 3100 x 1300 x 2470 mm
| - ustreza proizvod MAK CMC tip MINOM 9 z dodatno in nadgrajeno opremo ali enakovredno | - corresponds to a MAK CMC product type MINOM 9 with optional and upgraded equipment or equivalent
| Oznaka: MN60.10 | Code: MN60.10 | kpl | 1 |  | 0
1.7 | Kompaktna črpalna naprava za dvig tlaka vodovoda (pressure booster), PN16, certifikat za pitno vodo, CE izjava, material nerjavno jeklo AISI316 in siva litina, sestavljeno iz: vzporedno vezanih črpalnk s frekvenčno regulacijo, tlačnih tipal, ekspanzijske posode, zapornih, nepovratnih ter izpustnih ventilov, protivibracijskih elementov, nerjavnega jeklenega ogrodja AISI304 in električne krmilne omare, dobavljeno kot kompaktna naprava, vključno s protiprirobnicama, vijačnim in tesnilnim materialom. Tehnični podatki: | Compact pressure booster, PN16, drinking water certified, CE approved, material stainless steel AISI316 and grey cast iron, composed of: pumps in parallel with frequency control, pressure sensors, expansion tank, shut-off, non-return and discharge valves, anti-vibration elements, stainless steel frame AISI304 and electrical control cabinet, supplied as a compact unit, including counter-fittings, screwing and sealing material. Technical data:
| - tri črpalke, dve delovni in ena rezerva: pretok V = 5,17 l/s =18,6 m3/h, pri tlačna višina H= 5,0 bar | - three pumps, two working and one reserve: flow rate V = 5.17 l/s = 18.6 m3/h, pressure head H = 5.0 bar
| - črpalke, frekvenčno vodne s stalno kontrolo tlaka na tlačni strani črpalk | - pumps, water-frequency with continuous pressure control on the pressure side of the pumps
| - priključki: navojni, sesalni DN50, tlačni DN50 | - connections: threaded, suction DN50, pressure DN50
| - dimenzije ca: dolžina L x širina B x višina H = 1350 x 800 x 1460 mm; teža ca: m = 220 kg | - dimensions ca: length L x width B x height H = 1350 x 800 x 1460 mm; weight ca: m = 220 kg
| - električni podatki Pel = 3x 2,2 kW, 400V / 3 / 50Hz, IP54, IE3 ali bolše | - electrical data Pel = 3x 2,2 kW, 400V/3/50Hz, IP54, IE3 or better
| - delovanje črpalk na konstanten tlak 5,0 bar | - constant pressure operation of the pumps at 5.0 bar
| - kaskadno krmiljenje črpalk, avtomatična nastavljiva izmenjava vodeilne in sledljive črpalke, odvisno od obremenitve, časa in napake, | - cascade pump control, automatic adjustable waterline exchange and traceable pumps depending on load, time and fault,
| - električna krmilna omara s upravljalnim tablojem ter komunikacijo RS485 / Modbus RTU | - electrical control cabinet with control board and RS485 / Modbus RTU communication
| - javljanje alarma v primeru napake delovanja na požarno centralo in CNS | - alarm annunciation in the event of a malfunction to the fire panel and CNS
| - ustreza proizvod GRUNDFOS tip Hydro MPC-E 3 CRIE 5-9 ali enakovredno | - corresponds to GRUNDFOS product type Hydro MPC-E 3 CRIE 5-9 or equivalent
| Oznaka: P60.080 | Code: P60.080 | kpl | 1 |  | 0
1.8 | Obtočna črpalka PN10, z mokrim rotorjem, skladnost z EN806 za pitno vodo ter z ErP, elektronsko regulirana s PM motorjem, inegrirano tipalo diferenčnega tlaka in temperature, upravljalnik nastavitev s prikazovalnikom parametrov, z internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke nerjavno jeklo, z ustreznim tesnenjem za medij, navojna izvedba, vključno z navojnimi holandci, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump PN10, wet-rotor, EN806 compliant for drinking water and ErP compliant, electronically regulated with PM motor, integrated differential pressure and temperature sensor, setting control with parameter display, with internal hydraulic, electrical and communication connections, pump material stainless steel, with suitable medium seal, threaded version, including threaded hollands, fixing and sealing material. Technical data:
| - za obtok sanitarne tople vode, v temperaturnem območju od 10 do 90°C, | - for domestic hot water circulation, in the temperature range 10 to 90°C,
| - pretok V = 7,6 m3/h, tlačna višina H = 50 kPa | - flow rate V = 7,6 m3/h, pressure head H = 50 kPa
| - možnost izbire delovanja črpalke na proporcionalni tlak ter optimizacijo delovne točke z avtomatsko nastavitvijo, glede na trenutne potrebe obratovanja | - option to select proportional pressure operation and optimise the operating point by automatic adjustment, depending on the current operating requirements
| - električni podatki Pel = 267 W, 230V / 1 / 50Hz | - electrical data Pel = 267 W, 230V/1/50Hz
| - komunikacija s CNS, RS485 | - communication with CNS, RS485
| - ustreza proizvod GRUNDFOS tip MAGNA3 40-80 F N … za pitno vodo ali enakovredno | - corresponds to GRUNDFOS product type MAGNA3 40-80 F N ... for drinking water or equivalent
| Oznaka: P61.081 | Code: P61.081 | kpl | 1 |  | 0
1.9 | Obtočna črpalka PN10, z mokrim rotorjem, skladnost z EN806 za pitno vodo ter z ErP, elektronsko regulirana s PM motorjem, inegrirano tipalo diferenčnega tlaka in temperature, upravljalnik nastavitev s prikazovalnikom parametrov, z internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke nerjavno jeklo, z ustreznim tesnenjem za medij, prirobnična izvedba, vključno z nerjavnima protiprirobnicama, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump PN10, wet-rotor, EN806 compliant for drinking water and ErP compliant, electronically regulated with PM motor, integrated differential pressure and temperature sensor, setting control with parameter display, with internal hydraulic, electrical and communication connections, pump material stainless steel, with suitable medium seal, flanged design, including stainless steel counter flanges, fixing and sealing material. Technical data:
| - za obtok sanitarne tople vode, v temperaturnem območju od 10 do 90°C, | - for domestic hot water circulation, in the temperature range 10 to 90°C,
| - pretok V = 1,44 m3/h, tlačna višina H = 80 kPa | - flow rate V = 1,44 m3/h, pressure head H = 80 kPa
| - možnost izbire delovanja črpalke na proporcionalni tlak ter optimizacijo delovne točke z avtomatsko nastavitvijo, glede na trenutne potrebe obratovanja | - option to select proportional pressure operation and optimise the operating point by automatic adjustment, depending on the current operating requirements
| - električni podatki Pel = 171 W, 230V / 1 / 50Hz | - electrical data Pel = 171 W, 230V/1/50Hz
| - komunikacija s CNS, RS485 | - communication with CNS, RS485
| - ustreza proizvod GRUNDFOS tip MAGNA3 32-100 F N … za pitno vodo ali enakovredno | - corresponds to GRUNDFOS product type MAGNA3 32-100 F N ... for drinking water or equivalent
| Oznaka: P61.082 | Code: P61.082 | kpl | 1 |  | 0
1.10 | Ploščni izmenjevalnik toplote z dvojnimi stenami, sestavljive vijačene izvedbe, ustrezno za pitno vodo po EN806, PN10, material AISI304 (ali boljši), debeline plošč 0,6mm, tesnila EPDM do 100°C trajne obremenitve, skladnost s PED. Tehnični podatki: | Plate heat exchanger with double walls, bolted design, suitable for drinking water according to EN806, PN10, material AISI304 (or better), plate thickness 0,6mm, EPDM seals up to 100°C permanent load, PED compliant. Technical data:
| - ogrevanje sanitarne tople vode z ogrevno vodo, ustrezno za tri obratovalne režime: | - domestic hot water heating with heating water suitable for three operating regimes:
| 1. Delovni, stalno ogrevanje: 306 kW - primar: ogrevna voda, temperatura tOV = 50/40°C, pretok V = 26,6m3/h, padec tlaka Δp ≤ 30 kPa - sekundar: sanitarna voda, temp. tVS = 10/45°C, pretok V = 7,6 m3/h , padec tlaka Δp ≤ 20 kPa | 1. Working, continuous heating: 306 kW - primary: heating water, temperature tOV = 50/40°C, flow rate V = 26,6m3/h, pressure drop Δp ≤ 30 kPa - secondary: sanitary water, temp. tVS = 10/45°C, flow rate V = 7,6 m3/h, pressure drop Δp ≤ 20 kPa
| 2. Dnevno pregrevanje: 219 kW - primar: ogrevna voda, temperatura tOV = 68/53°C, pretok V = 12,8m3/h, padec tlaka Δp ≤ 30 kPa - sekundar: sanitarna voda, temp. tVS = 40/65°C, pretok V = 7,6 m3/h, padec tlaka Δp ≤ 20 kPa | 2. Daily superheat: 219 kW - primary: heating water, temperature tOV = 68/53°C, flow rate V = 12,8m3/h, pressure drop Δp ≤ 30 kPa - secondary: sanitary water, temp. tVS = 40/65°C, flow rate V = 7,6 m3/h, pressure drop Δp ≤ 20 kPa
| 3. Termična dezinfekcija: 219 kW - primar: ogrevna voda, temperatura tOV = 78/63°C, pretok V = 12,8m3/h, padec tlaka Δp ≤ 30 kPa - sekundar: sanitarna voda, temp. tVS = 50/75°C, pretok V = 7,6 m3/h, padec tlaka Δp ≤ 20 kPa | 3. Thermal disinfection: 219 kW - primary: heating water, temperature tOV = 78/63°C, flow rate V = 12,8m3/h, pressure drop Δp ≤ 30 kPa - secondary: sanitary water, temp. tVS = 50/75°C, flow rate V = 7,6 m3/h, pressure drop Δp ≤ 20 kPa
| - vsi priključki navojni PN10, primar P DN50, sekundar S DN50 | - all connections threaded PN10, primary P DN50, secondary S DN50
| - s podstavkom prenosnika, navojnimi holandci, pritrdilnim in tesnilnim materialom; | - with laptop base, threaded dutch, fixing and sealing material;
| - dimenzije do: dolžina L x širina W x višina H = 1200 x 800 x 2000 mm | - dimensions up to: length L x width W x height H = 1200 x 800 x 2000 mm
| - s toplotna parozaporna izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +105°C, debelina 50mm | - with thermal vapour barrier made of synthetic rubber-based elastomeric foam insulation according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0.040W/mK according to EN ISO8497, classification B-s3-d0 according to EN13501-1, for temperatures -50 to +105°C, thickness 50mm
| - ustrezen proizvod ALFA LAVAL tip T15-BDcFM + toplotna izolacija ali enakovredno | - suitable product ALFA LAVAL type T15-BDcFM + thermal insulation or equivalent
| Oznaka: HE61.12 | Code: HE61.12 | kpl | 1 |  | 0
1.11 | Regulacijski prehodni ventil prehodni, z elektromotornim zveznim pogonom, prirobnični priključki, PN16, napajanje 24V, izhod 2-10V, IP54, temperature do 120°C material nikljana medina, nerjavno jeklo / EPDM, PTFE, z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Control valve, solenoid operated, PN16, supply 24V, output 2-10V, IP54, temperature up to 120°C, material nickel-plated brass, stainless steel / EPDM, PTFE, with threaded Dutch plugs, fastening and sealing material;
| - ogrevna voda 50/40°C oz. 55/40°C | - heating water 50/40°C or 55/40°C
| DN 50, kvs= 40m3/h - ustreza proizvod BELIMO tip R2050-40-S4 +SR24A-SR ali enakovredno | DN 50, kvs= 40m3/h - corresponds to BELIMO product type R2050-40-S4 +SR24A-SR or equivalent
| Oznaka: VY44.053 | Code: VY44.053 | kpl | 1 |  | 0
1.12 | Rezervoar tolple pitne vode, ustrezno za pitno vodo po EN806, jeklena tlačna posoda PN10, emajlirano po DIN 4753-3, posoda je v celoti napolnjena s pitno toplo vodo, temperature do 95°C, pokončna izvedba, tovarniško izdelna kompaktna naprava, komplet z revizijskimi odprtinami, Mg anodami, rezervnim električnim grelnikom vsemi priključki ter toplotno izolacjo. Ostali tehnični podatki | Potable water tank, suitable for potable water according to EN806, steel pressure vessel PN10, enamelled according to DIN 4753-3, tank completely filled with potable hot water, temperatures up to 95°C, upright design, factory-built compact unit, complete with inspection openings, Mg anodes, back-up electric heater, all connections and thermal insulation. Other technical data
| - prostornina rezervoarja 2,78 m3 = 2780 litrov, premer D x višina H = ∅1500 x 300 mm | - tank capacity 2,78 m3 = 2780 litres, diameter D x height H = ∅1500 x 300 mm
| - priključki PN10: 4xDN50, 1xDN32, tipala DN15 | - pN10 connections: 4xDN50, 1xDN32, sensors DN15
| - prirobnične PN10 revizijske odprtine 3x DN 180: dve za revizijo oziroma čiščenje ter ena za vgradnjo električnega grelnika, | - 3x DN 180 flanged PN10 inspection openings: two for inspection or cleaning and one for the installation of an electric heater,
| - električni grelnika s trostopenjskim termostatom in zaščito, Pel = 16 kW, 400V / 3 / 50Hz, samo kot rezervna funkcija, sicer izklopljeno, | - electric heater with three-stage thermostat and protection, Pel = 16 kW, 400V/3/50Hz, only as a backup function, otherwise off,
| - zaščitne magnezijeve anode: 2x Mg anoda z možnostjo izvleka in zamenjave, | - protective magnesium anodes: 2x Mg anodes with the possibility of removal and replacement,
| - temperatura tople pitne vode od 15 do 82°C | - hot drinking water temperature from 15 to 82°C
| - certifikat za pitno vodo po EN806 oziroma DVGW, CE izjava, skladnost s PED | - drinking water certificate according to EN806 or DVGW, CE declaration, PED compliance
| - originalna izolacija proizvajalca rezervoarja, debelina 120mm, λ≤0,040W/mK, predvidoma PUR z zaščitnim plaščem, | - original insulation of the tank manufacturer, 120mm thick, λ≤0,040W/mK, presumably PUR with protective jacket,
| - ustreza proizvod REFLEX tip AL 3000/R3 + EFHR 16.0 ali enakovredno | - rEFLEX product type AL 3000/R3 + EFHR 16.0 or equivalent
| Oznaka: RVST61.11 | Code: RVST61.11 | kpl | 1 |  | 0
1.13 | Tipalo tlaka s pretvornikom, ustrezno za pitno vodo po EN806, za merilno območje 0 do 10 bar, material nerjavno jeklo AISI304 (ali boljši), navojni priključek 1/2", higijenska izvedba, PN16, elektični podatki: napajanje 24V, izhod 4-20mA, kompletno z ventilom za tipalo tlaka 1/2" ter tesnilnim in pritrdilnim materialom; | Pressure sensor with transducer, suitable for drinking water according to EN806, for measuring range 0 to 10 bar, material stainless steel AISI304 (or better), threaded connection 1/2", hygienic design, PN16, electrical data: power supply 24V, output 4-20mA, complete with pressure sensor valve 1/2" and sealing and fixing material;
| - ustreza proizvod ENDRESS+HAUSER tip PMP51 + PZAV ali enakovredno | - corresponds to ENDRESS+HAUSER product type PMP51 + PZAV or equivalent
| Oznaka: PI61.011 | Code: PI61.011 | kpl | 1 |  | 0
1.14 | Temperaturno tipalo v tulki, ustrezno za pitno vodo po EN806, za merilno območje 0 do 100°C bar, material nerjavno jeklo AISI304 (ali boljši), navojni priključek 1/2", higijenska izvedba, PN16, elektični podatki: napajanje 24V, izhod 4-20mA, kompletno tesnilnim in pritrdilnim materialom; | Temperature sensor in coil, suitable for drinking water according to EN806, for measuring range 0 to 100°C bar, material stainless steel AISI304 (or better), threaded connection 1/2", hygienic design, PN16, electrical data: power supply 24V, output 4-20mA, complete with sealing and fixing material;
| - potopna dolžina L= 200mm | - immersion length L= 200mm
| - ustreza proizvod ENDRESS+HAUSER tip TM411 ali enakovredno | - corresponds to ENDRESS+HAUSER product type TM411 or equivalent
| Oznaka: TIC61.001, TI61.002, TIC41.003 | Code: TIC61.001, TI61.002, TIC41.003 | kpl | 3 |  | 0
1.15 | Temperaturno tipalo v tulki, ustrezno za pitno vodo po EN806, za merilno območje 0 do 100°C bar, material nerjavno jeklo AISI304 (ali boljši), navojni priključek 1/2", higijenska izvedba, PN16, elektični podatki: napajanje 24V, izhod 4-20mA, kompletno tesnilnim in pritrdilnim materialom; | Temperature sensor in coil, suitable for drinking water according to EN806, for measuring range 0 to 100°C bar, material stainless steel AISI304 (or better), threaded connection 1/2", hygienic design, PN16, electrical data: power supply 24V, output 4-20mA, complete with sealing and fixing material;
| - potopna dolžina L= 50mm | - immersion length L= 50mm
| - ustreza proizvod ENDRESS+HAUSER tip TM411 ali enakovredno | - corresponds to ENDRESS+HAUSER product type TM411 or equivalent
| Oznaka: TI61.004, TIC61.005, TIC61.006, TIC61.007 | Code: TI61.004, TIC61.005, TIC61.006, TIC61.007 | kpl | 4 |  | 0
1.16 | Raztezna posoda za pitno vodo, PN10, za kompenzacijo toplotnih raztezkov pri pripravi sanitarne tople vode, certifikat za pitno vodo, skladnost s PED, navojni priključki DN32 (1 1/4"), dimenzije (premer D x višina H) ∅ 560 x 1460 mm, postavljeno na jeklenih nogah 100 mm od tal, kompletno tesnilnim in pritrdilnim materialom; | Drinking water expansion tank, PN10, for compensating thermal expansion in the preparation of domestic hot water, certified for drinking water, PED-compliant, threaded connections DN32 (1 1/4"), dimensions (diameter D x height H) ∅ 560 x 1460 mm, raised on steel legs 100 mm from the floor, complete with sealing and fixing material;
| - ustreza proizvod PNEVMATEX tip AUF 300.10 ali enakovredno | - corresponds to PNEVMATEX product type AUF 300.10 or equivalent
| Oznaka: EPS61.13 | Code: EPS61.13 | kpl | 1 |  | 0
1.17 | Varnostni ventil za pitno vodo z možnostjo ročnega odzračevanja, PN16, varnostna funkcija pri pripravi sanitarne tople vode, certifikat za pitno vodo, skladnost s PED, TUV, material nerjavno jeklo AISI316L (ali boljši), navojni priključki, kompletno tesnilnim in pritrdilnim materialom; | Drinking water safety valve with manual venting, PN16, safety function for domestic hot water, certified for drinking water, PED, TUV compliance, material stainless steel AISI316L (or better), threaded connections, complete with sealing and fastening material;
| - ustreza proizvod END ARMATUREN tip SV ali enakovredno | - corresponds to END ARMATUREN type SV or equivalent
| - DN 32 / 50 - tlak odpiranja 8 barg, | - DN 32/50 - opening pressure 8 barg,
| Oznaka: VV61.14, VV61.15 | Code: VV61.14, VV61.15 | kpl | 2 |  | 0
1.18 | Hidravlični ločilnik s kontrolirano tlačno cono tipa BA po EN1717 za ločitev od sistema pitne vode po DVGW, s filtrom, navojni priključki, PN10, s kontrolnimi priključki za testiranje ustreznosti tlačnih con, materiali za pitno vodo medenina/ nerjavno jeklo/ NBR, certifikat po EN12729, vključno z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Hydraulic pressure-controlled zone separator type BA according to EN1717 for separation from the drinking water system according to DVGW, with filter, threaded connections, PN10, with control connections for testing the adequacy of the pressure zones, materials for drinking water brass/stainless steel/NBR, certified according to EN12729, incl. threaded dutch, fastening and sealing material;
| - ustreza proizvod CALEFFI tip BA ali enakovredno | - corresponds to CALEFFI product type BA or equivalent
| DN 15 | DN 15 | kpl | 17 |  | 0
| DN 20 | DN 20 | kpl | 4 |  | 0
| DN 25 | DN 25 | kpl | 2 |  | 0
1.19 | Krogelni ventil za pitno vodo po EN806, navojni priključki oziroma zatisni press priključki, PN16, z ročico, material nerjavno jeklo, medenina, PTFE, vključno s pritrdilnim in tesnilnim materialom; | Drinking water ball valve according to EN806, threaded or press fit connections, PN16, with handle, material stainless steel, brass, PTFE, incl. fixing and sealing material;
| - ustreza proizvod END ARMATUREN oziroma VIEGA ali enakovredno | - corresponds to END ARMATUREN or VIEGA or equivalent
| DN 15 - s priključkom za dezinfekcijo | DN 15 - with disinfection connection | kos | 82 |  | 0
| DN 15 | DN 15 | kos | 120 |  | 0
| DN 20 | DN 20 | kos | 80 |  | 0
| DN 25 | DN 25 | kos | 60 |  | 0
| DN 32 | DN 32 | kos | 16 |  | 0
| DN 40 | DN 40 | kos | 12 |  | 0
| DN 50 | DN 50 | kos | 16 |  | 0
1.20 | Krogelni ventil iz nerjavnega jekla, ustrezno za pitno vodo po EN806, PN16, material AISI316 ali boljši, PTFE, tridelno telo ventila, navojni priključki, vključno s pritrdilnim in tesnilnim materialom; | Stainless steel ball valve, suitable for drinking water according to EN806, PN16, material AISI316 or better, PTFE, three-piece valve body, threaded connections, including fastening and sealing material;
| - ustreza proizvod END ARMATUREN ali enakovredno | - eND ARMATUREN or equivalent
| DN 65 | DN 65 | kos | 2 |  | 0
1.21 | Nepovratni ventil iz nerjavnega jekla, z vzmetjo, ustrezno za pitno vodo po EN806, PN16, material AISI316, PTFE, navojni priklučki, vključno s pritrdilnim in tesnilnim materialom; | Stainless steel non-return valve, with spring, suitable for drinking water according to EN806, PN16, material AISI316, PTFE, threaded couplings, incl. fixing and sealing material;
| - ustreza proizvod END ARMATUREN ali enakovredno | - eND ARMATUREN or equivalent
| DN 25 | DN 25 | kos | 6 |  | 0
| DN 32 | DN 32 | kos | 4 |  | 0
| DN 40 | DN 40 | kos | 2 |  | 0
| DN 50 | DN 50 | kos | 4 |  | 0
| DN 65 | DN 65 | kos | 1 |  | 0
1.22 | Ventil za hidravlično uravnoteženje, ustrezno za pitno vodo po EN806, PN16, medenina, nerjavno jeklo, PTFE, EPDM, navojni priključki, certifikat za pitno vodo, vključno z navojnima holandcema, s pritrdilnim in tesnilnim materialom; | Hydraulic balancing valve, suitable for drinking water according to EN806, PN16, brass, stainless steel, PTFE, EPDM, threaded connections, certified for drinking water, incl. threaded Dutch, with fastening and sealing material;
| - ustreza proizvod IMI TA tip STAD-B ali enakovredno | - corresponds to IMI TA product type STAD-B or equivalent
| DN 15 | DN 15 | kos | 6 |  | 0
| DN 20 | DN 20 | kos | 12 |  | 0
| DN 25 | DN 25 | kos | 4 |  | 0
| DN 32 | DN 32 | kos | 6 |  | 0
| DN 40 | DN 40 | kos | 5 |  | 0
| DN 50 | DN 50 | kos | 3 |  | 0
1.23 | Ventil za termično dezinfekcijo, večmanenski termostatski obtočni ventil MTCV (Multifunctional Thermostatic Circulation Valve) za obtok sanitarne tople vode po EN806, PN16, navojne izvedbe, material medenina oziroma rdeča litina / PTFE, s tesnilnim in pritrdilnim materialom, komplet z elementi za izvedbo avtomatskega postopka termične dezinfekcije: termostat za normalen obtok nastavljiv med 40 in 60°C, temperaturno tipalo za območje od 40 do 80°C s kabelsko povezavo, elektrotermični pogon ventila 24 V, on/off, brez napetosti zaprt ter adapterja za tipalo in pogon; | Thermal disinfection valve, MTCV (Multifunctional Thermostatic Circulation Valve) for circulation of sanitary hot water according to EN806, PN16, threaded version, material brass or red cast iron/PTFE, with sealing and fastening material, complete with elements for the implementation of the automatic thermal disinfection process: thermostat for normal circulation adjustable between 40 and 60°C, temperature sensor for the range 40 to 80°C with cable connection, electrothermal actuator for the valve, 24 V, on/off, non-voltage closed, as well as adapters for the sensor and the actuator;
| - vodovod, pitna voda, skladnost z EN 806 | - water supply, drinking water, EN 806 compliance
| - ustreza proizvod DANFOSS tip MTCV-C ali enakovredno | - corresponds to DANFOSS product type MTCV-C or equivalent
| DN 15 | DN 15 | kpl | 26 |  | 0
| DN 20 | DN 20 | kpl | 1 |  | 0
1.24 | Gavni regulator za programsko vodeno termično dezinfekcijo sanitarne tople vode v obtoku ter zapis temperatur: glavni krmilnik za vodenje do 20 krogov termične dezinfekcije in zapis temperatur, napajalna napetost 24 V, izhodni signal 24 V, vgradnja na DIN letev, web server modul z LAN portom, RS485 / Modbus RTU, komplet s kabelskimi povezavami MTCV-C ventilov; | Moveable controller for software-controlled thermal disinfection of circulating hot water and temperature recording: main controller for control of up to 20 thermal disinfection circuits and temperature recording, supply voltage 24 V, output signal 24 V, DIN rail mounting, web server module with LAN port, RS485 / Modbus RTU, complete with cable connections for MTCV-C valves;
| - ustreza proizvod DANFOSS tip CCR 2+ glavni krmilnik ali enakovredno | - corresponds to DANFOSS product type CCR 2+ main controller or equivalent
| Oznaka: CCR.61.060 | Code: CCR.61.060 | kpl | 1 |  | 0
1.25 | Podrejen regulator za programsko vodeno termično dezinfekcijo sanitarne tople vode v obtoku ter zapis temperatur: podrejeni krmilnik za vodenje do 16 krogov termične dezinfekcije in zapis temperatur, napajalna napetost 24 V, izhodni signal 24 V, komunikacija z glavnim krmilnikom, komplet s kabelskimi povezavami MTCV-C ventilov; | Slave controller for software-controlled thermal disinfection of circulating hot water and temperature recording: slave controller for control of up to 16 thermal disinfection circuits and temperature recording, supply voltage 24 V, output signal 24 V, communication with master controller, complete with cable connections for MTCV-C valves;
| - ustreza proizvod DANFOSS tip CCR 2+ podrejen krmilnik ali enakovredno | - corresponds to DANFOSS product type CCR 2+ slave controller or equivalent
| Oznaka: CCR.61.061 | Code: CCR.61.061 | kpl | 1 |  | 0
1.26 | Kompenzator vibracij in prenosa hrupa iz strojne opreme na cevovod ali iz hrupnega prostora po cevovodu v sosednji prostor, prirobnična izvedba, ustrezno za pitno vodo po EN806, PN16, material nerjavno jeklo AISI316 (ali boljši), butil, EPDM, vključno s pritrdilnim in tesnilnim materialom; | Vibration and noise compensator from hardware to pipeline or from noise room through pipeline to adjacent room, flanged design, suitable for drinking water according to EN806, PN16, material stainless steel AISI316 (or better), butyl, EPDM, including fastening and sealing material;
| - ustreza proizvod ELAFLEX tip ERV-R ali enakovredno | - corresponds to ELAFLEX product type ERV-R or equivalent
| DN 32 | DN 32 | kpl | 4 |  | 0
| DN 40 | DN 40 | kpl | 4 |  | 0
| DN 50 | DN 50 | kpl | 8 |  | 0
1.27 | Termometer, tekočinski, dolžina skale 100mm, kotni 90°, potopna dolžina 40mm, v zaščitni cevi iz nerjavnega jekla AISI 316, klasa točnosti 1%, navojni priključek 1/2" (DN15), material medenina, aluminij, steklo, nerjavno jeklo, ustrezno za pitno vodo po EN806, vključno s pritrdilnim in tesnilnim materialom; | Thermometer, liquid, scale length 100mm, angular 90°, immersion length 40mm, in stainless steel protective tube AISI 316, accuracy class 1%, threaded connection 1/2" (DN15), material brass, aluminium, glass, stainless steel, suitable for drinking water according to EN806, incl. fixing and sealing material;
| - ustreza proizvod INOL ali enakovredno | - corresponds to INOL or equivalent
| - območjem merjenja: 0 do 100°C | - measuring range: 0 to 100°C | kos | 12 |  | 0
1.28 | Manometer ø 68 mm, klasa točnosti 1,6% po EN837-1, navojni radialni priključek, material medenina, nerjavno jeklo, steklo / EPDM, komplet z manometrskim ventilom DN15 (1/2"), ustrezno za pitno vodo po EN806, vključno s pritrdilnim in tesnilnim materialom; | Pressure gauge ø 68 mm, accuracy class 1.6% according to EN837-1, threaded radial connection, material brass, stainless steel, glass/EPDM, complete with pressure gauge valve DN15 (1/2"), suitable for drinking water according to EN806, including fitting and sealing material;
| - ustreza proizvod INOL ali enakovredno | - corresponds to INOL or equivalent
| - območjem merjenja: 0 do 10 bar | - measuring range: 0 to 10 bar | kos | 12 |  | 0
1.29 | Nerjavne jeklene cevi za pitno vodo po EN806, zatisni press sistem, izdelane po EN10312 in EN 10088, PN16, material 1.4521 (AISI444) ali 1.4404 (AISI316L), vključno s spojnimi in oblikovnimi zatisnimi press kosi iz nerjavnega jekla (90°loki, T kosi, redukcije, ...), DVGW certifikat za uporabo v sistemih v pitne vode skladno z DIN11388 TRWI ali enakovreden certifikat, zatiskanje z originalnim press orodjem proizvajalca, komplet s prehodnimi navojnimi oblikovnimi kosi, ustreza proizvod VIEGA tip SANPRESS ali proizvod KANTHERM tip INOX ali enakovredno, | Stainless steel drinking water pipes according to EN806, press fitting system, manufactured according to EN10312 and EN 10088, PN16, material 1.4521 (AISI444) or 1.4404 (AISI316L), including stainless steel connecting and forming press fittings (90°bends, T-fittings, reducers, etc.), DVGW certificate for use in drinking water systems according to DIN11388 TRWI or equivalent, press fitting with original manufacturer's press tool, complete with threaded transition fittings, corresponding to VIEGA type SANPRESS or KANTHERM type INOX or equivalent,
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and pipe clamps with noise damping lining, suitable for HILTI or SIKLA, or equivalent;
| DN 15, ø 18 x 1,0 | DN 15, ø 18 x 1,0 | m | 5820 |  | 0
| DN 20, ø 22 x 1,2 | DN 20, ø 22 x 1,2 | m | 1980 |  | 0
| DN 25, ø 28 x 1,2 | DN 25, ø 28 x 1,2 | m | 1860 |  | 0
| DN 32, ø 35 x 1,5 | DN 32, ø 35 x 1,5 | m | 520 |  | 0
| DN 40, ø 42 x 1,5 | DN 40, ø 42 x 1,5 | m | 480 |  | 0
| DN 50, ø 54 x 1,5 | DN 50, ø 54 x 1,5 | m | 420 |  | 0
| DN 65, ø 76,1 x 2,0 | DN 65, ø 76,1 x 2,0 | m | 60 |  | 0
| DN 80, ø 88,9 x 2,0 | DN 80, ø 88,9 x 2,0 | m | 30 |  | 0
| 90°lok DN 15, ø 18 x 1,0 | 90°lock DN 15, ø 18 x 1,0 | kos | 1200 |  | 0
| 90°lok DN 20, ø 22 x 1,2 | 90°lok DN 20, ø 22 x 1,2 | kos | 350 |  | 0
| 90°lok DN 25, ø 28 x 1,2 | 90°lok DN 25, ø 28 x 1,2 | kos | 320 |  | 0
| 90°lok DN 32, ø 35 x 1,5 | 90°lok DN 32, ø 35 x 1,5 | kos | 90 |  | 0
| 90°lok DN 40, ø 42 x 1,5 | 90°lok DN 40, ø 42 x 1,5 | kos | 80 |  | 0
| 90°lok DN 50, ø 54 x 1,5 | 90°lok DN 50, ø 54 x 1,5 | kos | 70 |  | 0
| 90°lok DN 65, ø 76,1 x 2,0 | 90°block DN 65, ø 76,1 x 2,0 | kos | 10 |  | 0
| 90°lok DN 80, ø 88,9 x 2,0 | 90°lok DN 80, ø 88,9 x 2,0 | kos | 10 |  | 0
| T kos DN 15 / odcep DN 15 | T piece DN 15 / branch DN 15 | kos | 480 |  | 0
| T kos DN 20 / odcep DN 15 | T piece DN 20 / branch DN 15 | kos | 90 |  | 0
| T kos DN 20 / odcep DN 20 | T piece DN 20 / branch DN 20 | kos | 64 |  | 0
| T kos DN 25 / odcep DN 15 | T piece DN 25 / branch DN 15 | kos | 96 |  | 0
| T kos DN 25 / odcep DN 20 | T piece DN 25 / branch DN 20 | kos | 32 |  | 0
| T kos DN 25 / odcep DN 25 | T piece DN 25 / branch DN 25 | kos | 32 |  | 0
| T kos DN 32 / odcep DN 15 | T piece DN 32 / branch DN 15 | kos | 72 |  | 0
| T kos DN 32 / odcep DN 20 | T piece DN 32 / branch DN 20 | kos | 16 |  | 0
| T kos DN 32 / odcep DN 25 | T piece DN 32 / branch DN 25 | kos | 8 |  | 0
| T kos DN 32 / odcep DN 32 | T piece DN 32 / branch DN 32 | kos | 16 |  | 0
| T kos DN 40 / odcep DN 32 | T piece DN 40 / branch DN 32 | kos | 24 |  | 0
| T kos DN 50 / odcep DN 15 | T piece DN 50 / branch DN 15 | kos | 32 |  | 0
| T kos DN 50 / odcep DN 20 | T piece DN 50 / branch DN 20 | kos | 48 |  | 0
| T kos DN 50 / odcep DN 25 | T piece DN 50 / branch DN 25 | kos | 64 |  | 0
| T kos DN 50 / odcep DN 32 | T piece DN 50 / branch DN 32 | kos | 16 |  | 0
| T kos DN 50 / odcep DN 40 | T piece DN 50 / branch DN 40 | kos | 32 |  | 0
| T kos DN 50 / odcep DN 50 | T piece DN 50 / branch DN 50 | kos | 24 |  | 0
| T kos DN 65 / odcep DN 25 | T piece DN 65 / branch DN 25 | kos | 8 |  | 0
| T kos DN 65 / odcep DN 50 | T piece DN 65 / branch DN 50 | kos | 4 |  | 0
| T kos DN 65 / odcep DN 65 | T piece DN 65 / branch DN 65 | kos | 1 |  | 0
| T kos DN 80 / odcep DN 50 | T piece DN 80 / branch DN 50 | kos | 1 |  | 0
| redukcija DN 20 / DN 15 | dN 20 / DN 15 reduction | kos | 240 |  | 0
| redukcija DN 25 / DN 20 | dN 25 / DN 20 reduction | kos | 20 |  | 0
| redukcija DN 32 / DN 25 | dN 32 / DN 25 reduction | kos | 16 |  | 0
| redukcija DN 40 / DN 32 | dN 40 / DN 32 reduction | kos | 18 |  | 0
| redukcija DN 50 / DN 40 | dN 50 / DN 40 reduction | kos | 8 |  | 0
| redukcija DN 65 / DN 50 | dN 65 / DN 50 reduction | kos | 8 |  | 0
| redukcija DN 80 / DN 50 | dN 80 / DN 50 reduction | kos | 1 |  | 0
| kompenzator DN 15 | compensator DN 15 | kos | 24 |  | 0
| kompenzator DN 20 | compensator DN 20 | kos | 12 |  | 0
| kompenzator DN 25 | compensator DN 25 | kos | 12 |  | 0
| kompenzator DN 32 | compensator DN 32 | kos | 4 |  | 0
| kompenzator DN 40 | compensator DN 40 | kos | 4 |  | 0
| kompenzator DN 50 | compensator DN 50 | kos | 8 |  | 0
| prirobnica DN 40 po EN1092, PN16, z vijačnim in tesnilnim materialom | flange DN 40 to EN1092, PN16, with bolting and sealing material | kpl | 8 |  | 0
| prirobnica DN 50 po EN1092, PN16, z vijačnim in tesnilnim materialom | flange DN 50 to EN1092, PN16, with bolting and sealing material | kpl | 16 |  | 0
| prirobnica DN 65 po EN1092, PN16, z vijačnim in tesnilnim materialom | flange DN 65 to EN1092, PN16, with bolting and sealing material | kpl | 4 |  | 0
| prirobnica DN 80 po EN1092, PN16, z vijačnim in tesnilnim materialom | flange DN 80 to EN1092, PN16, with bolting and sealing material | kpl | 1 |  | 0
1.30 | Toplotna izolacija cevovodov in cevnih armatur s parozaporno izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z naslednjimi lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, požarna klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +110°C, lepljeno na cevovode in armature z originalnim lepilom proizvajalca, vključno s trakovi za šive; | Thermal insulation of pipelines and pipe fittings with vapour barrier insulation made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, fire classification B-s3-d0 according to EN13501-1, for temperatures from -50 to +110°C, bonded to pipelines and fittings with the original manufacturer's adhesive, including seam tapes;
| - barva izolacije črna | - insulation colour black
| - ustreza proizvod ARMACELL tip Armaflex ACE Plus ali enakovredno | - corresponds to ARMACELL product type Armaflex ACE Plus or equivalent
| DN 15, ø 18 ; debelina 13 mm | DN 15, ø 18; thickness 13 mm | m | 6680 |  | 0
| DN 20, ø 22 ; debelina 19 mm | DN 20, ø 22 ; thickness 19 mm | m | 2280 |  | 0
| DN 25, ø 28 ; debelina 19 mm | DN 25, ø 28 ; thickness 19 mm | m | 2140 |  | 0
| DN 32, ø 35 ; debelina 25 mm | DN 32, ø 35 ; thickness 25 mm | m | 590 |  | 0
| DN 40, ø 42 ; debelina 25 mm | DN 40, ø 42 ; thickness 25 mm | m | 550 |  | 0
| DN 50, ø 54 ; debelina 40 mm | DN 50, ø 54 ; thickness 40 mm | m | 480 |  | 0
| DN 65, ø 76,1 ; debelina 40 mm | DN 65, ø 76,1 ; thickness 40 mm | m | 70 |  | 0
| DN 80, ø 88,9 ; debelina 40 mm | DN 80, ø 88,9 ; thickness 40 mm | m | 40 |  | 0
1.31 | Umivalnik za roke z iztočno armaturo, kompletno s pripadajočo opremo, ustrezajo proizvodi po izbiri arhitekta SADAR+VUGA ali enakovredno: | Hand wash basin with outlet mixer, complete with associated fittings, to suit products of the architect's choice SADAR+VUGA or equivalent:
| - umivalnik iz sanitarnega porcelana 600x450 po izbiri arhitekta, predvidoma LAUFEN ali enakovredno | - 600x450 sanitary porcelain washbasin of the architect's choice, presumably LAUFEN or equivalent
| - iztočna armatura za umivalnik po izbiri arhitekta, predvidoma HANSGROHE oziroma ELMER ELEKTRONIKA ali enakovredno | - washbasin outlet fitting of the architect's choice, presumably HANSGROHE or ELMER ELEKTRONIKA or equivalent
| - dva kotna ventila DN15 in veznima cevkama | - two DN15 angle valves and connecting tubes
| - podometni sifon za umivalnik, odtok horizontalen; | - concealed trap for washbasin, horizontal drain;
| - jeklena podkonstrukcija za vgradnjo umivalnika na montažno steno; GEBERIT DUOFIX | - steel substructure for mounting the washbasin on a prefabricated wall; GEBERIT DUOFIX
| - držalo za papirnate brisače; | - paper towel holder;
| - milnik za umivalnik; | - soap dispenser for washbasin;
| - koš za odpadne papirnate brisače; | - waste paper towel bin;
| - vključno s pritrdilnim in tesnilnim materialom; | - including fixing and sealing materials; | kpl | 75 |  | 0
1.32 | Umivalnik za gibalno ovirane z iztočno armaturo, kompletno s pripadajočo opremo, ustrezajo proizvodi po izbiri arhitekta SADAR+VUGAa ali enakovredno: | Washbasin for the physically handicapped with outlet mixer, complete with associated fittings, to suit products of the architect's choice SADAR+VUGAa or equivalent:
| - umivalnik iz sanitarnega porcelana 660x550 po izbiri arhitekta, predvidoma LAUFEN 810603 ali enakovredno | - sanitary porcelain washbasin 660x550 of the architect's choice, presumably LAUFEN 810603 or equivalent
| - iztočna armatura za umivalnik po izbiri arhitekta, predvidoma HANSGROHE ali enakovredno | - washbasin outlet fitting of the architect's choice, presumably HANSGROHE or equivalent
| - dva kotna ventila DN15 in veznima cevkama | - two DN15 angle valves and connecting tubes
| - podometni sifon za umivalnik, odtok horizontalen; | - concealed trap for washbasin, horizontal drain;
| - jeklena podkonstrukcija za vgradnjo umivalnika na montažno steno; GEBERIT DUOFIX | - steel substructure for mounting the washbasin on a prefabricated wall; GEBERIT DUOFIX
| - držalo za papirnate brisače; | - paper towel holder;
| - milnik za umivalnik; | - soap dispenser for washbasin;
| - koš za odpadne papirnate brisače; | - waste paper towel bin;
| - vključno s pritrdilnim in tesnilnim materialom; | - including fixing and sealing materials; | kpl | 4 |  | 0
1.33 | Stranšče kompletno s pripadajočo opremo, ustrezajo proizvodi po izbiri arhitekta SADAR+VUGA ali enakovredno: | Site complete with associated equipment, corresponding to products of the architect's choice SADAR+VUGA or equivalent:
| - straniščna školjka iz sanitarnega porcelana 355x530, s stenskim iztokom po izbiri arhitekta, predvidoma GEBERIT SELANOVA ali enakovredno | - toilet bowl made of sanitary porcelain 355x530, with wall outlet of the architect's choice, preferably GEBERIT SELANOVA or equivalent
| - sedežna deska s pokrovom, mehko zapiranje po izbiri arhitekta, predvidoma GEBERIT SELANOVA ali enakovredno | - seat with cover, soft-closing of the architect's choice, presumably GEBERIT SELANOVA or equivalent
| - aktivirna tipka dvokoličinsko splakovanje po izbiri arhitekta, predvidom GEBERIT ali enakovredno | - activation key architect's choice of dual flush, GEBERIT or equivalent
| - podometni izplakovalni kotliček z dvema izplakovalnima količinama (do 4 litre in do 9 litrov); GEBERIT DUOFIX | - flush-mounted flushing kettle with two flushing volumes (up to 4 litres and up to 9 litres); GEBERIT DUOFIX
| - zapornega ventila DN15 (vgrajen v podometnem kotličku) | - dN15 stop valve (installed in the flush-mounted boiler)
| - jeklena podkonstrukcija za vgradnjo stranišča na montažno steno; GEBERIT DUOFIX | - steel substructure for mounting the toilet on a prefabricated wall; GEBERIT DUOFIX
| - držalo za toaletni papir; | - toilet paper holder;
| - čistilna straniščna metlica; | - toilet cleaning broom;
| - koš za odpadne papirnate brisače 5L; | - waste paper towel bin 5L;
| - osvežilec zraka; | - air freshener;
| - vključno s pritrdilnim in tesnilnim materialom; | - including fixing and sealing materials; | kpl | 88 |  | 0
1.34 | Pisoar z elektronsko izplakovalno armaturo, kompletno s pripadajočo opremo, ustrezajo proizvodi po izbiri arhitekta SADAR+VUGA ali enakovredno: | Urinal with electronic flush valve, complete with associated equipment, to suit products of the architect's choice SADAR+VUGA or equivalent:
| - pisoarja iz sanitarnega porcelana 320x350x645, z odtočnim sifonom in sitom po izbiri arhitekta, predvidoma LAUFEN ali enakovredno | - urinal made of sanitary porcelain 320x350x645, with drain trap and sieve of the architect's choice, presumably LAUFEN or equivalent
| - senzorskega podometnega izplakovalnega elektronskega sistema za pisoar, po izbiri arhitekta, predvidoma GEBERIT DUOFIX oziroma ELMER ELEKTRONIKA ali enakovredno | - a sensor-based flushing electronic urinal flushing system of the architect's choice, presumably GEBERIT DUOFIX or ELMER ELEKTRONIKA or equivalent
| - podometnega kotnega ventila DN15 | - angle valve DN15
| - jeklena podkonstrukcija za vgradnjo pisoarja na montažno steno; GEBERIT DUOFIX | - steel substructure for mounting the urinal on a prefabricated wall; GEBERIT DUOFIX
| - vključno s pritrdilnim in tesnilnim materialom; | - including fixing and sealing materials; | kpl | 45 |  | 0
1.35 | Prha kompletno s pripadajočo opremo, ustrezajo proizvodi po izbiri arhitekta SADAR+VUGA ali enakovredno: | Shower complete with associated fittings, to suit products of the architect's choice SADAR+VUGA or equivalent:
| - tuš pršna plošča, utopljena vgradnja v liniji finalnega tlaka 900x900 po izbiri arhitekta, predvidoma GEBERIT SETAPLANO ali enakovredno | - shower shower panel, sunken installation in the 900x900 finish flooring line of the architect's choice, presumably GEBERIT SETAPLANO or equivalent
| - namestitveno ogrodje za talno pršno ploščo po izbiri arhitekta, predvidoma GEBERIT SETAPLANO ali enakovredno | - installation frame for the floor shower panel of the architect's choice, presumably GEBERIT SETAPLANO or equivalent
| - odtok za prho s štiri nožnimi podporami, višina vodne pregrade 50 mm; za talno pršno ploščo po izbiri arhitekta, predvidoma GEBERIT SETAPLANO ali enakovredno | - shower drain with four foot supports, water barrier height 50 mm; for a shower floor panel of the architect's choice, presumably GEBERIT SETAPLANO or equivalent
| - iztočna armatura za prho po izbiri arhitekta, predvidoma HANSGROHE ali enakovredno | - shower outlet fitting of the architect's choice, presumably HANSGROHE or equivalent
| - pršna glava, povezovalna gladka gibka cev na armaturo ter konzola za višinsko nastavitev pršne glave, po izbiri arhitekta, predvidoma HANSGROHE ali enakovredno | - shower head, connecting smooth flexible hose to the mixer and bracket for height adjustment of the shower head, architect's choice, presumably HANSGROHE or equivalent
| - dva podometna krogelna ventila DN15 s kromano kapo | - two DN15 flush ball valves with chrome cap
| - jeklena podkonstrukcija za vgradnjo armature in konzole za pršno glavo; GEBERIT DUOFIX | - steel substructure for fittings and shower head bracket; GEBERIT DUOFIX
| - obešalnik za garderobo; | - wardrobe hanger;
| - vključno s pritrdilnim in tesnilnim materialom; | - including fixing and sealing materials; | kpl | 7 |  | 0
1.36 | Trokadero kompletno s pripadajočo opremo, ustrezajo proizvodi po izbiri arhitekta SADAR+VUGA ali enakovredno: | Trocadero complete with associated equipment, corresponding to products of the architect's choice SADAR+VUGA or equivalent:
| - trokadero iz sanitarnega porcelana s stenskim iztokom 400x490, komplet z nerjavno dvižno rešetko za trokadero z blažilnikom, po izbiri arhitekta, predvidoma GEBERIT PUBLICA ali enakovredno | - trocadero in sanitary porcelain with wall outlet 400x490, complete with stainless steel trocadero lifting grate with damper, architect's choice, GEBERIT PUBLICA or equivalent
| - iztočna armatura z dolgim izlivom ter s pršno glavo po izbiri arhitekta, predvidoma HANSGROHE ali enakovredno | - long spout mixer with a shower head of the architect's choice, presumably HANSGROHE or equivalent
| - pršna glava in povezovalna gladka gibka cev na armaturo ter konzola za odlaganje pršne glave, po izbiri arhitekta, predvidoma HANSGROHE ali enakovredno | - shower head and connecting smooth flexible hose to the mixer and console for shower head storage, architect's choice, preferably HANSGROHE or equivalent
| - dva kotna ventila DN15 in veznima cevkama | - two DN15 angle valves and connecting tubes
| - jeklena podkonstrukcija za vgradnjo trokadera v montažno steno; GEBERIT DUOFIX | - steel substructure for installation of the trocadero in the precast wall; GEBERIT DUOFIX
| - obešalnik za garderobo; | - wardrobe hanger;
| - vključno s pritrdilnim in tesnilnim materialom; | - including fixing and sealing materials; | kpl | 6 |  | 0
1.37 | Drobna oprema za kuhinjsko pomivalno korito in montaža, izvedba za vgradnjo v kuhinjski pult, z ročno armaturo, ustrezajo proizvodi po izbiri arhitekta SADAR+VUGA ali enakovredno: | Kitchen sink fittings and installation, countertop-mounted version, with hand-held mixer taps, to match products of the architect's choice SADAR+VUGA or equivalent:
| - vgradnja stoječe enoročna armature za kuhinjsko pomivalno korito | - installation of a single-handle standing mixer for the kitchen sink
| - dva kotna ventila DN15 in veznima cevkama | - two DN15 angle valves and connecting tubes
| - sifon za kuhinjsko pomivalno korito | - siphon for kitchen sink
| - vključno s pritrdilnim in tesnilnim materialom; | - including fixing and sealing materials; | kpl | 8 |  | 0
1.38 | Umivalnik korito za laboratorij z iztočno armaturo, kompletno s pripadajočo opremo, ustrezajo proizvodi po izbiri arhitekta SADAR+VUGA oziroma BIRO ARCUS ali enakovredno: | Laboratory sink with draining mixer, complete with associated fittings, to suit products of the architect's choice SADAR+VUGA or BIRO ARCUS or equivalent:
| - umivalnik iz nerjavnega jekla 550x420 po izbiri arhitekta, predvidoma standard izvedba; | - stainless steel washbasin 550x420 of the architect's choice, presumably standard version;
| - iztočna armatura za umivalnik korito po izbiri arhitekta, predvidoma HANSGROHE ali enakovredno | - sink basin outlet fitting of the architect's choice, presumably HANSGROHE or equivalent
| - dva kotna ventila DN15 in veznima cevkama | - two DN15 angle valves and connecting tubes
| - podometni sifon za umivalnik, odtok horizontalen; | - concealed trap for washbasin, horizontal drain;
| - jeklena podkonstrukcija za vgradnjo umivalnika na montažno steno; GEBERIT DUOFIX | - steel substructure for mounting the washbasin on a prefabricated wall; GEBERIT DUOFIX
| - držalo za papirnate brisače; | - paper towel holder;
| - milnik za umivalnik; | - soap dispenser for washbasin;
| - koš za odpadne papirnate brisače; | - waste paper towel bin;
| - vključno s pritrdilnim in tesnilnim materialom; | - including fixing and sealing materials; | kpl | 91 |  | 0
1.39 | Umivalnik korito za laboratorij z iztočno armaturo, kompletno s pripadajočo opremo, ustrezajo proizvodi po izbiri arhitekta SADAR+VUGA oziroma BIRO ARCUS ali enakovredno: | Laboratory sink with draining mixer, complete with associated fittings, to suit products of the architect's choice SADAR+VUGA or BIRO ARCUS or equivalent:
| - umivalnik iz nerjavnega jekla 400x200 po izbiri arhitekta, predvidoma mini podolgovata izvedba ali enakovredno | - 400x200 stainless steel washbasin of the architect's choice, presumably mini-oblong or equivalent
| - iztočna armatura za umivalnik korito po izbiri arhitekta, predvidoma HANSGROHE ali enakovredno | - sink basin outlet fitting of the architect's choice, presumably HANSGROHE or equivalent
| - dva kotna ventila DN15 in veznima cevkama | - two DN15 angle valves and connecting tubes
| - podometni sifon za umivalnik, odtok horizontalen; | - concealed trap for washbasin, horizontal drain;
| - jeklena podkonstrukcija za vgradnjo umivalnika na montažno steno; GEBERIT DUOFIX | - steel substructure for mounting the washbasin on a prefabricated wall; GEBERIT DUOFIX
| - držalo za papirnate brisače; | - paper towel holder;
| - milnik za umivalnik; | - soap dispenser for washbasin;
| - koš za odpadne papirnate brisače; | - waste paper towel bin;
| - vključno s pritrdilnim in tesnilnim materialom; | - including fixing and sealing materials; | kpl | 6 |  | 0
1.40 | Umivalnik korito za laboratorij z iztočno armaturo, kompletno s pripadajočo opremo, ustrezajo proizvodi po izbiri arhitekta SADAR+VUGA oziroma BIRO ARCUS ali enakovredno: | Laboratory sink with draining mixer, complete with associated fittings, to suit products of the architect's choice SADAR+VUGA or BIRO ARCUS or equivalent:
| - umivalnik iz nerjavnega jekla, 1200x600 po izbiri arhitekta, predvidoma, globoka izvedba ali enakovredno; | - stainless steel washbasin, 1200x600 of the architect's choice, presumably deep or equivalent;
| - iztočna armatura za umivalnik korito po izbiri arhitekta, predvidoma HANSGROHE ali enakovredno | - sink basin outlet fitting of the architect's choice, presumably HANSGROHE or equivalent
| - dva kotna ventila DN15 in veznima cevkama | - two DN15 angle valves and connecting tubes
| - podometni sifon za umivalnik, odtok horizontalen; | - concealed trap for washbasin, horizontal drain;
| - jeklena podkonstrukcija za vgradnjo umivalnika na montažno steno; GEBERIT DUOFIX | - steel substructure for mounting the washbasin on a prefabricated wall; GEBERIT DUOFIX
| - držalo za papirnate brisače; | - paper towel holder;
| - milnik za umivalnik; | - soap dispenser for washbasin;
| - koš za odpadne papirnate brisače; | - waste paper towel bin;
| - vključno s pritrdilnim in tesnilnim materialom; | - including fixing and sealing materials; | kpl | 2 |  | 0
1.41 | Krogelna iztočni ventil za pitno vodo po EN806, navojni priključki, PN16, z ročico, material nerjavno jeklo, medenina, PTFE, vključno s pritrdilnim in tesnilnim materialom; | Ball drinking water outlet valve according to EN806, threaded connections, PN16, with handle, material stainless steel, brass, PTFE, incl. fitting and sealing material;
| - ustreza proizvod END ARMATUREN tip BT ali enakovredno | - corresponds to END ARMATUREN type BT or equivalent
| DN 15 - s priključkom za gibki spoj | DN 15 - with flexible coupling | kos | 96 |  | 0
| DN 20 - s priključkom za gibki spoj | DN 20 - with flexible coupling | kos | 16 |  | 0
| DN 25 - s priključkom za gibki spoj | DN 25 - with flexible coupling | kos | 24 |  | 0
1.42 | Naprava za pripravo prečiščene vode, za analitsko laboratorijsko uporabo po SIST EN ISO 3696, razred 2: elek.prevodnost, max: 0,1 mS/m (1µS/cm) oz. elek.upornost, min: 5 MΩcm; | Purified water preparation device for analytical laboratory use according to SIST EN ISO 3696, class 2: electrical conductivity, max: 0,1 mS/m (1µS/cm) or electrical resistivity, min: 5 MΩcm;
| Tehnični podatki: | Technical data:
| - vstop mehčana voda 5 °dH vsaj 10 l/min, DN15, 2 do 6 bar, priprava z RO in EDI, | - softened water inlet 5 °dH at least 10 l/min, DN15, 2 to 6 bar, RO and EDI preparation,
| - izstop kvaliteta vode tip 2, kapaciteta naprave 40 l/h, rezervoar 90 litrov, UV dezinfekcija | - outlet water quality type 2, plant capacity 40 l/h, 90 litres tank, UV disinfection
| - dimenzije LxBxH= 950x620x1260mm, delovna teža 250 kg, hrup do 50 dB na razdalji 1m; | - dimensions LxBxH= 950x620x1260mm, working weight 250 kg, noise up to 50 dB at a distance of 1m;
| - kompaktna stoječa izvedba z iztočnim mestom; | - compact, standing design with outlet point;
| - ustreza proizvod MERCK tip Milli-Q HX 7040 SD ali enakovredno | - corresponds to MERCK product type Milli-Q HX 7040 SD or equivalent
| Postavitev v hodnik P1.J4.001, ob stebru M-14 | Placement in corridor P1.J4.001, next to column M-14 | kpl | 1 |  | 0
1.43 | Naprava za pripravo prečiščene vode, za analitsko laboratorijsko uporabo po SIST EN ISO 3696, razred 2: elek.prevodnost, max: 0,1 mS/m (1µS/cm) oz. elek.upornost, min: 5 MΩcm; | Purified water preparation device for analytical laboratory use according to SIST EN ISO 3696, class 2: electrical conductivity, max: 0,1 mS/m (1µS/cm) or electrical resistivity, min: 5 MΩcm;
| Tehnični podatki: | Technical data:
| - vstop mehčana voda 5 °dH, DN15, 1 do 6 bar, priprava z RO in DI smolo, | - softened water inlet 5 °dH, DN15, 1 to 6 bar, preparation with RO and DI resin,
| - izstop kvaliteta vode tip 2, kapaciteta naprave 3 l/h, rezervoar 6 litrov, UV dezinfekcija, | - water quality outlet type 2, plant capacity 3 l/h, 6 litre tank, UV disinfection,
| - dimenzije LxBxH= 330x290x500mm, delovna teža 18 kg, | - dimensions LxBxH= 330x290x500mm, working weight 18 kg,
| - namizna lab izvedba z iztočnim mestom; | - table-top lab version with outlet;
| - ustreza proizvod MERCK tip MERCK tip RiOs DI 3 UV ali enakovredno | - corresponds to MERCK product type MERCK type RiOs DI 3 UV or equivalent
| Postavitev v laboratorijih: FOLAS N2, LFDT N2, LTT N2, LTT N2, TINT PR, … | Laboratory set-up: FOLAS N2, LFDT N2, LTT N2, LTT N2, TINT PR, .. | kpl | 10 |  | 0
1.44 | Pitnik z ročno armaturo, kompletno s pripadajočo opremo, ustrezajo proizvodi po izbiri arhitekta SADAR+VUGA ali enakovredno: | Drinking fountain with hand mixer, complete with associated fittings, to suit products of the architect's choice SADAR+VUGA or equivalent:
| - pitnik iz nerjavnega jekla AISO304 polirano, prostostoječa izvedba v obliki valja, D= 320mm H= 915 mm; DELABIE ILHA koda 180100 | - drinking bowl made of stainless steel AISO304 polished, free-standing, cylindrical, D= 320mm H= 915 mm; DELABIE ILHA code 180100
| - armatura za pitnik; DELABIE | - drinking fountain; DELABIE
| - dva kotna ventila DN15 in veznima cevkama | - two DN15 angle valves and connecting tubes
| - podometni sifon za umivalnik, odtok vertikalen; | - concealed trap for washbasin, vertical drain;
| - vključno s pritrdilnim in tesnilnim materialom; | - including fixing and sealing materials; | kpl | 8 |  | 0
1.45 | Tlačni preskus trdnosti in tesnenja sistema cevovodov, skladeno z opisom v "IZS Priročnik tlačnih preizkusov strojnih inštalacij", vključno s potrebnim materialom za izvedbo preizkusa, ter izdelavo pisnega poročila o uspešno opravljenem tlačnem preizkusu; | Pressure test of the strength and tightness of the piping system, as described in the "IZS Manual for Pressure Testing of Mechanical Installations", including the necessary materials for the test, and the production of a written report on the successful completion of the pressure test;
| - vodovod, pitna voda, skladnost z EN805, EN806 | - water supply, drinking water, EN805, EN806 compliance
| preskusni tlak = 1,1 x najvišji delovni tlak = 8,8 barg | test pressure = 1,1 x maximum working pressure = 8,8 barg | kpl | 1 |  | 0
1.46 | Izpiranje cevovodov s sanitarno hladno vodo v celotnem sistemu novoinstaliranih razvodov z namenom odstranjevanja nečistoč v sistemu cevovodov, vključno s čiščenjem filtrov in perlatorjev na iztočnih pipah; | Flushing of sanitary cold water pipelines throughout the newly installed piping system to remove impurities in the piping system, including cleaning of filters and perlators at outlet taps; | kpl | 1 |  | 0
1.47 | Dezinfekcija, vzorčenje in analiza sistema internega vodovoda v skladi s standardom SIST EN 806 za pitno vodo s strani pooblaščene organizacije, vključno z izdelavo pisnega poročila o uspešno opravljeni dezinfekciji in ustreznosti anliziranih vzorcev pitne vode; | Disinfection, sampling and analysis of the internal water supply system in accordance with SIST EN 806 for drinking water by an approved organisation, including the production of a written report on the successful disinfection and the adequacy of the analysed drinking water samples; | kpl | 1 |  | 0
1.48 | Ognjeodporna tesnilna masa, vgradnja na prehodu cevovodov skozi zid med požarnima sektortjema, požarna odpornost 90 minut, ustreza proizvod HILTI ali enakovredno. | Fire-resistant sealant, for installation at the transition of pipelines through the wall between the two fire sectors, fire resistance 90 minutes, equivalent to HILTI or equivalent.
| Vsak prehod mora biti označen z nalepko ali tablico z osnovnimi požarnimi podatki; | Each passageway must be marked with a sticker or placard with basic fire information; | kpl | 1 |  | 0
1.49 | Preizkusno obratovanje delovanja sistema v obsegu: | Operational test of the system in scope:
| - pregled instalacije, armatur in opreme, | - inspection of plumbing, fixtures and fittings,
| - pregled delovanja naprav, elementov regulacije in nastavitve parametrov, | - overview of the operation of the devices, control elements and parameter settings,
| - pregled odjemnih mest; | - a review of the customer sites;
| Preizkusno obratovanje traja neprekinjeno 72 ur. | The test operation shall be continuous for 72 hours. | kpl | 1 |  | 0
1.50 | Napisne ploščice iz nerjavne pločevine z vgravirano oznako po shemi za opremo in armature, kompletno z jekleno pritrdilno žico ali visoko kvalitetne nalepke; visoko trajanje H (več kot 15 let) | Stainless steel nameplates with engraved marking according to the scheme for fittings and fixtures, complete with steel fixing wire or high quality stickers; high durability H (more than 15 years) | kpl | 1 |  | 0
1.51 | Samolepilne puščice za označitev smeri pretoka ter z napisom vrste medija: visoko trajanje H (več kot 15 let) | Self-adhesive arrows to indicate the direction of flow and the type of media: high durability H (more than 15 years) | kpl | 1 |  | 0
1.52 | Izdelava montažnih risb za izvedbo inštalacij med gradnjo objekta, kot so: detajli priključkov, montažne skice, montažni detajli, ipd. | Preparation of assembly drawings for the installation of services during the construction of the building, such as: connection details, assembly sketches, assembly details, etc. | kpl | 1 |  | 0
1.53 | Kvalifikacije montaže IQ-pregledi (instalation qualification) po GEP Commissioning protokolu in dokumentiranje kvalifikacije montaže, vključno z odpravo prvotnih napak montaže; | Installation qualification IQ-checks (installation qualification) according to the GEP Commissioning Protocol and documentation of installation qualification, including correction of original installation faults; | kpl | 1 |  | 0
1.54 | Meritve delovanja OQ-kvalifikacija (operation qualification) ter dokumentiranje meritev delovanja, vključno z nastavitvijo parametrov; | OQ (operation qualification) measurements and documentation of performance measurements, including parameter setting; | kpl | 1 |  | 0
1.55 | Posnetki izvedenega stanja, sprotno beleženje vseh sprememb nastalih med izvedbo, vrisovanje in vpisovanje v PZI projektno dokumentacijo; | Recording of the as-built condition, keeping a running record of any changes made during the execution, plotting and recording in the PZI project documentation; | kpl | 1 |  | 0
1.56 | Stenska shema sistema, vloženo v zaščitni okvir s prosojnim umetnim steklom (plastika) ali plastificirano, vključno s pritrditvijo na notranjo steno v strojnici objekta; | A wall diagram of the system, enclosed in a protective frame with transparent plastic or plasticised glass, including fixing to an internal wall in the mechanical room of the building; | kpl | 1 |  | 0
1.57 | Primopredajna dokumentacija, ki mora vsebovati: izjave, dokazilo o zanesljivosti objekta, certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo, obratovanje in vzdrževanje ter ostalo primopredajno dokumantacijo. Predaja se v dveh mapiranih izvodih ter en izvod v elektronski obliki; | The handover documentation, which shall include: declarations, proof of the reliability of the facility, certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use, operation and maintenance, and other handover documentation. It shall be handed over in two mapped copies and one copy in electronic form; | kpl | 1 |  | 0
| VODOVOD, SANITARNA PITNA VODA | WATER SUPPLY, SANITARY DRINKING WATER |  |  |  | 0

## 4.8.2_Kanalizacija
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.8 | STROJNA DELA | MECHANICAL WORKS
4.8.2 | KANALIZACIJA | SEWER SYSTEM |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
2 | KANALIZACIJA | SEWER SYSTEM
| Vse postavke v nadalevanju zajemajo dobavo in montažo (razen tam kjer je to posebej navedeno). | All items below include delivery and installation (except where specifically indicated).
| Vertikalna fekalna kanalizacija | Vertical faecal sewerage
2.1 | Odtočne kanalizacijske cevi za vertikalno kanalizacijo, tesnjene izvedbe, skladnost z EN1451, razred B in EN14366, material homopolimerni polipropilen PP-M z notranjo PP in zunanjo PP zaščito, tiha izvedba LSC,A ≤ 16dB(A) pri pretoku vode 2 l/s, kemična odpornost pH 2÷12, temperature do 80°C, tlaki od -0,5 do 1,5 barg, požarna klasifikacija B1 oz. C-s3-d0 po EN13501-1, vključno z oblikovnimi kosi (kolena, redukcije, odcepi, …), spojnim in tesnilnim materialom, ustreza proizvod VALSIR tip BLACKFIRE ali TRIPLUS črne barve ali enakovredno, | Drainage pipes for vertical sewers, sealed design, compliance with EN1451, class B and EN14366, material homopolymer polypropylene PP-M with PP inner and PP outer protection, quiet design LSC,A ≤ 16dB(A) at a water flow of 2 l/s, chemical resistance pH 2÷12, temperatures up to 80°C, pressures from -0,5 to 1,5 barg, fire classification B1 or C-s3-d0 according to EN13501-1, including fittings (elbows, reducers, branches, etc.), jointing and sealing material, corresponding to VALSIR product type BLACKFIRE or TRIPLUS black or equivalent,
| - barva črna in požarna klasifikacija B1 za vidne ali delno vidne razvode v dvojnem stropu | - colour black and fire classification B1 for visible or partially visible ducts in a double ceiling
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and pipe clamps with noise damping lining, suitable for HILTI or SIKLA, or equivalent;
| DN 40, ø 40 x 1,8 | DN 40, ø 40 x 1,8 | m | 200 |  | 0
| DN 50, ø 50 x 1,8 | DN 50, ø 50 x 1,8 | m | 340 |  | 0
| DN 70, ø 75 x 2,6 | DN 70, ø 75 x 2,6 | m | 320 |  | 0
| DN 100, ø 110 x 3,4 | DN 100, ø 110 x 3,4 | m | 400 |  | 0
| DN 125, ø 125 x 3,9 | DN 125, ø 125 x 3,9 | m | 140 |  | 0
| DN 150, ø 160 x 4,9 | DN 150, ø 160 x 4,9 | m | 500 |  | 0
| DN 200, ø 200 x 6,2 | DN 200, ø 200 x 6,2 | m | 80 |  | 0
| 45°lok DN 40, ø 40 x 1,8 | 45°arc DN 40, ø 40 x 1,8 | kos | 30 |  | 0
| 45°lok DN 50, ø 50 x 1,8 | 45°arc DN 50, ø 50 x 1,8 | kos | 60 |  | 0
| 45°lok DN 70, ø 75 x 2,6 | 45°arc DN 70, ø 75 x 2,6 | kos | 40 |  | 0
| 45°lok DN 100, ø 110 x 3,4 | 45°arc DN 100, ø 110 x 3,4 | kos | 60 |  | 0
| 45°lok DN 125, ø 125 x 3,9 | 45°block DN 125, ø 125 x 3,9 | kos | 20 |  | 0
| 45°lok DN 150, ø 160 x 4,9 | 45°arc DN 150, ø 160 x 4,9 | kos | 60 |  | 0
| 45°lok DN 200, ø 200 x 6,2 | 45°arc DN 200, ø 200 x 6,2 | kos | 20 |  | 0
| 90°lok DN 40, ø 40 x 1,8 | 90°lok DN 40, ø 40 x 1,8 | kos | 60 |  | 0
| 90°lok DN 50, ø 50 x 1,8 | 90°lok DN 50, ø 50 x 1,8 | kos | 90 |  | 0
| 90°lok DN 70, ø 75 x 2,6 | 90°lok DN 70, ø 75 x 2,6 | kos | 80 |  | 0
| 90°lok DN 100, ø 110 x 3,4 | 90°lok DN 100, ø 110 x 3,4 | kos | 90 |  | 0
| 90°lok DN 125, ø 125 x 3,9 | 90°lok DN 125, ø 125 x 3,9 | kos | 20 |  | 0
| 90°lok DN 150, ø 160 x 4,9 | 90°lok DN 150, ø 160 x 4,9 | kos | 60 |  | 0
| 90°lok DN 200, ø 200 x 6,2 | 90°lok DN 200, ø 200 x 6,2 | kos | 20 |  | 0
| Y kos DN 50 / priključek DN 50 | Y piece DN 50 / connection DN 50 | kos | 160 |  | 0
| Y kos DN 70 / priključek DN 50 | Y piece DN 70 / connection DN 50 | kos | 160 |  | 0
| Y kos DN 100 / priključek DN 50 | Y piece DN 100 / connection DN 50 | kos | 80 |  | 0
| Y kos DN 100 / priključek DN 70 | Y piece DN 100 / connection DN 70 | kos | 160 |  | 0
| Y kos DN 100 / priključek DN 100 | Y piece DN 100 / connection DN 100 | kos | 160 |  | 0
| Y kos DN 125 / priključek DN 100 | Y piece DN 125 / connection DN 100 | kos | 40 |  | 0
| Y kos DN 150 / priključek DN 100 | Y piece DN 150 / connection DN 100 | kos | 40 |  | 0
| Y kos DN 150 / priključek DN 125 | Y piece DN 150 / connection DN 125 | kos | 20 |  | 0
| Y kos DN 200 / priključek DN 100 | Y piece DN 200 / connection DN 100 | kos | 20 |  | 0
| Y kos DN 200 / priključek DN 125 | Y piece DN 200 / connection DN 125 | kos | 8 |  | 0
| Y kos DN 200 / priključek DN 150 | Y piece DN 200 / connection DN 150 | kos | 8 |  | 0
| redukcija DN 50 / DN 40 | dN 50 / DN 40 reduction | kos | 120 |  | 0
| redukcija DN 70 / DN 50 | dN 70 / DN 50 reduction | kos | 100 |  | 0
| redukcija DN 100 / DN 50 | dN 100 / DN 50 reduction | kos | 60 |  | 0
| redukcija DN 100 / DN 70 | dN 100 / DN 70 reduction | kos | 80 |  | 0
| redukcija DN 125 / DN 100 | dN 125 / DN 100 reduction | kos | 60 |  | 0
| redukcija DN 150 / DN 125 | reduction DN 150 / DN 125 | kos | 40 |  | 0
| redukcija DN 150 / DN 125 | reduction DN 150 / DN 125 | kos | 16 |  | 0
| redukcija DN 200 / DN 150 | reduction DN 200 / DN 150 | kos | 12 |  | 0
| čistilni kanalizacijski kos DN 100 | sewer cleaning piece DN 100 | kos | 16 |  | 0
| čistilni kanalizacijski kos DN 125 | sewer cleaning piece DN 125 | kos | 12 |  | 0
| čistilni kanalizacijski kos DN 150 | sewer cleaning piece DN 150 | kos | 8 |  | 0
| čistilni kanalizacijski kos DN 200 | sewer cleaning piece DN 200 | kos | 4 |  | 0
| oddušna strešna kapa s strešno obrobo DN 100 | vented roof cap with roof flashing DN 100 | kos | 4 |  | 0
| oddušna strešna kapa s strešno obrobo DN 125 | vented roof cap with roof flashing DN 125 | kos | 8 |  | 0
| oddušna strešna kapa s strešno obrobo DN 150 | vented roof cap with roof flashing DN 150 | kos | 4 |  | 0
2.2 | Oddušni ventil za vertikalno kanalizacijo, skladno s EN12380 in EN12056, material polipropilen PP, vključno s spojnim, tesnilnim materialom, ustreza proizvod VALSIR tip VENTILO ali enakovredno; | Vent valve for vertical sewerage, according to EN12380 and EN12056, material polypropylene PP, including jointing, sealing material, corresponding to VALSIR product type VENTILO or equivalent;
| - za oddušno kanalizacijsko cev DN50, ø 50 | - for vented sewer pipe DN50, ø 50 | kos | 50 |  | 0
| - za oddušno kanalizacijsko cev DN100, ø 110 | - for vented sewer pipe DN100, ø 110 | kos | 20 |  | 0
2.3 | Talni odtok z navpičnim ali vodoravnim iztočnim delom, z razstavljivo vodno smradno zaporo (sifon) in protizdrsno mrežno rešetko, material AISI304, kapaciteta iztekanja 2,5 l/s, vključno s spojnim in tesnilnim materialom, za dimenzijo rešetke in priključenega odtoka: | Floor drain with vertical or horizontal outlet, with demountable water odour trap (siphon) and non-slip mesh grate, material AISI304, outlet capacity 2,5 l/s, including jointing and sealing material, for the grate and connected outlet dimensions:
| - ustreza proizvod ACO Inox talni požiralnik 157 - vertikalni iztok ali enakovredno | - corresponds to ACO Inox Floor Swallower 157 - Vertical outlet or equivalent
| 200 x 200 - DN 100 - priklop na cev PP ø 110 | 200 x 200 - DN 100 - connection to PP pipe ø 110 | kpl | 4 |  | 0
2.4 | Talni sifon pretočni z vodno smradno zaporo, sestavljen iz ohišja sifona material PP ter nerjavne rešetke dimenzije 150 x 150 mm, horizontalni vtok ø 50, horizontalni iztok ø 50, vključno z vsem spojnim, tesnilnim in pritrdilnim materialom; | Floor flow trap with water odour stop, consisting of trap body PP material and stainless steel grating 150 x 150 mm, horizontal inlet ø 50, horizontal outlet ø 50, including all joining, sealing and fixing material;
| - ustreza proizvod VALSIR ali enakovredno | - corresponds to a VALSIR product or equivalent | kpl | 40 |  | 0
2.5 | Sifon za kondenzat odvodni priključek DN40, dovodni priključkom 5/4' (DN32 - stisnjen spoj) oz. d 12 - 18 mm (za gladke cevne nastavke) vertikalno ali vodoravno, z vodno smradno zaporo (60 mm) in mehansko smradno zaporo s kroglico ter čistilnim vložkom, predviden za klimatske naprave, material PP, skladnost z EN12056, vključno s spojnim in tesnilnim materialom; | Condensate trap outlet connection DN40, inlet connection 5/4' (DN32 - compression joint) or d 12 - 18 mm (for plain pipe fittings) vertically or horizontally, with water odour stop (60 mm) and mechanical odour stop with ball and cleaning insert, intended for air-conditioning systems, material PP, compliance with EN12056, incl. jointing and sealing material;
| - ustreza proizvod Hutterer & Lechner tip HL136.N oziroma .3 ali enakovredno | - corresponds to Hutterer & Lechner product type HL136.N or .3 or equivalent | kpl | 40 |  | 0
2.6 | Požarna objemka z kanalizacijske cevi iz umetne mase PP ipd, požarne odpornost EI240 po EN 1366-3, ustreza proizvod VALSIR tip COLLARWINGS ali enakovredno, vključno s tesnilnim in pritrdilnim materialom; za cev | Fire clamp for sewer pipes made of PP plastic, etc., fire-resistance rating EI240 according to EN 1366-3, corresponding to VALSIR product type COLLARWINGS or equivalent, including sealing and fixing material; for the pipe
| DN 50, ø 50 x 1,8 | DN 50, ø 50 x 1,8 | kos | 80 |  | 0
| DN 70, ø 75 x 2,6 | DN 70, ø 75 x 2,6 | kos | 60 |  | 0
| DN 100, ø 110 x 3,4 | DN 100, ø 110 x 3,4 | kos | 120 |  | 0
| DN 125, ø 125 x 3,9 | DN 125, ø 125 x 3,9 | kos | 16 |  | 0
| DN 150, ø 160 x 4,9 | DN 150, ø 160 x 4,9 | kos | 12 |  | 0
| DN 200, ø 200 x 6,2 | DN 200, ø 200 x 6,2 | kos | 8 |  | 0
| Kanalizacija iz kuhinje | Drainage from the kitchen
2.7 | Talni odtok, talni požiralnik, talna kanaleta, talno korito, z razstavljivo smradno zaporo, s sifonom za čiščenje od zgoraj, protizdrsna letvena rešetka, obremenitve M125, material AISI304 (1.4301), higijenska izvedba za uporabo v profesionalnih kuhinjah, z zaokrožnicami, higienski zvari, pasivirano, skladnost s standardi EN1253, EN1433, EN1672, EN ISO14159, HACCAP, EHEDG, CE izjava, dobavljeno z nogicami za niveliranje in sidri za vbetoniranje; | Floor drain, floor eschar, floor channel, floor sink, with demountable odour trap, with siphon for cleaning from above, non-slip slatted grate, load capacity M125, material AISI304 (1.4301), hygienic design for use in professional kitchens, with rounded edges, hygienic welds, passivated, compliance with EN1253, EN1433, EN1672, EN ISO14159, HACCAP, EHEDG, CE declaration, supplied with levelling feet and anchors for concreting;
| - namestitev in vgradnja v betonsko talno ploščo, vključno s higijenskim spojnim in tesnilnim materialom; | - installation and installation in the concrete floor slab, including hygienic jointing and sealing material;
| - ustreza proizvod ACO ali enakovredno - dimenzija v mm - iztok DN, vertiklno ali horizontalno | - corresponds to product ACO or equivalent - dimension in mm - outlet DN, vertical or horizontal
| 200 x 200 - DN 75 (ø 75) | 200 x 200 - DN 75 (ø 75) | kpl | 5 |  | 0
| 300 x 300 - DN 75 (ø 75) | 300 x 300 - DN 75 (ø 75) | kpl | 4 |  | 0
| 400 x 600 - DN 100 (ø 110) | 400 x 600 - DN 100 (ø 110) | kpl | 2 |  | 0
| 400 x 800 - DN 100 (ø 110) | 400 x 800 - DN 100 (ø 110) | kpl | 1 |  | 0
2.8 | Odtočne jeklene nerjavne cevi za vertikalno kanalizacijo, tesnjene izvedbe, skladnost z EN1124, material AISI304 ali boljši, tesnila FPM Viton, kemična odpornost na olja, kisline in baze, temperature do 100°C, tlaki v ceveh od -0,5 do 1,5 barg, požarna klasifikacija A1 po EN13501, vključno z oblikovnimi kosi (kolena, redukcije, odcepi, …), spojnim in tesnilnim materialom, ustreza proizvod ACO tip ACO PIPE stinless steel pipework system ali enakovredno, | Stainless steel drain pipes for vertical sewers, sealed design, EN1124 compliant, material AISI304 or better, FPM Viton gaskets, chemical resistance to oils, acids and bases, temperatures up to 100°C, pipe pressures from -0.5 to 1.5 barg, fire classification A1 according to EN13501, including forming pieces (elbows, reducers, branches, etc.), joining and sealing material, corresponding to the product ACO type ACO PIPE stinless steel pipework system or equivalent,
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and pipe clamps with noise damping lining, suitable for HILTI or SIKLA, or equivalent;
| - prečrpavanje sanitarnih fekalnih odtokov | - pumping of sanitary fecal effluents
| DN 50, ø 50 x 1,0 | DN 50, ø 50 x 1,0 | m | 60 |  | 0
| DN 75, ø 75 x 1,0 | DN 75, ø 75 x 1,0 | m | 12 |  | 0
| DN 100, ø 110 x 1,0 | DN 100, ø 110 x 1,0 | m | 72 |  | 0
| DN 125, ø 125 x 1,0 | DN 125, ø 125 x 1,0 | m | 42 |  | 0
| DN 150, ø 160 x 1,25 | DN 150, ø 160 x 1,25 | m | 36 |  | 0
| 45°lok DN 50, ø 50 x 1,0 | 45°arc DN 50, ø 50 x 1,0 | kos | 10 |  | 0
| 45°lok DN 75, ø 75 x 1,0 | 45°arc DN 75, ø 75 x 1,0 | kos | 4 |  | 0
| 45°lok DN 100, ø 110 x 1,0 | 45°arc DN 100, ø 110 x 1,0 | kos | 12 |  | 0
| 45°lok DN 125, ø 125 x 1,0 | 45°arc DN 125, ø 125 x 1,0 | kos | 8 |  | 0
| 45°lok DN 150, ø 160 x 1,25 | 45°arc DN 150, ø 160 x 1,25 | kos | 8 |  | 0
| 90°lok DN 50, ø 50 x 1,0 | 90°lock DN 50, ø 50 x 1,0 | kos | 20 |  | 0
| 90°lok DN 75, ø 75 x 1,0 | 90°lock DN 75, ø 75 x 1,0 | kos | 8 |  | 0
| 90°lok DN 100, ø 110 x 1,0 | 90°lok DN 100, ø 110 x 1,0 | kos | 24 |  | 0
| 90°lok DN 125, ø 125 x 1,0 | 90°lock DN 125, ø 125 x 1,0 | kos | 16 |  | 0
| 90°lok DN 150, ø 160 x 1,25 | 90°lok DN 150, ø 160 x 1,25 | kos | 12 |  | 0
| Y kos DN 50 / priključek DN 50 | Y piece DN 50 / connection DN 50 | kos | 20 |  | 0
| Y kos DN 70 / priključek DN 50 | Y piece DN 70 / connection DN 50 | kos | 8 |  | 0
| Y kos DN 100 / priključek DN 50 | Y piece DN 100 / connection DN 50 | kos | 24 |  | 0
| Y kos DN 100 / priključek DN 70 | Y piece DN 100 / connection DN 70 | kos | 16 |  | 0
| Y kos DN 100 / priključek DN 100 | Y piece DN 100 / connection DN 100 | kos | 12 |  | 0
| Y kos DN 125 / priključek DN 100 | Y piece DN 125 / connection DN 100 | kos | 8 |  | 0
| Y kos DN 150 / priključek DN 100 | Y piece DN 150 / connection DN 100 | kos | 8 |  | 0
| čistilni kanalizacijski kos DN 100 | sewer cleaning piece DN 100 | kos | 1 |  | 0
| čistilni kanalizacijski kos DN 125 | sewer cleaning piece DN 125 | kos | 1 |  | 0
| čistilni kanalizacijski kos DN 150 | sewer cleaning piece DN 150 | kos | 1 |  | 0
| oddušna strešna kapa s strešno obrobo DN 100 | vented roof cap with roof flashing DN 100 | kos | 1 |  | 0
| prirobnica DN 150 po EN1092, PN16, z vijačnim in tesnilnim materialom | flange DN 150 to EN1092, PN16, with bolting and sealing material | kos | 2 |  | 0
2.9 | Naprava za izločanje olja in maščob iz kuhinje, kompaktna nerjanvna prosto stoječa izvedba, s samočistilnim sistemom, črpalko za prečrpavanje v cisterno ter posodo za vzorčanje na iztoku v komunalno kanalizacijo, vgradnja na tleh kleti, skladnost z EN1825 in DIN4040-100, material nerjavno jeklo AISI316, sestavljeno iz: rezervoarja za separacijo z revizijskimi odprtinami, vizuelnim oknom in priključki, samočistilni sistem s črpalko za pranje pralno glavo in pralnimi povezavami, črpalko za prečrpavanje v cisterno s priključkom za ciseterno, priključek za sanitarno vodo z ventilskim setom in zaščito pred povratnim tokom po EN1717 tip AA, nivojska sonda s stikalnimi funkcijami in alarmnimi nivoji, ostala pripadajoča senzorika, ter elektro krmilna omara, dobavljeno kot kompaktna naprava, vključno s protiprirobnicama, vijačnim in tesnilnim materialom. Tehnični podatki: | Naprava za izločanje olja in maščob iz kuhinje, kompaktna nerjanvna prosto stoječa izvedba, s samočistilnim sistemom, črpalko za prečrpavanje v cisterno ter posodo za vzorčanje na iztoku v komunalno kanalizacijo, vgradnja na tleh kleti, skladnost z EN1825 in DIN4040-100, material nerjavno jeklo AISI316, sestavljeno iz: rezervoarja za separacijo z revizijskimi odprtinami, vizuelnim oknom in priključki, samočistilni sistem s črpalko za pranje pralno glavo in pralnimi povezavami, črpalko za prečrpavanje v cisterno s priključkom za ciseterno, priključek za sanitarno vodo z ventilskim setom in zaščito pred povratnim tokom po EN1717 tip AA, nivojska sonda s stikalnimi funkcijami in alarmnimi nivoji, ostala pripadajoča senzorika, ter elektro krmilna omara, dobavljeno kot kompaktna naprava, vključno s protiprirobnicama, vijačnim in tesnilnim materialom. Tehnični podatki:
| - kapaciteta 7 l/s = 25,2 m3/h | - capacity 7 l/s = 25.2 m3/h
| - rezervoar volumen 1600 l = 1,6 m3 | - tank volume 1600 l = 1,6 m3
| - priključki: natočni vstop kuhinske kanalizacije DN150, iztok na posodo za vzorčenje DN150, prečrpavanje v cisterno DN100/65, odduh DN100, priključek sanitarne vode DN20/65 | - connections: kitchen sewer inlet DN150, outlet to sampling tank DN150, pumping to cistern DN100/65, vent DN100, sanitary water connection DN20/65
| - posoda za vzorčenje z horizontalnim natokom, DN150 in vertikalnim iztokom DN150, pokrov posode , skladnost z EN877, material AISI316 | - sampling container with horizontal inlet DN150 and vertical outlet DN150, container cover, EN877 compliance, material AISI316
| - dimenzije ca: dolžina L x širina B x višina H = 3500 x 1200 x 2000 mm; transportna teža ca 500 kg, obratovalna teža ca 2000 kg | - dimensions ca: length L x width B x height H = 3500 x 1200 x 2000 mm; transport weight ca 500 kg, operating weight ca 2000 kg
| - električni podatki: Pel= 8kW, 400V/3/50Hz; | - electrical data: Pel= 8kW, 400V/3/50Hz;
| - krmiljenje naprave za vse delovne režime obratovana in komunikacija z napravo za prečrpavanje v komunalno kanalizacijo; | - control of the plant for all operating modes and communication with the sewage pumping plant;
| - električna krmilna omara z upravljalnim tablojem ter komunikacijo RS485 / Modbus RTU | - electrical control cabinet with control board and RS485 / Modbus RTU communication
| - ustreza proizvod ACO tip LipuJet-S-OAP z opremo 3 - NS7 ter opisano dodatno opremo ali enakovredno | - corresponds to the ACO product type LipuJet-S-OAP with equipment 3 - NS7 and the described accessories or equivalent
| Oznaka: LOM89.080 | Code: LOM89.080 | kpl | 1 |  | 0
2.10 | Kompaktna črpalna naprava za prečrpavanje odpadne vode iz naprave za izločanje olja in maščob, sestavljeno iz dveh vzporedno vezanih črpalk, rezervoarja odpadne vode, nivojskega tipala s stikalnimi funkcijami in alarmnimi nivoji, set za priklop dveh cevovodov z nepovratnimi in zapornimi ventili ter elektro krmilne omare, dobavljeno kot kompaktna naprava, vključno s protiprirobnicama, vijačnim in tesnilnim materialom. Tehnični podatki: | Compact pumping unit for pumping waste water from an oil and grease extraction plant, consisting of two pumps connected in parallel, waste water tank, level sensor with switching functions and alarm levels, set for connecting two pipelines with non-return and shut-off valves and electrical control cabinet, supplied as a compact unit, including counter-fittings, screwing and sealing material. Technical data:
| - prečrpavanje nevtralizirane odpadne vode iz naprave za izločanje olja in maščob kuhinje; | - pumping neutralised waste water from the kitchen oil and grease extraction plant;
| - pretok V= 8 l/s = 28,8 m3/h pri tlačna višina prečrpavanja H= 10 m | - flow rate V= 8 l/s = 28,8 m3/h at pumping pressure head H= 10 m
| - 2 črpalki za prečrpavanje (vodilna in sledljiva) | - 2 pumping pumps (lead and traceable)
| - rezervoar material PE, volumen 150 litrov | - tank material PE, volume 150 litres
| - priključki: natočni DN150, tlačni DN100 | - connections: flow DN150, pressure DN100
| - dimenzije ca: dolžina L x širina B x višina H = 1550 x 800 x 700 mm; teža ca 150 kg | - dimensions ca: length L x width B x height H = 1550 x 800 x 700 mm; weight ca 150 kg
| - električni podatki: Pel= 3,5+3kW, 400V/3/50Hz, IP68 | - electrical data: Pel= 3,5+3kW, 400V/3/50Hz, IP68
| - kaskadno krmiljenje črpalk, avtomatsko nastavljiva izmenjava vodeilne in sledljive črpalke | - cascade pump control, automatically adjustable waterline exchange and traceable pumps
| - električna krmilna omara z upravljalnim tablojem ter komunikacijo RS485 / Modbus RTU | - electrical control cabinet with control board and RS485 / Modbus RTU communication
| - ustreza proizvod ACO tip MuliStar DDP1.2 z opisano dodatno opremo ali enakovredno | - corresponds to ACO product type MuliStar DDP1.2 with the described accessories or equivalent
| Oznaka: PN89.081 | Code: PN89.081 | kpl | 1 |  | 0
2.11 | Oddušni ventil za vertikalno kanalizacijo, skladno s EN12380 in EN12056, material polipropilen PP, vključno s spojnim, tesnilnim materialom, ustreza proizvod VALSIR tip VENTILO ali enakovredno; | Vent valve for vertical sewerage, according to EN12380 and EN12056, material polypropylene PP, including jointing, sealing material, corresponding to VALSIR product type VENTILO or equivalent;
| - za oddušno kanalizacijsko cev DN50, ø 50 | - for vented sewer pipe DN50, ø 50 | kos | 4 |  | 0
| - za oddušno kanalizacijsko cev DN100, ø 110 | - for vented sewer pipe DN100, ø 110 | kos | 2 |  | 0
2.12 | Jeklene nerjavne cevi izdelane po ISO1127, material AISI304 ali boljši, vključno z oblikovnimi kosi (loki, redukcije, T kosi, ...) in varilnim materialom, varjenje TIG pod inertnim plinom, | Stainless steel tubes manufactured according to ISO1127, material AISI304 or better, including forming pieces (bends, reductions, T-pieces, etc.) and welding consumables, TIG welding under inert gas,
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno za tlačne vode prečrpavanja; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and pipe clamps with noise damping lining, corresponding to HILTI or SIKLA product, or equivalent for pressurised pumping lines;
| DN 100, ø 114,3 x 2,3 | DN 100, ø 114,3 x 2,3 | m | 90 |  | 0
| 45°lok DN 100, ø 114,3 x 2,3 | 45°arc DN 100, ø 114,3 x 2,3 | kos | 12 |  | 0
| 90°lok DN 100, ø 114,3 x 2,3 | 90°lok DN 100, ø 114,3 x 2,3 | kos | 8 |  | 0
| prirobnica DN 100 po EN1092, PN16, z vijačnim in tesnilnim materialom | flange DN 100 to EN1092, PN16, with bolting and sealing material | kos | 4 |  | 0
| slepa prirobnica DN 100 po EN1092, PN16, z vijačnim in tesnilnim materialom | blind flange DN 100 to EN1092, PN16, with bolting and sealing material | kos | 1 |  | 0
2.13 | Polietilenske cevi visoke gostote PEHD za tlačno kanalizacijo (prečrpavanje), PN10, material PE100, v skladu s standardom EN 13244, vključno z elekrofuzijskimi oblikovnimi kosi (spojke, loki, redukcije, T kosi, ...) ter elektrofuzijskim materilom za varjenje, (OD x s = zunanji premer cevi x debelina stene cevi), ustreza proizvod ARGO z oblikovnimi kosi GEORG FISCHER ali enakovredno: | High-density polyethylene PEHD pipes for pressure sewers (pumping), PN10, material PE100, in accordance with EN 13244, including electrofusion fittings (couplings, bends, reducers, T-pieces, etc.) and electrofusion welding consumables, (OD x s = outer diameter of the pipe x wall thickness of the pipe), corresponding to the product ARGO with GEORG FISCHER fittings or equivalent:
| komplet s polaganjem podzemnega voda v peščeni posteljici ter s PVC označevalnim trakom za kanalizacijo; | complete with underground water laying in a sand bed and PVC sewer marking tape;
| OD 125 (ø 125 x 7,4) | OD 125 (ø 125 x 7,4) | m | 30 |  | 0
| Spojka OD 125 (ø 125 x 7,4) | Coupling OD 125 (ø 125 x 7,4) | kos | 6 |  | 0
| 45°lok OD 125 (ø 125 x 7,4) | 45°block OD 125 (ø 125 x 7,4) | kos | 6 |  | 0
| 90°lok OD 125 (ø 125 x 7,4) | 90°block OD 125 (ø 125 x 7,4) | kos | 4 |  | 0
| Prirobnica DN 100 / OD 125 po EN1092, PN16, komplet s prirobničnim spojem in tesnilom | Flange DN 100 / OD 125 to EN1092, PN16, complete with flange joint and gasket | kpl | 1 |  | 0
| Kanalizacija iz laboratorijev | Sewage from laboratories
2.14 | Talni odtok, talni požiralnik, talna kanaleta, talno korito, z razstavljivo smradno zaporo, s sifonom za čiščenje od zgoraj, protizdrsna letvena rešetka, obremenitve M125, material AISI304 (1.4301), higijenska izvedba za uporabo v profesionalnih kuhinjah, z zaokrožnicami, higienski zvari, pasivirano, skladnost s standardi EN1253, EN1433, EN1672, EN ISO14159, HACCAP, EHEDG, CE izjava, dobavljeno z nogicami za niveliranje in sidri za vbetoniranje; | Floor drain, floor eschar, floor channel, floor sink, with demountable odour trap, with siphon for cleaning from above, non-slip slatted grate, load capacity M125, material AISI304 (1.4301), hygienic design for use in professional kitchens, with rounded edges, hygienic welds, passivated, compliance with EN1253, EN1433, EN1672, EN ISO14159, HACCAP, EHEDG, CE declaration, supplied with levelling feet and anchors for concreting;
| - namestitev in vgradnja v betonsko talno ploščo, vključno s higijenskim spojnim in tesnilnim materialom; | - installation and installation in the concrete floor slab, including hygienic jointing and sealing material;
| - ustreza proizvod ACO ali enakovredno - dimenzija v mm - iztok DN, vertiklno ali horizontalno | - corresponds to product ACO or equivalent - dimension in mm - outlet DN, vertical or horizontal
| - talni odtok, talni požiralnik | - floor drain, floor water trap
| 200 x 200 - DN 75 (ø 75) | 200 x 200 - DN 75 (ø 75) | kpl | 42 |  | 0
| 200 x 200 - DN 100 (ø 110) | 200 x 200 - DN 100 (ø 110) | kpl | 48 |  | 0
| - talna kanaleta, sestavljiva s tesnili, modular | - floor channel, assembled with seals, modular
| linijska 200 x 500 - brez iztoka | inline 200 x 500 - without outlet | kpl | 8 |  | 0
| linijska 200 x 1000 - brez iztoka | inline 200 x 1000 - without outlet | kpl | 8 |  | 0
| linijska 200 x 2000 - brez iztoka | inline 200 x 2000 - without outlet | kpl | 2 |  | 0
| linijska 200 x 3000 - brez iztoka | inline 200 x 3000 - without outlet | kpl | 6 |  | 0
| kotna 200 x 500 (oba kraka) - brez iztoka | angular 200 x 500 (both arms) - without outlet | kpl | 2 |  | 0
| linijska 200 x 500 - DN 100 (ø 110) | line 200 x 500 - DN 100 (ø 110) | kpl | 6 |  | 0
| linijski zakluček 200 | line lock 200 | kpl | 10 |  | 0
2.15 | Odtočne jeklene nerjavne cevi za vertikalno kanalizacijo, tesnjene izvedbe, skladnost z EN1124, material AISI304 ali boljši, tesnila FPM Viton, kemična odpornost na olja, kisline in baze, temperature do 100°C, tlaki v ceveh od -0,5 do 1,5 barg, požarna klasifikacija A1 po EN13501, vključno z oblikovnimi kosi (kolena, redukcije, odcepi, …), spojnim in tesnilnim materialom, ustreza proizvod ACO tip ACO PIPE stinless steel pipework system ali enakovredno, | Stainless steel drain pipes for vertical sewers, sealed design, EN1124 compliant, material AISI304 or better, FPM Viton gaskets, chemical resistance to oils, acids and bases, temperatures up to 100°C, pipe pressures from -0.5 to 1.5 barg, fire classification A1 according to EN13501, including forming pieces (elbows, reducers, branches, etc.), joining and sealing material, corresponding to the product ACO type ACO PIPE stinless steel pipework system or equivalent,
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and hose clamps with noise damping lining, suitable for HILTI or SIKLA, or equivalent;
| - prečrpavanje sanitarnih fekalnih odtokov | - pumping of sanitary fecal effluents
| DN 50, ø 50 x 1,0 | DN 50, ø 50 x 1,0 | m | 870 |  | 0
| DN 75, ø 75 x 1,0 | DN 75, ø 75 x 1,0 | m | 390 |  | 0
| DN 100, ø 110 x 1,0 | DN 100, ø 110 x 1,0 | m | 600 |  | 0
| DN 125, ø 125 x 1,0 | DN 125, ø 125 x 1,0 | m | 30 |  | 0
| DN 150, ø 160 x 1,25 | DN 150, ø 160 x 1,25 | m | 390 |  | 0
| DN 200, ø 200 x 1,5 | DN 200, ø 200 x 1,5 | m | 30 |  | 0
| 45°lok DN 50, ø 50 x 1,0 | 45°arc DN 50, ø 50 x 1,0 | kos | 180 |  | 0
| 45°lok DN 75, ø 75 x 1,0 | 45°arc DN 75, ø 75 x 1,0 | kos | 90 |  | 0
| 45°lok DN 100, ø 110 x 1,0 | 45°arc DN 100, ø 110 x 1,0 | kos | 150 |  | 0
| 45°lok DN 125, ø 125 x 1,0 | 45°arc DN 125, ø 125 x 1,0 | kos | 10 |  | 0
| 45°lok DN 150, ø 160 x 1,25 | 45°arc DN 150, ø 160 x 1,25 | kos | 60 |  | 0
| 90°lok DN 200, ø 200 x 1,5 | 90°lok DN 200, ø 200 x 1,5 | kos | 10 |  | 0
| 90°lok DN 50, ø 50 x 1,0 | 90°lock DN 50, ø 50 x 1,0 | kos | 180 |  | 0
| 90°lok DN 75, ø 75 x 1,0 | 90°lock DN 75, ø 75 x 1,0 | kos | 90 |  | 0
| 90°lok DN 100, ø 110 x 1,0 | 90°lok DN 100, ø 110 x 1,0 | kos | 150 |  | 0
| 90°lok DN 125, ø 125 x 1,0 | 90°lock DN 125, ø 125 x 1,0 | kos | 10 |  | 0
| 90°lok DN 150, ø 160 x 1,25 | 90°lok DN 150, ø 160 x 1,25 | kos | 60 |  | 0
| 90°lok DN 200, ø 200 x 1,5 | 90°lok DN 200, ø 200 x 1,5 | kos | 10 |  | 0
| Y kos DN 50 / priključek DN 50 | Y piece DN 50 / connection DN 50 | kos | 60 |  | 0
| Y kos DN 70 / priključek DN 50 | Y piece DN 70 / connection DN 50 | kos | 120 |  | 0
| Y kos DN 100 / priključek DN 50 | Y piece DN 100 / connection DN 50 | kos | 60 |  | 0
| Y kos DN 100 / priključek DN 70 | Y piece DN 100 / connection DN 70 | kos | 90 |  | 0
| Y kos DN 100 / priključek DN 100 | Y piece DN 100 / connection DN 100 | kos | 120 |  | 0
| Y kos DN 125 / priključek DN 100 | Y piece DN 125 / connection DN 100 | kos | 10 |  | 0
| Y kos DN 150 / priključek DN 100 | Y piece DN 150 / connection DN 100 | kos | 60 |  | 0
| R kos DN 200 / priključek DN 150 | R piece DN 200 / connection DN 150 | kos | 1 |  | 0
| čistilni kanalizacijski kos DN 100 | sewer cleaning piece DN 100 | kos | 10 |  | 0
| čistilni kanalizacijski kos DN 125 | sewer cleaning piece DN 125 | kos | 10 |  | 0
| čistilni kanalizacijski kos DN 150 | sewer cleaning piece DN 150 | kos | 10 |  | 0
| oddušna strešna kapa s strešno obrobo DN 100 | vented roof cap with roof flashing DN 100 | kos | 12 |  | 0
| prirobnica DN 200 po EN1092, PN16, z vijačnim in tesnilnim materialom | flange DN 200 to EN1092, PN16, with bolting and sealing material | kos | 4 |  | 0
2.16 | Naprava za izločanje mineralnega olja in nečistoč iz laboratorijev, kompaktna nerjanvna prosto stoječa izvedba, sestavljena iz dveh ločenih izločevalnikov, eden za nečistoče, drugi za olje, vključno s posodo za vzorčanje na iztoku v komunalno kanalizacijo, vgradnja na tleh kleti, skladnost z EN858, DIN1999-100, material nerjavno jeklo AISI304, AISI316 sestavljeno iz: rezervoarja za separacijo nečistoč z revizijskimi odprtinami, rezervoarja za separacijo mineralnega olja z mehansko zaporo in revizijskimi odprtinami, nivojska sonda s stikalnimi funkcijami in alarmnimi nivoji, ostala pripadajoča senzorika, ter elektro krmilna omara, dobavljeno kot kompaktna naprava, vključno s protiprirobnicama, vijačnim in tesnilnim materialom. Tehnični podatki: | Naprava za izločanje mineralnega olja in nečistoč iz laboratorijev, kompaktna nerjanvna prosto stoječa izvedba, sestavljena iz dveh ločenih izločevalnikov, eden za nečistoče, drugi za olje, vključno s posodo za vzorčanje na iztoku v komunalno kanalizacijo, vgradnja na tleh kleti, skladnost z EN858, DIN1999-100, material nerjavno jeklo AISI304, AISI316 sestavljeno iz: rezervoarja za separacijo nečistoč z revizijskimi odprtinami, rezervoarja za separacijo mineralnega olja z mehansko zaporo in revizijskimi odprtinami, nivojska sonda s stikalnimi funkcijami in alarmnimi nivoji, ostala pripadajoča senzorika, ter elektro krmilna omara, dobavljeno kot kompaktna naprava, vključno s protiprirobnicama, vijačnim in tesnilnim materialom. Tehnični podatki:
| - kapaciteta 20 l/s = 72 m3/h | - capacity 20 l/s = 72 m3/h
| - rezervoarja volumen: 2500+1750 l = 2,5 +1,75 m3 | - tank volume: 2500+1750 l = 2.5+1.75 m3
| - priključki: natočni vstop kanalizacije DN200, iztok na posodo za vzorčenje DN200, odduh DN100 | - connections: sewer inlet DN200, outlet to sampling tank DN200, outlet DN100
| - posoda za vzorčenje z horizontalnim natokom, DN200 in vertikalnim iztokom DN200, pokrov posode , skladnost z EN877, material AISI316 | - sampling container with horizontal inlet DN200 and vertical outlet DN200, container cover, EN877 compliance, material AISI316
| - dimenzije ca: dolžina L x širina B x višina H = 5000 x 1200 x 1400 mm; transportna teža ca 400+850 kg, obratovalna teža ca 2900+26000 kg | - dimensions ca: length L x width B x height H = 5000 x 1200 x 1400 mm; transport weight ca 400+850 kg, operating weight ca 2900+26000 kg
| - električni podatki: 230V/1/50Hz; | - electrical data: 230V/1/50Hz;
| - krmiljenje senzorike naprave in komunikacija z napravo za prečrpavanje v komunalno kanalizacijo; | - control of the plant's sensors and communication with the sewage pumping plant;
| - električna krmilna omara z upravljalnim tablojem ter komunikacijo RS485 / Modbus RTU | - electrical control cabinet with control board and RS485 / Modbus RTU communication
| - ustreza proizvod AACO tip Coalisator-E - NS20 +Sludge trap for Coalisator-E +Securat idOil 20 alarm system ter opisano dodatno opremo ali enakovredno | - corresponds to the product AACO type Coalisator-E - NS20 +Sludge trap for Coalisator-E +Securat idOil 20 alarm system and the described accessories or equivalent
| Oznaka: LOM88.080 | Code: LOM88.080 | kpl | 1 |  | 0
2.17 | Kompaktna črpalna naprava za prečrpavanje odpadne vode iz naprave za izločanje olja in nečistoč, sestavljeno iz dveh vzporedno vezanih črpalk, rezervoarja odpadne vode, nivojskega tipala s stikalnimi funkcijami in alarmnimi nivoji, set za priklop dveh cevovodov z nepovratnimi in zapornimi ventili ter elektro krmilne omare, dobavljeno kot kompaktna naprava, vključno s protiprirobnicama, vijačnim in tesnilnim materialom. Tehnični podatki: | Compact pumping unit for pumping waste water from an oil and dirt extraction plant, consisting of two pumps connected in parallel, waste water tank, level sensor with switching functions and alarm levels, set for connecting two pipelines with non-return and shut-off valves and electrical control cabinet, supplied as a compact unit, including counter-fittings, screwing and sealing material. Technical data:
| - prečrpavanje nevtralizirane odpadne vode iz naprave za izločanje olja in nečistoč laboratorijev; | - pumping of neutralised waste water from the oil and impurities removal plant of the laboratories;
| - pretok V= 21 l/s = 75,6 m3/h pri tlačna višina prečrpavanja H= 10 m | - flow rate V= 21 l/s = 75,6 m3/h at pumping pressure head H= 10 m
| - 2 črpalki za prečrpavanje (vodilna in sledljiva) | - 2 pumping pumps (lead and traceable)
| - rezervoar material PE, volumen 520 litrov | - tank material PE, volume 520 litres
| - priključki: natočni DN200, tlačni DN150 | - connections: pressure DN200, pressure DN150
| - dimenzije ca: dolžina L x širina B x višina H = 1550 x 800 x 1500 mm; teža ca 400 kg | - dimensions ca: length L x width B x height H = 1550 x 800 x 1500 mm; weight ca 400 kg
| - električni podatki: Pel= 6,71+5,5kW, 400V/3/50Hz, IP68 | - electrical data: Pel= 6,71+5,5kW, 400V/3/50Hz, IP68
| - kaskadno krmiljenje črpalk, avtomatsko nastavljiva izmenjava vodeilne in sledljive črpalke | - cascade pump control, automatically adjustable waterline exchange and traceable pumps
| - električna krmilna omara z upravljalnim tablojem ter komunikacijo RS485 / Modbus RTU | - electrical control cabinet with control board and RS485 / Modbus RTU communication
| - ustreza proizvod ACO tip MuliPro-PE K-55 duo +set za priključitev sesalnih in tlačnih priključkov z opisano dodatno opremo ali enakovredno | - aCO product type MuliPro-PE K-55 duo +set for connection of suction and pressure connections with the described accessories or equivalent
| Oznaka: PN88.081 | Code: PN88.081 | kpl | 1 |  | 0
2.18 | Oddušni ventil za vertikalno kanalizacijo, skladno s EN12380 in EN12056, material polipropilen PP, vključno s spojnim, tesnilnim materialom, ustreza proizvod VALSIR tip VENTILO ali enakovredno; | Vent valve for vertical sewerage, according to EN12380 and EN12056, material polypropylene PP, including jointing, sealing material, corresponding to VALSIR product type VENTILO or equivalent;
| - za oddušno kanalizacijsko cev DN50, ø 50 | - for vented sewer pipe DN50, ø 50 | kos | 80 |  | 0
| - za oddušno kanalizacijsko cev DN100, ø 110 | - for vented sewer pipe DN100, ø 110 | kos | 40 |  | 0
2.19 | Jeklene nerjavne cevi izdelane po ISO1127, material AISI304 ali boljši, vključno z oblikovnimi kosi (loki, redukcije, T kosi, ...) in varilnim materialom, varjenje TIG pod inertnim plinom, | Stainless steel tubes manufactured according to ISO1127, material AISI304 or better, including forming pieces (bows, reducers, T-pieces, etc.) and welding consumables, TIG welding under inert gas,
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno za tlačne vode prečrpavanja; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and pipe clamps with noise damping lining, corresponding to HILTI or SIKLA product, or equivalent for pressurised pumping lines;
| DN 150, ø 168,3 x 2,6 | DN 150, ø 168,3 x 2,6 | m | 90 |  | 0
| 45°lok DN 150, ø 168,3 x 2,6 | 45°arc DN 150, ø 168,3 x 2,6 | kos | 12 |  | 0
| 90°lok DN 150, ø 168,3 x 2,6 | 90°lok DN 150, ø 168,3 x 2,6 | kos | 8 |  | 0
| prirobnica DN 150 po EN1092, PN16, z vijačnim in tesnilnim materialom | flange DN 150 to EN1092, PN16, with bolting and sealing material | kos | 4 |  | 0
| slepa prirobnica DN 150 po EN1092, PN16, z vijačnim in tesnilnim materialom | blind flange DN 150 to EN1092, PN16, with bolting and sealing material | kos | 1 |  | 0
2.20 | Polietilenske cevi visoke gostote PEHD za tlačno kanalizacijo (prečrpavanje), PN10, material PE100, v skladu s standardom EN 13244, vključno z elekrofuzijskimi oblikovnimi kosi (spojke, loki, redukcije, T kosi, ...) ter elektrofuzijskim materilom za varjenje, (OD x s = zunanji premer cevi x debelina stene cevi), ustreza proizvod ARGO z oblikovnimi kosi GEORG FISCHER ali enakovredno: | High-density polyethylene PEHD pipes for pressure sewers (pumping), PN10, material PE100, in accordance with EN 13244, including electrofusion fittings (couplings, bends, reducers, T-pieces, etc.) and electrofusion welding consumables, (OD x s = outer diameter of the pipe x wall thickness of the pipe), corresponding to the product ARGO with GEORG FISCHER fittings or equivalent:
| komplet s polaganjem podzemnega voda v peščeni posteljici ter s PVC označevalnim trakom za kanalizacijo; | complete with underground water installation in a sand bed and PVC sewer marking tape;
| OD 180 (ø 180 x 10,7) | OD 180 (ø 180 x 10,7) | m | 30 |  | 0
| Spojka OD 180 (ø 180 x 10,7) | Coupling OD 180 (ø 180 x 10.7) | kos | 6 |  | 0
| 45°lok OD 180 (ø 180 x 10,7) | 45°block OD 180 (ø 180 x 10.7) | kos | 6 |  | 0
| 90°lok OD 180 (ø 180 x 10,7) | 90°block OD 180 (ø 180 x 10.7) | kos | 4 |  | 0
| Prirobnica DN 150 / OD 180 po EN1092, PN16, komplet s prirobničnim spojem in tesnilom | Flange DN 150 / OD 180 to EN1092, PN16, complete with flange joint and gasket | kpl | 1 |  | 0
| Kanalizacija v energetski strojnici v kleti | Sewerage in the energy engine room in the basement
2.21 | Jeklene nerjavne cevi izdelane po ISO1127, material AISI304 ali boljši, vključno z oblikovnimi kosi (loki, redukcije, T kosi, ...) in varilnim materialom, varjenje TIG pod inertnim plinom, | Stainless steel tubes manufactured according to ISO1127, material AISI304 or better, including forming pieces (bends, reductions, T-pieces, etc.) and welding consumables, TIG welding under inert gas,
| komplet s hidroizolacijsko zaščito cevovodov za garvitacijske vode v betonu; | complete with waterproofing protection for pipelines for gravity lines in concrete;
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno za tlačne vode prečrpavanja; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and pipe clamps with noise damping lining, corresponding to HILTI or SIKLA product, or equivalent for pressurised pumping lines;
| DN 40, ø 48,3 x 2,0 | DN 40, ø 48,3 x 2,0 | m | 24 |  | 0
| DN 65, ø 76,1 x 2,0 | DN 65, ø 76,1 x 2,0 | m | 12 |  | 0
| DN 100, ø 114,3 x 2,3 | DN 100, ø 114,3 x 2,3 | m | 96 |  | 0
| DN 125, ø 139,7 x 2,6 | DN 125, ø 139,7 x 2,6 | m | 72 |  | 0
| DN 150, ø 168,3 x 2,6 | DN 150, ø 168,3 x 2,6 | m | 66 |  | 0
| DN 200, ø 219,1 x 2,6 | DN 200, ø 219,1 x 2,6 | m | 18 |  | 0
| 45°lok DN 65, ø 76,1 x 2,0 | 45°arc DN 65, ø 76,1 x 2,0 | kos | 4 |  | 0
| 45°lok DN 100, ø 114,3 x 2,3 | 45°arc DN 100, ø 114,3 x 2,3 | kos | 20 |  | 0
| 45°lok DN 125, ø 139,7 x 2,6 | 45°block DN 125, ø 139,7 x 2,6 | kos | 16 |  | 0
| 45°lok DN 150, ø 168,3 x 2,6 | 45°arc DN 150, ø 168,3 x 2,6 | kos | 12 |  | 0
| 45°lok DN 200, ø 219,1 x 2,6 | 45°block DN 200, ø 219.1 x 2.6 | kos | 4 |  | 0
| 90°lok DN 65, ø 76,1 x 2,0 | 90°block DN 65, ø 76,1 x 2,0 | kos | 2 |  | 0
| 90°lok DN 100, ø 114,3 x 2,3 | 90°block DN 100, ø 114,3 x 2,3 | kos | 16 |  | 0
| 90°lok DN 125, ø 139,7 x 2,6 | 90°lok DN 125, ø 139,7 x 2,6 | kos | 60 |  | 0
| 90°lok DN 150, ø 168,3 x 2,6 | 90°lok DN 150, ø 168,3 x 2,6 | kos | 8 |  | 0
| 90°lok DN 200, ø 219,1 x 2,6 | 90°lok DN 200, ø 219.1 x 2.6 | kos | 4 |  | 0
| Y kos DN 100 / priključek DN 65 | Y piece DN 100 / connection DN 65 | kos | 24 |  | 0
| Y kos DN 100 / priključek DN 80 | Y piece DN 100 / connection DN 80 | kos | 6 |  | 0
| Y kos DN 100 / priključek DN 100 | Y piece DN 100 / connection DN 100 | kos | 12 |  | 0
| Y kos DN 125 / priključek DN 40 | Y piece DN 125 / connection DN 40 | kos | 2 |  | 0
| Y kos DN 125 / priključek DN 80 | Y piece DN 125 / connection DN 80 | kos | 2 |  | 0
| Y kos DN 125 / priključek DN 100 | Y piece DN 125 / connection DN 100 | kos | 8 |  | 0
| Y kos DN 150 / priključek DN 150 | Y piece DN 150 / connection DN 150 | kos | 1 |  | 0
| R kos DN 100 / DN 65 | R piece DN 100 / DN 65 | kos | 4 |  | 0
| R kos DN 100 / DN 80 | R piece DN 100 / DN 80 | kos | 1 |  | 0
| R kos DN 125 / DN 100 | R piece DN 125 / DN 100 | kos | 1 |  | 0
| R kos DN 150 / DN 125 | R piece DN 150 / DN 125 | kos | 1 |  | 0
| R kos DN 200 / DN 150 | R piece DN 200 / DN 150 | kos | 1 |  | 0
| prirobnica DN 100 po EN1092, PN16, z vijačnim in tesnilnim materialom | flange DN 100 to EN1092, PN16, with bolting and sealing material | kos | 2 |  | 0
| prirobnica DN 125 po EN1092, PN16, z vijačnim in tesnilnim materialom | flange DN 125 to EN1092, PN16, with bolting and sealing material | kos | 1 |  | 0
| prirobnica DN 150 po EN1092, PN16, z vijačnim in tesnilnim materialom | flange DN 150 to EN1092, PN16, with bolting and sealing material | kos | 1 |  | 0
| slepa prirobnica DN 125 po EN1092, PN16, z vijačnim in tesnilnim materialom | blind flange DN 125 to EN1092, PN16, with bolting and sealing material | kos | 1 |  | 0
2.22 | Oddušni ventil za vertikalno kanalizacijo, skladno s EN12380 in EN12056, material polipropilen PP, vključno s spojnim, tesnilnim materialom, ustreza proizvod VALSIR tip VENTILO ali enakovredno; | Vent valve for vertical sewerage, according to EN12380 and EN12056, material polypropylene PP, including jointing, sealing material, corresponding to VALSIR product type VENTILO or equivalent;
| - za oddušno kanalizacijsko cev DN50, ø 50 | - for vented sewer pipe DN50, ø 50 | kos | 2 |  | 0
| - za oddušno kanalizacijsko cev DN100, ø 110 | - for vented sewer pipe DN100, ø 110 | kos | 2 |  | 0
2.23 | Talni odtok z navpičnim ali vodoravnim iztočnim delom, z razstavljivo vodno smradno zaporo (sifon) in protizdrsno mrežno rešetko, material AISI304, kapaciteta iztekanja 2,5 l/s, vključno s spojnim in tesnilnim materialom, za dimenzijo rešetke in priključenega odtoka: | Floor drain with vertical or horizontal outlet, with demountable water odour trap (siphon) and non-slip mesh grate, material AISI304, outlet capacity 2,5 l/s, including jointing and sealing material, for the grate and connected outlet dimensions:
| - ustreza proizvod ACO Inox talni požiralnik 157 - vertikalni iztok ali enakovredno | - corresponds to ACO Inox Floor Swallower 157 - Vertical outlet or equivalent
| 200 x 200 - DN 100 | 200 x 200 - DN 100 | kpl | 20 |  | 0
2.24 | Kompaktna črpalna naprava za prečrpavanje odpadne vode iz strojnice, sestavljeno iz dveh vzporedno vezanih črpalk, rezervoarja odpadne vode, nivojskega tipala s stikalnimi funkcijami in alarmnimi nivoji, set za priklop dveh cevovodov z nepovratnimi in zapornimi ventili ter elektro krmilne omare, dobavljeno kot kompaktna naprava, vključno s protiprirobnicama, vijačnim in tesnilnim materialom. Tehnični podatki: | Compact pumping unit for pumping waste water from the engine room, consisting of two pumps connected in parallel, waste water tank, level sensor with switching functions and alarm levels, set for connecting two pipelines with non-return and shut-off valves and electrical control cabinet, supplied as a compact unit, including counter-fittings, screwing and sealing material. Technical data:
| - prečrpavanje odpadne vode iz strojnice v kleti; | - pumping waste water from the engine room to the basement;
| - pretok V= 12,5 l/s = 45 m3/h pri tlačna višina prečrpavanja H= 14 m | - flow rate V= 12,5 l/s = 45 m3/h at pumping pressure head H= 14 m
| - 2 črpalki za prečrpavanje (vodilna in sledljiva) | - 2 pumping pumps (lead and traceable)
| - rezervoar material PE, volumen 450 litrov | - tank material PE, volume 450 litres
| - priključki: natočni DN100/150, tlačni DN80 | - connections: pressure DN100/150, pressure DN80
| - dimenzije ca: dolžina L x širina B x višina H = 2100 x 900 x 1000 mm; teža ca 520 kg | - dimensions ca: length L x width B x height H = 2100 x 900 x 1000 mm; weight ca 520 kg
| - električni podatki Pel= 2x 6,5kW, 400V/3/50Hz, IP68 | - electrical data Pel= 2x 6,5kW, 400V/3/50Hz, IP68
| - kaskadno krmiljenje črpalk, avtomatična nastavljiva izmenjava vodeilne in sledljive črpalke | - cascade pump control, automatic adjustable waterline exchange and traceable pumps
| - električna krmilna omara z upravljalnim tablojem ter komunikacijo RS485 / Modbus RTU | - electrical control cabinet with control board and RS485 / Modbus RTU communication
| - ustreza proizvod GRUNDFOS tip MD1.80.80.55.4.51D /450.SE z dodatno opremo ali enakovredno | - corresponds to GRUNDFOS product type MD1.80.80.80.55.4.51D /450.SE with accessories or equivalent
| Oznaka: PN90.080 | Code: PN90.080 | kpl | 1 |  | 0
2.25 | Potopna črpalka za prečrpavanje odpadne vode, sesalno podnožje primerno za postavitev na dnu jaška, temperatura tekočine od 0 do 50°C, PN10, materialii črpalke nerjavno jeklo AISI304, komplet z nivojskim stikalom, set za priklop cevovoda z nepovratnim in zapornim ventilom, napajalnim kablom in električno priključno omarico, vključno s pritrdilnim, vijačnim in tesnilnim materialom. Tehnični podatki: | Submersible pump for pumping waste water, suction base suitable for installation at the bottom of the shaft, liquid temperature from 0 to 50°C, PN10, pump material stainless steel AISI304, complete with level switch, pipeline connection kit with non-return and shut-off valve, power cable and electrical junction box, including fixing, screwing and sealing material. Technical data:
| - enostopenjska črpalka za prečrpavanje odpadnih vod, za občasno ali neprekinjeno delovanje, motor vodotesen z napajalnim električnim kabelom 10m in vodotesnimi kabelskimi uvodnicami; | - single-stage sewage pump for intermittent or continuous operation, watertight motor with 10m power supply cable and watertight cable glands;
| - pretok V= 2 l/s = 7,2 m3/h, tlačna višina H= 10 m, | - flow rate V= 2 l/s = 7,2 m3/h, pressure head H= 10 m,
| - dimenzija tlačega priključka DN40 | - pressure connection dimension DN40
| - električni podatki Pel = 0,9 kW, 400V/3/50Hz, IP68, ročni vklop / izklop s stikalom | - electrical data Pel = 0,9 kW, 400V/3/50Hz, IP68, manual on/off with switch
| - ustreza proizvod GRUNDFOS tip Unilift AP12.40.06.A3 z dodatno opremo ali enakovredno | - corresponds to GRUNDFOS product type Unilift AP12.40.06.A3 with accessories or equivalent
| Oznaka: P90.081 | Code: P90.081 | kpl | 1 |  | 0
2.26 | Ročna membranska črpalka za ročno črpanje ostankov odpadne vode v rezervoarju za vgradnjjo na cev DN40 (1½"), dolžina ročice daljša od 400 mm, komplet ssetom za priklop cevovoda z zapornim ventilom, vključno s pritrdilnim, vijačnim in tesnilnim materialom; | Manual diaphragm pump for manual pumping of residual waste water in a tank, for installation on DN40 (1½") pipe, boom length longer than 400 mm, complete set for connection to the pipeline with shut-off valve, including fixing, screwing and sealing material;
| - ustreza proizvod GRUNDFOS tip 96003721 z dodatno opremo ali enakovredno | - corresponds to GRUNDFOS product type 96003721 with accessories or equivalent | kpl | 1 |  | 0
2.27 | Polietilenske cevi visoke gostote PEHD za tlačno kanalizacijo (prečrpavanje), PN10, material PE100, v skladu s standardom EN 13244, vključno z elekrofuzijskimi oblikovnimi kosi (spojke, loki, redukcije, T kosi, ...) ter elektrofuzijskim materilom za varjenje, (OD x s = zunanji premer cevi x debelina stene cevi), ustreza proizvod ARGO z oblikovnimi kosi GEORG FISCHER ali enakovredno: | High-density polyethylene PEHD pipes for pressure sewers (pumping), PN10, material PE100, in accordance with EN 13244, including electrofusion fittings (couplings, bends, reducers, T-pieces, etc.) and electrofusion welding consumables, (OD x s = outer diameter of the pipe x wall thickness of the pipe), corresponding to the product ARGO with GEORG FISCHER fittings or equivalent:
| komplet s polaganjem podzemnega voda v peščeni posteljici ter s PVC označevalnim trakom za kanalizacijo; | complete with underground water installation in a sand bed and PVC sewer marking tape;
| OD 160 (ø 160 x 9,5) | OD 160 (ø 160 x 9,5) | m | 30 |  | 0
| Spojka OD 160 (ø 160 x 9,5) | Coupling OD 160 (ø 160 x 9,5) | kos | 6 |  | 0
| 45°lok OD 160 (ø 160 x 9,5) | 45°block OD 160 (ø 160 x 9,5) | kos | 6 |  | 0
| 90°lok OD 160 (ø 160 x 9,5) | 90°block OD 160 (ø 160 x 9,5) | kos | 4 |  | 0
| Prirobnica DN 125 / OD 160 po EN1092, PN16, komplet s prirobničnim spojem in tesnilom | Flange DN 125 / OD 160 to EN1092, PN16, complete with flange joint and gasket | kpl | 1 |  | 0
| Kanalizacija meteorne vode iz jaškov kleti | Storm water drainage from cellar shafts
2.28 | Jeklene nerjavne cevi izdelane po ISO1127, material AISI304 ali boljši, vključno z oblikovnimi kosi (loki, redukcije, T kosi, ...) in varilnim materialom, varjenje TIG pod inertnim plinom, | Stainless steel tubes manufactured according to ISO1127, material AISI304 or better, including forming pieces (bends, reductions, T-pieces, etc.) and welding consumables, TIG welding under inert gas,
| komplet s hidroizolacijsko zaščito cevovodov za garvitacijske vode v betonu; | complete with waterproofing protection for pipelines for gravity lines in concrete;
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno za tlačne vode prečrpavanja; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and pipe clamps with noise damping lining, corresponding to HILTI or SIKLA product, or equivalent for pressurised pumping lines;
| DN 40, ø 48,3 x 2,0 | DN 40, ø 48,3 x 2,0 | m | 18 |  | 0
| DN 50, ø 60,3 x 2,0 | DN 50, ø 60,3 x 2,0 | m | 60 |  | 0
| DN 80, ø 88,9 x 2,0 | DN 80, ø 88,9 x 2,0 | m | 120 |  | 0
| DN 100, ø 114,3 x 2,3 | DN 100, ø 114,3 x 2,3 | m | 150 |  | 0
| DN 150, ø 168,3 x 2,6 | DN 150, ø 168,3 x 2,6 | m | 90 |  | 0
| 45°lok DN 50, ø 60,3 x 2,0 | 45°arc DN 50, ø 60,3 x 2,0 | kos | 16 |  | 0
| 45°lok DN 80, ø 88,9 x 2,0 | 45°arc DN 80, ø 88,9 x 2,0 | kos | 30 |  | 0
| 45°lok DN 100, ø 114,3 x 2,3 | 45°arc DN 100, ø 114,3 x 2,3 | kos | 48 |  | 0
| 45°lok DN 125, ø 139,7 x 2,6 | 45°block DN 125, ø 139,7 x 2,6 | kos | 24 |  | 0
| 45°lok DN 150, ø 168,3 x 2,6 | 45°arc DN 150, ø 168,3 x 2,6 | kos | 4 |  | 0
| 90°lok DN 50, ø 60,3 x 2,0 | 90°lok DN 50, ø 60,3 x 2,0 | kos | 16 |  | 0
| 90°lok DN 80, ø 88,9 x 2,0 | 90°lok DN 80, ø 88,9 x 2,0 | kos | 30 |  | 0
| 90°lok DN 100, ø 114,3 x 2,3 | 90°block DN 100, ø 114,3 x 2,3 | kos | 48 |  | 0
| 90°lok DN 125, ø 139,7 x 2,6 | 90°lok DN 125, ø 139,7 x 2,6 | kos | 24 |  | 0
| 90°lok DN 150, ø 168,3 x 2,6 | 90°lok DN 150, ø 168,3 x 2,6 | kos | 4 |  | 0
| Y kos DN 80 / priključek DN 50 | Y piece DN 80 / connection DN 50 | kos | 8 |  | 0
| Y kos DN 80 / priključek DN 80 | Y piece DN 80 / connection DN 80 | kos | 6 |  | 0
| Y kos DN 100 / priključek DN 100 | Y piece DN 100 / connection DN 100 | kos | 24 |  | 0
| Y kos DN 150 / priključek DN 100 | Y piece DN 150 / connection DN 100 | kos | 24 |  | 0
| R kos DN 50 / DN 40 | R piece DN 50 / DN 40 | kos | 12 |  | 0
| R kos DN 150 / DN 100 | R piece DN 150 / DN 100 | kos | 6 |  | 0
| prirobnica DN 80 po EN1092, PN16, z vijačnim in tesnilnim materialom | flange DN 80 to EN1092, PN16, with bolting and sealing material | kos | 6 |  | 0
| prirobnica DN 100 po EN1092, PN16, z vijačnim in tesnilnim materialom | flange DN 100 to EN1092, PN16, with bolting and sealing material | kos | 8 |  | 0
| prirobnica DN 150 po EN1092, PN16, z vijačnim in tesnilnim materialom | flange DN 150 to EN1092, PN16, with bolting and sealing material | kos | 6 |  | 0
| slepa prirobnica DN 80 po EN1092, PN16, z vijačnim in tesnilnim materialom | blind flange DN 80 to EN1092, PN16, with screw and sealing material | kos | 16 |  | 0
2.29 | Talni odtok z navpičnim ali vodoravnim iztočnim delom, z razstavljivo vodno smradno zaporo (sifon) in protizdrsno mrežno rešetko, material AISI304, kapaciteta iztekanja 2,5 l/s, vključno s spojnim in tesnilnim materialom, za dimenzijo rešetke in priključenega odtoka: | Floor drain with vertical or horizontal outlet, with demountable water odour trap (siphon) and non-slip mesh grate, material AISI304, outlet capacity 2,5 l/s, including jointing and sealing material, for the grate and connected outlet dimensions:
| - ustreza proizvod ACO Inox talni požiralnik 157 - vertikalni iztok ali enakovredno | - corresponds to ACO Inox Floor Swallower 157 - Vertical outlet or equivalent
| 200 x 200 - DN 100 | 200 x 200 - DN 100 | kpl | 48 |  | 0
2.30 | Kompaktna črpalna naprava za prečrpavanje odpadne vode, sestavljeno iz dveh vzporedno vezanih črpalk, rezervoarja odpadne vode, nivojskega tipala s stikalnimi funkcijami in alarmnimi nivoji, set za priklop dveh cevovodov z nepovratnimi in zapornimi ventili ter elektro krmilne omare, dobavljeno kot kompaktna naprava, vključno s protiprirobnicama, vijačnim in tesnilnim materialom. Tehnični podatki: | Compact pumping unit for pumping waste water, consisting of two pumps connected in parallel, waste water tank, level sensor with switching functions and alarm levels, set for connecting two pipelines with non-return and shut-off valves and electrical control cabinet, supplied as a compact unit, including counter-fittings, screwing and sealing material. Technical data:
| - prečrpavanje meteorne vode iz jaška v v kleti; | - pumping rainwater from a manhole into the basement;
| - pretok V= 3 l/s = 10,8 m3/h pri tlačna višina prečrpavanja H= 12 m | - flow rate V= 3 l/s = 10,8 m3/h at pumping pressure head H= 12 m
| - 2 črpalki za prečrpavanje (vodilna in sledljiva) | - 2 pumping pumps (lead and traceable)
| - rezervoar material PE, volumen 50 litrov | - tank material PE, volume 50 litres
| - priključki: natočni DN100/150, tlačni DN40 | - connections: pressure DN100/150, pressure DN40
| - dimenzije ca: dolžina L x širina B x višina H = 750 x 750 x 800 mm; teža ca 140 kg | - dimensions ca: length L x width B x height H = 750 x 750 x 800 mm; weight ca 140 kg
| - električni podatki Pel= 2x 1,8kW, 400V/3/50Hz, IP68 | - electrical data Pel= 2x 1,8kW, 400V/3/50Hz, IP68
| - kaskadno krmiljenje črpalk, avtomatična nastavljiva izmenjava vodeilne in sledljive črpalke | - cascade pump control, automatic adjustable waterline exchange and traceable pumps
| - električna krmilna omara z upravljalnim tablojem ter komunikacijo RS485 / Modbus RTU | - electrical control cabinet with control board and RS485 / Modbus RTU communication
| - ustreza proizvod GRUNDFOS tip MDG.12.3.2 z dodatno opremo ali enakovredno | - corresponds to GRUNDFOS product type MDG.12.3.2 with accessories or equivalent
| Oznaka: PN91.081, PN91.082, PN91.083, PN91.084, PN91.085, PN91.086, PN91.087 | Code: PN91.081, PN91.082, PN91.083, PN91.084, PN91.085, PN91.086, PN91.087 | kpl | 7 |  | 0
2.31 | Kompaktna črpalna naprava za prečrpavanje odpadne vode, sestavljeno iz dveh vzporedno vezanih črpalk, rezervoarja odpadne vode, nivojskega tipala s stikalnimi funkcijami in alarmnimi nivoji, set za priklop dveh cevovodov z nepovratnimi in zapornimi ventili ter elektro krmilne omare, dobavljeno kot kompaktna naprava, vključno s protiprirobnicama, vijačnim in tesnilnim materialom. Tehnični podatki: | Compact pumping unit for pumping waste water, consisting of two pumps connected in parallel, waste water tank, level sensor with switching functions and alarm levels, set for connecting two pipelines with non-return and shut-off valves and electrical control cabinet, supplied as a compact unit, including counter-fittings, screwing and sealing material. Technical data:
| - prečrpavanje meteorne vode iz jaška v v kleti; | - pumping rainwater from a manhole into the basement;
| - pretok V= 5 l/s = 18 m3/h pri tlačna višina prečrpavanja H= 10 m | - flow rate V= 5 l/s = 18 m3/h at pumping pressure head H= 10 m
| - 2 črpalki za prečrpavanje (vodilna in sledljiva) | - 2 pumping pumps (lead and traceable)
| - rezervoar material PE, volumen 130 litrov | - tank material PE, volume 130 litres
| - priključki: natočni DN100/150, tlačni DN80 | - connections: pressure DN100/150, pressure DN80
| - dimenzije ca: dolžina L x širina B x višina H = 750 x 900 x 800 mm; teža ca 160 kg | - dimensions ca: length L x width B x height H = 750 x 900 x 800 mm; weight ca 160 kg
| - električni podatki Pel= 2x 3,1kW, 400V/3/50Hz, IP68 | - electrical data Pel= 2x 3,1kW, 400V/3/50Hz, IP68
| - kaskadno krmiljenje črpalk, avtomatična nastavljiva izmenjava vodeilne in sledljive črpalke | - cascade pump control, automatic adjustable waterline exchange and traceable pumps
| - električna krmilna omara z upravljalnim tablojem ter komunikacijo RS485 / Modbus RTU | - electrical control cabinet with control board and RS485 / Modbus RTU communication
| - ustreza proizvod GRUNDFOS tip MD.24.3.2 z dodatno opremo ali enakovredno | - corresponds to GRUNDFOS product type MD.24.3.2 with accessories or equivalent
| Oznaka: PN92.081, PN92.082, PN92.083, PN92.084, PN92.085, PN92.086 | Code: PN92.081, PN92.082, PN92.083, PN92.084, PN92.085, PN92.086 | kpl | 6 |  | 0
2.32 | Polietilenske cevi visoke gostote PEHD za tlačno kanalizacijo (prečrpavanje), PN10, material PE100, v skladu s standardom EN 13244, vključno z elekrofuzijskimi oblikovnimi kosi (spojke, loki, redukcije, T kosi, ...) ter elektrofuzijskim materilom za varjenje, (OD x s = zunanji premer cevi x debelina stene cevi), ustreza proizvod ARGO z oblikovnimi kosi GEORG FISCHER ali enakovredno: | High-density polyethylene PEHD pipes for pressure sewers (pumping), PN10, material PE100, in accordance with EN 13244, including electrofusion fittings (couplings, bends, reducers, T-pieces, etc.) and electrofusion welding consumables, (OD x s = outer diameter of the pipe x wall thickness of the pipe), corresponding to the product ARGO with GEORG FISCHER fittings or equivalent:
| komplet s polaganjem podzemnega voda v peščeni posteljici ter s PVC označevalnim trakom za kanalizacijo; | complete with underground water laying in a sand bed and PVC sewer marking tape;
| OD 90 (ø 90 x 5,4) | OD 90 (ø 90 x 5,4) | m | 240 |  | 0
| Spojka OD 90 (ø 90 x 5,4) | Coupling OD 90 (ø 90 x 5,4) | kos | 40 |  | 0
| 45°lok OD 90 (ø 90 x 5,4) | 45°block OD 90 (ø 90 x 5,4) | kos | 24 |  | 0
| 90°lok OD 90 (ø 90 x 5,4) | 90°lock OD 90 (ø 90 x 5,4) | kos | 18 |  | 0
| Prirobnica DN 80 / OD 90 po EN1092, PN16, komplet s prirobničnim spojem in tesnilom | Flange DN 80 / OD 90 to EN1092, PN16, complete with flange joint and gasket | kpl | 13 |  | 0
| Skupne pozicije | Common positions
2.33 | Vodotesno tesnilo za prehod cevi skozi betonsko steno zemlja / klet objekta, vodotesnost W2.1-E po DIN18533 za hidrostatični tlak do 3 m, sestavljeno iz: elastomernih tesnil EPDM ali NBR, z zategovalnimi korozijsko odpornimi prirobnicami in vijačnim materialom iz nerjavnega jekla; | Watertight seal for the passage of pipes through the concrete wall of a soil/basement building, watertightness W2.1-E according to DIN18533 for hydrostatic pressure up to 3 m, consisting of: elastomeric EPDM or NBR seals, with corrosion-resistant tightening flanges and stainless steel screw material;
| - zaščitna cev za vbetoniranje oziroma uvodnica in njena namestitev je del načrtov s področja arhitekture ter gradbeništva; | - the concrete protection pipe or introducer and its installation is part of the architectural and civil engineering plans;
| - ustreza proizvod HAUFF TECHNIK tip HSD ali enakovredno; | - corresponds to HAUFF TECHNIK product type HSD or equivalent;
| - prehod cevi Ø 90 mm | - pipe passage Ø 90 mm | kpl | 13 |  | 0
| - prehod cevi Ø 125 mm | - pipe passage Ø 125 mm | kpl | 3 |  | 0
| - prehod cevi Ø 160 mm | - pipe passage Ø 160 mm | kpl | 5 |  | 0
| - prehod cevi Ø 180 mm | - pipe passage Ø 180 mm | kpl | 1 |  | 0
| - prehod cevi Ø 200 mm | - pipe passage Ø 200 mm | kpl | 4 |  | 0
2.34 | Tlačni preizkus trdnosti in tesnenja sistema cevovodov vertikalne kanalizacije z vodo po EN12056 in EN1610, skladeno z opisom v "IZS Priročnik tlačnih preizkusov strojnih inštalacij", vključno s potrebnim materialom za izdelavo preizkusa, ter izdelavo pisnega poročila o uspešno opravljenem tlačnem preizkusu; | Pressure test of the strength and sealing of the vertical sewerage piping system with water according to EN12056 and EN1610, as described in the "IZS Manual for pressure tests of mechanical installations", including the necessary materials for the test, and the production of a written report on the successful completion of the pressure test;
| - gravitacijska kanalizacija odpadne vode, preizkusni tlak = 30 kPa = 0,3 bar | - gravity sewer, test pressure = 30 kPa = 0,3 bar | kpl | 5 |  | 0
| - tlačna kanalizacija prečrpavanja odpadne vode, preizkusni tlak = 3 bar | - waste water pumping pressure sewer, test pressure = 3 bar | kpl | 4 |  | 0
2.35 | Izpiranje cevovodov s sanitarno hladno vodo v celotnem sistemu novoinstaliranih razvodov z namenom odstranjevanja nečistoč v sistemu cevovodov; | Flushing of sanitary cold water piping throughout the newly installed piping system to remove impurities in the piping system; | kpl | 1 |  | 0
2.36 | Kvalifikacija zvarov jeklenih varjenih cevovodov ter izdelava dokumentacije o zvarih: | Weld qualification of welded steel pipelines and preparation of weld documentation:
| - zvare lahko izvajajo samo varilci s certifikatom pooblaščenih organizacij, | - welds can only be carried out by welders certified by approved organisations,
| - postopek vizualne kontrole zvarov, kontrolirajo se vsi zvari - 100% zvarov, | - visual weld inspection procedure, all welds are inspected - 100% of welds,
| - postopek kontrole s snemanja zvarov - 10% zvarov, kjer so enakomerno zastopani vsi premeri, | - weld stripping inspection procedure - 10% of welds where all diameters are equally represented,
| - označevanje zvarov, izdelava dokumentacije z dokazili o ustreznosti ter slikovnim materialom; | - marking welds, producing documentation with proof of conformity and pictorial material; | kpl | 1 |  | 0
2.37 | Ognjeodporna tesnilna masa, vgradnja na prehodu cevovodov skozi zid med požarnima sektortjema, požarna odpornost 90 minut, ustreza proizvod HILTI ali enakovredno. | Fire-resistant sealant, for installation at the transition of pipelines through the wall between the two fire sectors, fire resistance 90 minutes, equivalent to HILTI or equivalent.
| Vsak prehod mora biti označen z nalepko ali tablico z osnovnimi požarnimi podatki; | Each passageway must be marked with a sticker or placard with basic fire information; | kpl | 1 |  | 0
2.38 | Preizkusno obratovanje delovanja sistema v obsegu: | Operational test of the system in scope:
| - pregled instalacije, vodov in opreme, | - inspection of installations, ducts and equipment,
| - pregled delovanja naprav, elementov regulacije in nastavitve parametrov, | - overview of the operation of the devices, control elements and parameter settings,
| - pregled delovanja kanalizacije, | - a review of the functioning of the sewerage system,
| Preizkusno obratovanje traja neprekinjeno 72 ur. | The test operation shall be continuous for 72 hours. | kpl | 1 |  | 0
2.39 | Napisne ploščice iz nerjavne pločevine z vgravirano oznako po shemi za opremo in armature, kompletno z jekleno pritrdilno žico ali visoko kvalitetne nalepke; visoko trajanje H (več kot 15 let) | Stainless steel nameplates with engraved marking according to the scheme for fittings and fixtures, complete with steel fixing wire or high quality stickers; high durability H (more than 15 years) | kpl | 1 |  | 0
2.40 | Samolepilne puščice za označitev smeri pretoka ter z napisom vrste medija: visoko trajanje H (več kot 15 let) | Self-adhesive arrows to indicate the direction of flow and the type of media: high durability H (more than 15 years) | kpl | 1 |  | 0
2.41 | Izdelava montažnih risb za izvedbo inštalacij med gradnjo objekta, kot so: detajli priključkov, montažne skice, montažni detajli, ipd. | Preparation of assembly drawings for the installation of services during the construction of the building, such as: connection details, assembly sketches, assembly details, etc. | kpl | 1 |  | 0
2.42 | Kvalifikacije montaže IQ-pregledi (instalation qualification) po GEP Commissioning protokolu in dokumentiranje kvalifikacije montaže, vključno z odpravo prvotnih napak montaže; | Installation qualification IQ-checks (installation qualification) according to the GEP Commissioning Protocol and documentation of installation qualification, including correction of original installation faults; | kpl | 1 |  | 0
2.43 | Meritve delovanja OQ-kvalifikacija (operation qualification) ter dokumentiranje meritev delovanja, vključno z nastavitvijo parametrov; | OQ (operation qualification) measurements and documentation of performance measurements, including parameter settings; | kpl | 1 |  | 0
2.44 | Posnetki izvedenega stanja, sprotno beleženje vseh sprememb nastalih med izvedbo, vrisovanje in vpisovanje v PZI projektno dokumentacijo; | Recording of the as-built condition, keeping a running record of any changes made during the execution, plotting and recording in the PZI project documentation; | kpl | 1 |  | 0
2.45 | Stenska shema sistema, vloženo v zaščitni okvir s prosojnim umetnim steklom (plastika) ali plastificirano, vključno s pritrditvijo na notranjo steno v strojnici objekta; | A wall diagram of the system, encased in a protective frame with transparent plastic or plasticised glass, including fixing to an internal wall in the mechanical room of the building; | kpl | 1 |  | 0
2.46 | Primopredajna dokumentacija, ki mora vsebovati: izjave, dokazilo o zanesljivosti objekta, certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo, obratovanje in vzdrževanje ter ostalo primopredajno dokumantacijo. Predaja se v dveh mapiranih izvodih ter en izvod v elektronski obliki; | The handover documentation, which shall include: declarations, proof of the reliability of the facility, certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use, operation and maintenance, and other handover documentation. It shall be handed over in two mapped copies and one copy in electronic form; | kpl | 1 |  | 0
| KANALIZACIJA | SEWER SYSTEM |  |  |  | 0

## 4.8.3_Zalivanje
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.8 | STROJNA DELA | MECHANICAL WORKS
4.8.3 | ZALIVANJE | IRRIGATING |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
3 | ZALIVANJE | IRRIGATING
| Vse postavke v nadalevanju zajemajo dobavo in montažo (razen tam kjer je to posebej navedeno). | All items below include delivery and installation (except where specifically indicated).
3.1 | P polietilenske cevi visoke gostote PEHD za vodovod, PN10, material PE100, v skladu s standardom ISO4427 / EN12201-2 / DVGW za pitno vodo, vključno z elekrofuzijskimi oblikovnimi kosi (spojke, loki, redukcije, T kosi, ...) ter elektrofuzijskim materilom za varjenje, (OD x s = zunanji premer cevi x debelina stene cevi), ustreza proizvod TOTRA z oblikovnimi kosi GEORG FISCHER ali enakovredno: | High density PEHD polyethylene pipes for water supply, PN10, material PE100, in accordance with ISO4427 / EN12201-2 / DVGW for drinking water, including electrofusion fittings (couplings, bends, reducers, T-pieces, etc.) and electrofusion welding consumables, (OD x s = pipe outer diameter x pipe wall thickness), corresponding to the product TOTRA with GEORG FISCHER fittings or equivalent:
| OD 63 (ø 63 x 3,8) | OD 63 (ø 63 x 3,8) | m | 18 |  | 0
| Spojka OD 6,3 (ø 63 x 3,8) | Coupling OD 6,3 (ø 63 x 3,8) | kos | 4 |  | 0
| 90°lok OD 63 (ø 63 x 3,8) | 90°block OD 63 (ø 63 x 3,8) | kos | 4 |  | 0
| Prirobnica DN50 / OD 63 po EN1092, PN16, komplet s prirobničnim spojem in tesnilom | Flange DN50 / OD 63 to EN1092, PN16, complete with flange joint and gasket | kpl | 2 |  | 0
3.2 | Kompaktna črpalna naprava za dvig tlaka vodovoda (pressure booster), PN10, CE izjava, material nerjavno jeklo AISI316 in siva litina, sestavljeno iz: vzporedno vezanih črpalnk s frekvenčno regulacijo, tlačnih tipal, ekspanzijske posode, zapornih, nepovratnih ter izpustnih ventilov, protivibracijskih elementov, nerjavnega podstavka AISI304 in električne krmilne omare, dobavljeno kot kompaktna naprava, vključno s protiprirobnicama, vijačnim in tesnilnim materialom. Tehnični podatki: | Compact pressure booster, PN10, CE approved, material stainless steel AISI316 and grey cast iron, composed of: frequency-controlled pumps in parallel, pressure sensors, expansion tank, stop, non-return and drain valves, anti-vibration elements, stainless steel base AISI304 and electrical control cabinet, supplied as a compact unit, including counter-fittings, screwing and sealing material. Technical data:
| - dve črpalke (delovni in rezerva): pretok V= 4,8 m3/h, pri tlačna višina H= 550 bar | - two pumps (working and reserve): flow V= 4,8 m3/h, pressure head H= 550 bar
| - črpalke, frekvenčno vodne s stalno kontrolo tlaka na tlačni strani črpalk | - pumps, water-frequency with continuous pressure control on the pressure side of the pumps
| - priključki: navojni, sesalni DN32, tlačni DN25 | - connections: threaded, suction DN32, pressure DN25
| - dimenzije ca: dolžina L x širina B x višina H = 500 x 500 x 600 mm; teža ca: m = 50 kg | - dimensions ca: length L x width B x height H = 500 x 500 x 600 mm; weight ca: m = 50 kg
| - električni podatki Pel = 2x 1,5 kW, 230V / 1 / 50Hz, IP 55 | - electrical data Pel = 2x 1,5 kW, 230V/1/50Hz, IP 55
| - delovanja črpalk na konstanten tlak 5,0 bar | - pump operation at a constant pressure of 5.0 bar
| - kaskadno krmiljenje črpalk, avtomatična nastavljiva izmenjava vodeilne in sledljive črpalke, odvisno od obremenitve, časa in napake, | - cascade pump control, automatic adjustable waterline exchange and traceable pumps depending on load, time and fault,
| - električna krmilna omara s upravljalnim tablojem ter komunikacijo RS485 / Modbus RTU | - electrical control cabinet with control board and RS485 / Modbus RTU communication
| - javljanje alarma v primeru napake delovanja na požarno centralo in CNS | - alarm annunciation in the event of a malfunction to the fire panel and CNS
| - ustreza proizvod GRUNDFOS tip CMBE TWIN 5-62 z dodatno opremo ali enakovredno | - corresponds to GRUNDFOS product type CMBE TWIN 5-62 with accessories or equivalent | kpl | 1 |  | 0
3.3 | Kompenzator vibracij iz strojne opreme na cevovod, navojna izvedba, ustrezno za pitno vodo po EN806, PN16, material nerjavno jeklo AISI304, EPDM, vključno s pritrdilnim in tesnilnim materialom; | Vibration compensator from hardware to pipeline, threaded version, suitable for drinking water according to EN806, PN16, material stainless steel AISI304, EPDM, incl. fixing and sealing material;
| DN 32 - ustreza proizvod END ARMATUREN tip KP ali enakovredno | DN 32 - corresponds to END ARMATUREN type KP or equivalent | kpl | 2 |  | 0
3.4 | Krogelni ventil, navojni priključki oziroma zatisni press priključki, PN16, z ročico, material nerjavno jeklo, medenina, PTFE, vključno s pritrdilnim in tesnilnim materialom; | Ball valve, threaded connections or press fittings, PN16, with handle, material stainless steel, brass, PTFE, incl. fitting and sealing material;
| - ustreza proizvod END ARMATUREN oziroma VIEGA ali enakovredno | - corresponds to END ARMATUREN or VIEGA or equivalent
| DN 15 | DN 15 | kos | 16 |  | 0
| DN 15 - s priključkom za gibko povezavo | DN 15 - with flexible connection | kos | 20 |  | 0
| DN 25 | DN 25 | kos | 28 |  | 0
| DN 25 - s priključkom za gibko povezavo | DN 25 - with flexible connection | kos | 20 |  | 0
| DN 32 | DN 32 | kos | 4 |  | 0
| DN 50 | DN 50 | kos | 20 |  | 0
3.5 | Nepovratni ventil iz nerjavnega jekla, z vzmetjo, PN16, material AISI316, PTFE, navojni priklučki, vključno s pritrdilnim in tesnilnim materialom; | Stainless steel non-return valve, spring loaded, PN16, material AISI316, PTFE, threaded unions, incl. fittings and gaskets;
| - ustreza proizvod END ARMATUREN ali enakovredno | - eND ARMATUREN or equivalent
| DN 50 | DN 50 | kos | 2 |  | 0
3.6 | Ventil za hidravlično uravnoteženje, ustrezno za pitno vodo po EN806, PN16, medenina, nerjavno jeklo, PTFE, EPDM, navojni priključki, vključno s pritrdilnim in tesnilnim materialom; | Hydraulic balancing valve, suitable for drinking water according to EN806, PN16, brass, stainless steel, PTFE, EPDM, threaded connections, incl. fittings and sealing material;
| - ustreza proizvod IMI TA tip STAD ali enakovredno | - the product conforms to IMI TA type STAD or equivalent
| DN 25 | DN 25 | kos | 20 |  | 0
3.7 | Membranski ventil z elektromagnetnim servo pogonom, normalno zaprt, PN16, material AISI304 (ali boljši) / NBR, navojni priključki, električno napajanje 24V oz. 230V, vključno s pritrdilnim in tesnilnim materialom; | Diaphragm valve with electromagnetic servo actuator, normally closed, PN16, material AISI304 (or better) / NBR, threaded connections, electrical supply 24V or 230V, incl. fastening and sealing material;
| - ustreza proizvod END ARMATUREN tip MEM ali enakovredno | - corresponds to END ARMATUREN type MEM or equivalent
| DN 25 | DN 25 | kos | 20 |  | 0
3.8 | Omarica za garnituro ventilov zalivanja, s krilnimi vrati in cilindično ključavnico, material jeklena nerjavna pločevina AISI304 (ali boljše), primerno za vgradnjo v zid ali obešanje na zid, vključno s pritrdilnim in tesnilnim materialom; | Cabinet for a set of sprinkler valves, with hinged door and cylinder lock, material stainless steel sheet AISI304 (or better), suitable for installation in a wall or hanging on a wall, including fixing and sealing material;
| - dimenzije: dolžina L x višina H x globina B | - dimensions: length L x height H x depth B
| 400 x 400 x 250 mm | 400 x 400 x 250 mm | kpl | 21 |  | 0
| 600 x 600 x 250 mm | 600 x 600 x 250 mm | kpl | 17 |  | 0
3.9 | Manometer ø 68 mm, klasa točnosti 1,6% po EN837-1, navojni radialni priključek, material medenina, nerjavno jeklo, steklo / EPDM, komplet z manometrskim ventilom DN15 (1/2"), ustrezno za pitno vodo po EN806, vključno s pritrdilnim in tesnilnim materialom; | Pressure gauge ø 68 mm, accuracy class 1.6% according to EN837-1, threaded radial connection, material brass, stainless steel, glass/EPDM, complete with pressure gauge valve DN15 (1/2"), suitable for drinking water according to EN806, including fitting and sealing material;
| - ustreza proizvod INOL ali enakovredno | - corresponds to INOL or equivalent
| - območjem merjenja: 0 do 10 bar | - measuring range: 0 to 10 bar | kos | 1 |  | 0
3.10 | Nerjavne jeklene cevi, zatisni press sistem, izdelane po EN10312 in EN 10088, PN16, material 1.4521 / AISI444, vključno s spojnimi in oblikovnimi zatisnimi press kosi iz rdeče litine ali nerjavni (90°loki, T kosi, redukcije, ...), DVGW certifikat za uporabo v sistemih v pitne vode skladno z DIN11388 TRWI, zatiskanje z originalnim press orodjem proizvajalca, komplet s prehodnimi navojnimi oblikovnimi kosi, ustreza proizvod VIEGA tip SANPRESS ali enakovredno, | Stainless steel pipes, press fitting system, manufactured according to EN10312 and EN 10088, PN16, material 1.4521 / AISI444, including coupling and press fittings in red cast iron or stainless (90°bows, T-pieces, reducers, etc.), DVGW certified for use in drinking water systems according to DIN11388 TRWI, press fitting with original manufacturer's press tool, complete with threaded transition fittings, corresponds to VIEGA product type SANPRESS or equivalent,
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and pipe clamps with noise damping lining, suitable for HILTI or SIKLA, or equivalent;
| DN 15, ø 18 x 1,0 | DN 15, ø 18 x 1,0 | m | 30 |  | 0
| DN 20, ø 22 x 1,2 | DN 20, ø 22 x 1,2 | m | 24 |  | 0
| DN 25, ø 28 x 1,2 | DN 25, ø 28 x 1,2 | m | 510 |  | 0
| DN 32, ø 35 x 1,5 | DN 32, ø 35 x 1,5 | m | 90 |  | 0
| DN 50, ø 54 x 1,5 | DN 50, ø 54 x 1,5 | m | 420 |  | 0
| 90°lok DN 15, ø 18 x 1,0 | 90°lock DN 15, ø 18 x 1,0 | kos | 20 |  | 0
| 90°lok DN 20, ø 22 x 1,2 | 90°lok DN 20, ø 22 x 1,2 | kos | 8 |  | 0
| 90°lok DN 25, ø 28 x 1,2 | 90°lok DN 25, ø 28 x 1,2 | kos | 120 |  | 0
| 90°lok DN 32, ø 35 x 1,5 | 90°lok DN 32, ø 35 x 1,5 | kos | 16 |  | 0
| 90°lok DN 50, ø 54 x 1,5 | 90°lok DN 50, ø 54 x 1,5 | kos | 90 |  | 0
| T kos DN 20 / odcep DN 15 | T piece DN 20 / branch DN 15 | kos | 20 |  | 0
| T kos DN 25 / odcep DN 15 | T piece DN 25 / branch DN 15 | kos | 20 |  | 0
| T kos DN 25 / odcep DN 20 | T piece DN 25 / branch DN 20 | kos | 2 |  | 0
| T kos DN 25 / odcep DN 25 | T piece DN 25 / branch DN 25 | kos | 60 |  | 0
| T kos DN 32 / odcep DN 25 | T piece DN 32 / branch DN 25 | kos | 4 |  | 0
| T kos DN 50 / odcep DN 25 | T piece DN 50 / branch DN 25 | kos | 24 |  | 0
| T kos DN 50 / odcep DN 32 | T piece DN 50 / branch DN 32 | kos | 2 |  | 0
| T kos DN 50 / odcep DN 50 | T piece DN 50 / branch DN 50 | kos | 30 |  | 0
| redukcija DN 20 / DN 15 | reduction DN 20 / DN 15 | kos | 6 |  | 0
| redukcija DN 25 / DN 15 | dN 25 / DN 15 reduction | kos | 30 |  | 0
| redukcija DN 32 / DN 25 | dN 32 / DN 25 reduction | kos | 2 |  | 0
| redukcija DN 50 / DN 32 | dN 50 / DN 32 reduction | kos | 8 |  | 0
3.11 | Toplotna izolacija cevovodov in cevnih armatur s parozaporno izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z naslednjimi lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, požarna klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +110°C, lepljeno na cevovode in armature z originalnim lepilom proizvajalca, vključno s trakovi za šive; | Thermal insulation of pipelines and pipe fittings with vapour barrier insulation made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, fire classification B-s3-d0 according to EN13501-1, for temperatures from -50 to +110°C, bonded to pipelines and fittings with the original manufacturer's adhesive, including seam tapes;
| - barva izolacije črna | - insulation colour black
| - ustreza proizvod ARMACELL tip Armaflex ACE Plus ali enakovredno | - corresponds to ARMACELL product type Armaflex ACE Plus or equivalent
| DN 15, ø 18 ; debelina 13 mm | DN 15, ø 18; thickness 13 mm | m | 40 |  | 0
| DN 20, ø 22 ; debelina 13 mm | DN 20, ø 22; thickness 13 mm | m | 30 |  | 0
| DN 25, ø 28 ; debelina 13 mm | DN 25, ø 28; thickness 13 mm | m | 620 |  | 0
| DN 32, ø 35 ; debelina 13 mm | DN 32, ø 35; thickness 13 mm | m | 120 |  | 0
| DN 50, ø 54 ; debelina 19 mm | DN 50, ø 54 ; thickness 19 mm | m | 520 |  | 0
3.12 | Tlačni preskus trdnosti in tesnenja sistema cevovodov, skladeno z opisom v "IZS Priročnik tlačnih preizkusov strojnih inštalacij", vključno s potrebnim materialom za izvedbo preizkusa, ter izdelavo pisnega poročila o uspešno opravljenem tlačnem preizkusu; | Pressure test of the strength and tightness of the piping system, as described in the "IZS Manual for Pressure Testing of Mechanical Installations", including the necessary materials for the test, and the production of a written report on the successful completion of the pressure test;
| preskusni tlak = 1,1 x najvišji delovni tlak = 7,5 barg | test pressure = 1,1 x maximum working pressure = 7,5 barg | kpl | 1 |  | 0
3.13 | Izpiranje cevovodov z vodo v celotnem sistemu novoinstaliranih razvodov z namenom odstranjevanja nečistoč v sistemu cevovodov; | Flushing of pipelines with water throughout the newly installed piping system to remove impurities in the piping system; | kpl | 1 |  | 0
3.14 | Ognjeodporna tesnilna masa, vgradnja na prehodu cevovodov skozi zid med požarnima sektortjema, požarna odpornost 90 minut, ustreza proizvod HILTI ali enakovredno. | Fire-resistant sealant, for installation at the transition of pipelines through the wall between the two fire sectors, fire resistance 90 minutes, equivalent to HILTI or equivalent.
| Vsak prehod mora biti označen z nalepko ali tablico z osnovnimi požarnimi podatki; | Each passageway must be marked with a sticker or placard with basic fire information; | kpl | 1 |  | 0
3.15 | Preizkusno obratovanje delovanja sistema v obsegu: | Operational test of the system in scope:
| - pregled instalacije, armatur in opreme, | - inspection of plumbing, fixtures and fittings,
| - pregled delovanja naprav, elementov regulacije in nastavitve parametrov, | - overview of the operation of the devices, control elements and parameter settings,
| - pregled odjemnih mest; | - a review of the customer sites;
| Preizkusno obratovanje traja neprekinjeno 72 ur. | The test operation shall be continuous for 72 hours. | kpl | 1 |  | 0
3.16 | Napisne ploščice iz nerjavne pločevine z vgravirano oznako po shemi za opremo in armature, kompletno z jekleno pritrdilno žico ali visoko kvalotetne nalepke; visoko trajanje H (več kot 15 let) | Stainless steel nameplates with engraved marking according to the scheme for fittings and fixtures, complete with steel fixing wire or high quality labels; high durability H (more than 15 years) | kpl | 1 |  | 0
3.17 | Samolepilne puščice za označitev smeri pretoka ter z napisom vrste medija; visoko trajanje H (več kot 15 let) | Self-adhesive arrows to indicate direction of flow and type of media; high H lifetime (more than 15 years) | kpl | 1 |  | 0
3.18 | Izdelava montažnih risb za izvedbo inštalacij med gradnjo objekta, kot so: detajli priključkov, montažne skice, montažni detajli, ipd. | Preparation of assembly drawings for the installation of services during the construction of the building, such as: connection details, assembly sketches, assembly details, etc. | kpl | 1 |  | 0
3.19 | Kvalifikacije montaže IQ-pregledi (instalation qualification) po GEP Commissioning protokolu in dokumentiranje kvalifikacije montaže, vključno z odpravo prvotnih napak montaže; | Installation qualification IQ-checks (installation qualification) according to the GEP Commissioning Protocol and documentation of installation qualification, including correction of original installation faults; | kpl | 1 |  | 0
3.20 | Meritve delovanja OQ-kvalifikacija (operation qualification) ter dokumentiranje meritev delovanja, vključno z nastavitvijo parametrov; | OQ (operation qualification) measurements and documentation of performance measurements, including parameter setting; | kpl | 1 |  | 0
3.21 | Posnetki izvedenega stanja, sprotno beleženje vseh sprememb nastalih med izvedbo, vrisovanje in vpisovanje v PZI projektno dokumentacijo; | Recording of the as-built condition, keeping a running record of any changes made during the execution, plotting and recording in the PZI project documentation; | kpl | 1 |  | 0
3.22 | Stenska shema sistema, vloženo v zaščitni okvir s prosojnim umetnim steklomo (plastika) ali plastificirano, vključno s pritrditvijo na notranjo steno v strojnici objekta; | Wall diagram of the system, enclosed in a protective frame with transparent plastic or plasticised glass, including fixing to an internal wall in the mechanical room of the building; | kpl | 1 |  | 0
3.23 | Primopredajna dokumentacija, ki mora vsebovati: izjave, dokazilo o zanesljivosti objekta, certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo, obratovanje in vzdrževanje ter ostalo primopredajno dokumantacijo. Predaja se v dveh mapiranih izvodih ter en izvod v elektronski obliki; | The handover documentation, which shall include: declarations, proof of the reliability of the facility, certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use, operation and maintenance, and other handover documentation. It shall be handed over in two mapped copies and one copy in electronic form; | kpl | 1 |  | 0
| ZALIVANJE | IRRIGATING |  |  |  | 0