## 0_Naslovnica
OPOZORILO! Vsi prevodi v angleščino so strojno izdelani in zgolj informativne narave. V primeru kakršnekoli nejasnosti ali dvoma izključno velja izvirno besedilo v slovenščini. WARNING! All translations into English have been produced by machine translation and are provided for informational purposes only. In the event of any ambiguity or uncertainty, the original Slovenian text shall prevail exclusively.
| / | / | [5 empty] | /
| Sprem./Rev.: | Opis spremembe/Description of Changes: | [5 empty] | Datum/Date: | Podpis/Signature:
| Investitor/Investor: |  |  |  |  | Gradnja/Facility
|  |  | Univerza v Ljubljani Kongresni trg 12 1000 Ljubljana, Slovenija |  |  | Fakulteta za strojništvo/Faculty of Mechanical Engineering
| Projektant/Design Engineer: |  |  |  |  | Del objekta/sistem/Building/System:
|  |  | IBE, svetovanje, projektiranje in inženiring Ljubljana, Slovenija |  |  | STAVBA FAKULTETE/FACULTY BUILDING
| Projektant/Design Engineer: |  |  |  |  | Vrsta načrta/Documentation:
4 NAČRT S PODROČJA STROJNIŠTVA/ DOC. IN THE FIELD OF MECHANICAL ENGINEERING
|  | Ime in priimek/Name and Surname: |  |  | Id. št./Id. No: | Vsebina risbe (dokumenta)/Document Title:
| Vodja proj./ Des. Manager: | Boštjan Vuga, univ. dipl. inž. arh., grad. dip. (AA) |  |  | ZAPS 0035 PA PPN | PR. POPIS STROJNIH DEL/BOQ OF MECH. WORKS 4/10 Strojno-tehnološki mediji/Mechanical-Technological Media
| Poobl. strok./ Cert. Profess.: | Sašo Ocvirk, univ. dipl. inž. str. |  |  | IZS S-0717
| Poobl. strok./ Cert. Profess.: |  |  |  |  | Št. proj./ Proj. No.: | 362-19 |  | Vrsta dokument./ Document. Type: | DZR
| Izdelal/ Creator: | Sašo Ocvirk, univ. dipl. inž. str. |  |  | IZS S-0717 | Klas. ozn./ Class. No.: | -- |  | Stran/ Page: | 1/*
| Datum/ Date: | maj/May 2026 |  | Merilo/ Scale: | / | Ident. ozn./ Id. No: | JULFS--6S1002P

## 0_Osebe
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
POOBLAŠČENI STROKOVNJAKI, ODGOVORNI ZA IZDELAVO PROJEKTANTSKEGA POPISA:
Id. št. ZAPS/IZS | Pooblaščeni strokovnjak | Strokovno področje
IZS S-0717 | Sašo Ocvirk, univ. dipl. inž. str. | Strojno tehnološki mediji
SODELAVCI PRI IZDELAVI PROJEKTANTSKEGA POPISA:
CERTIFIED EXPERTS RESPONSIBLE FOR ELABORATING THE BILL OF QUANTITIES:
Id. No ZAPS/IZS | Certified Expert | Area of Expertise
IZS S-0717 | Sašo Ocvirk, univ. dipl. inž. str. | Hardware technology media
COLABORATORS IN THE ELABORATING THE BILL OF QUANTITIES:

## 0.1_Uvod-STP
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
0.1 | SPLOŠNI TEHNIČNI POGOJI | GENERAL TECHNICAL CONDITIONS
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic operator with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
0.1.1 | Izvajalec se obveže, da bo upošteval veljavno zakonodajo, ki ureja graditev objektov v Republiki Sloveniji, vključno s povezanimi podzakonskimi akti, predpisi, tehničnimi smernicami, standardi, pravili stroke in dobro gradbeno prakso. Prav tako mora izvajalec upoštevati vse zahteve izdanega integralnega gradbenega dovoljenja in vsa dela izvesti skladno s projektno dokumentacijo ter ostalimi pogoji, objavljenimi v razpisni dokumentaciji. | The Contractor undertakes to comply with the applicable legislation governing the construction of buildings in the Republic of Slovenia, including related by-laws, regulations, technical guidelines, standards, professional rules and good construction practice. The Contractor shall also comply with all the requirements of the integral building permit issued and shall carry out all works in accordance with the project documentation and other conditions published in the tender documentation.
0.1.2 | Dela lahko izvaja samo izvajalec, ki je registriran za opravljanje gradbene dejavnosti in ima za tovrstna dela ustrezno zavarovanje za škodo, certifikate, tehnično izobražen kader, sredstva ter je usposobljen za samostojno pripravo in izvedbo del. | The work may only be carried out by a contractor who is registered to carry out construction work and who has the appropriate insurance for such work, certificates, technically trained staff, resources and is qualified to prepare and carry out the work independently.
0.1.3 | Izvajalec odgovarja za kakovost izvedbe vseh del. | The Contractor shall be responsible for the quality of the execution of all works.
0.1.4 | Izvajalec nosi vso odgovornost za nesreče in škodo, ki nastane na objektu ali v okolici zaradi njegovega dela. | The Contractor shall bear all liability for accidents and damage to the installation or the surrounding area caused by his work.
0.1.5 | Pred oddajo ponudbe se je izvajalec dolžan seznaniti z območjem predvidenim za gradnjo in temu prilagoditi vsa potrebna dela, kar mora biti zajeto v ponudbi. V neposredni bližini predvidene gradnje se nahajajo stavbe, v katerih potekajo izobraževalni in raziskovalni procesi. Zato bo izvajalec moral izvajati kontrolo hrupa in kontrolo vibracij. Dela, ki so hrupna in dela, ki povzročajo vibracije bo izvajalec moral preprečiti oziroma jih izvesti na način, da povzročajo minimalne vplive. Tehnologijo rušenja, pilotiranja in tehnologijo izvedbe ostalih del bo izvajalec moral prilagoditi tako, da bo vpliv minimalen. Izvajalec mora preprečiti in zmanjšati emisije delcev iz gradbišča na najmanjšo možno mero. | Before submitting a tender, the contractor is obliged to familiarise himself with the area to be constructed and to adapt any necessary works accordingly, which must be included in the tender. In the immediate vicinity of the proposed construction, there are buildings in which educational and research processes take place. The contractor will therefore be required to carry out noise and vibration control. Noise and vibration works will have to be avoided or carried out in such a way as to minimise the impact. Demolition, piling and other works will have to be adapted to minimise the impact. The contractor must avoid and minimise the emission of particulates emitted from the construction site as far as is reasonably practicable.
0.1.6 | Izvajalec je pred oddajo ponudbe dolžan pregledati projektno dokumentacijo in ostale pogoje, ki so del razpisne dokumentacije V primeru morebitnih napak in neskladij je izvajalec dolžan na to opozoriti naročnika pred oddajo ponudbe. | The Contractor is obliged to review the project documentation and other conditions forming part of the tender documentation before submitting the tender In case of any errors or inconsistencies, the Contractor is obliged to bring these to the attention of the Contracting Authority before submitting the tender.
0.1.7 | Pred oddajo ponudbe je izvajalec dolžan preveriti ustreznost popisov del in količin v teh popisih ter njihovo skladnost z ostalimi dokumenti projektne dokumentacije, ki so del razpisne dokumentacije. Prav tako je izvajalec dolžan preveriti vse detajle in sheme. Vse izmere je potrebno preveriti po posameznih projektih oz. načrtih, ki sestavljajo razpisno dokumentacijo. V primeru ugotovljenih neskladij je v času priprave ponudbe obvezan o tem obvestiti naročnika. | Before submitting a tender, the Contractor shall check the adequacy of the inventories of works and quantities in these Bills of Quantities and their conformity with the other documents of the project documentation forming part of the tender documentation. The Contractor shall also check all details and diagrams. All measurements shall be checked against the individual projects or plans forming part of the tender documentation. In the event of any discrepancies, the Contractor shall inform the Contracting Authority at the time of preparing the tender.
0.1.8 | Pred oddajo ponudbe je izvajalec dolžan v tem popisu preveriti zmnožke in seštevke ter prenose le-teh v rekapitulacijo. Izvajalec se s pripravo ponudbe obvezuje, da je prebral vse celice in elemente celotnega popisa, vključno z vsemi postavkami in splošnimi navodili ali določili in je preveril pravilnost preračuna ter s tem zagotavlja ponudbeno vrednost. | Before submitting a tender, the Contractor is required to check the products and totals in this Bill of Quantities (BoQ) and their transfer to the recapitulation. The Contractor undertakes, by preparing a tender, to have read all the cells and elements of the complete BoQ, including all headings and general instructions or provisions, and to have checked the correctness of the conversion, thereby guaranteeing the value of the tender.
0.1.9 | Dela bo izvajalec moral izvajati po predloženi projektni dokumentaciji, detajlih in z upoštevanjem navodil in potrditev projektanta, nadzornika in investitorja. Vso potrebno delavniško dokumentacijo zagotovi izvajalec del v okviru ponujene cene. | The Contractor shall carry out the works in accordance with the submitted design documents, details and subject to the instructions and approvals of the Designer, the Supervisor and the Investor. All necessary workshop documentation shall be provided by the Contractor within the scope of the price quoted.
0.1.10 | Pred izvedbo posameznih del je izvajalec dolžan pregledati projektno dokumentacijo za izvedbo gradnje (PZI) in elaborate. Na morebitne napake v dokumentaciji ali neskladja med posameznimi načrti ali deli načrtov (popisi del, tehnična poročila, lokacijski in tehnični prikazi) izvajalec opozori nadzornika in projektanta, in se z njima pravočasno uskladi. | The Contractor shall review the Detailed Design documentation (PZI) and the studies before carrying out the individual works. The Contractor shall draw the attention of the Supervisor and the Designer to any errors in the documentation or discrepancies between the individual designs or parts of designs (BoQ, technical reports, location and technical drawings) and shall coordinate with them in good time.
0.1.11 | Tehnični opisi, prikazi, detajli, sheme ter ostali dokumenti v PZI dokumentaciji predstavljajo dodaten opis popisnih postavk gradbeno obrtniških in inštalacijskih del ter jih je potrebno dosledno upoštevati skupaj s popisom del. | The technical descriptions, illustrations, details, diagrams and other documents in the Detailed Design documentation (PZI) are additional descriptions of the BoQ inventory items of the building, construction and installation works and must be strictly followed together with the BoQ.
0.1.12 | Specifikacije in zahteve, navedene v popisu, se ne smejo upoštevati kot edine zahteve. Izvajalec je dolžan v ceni zajeti in dobaviti vse elemente opreme ter opraviti dela in storitve, ki niso eksplicitno navedeni, a so bistvenega pomena za funkcionalnost, skladnost s predpisi ter kontinuirano, zanesljivo in varno obratovanje opreme. | The specifications and requirements set out in the BoQ shall not be taken as the only requirements. The Contractor shall be obliged to include in the price and supply all items of equipment and to carry out works and services which are not expressly mentioned but which are essential for the functionality, regulatory compliance and continuous, reliable and safe operation of the equipment.
0.1.13 | Vsa dela morajo biti izvedena kvalitetno in iz materialov z zahtevanimi lastnostmi, izvedena skladno z veljavno zakonodajo in z upoštevanjem navodil za vgradnjo za izbrane materiale in opremo, s predložitvijo predpisanih izjav o lastnostih in/ali certifikatov. Vsi gradbeni proizvodi (GP) morajo biti označeni s CE oznako. | All work shall be of good quality and be executed with materials of the required characteristics, in accordance with the applicable legislation and in compliance with the installation instructions for the materials and equipment selected, and shall be accompanied by the prescribed declarations of performance and/or certificates. All construction products (GP) shall bear the CE marking.
0.1.14 | Za vsako opisano delo v popisu je potrebno upoštevati celotno potrebno delo, ves osnovni in pomožni material, prevoz materiala in orodja na objekt, notranje transporte, delovne in pomožne odre, zaključno čiščenje in odstranitev odpadkov po dovršenem delu. | For each work described in the inventory, the total work required, all basic and ancillary materials, the transport of materials and tools to the site, internal transports, working and ancillary scaffolding, final cleaning and the disposal of waste after the work has been completed must be taken into account.
0.1.15 | Vsa delovna sredstva, organizacija in koordinacija del, pripravljalna, spremljajoča in zaključna dela, potrebni montažni in tesnilni materiali ter podkonstrukcije so sestavni del posameznih postavk. | All labour, organisation and coordination of the works, preparatory, accompanying and finishing works, necessary prefabrication and sealing materials and substructures are part of the individual items.
0.1.16 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - načrt organizacije gradbišča s podrobnim terminskim planom in izvedba vseh pripravljalnih del, postavitev, organizacija, zaščita in prijava gradbišča, gradbiščnih objektov, ureditev začasnih deponij, tekoče vzdrževanje, skupaj s plačilom splošnih stroškov pristojbin in davkov upravnih organov, pridobivanju raznih dovoljenj in soglasij za izvedbo, ograditev gradbišča in postavitev gradbene table in prometne signalizacije, zagotavljanje ustrezne varnosti na gradbišču, tekoče vzdrževanje in končna odstranitev gradbišča; - zagotovitev potrebnih začasnih površin za transportne poti in gradnjo izven območja gradbišča s plačilom stroškov za sanacijo in vzpostavitev okoliških zemljišč in objektov v prvotno stanje (soglasja, odškodnine, itd.); - začasni odvoz, deponiranje in vračanje izkopanega materiala, ki ga ne bo možno deponirati na gradbišču; - odvoz in zagotovitev odstranjevanja odpadnega gradbenega materiala skladno z zakonodajo na področju ravnanja z odpadki (odvoz na urejene deponije s plačilom komunalnih prispevkov in taks itd.); - oteženi izkop v mokrem terenu, izkop v vodi, odvod meteorne vode iz gradbene jame in vode, ki se izceja iz bočnih strani izkopov; - ustrezno varovanje izkopa gradbene jame za objekt in ostalih manjših posameznih izkopov za izvedbo komunalne infrastrukture brez posegov na sosednja zemljišča; - ustrezno varovanje obstoječih objektov, infrastrukture in okolice v času gradnje ter dokumentiranje vseh morebitnih škodnih dogodkov; - pripravljalna, spremljajoča in zaključna dela (zakoličbe, zagotovitev potrebnih komunalnih priključkov za potrebe izvajanja gradnje, izvedba začasnih inštalacij, označevanje podzemnih vodov, postavljanje in vzdrževanje zakoličbenih profilov, izvedba in označevanje novih in starih križanj ter morebitna zaščita križanj komunalnih vodov, geodetski posnetki in izdajanje vmesnih posnetkov izvedene infrastrukture naročniku, izdelava zbirnih kart, itd.), v kolikor ni to drugače določeno; - pridobivanje soglasij in izvedba morebitnih zapor na vseh cestah s plačilom stroškov, nadomestil in pristojbin; - zagotovitev oz. postavitev in končna odstranitev po zaključku gradnje začasnih skladišč in začasnega pisarniškega kontejnerskega objekta vključno z opremo za dve delovni mesti in za skupne operativne sestanke vel. ca. 40 m2 za potrebe naročnika, s tekočim vzdrževanjem in čiščenjem. | The following must also be included or taken into account in the uniform prices for individual items: - a construction site organisation plan with a detailed timetable and the execution of all preparatory works, the setting-up, organisation, protection and registration of the construction site, site facilities, the arrangement of temporary storage facilities, ongoing maintenance, including the payment of general costs of fees and taxes of the administrative authorities, the obtaining of various permits and consents for the execution, the fencing of the site and the erection of construction signs and traffic signals, the provision of adequate security on the site, ongoing maintenance and the final dismantling of the construction site; - provision of the necessary temporary areas for transport routes and off-site construction, with costs for restoration and reinstatement of surrounding land and buildings (consents, compensation, etc.); - temporary removal, storage and return of excavated material that cannot be stored on site; - removing and disposing of waste building materials in accordance with waste management legislation (removal to regulated landfill sites with payment of municipal fees and charges, etc.); - difficult excavation in wet ground, excavation in water, drainage of rainwater from the construction pit and water draining from the sides of excavations; - adequate protection of the excavation of the construction pit for the building and other small individual excavations for the implementation of the utility infrastructure without encroaching on neighbouring land; - adequate protection of existing facilities, infrastructure and the surrounding area during construction, and documentation of any damage incidents; - preparatory, accompanying and finishing works (stake-out, provision of the necessary utility connections for the needs of construction, execution of temporary installations, marking of underground lines, installation and maintenance of stake-out profiles, execution and marking of new and old crossings and possible protection of crossings of utility lines, geodetic surveys and issuing of intermediate images of the completed infrastructure to the client, production of summary maps, etc.), unless otherwise specified; - obtaining consents and implementing any road closures, with costs, compensation and fees; - provision or erection and final removal on completion of construction of temporary storage and temporary office container building including equipment for two workstations and for joint operational meetings of approx. 40 m2 for the needs of the client, with ongoing maintenance and cleaning.
0.1.17 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - izdelava montažne tehnične dokumentacije, detajlov izvedbe in vse druge potrebne delavniške dokumentacije (s področja arhitekture, gradbeništva, elektrotehnike, strojništva in zunanje ter krajinske ureditve) ter pridobitev obvezne potrditve s strani projektanta, nadzornika in investitorja; - odprava vseh vrst inštalacijskih kolizij z izvajanjem potrebnih premikov inštalacij in njihovim usklajevanjem na mestu montaže, vse v obsegu, ki ne vpliva na projektirano rešitev ali tip inštalacij oz. opreme; - zagotavljanje kompletnosti elektro-instalacijskih sistemov s področja avtomatike za doseganje njihove popolne funkcionalnosti delovanja; - stroški za nadzor in koordinacijo izvedbe vseh elektro napeljav, ki so predmet končne instalacije proizvoda (senčila, vrata, okna,…); - izdelava montažnih skic in detajlov za izvedbo v dogovoru z vodjo gradnje in nadzornikom; - izdelava in predstavitev vzorcev v ustrezni velikosti za potrditev projektanta, nadzornika in investitorja; - zagotavljanje varnosti in zdravja pri delu, zlasti izvajanje vseh del, ki izhajajo in ukrepov, ki izhajajo iz določil veljavnih predpisov varstva pri delu in zahtev Varnostnega načrta;- stroški garancij, ki jih mora izvajalec predložiti naročniku. | The following must also be included or taken into account in the uniform prices for individual items: - preparation of prefabricated technical documentation, construction details and all other necessary workshop documentation (architectural, civil, electrical, mechanical, exterior and landscaping) and obtaining the mandatory approval of the designer, the supervisor and the investor; - elimination of all types of installation conflicts by carrying out the necessary relocation of installations and their coordination at the installation site, all to the extent that it does not affect the design solution or the type of installation or equipment; - ensuring the completeness of electrical installation systems in the automation sector to achieve their full operational functionality; - the cost of supervising and coordinating the installation of all the electrical installations that are the subject of the final installation of the product (blinds, doors, windows, etc.); - preparation of erection drawings and details for implementation in agreement with the construction manager and supervisor; - production and presentation of samples in appropriate sizes for the approval of the designer, the supervisor and the investor; - ensuring health and safety at work, in particular the implementation of all the works arising from and the measures resulting from the provisions of the applicable occupational safety regulations and the requirements of the Safety Plan; - the cost of the guarantees to be provided by the contractor to the client.
0.1.18 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - strošek vodje del glavnega izvajalca, ki bo izvajal tudi koordinacijo s podizvajalci in z drugimi izvajalci, ki jih bo izbral naročnik in bo opravljal delo vodje gradbišča; - koordinacija del z ostalimi izvajalci oz. podizvajalci del, projektantom, nadzornikom in investitorjem pri medsebojnem usklajevanju organizacije gradbišča in časovnega načrta del ter pri usklajevanju izdelave plana montaže, potrjenih s strani vseh udeležencev gradnje; - stroški koordinacije, sodelovanja in usklajevanja z dobavitelji tehnološke, laboratorijske, eksperimentalne in vse ostale pohištvene ter multimedijske opreme ter z vsemi ostalimi dobavitelji oz. podizvajalci na objektu; - stroški izdelave situacij; - stroški zavarovanja objekta v času izvedbe del in delavcev ter materiala na gradbišču v času izvajanja del, od začetka del do pridobitve uporabnega dovoljenja za objekt. Zavarovanje mora biti sklenjeno pri ustrezni zavarovalni družbi najmanj v višini pogodbene vrednosti ali v zakonsko predpisani vrednosti (v kolikor zavarovanje v višini pogodbene vrednosti presega zakonsko dovoljeno), za ves čas trajanja izvedbe del do uspešne primopredaje objekta; - preizkušanje kvalitete materiala, ki se vgrajuje in dokazovanje kvalitete s certifikati oz. tehničnimi soglasji; - izvedba vseh zahtevanih testov in preizkusov (npr. tlačni preizkusi, termografski pregledi, meritve elektromagnetnega sevanja, hrupa, itd.), poskusnega obratovanja celotnega objekta s poudarkom na vseh inštalacijah ter izvajanje predpisanega monitoringa v skladu s Poročilom o vplivih na okolje (pred gradnjo, med gradnjo in po končani gradnji); - izdelava izkaza požarne varnosti, vključno s sprotnim spremljanjem gradnje in izvajanjem požarnovarnostnih zahtev ter izdelava Požarnega reda z obveznimi prilogami; - izdelava Izkaza zaščite pred hrupom v stavbah; - izdelava Izkaza energijskih lastnosti stavbe in energetske izkaznice; - sodelovanje z izvajalci gradbenega in projektantskega nadzora in investitorjem za izvedbo tehničnega pregleda in priprava primopredaje, ki mora vsebovati vso zahtevano dokumentacijo, predvsem pa: izjave o skladnosti, požarni izkaz in ostale izkaze ter obvezne tabele, dokazilo o zanesljivosti objekta (DZO), certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo in vzdrževanje ter vse ostale dokumente v skladu s predpisi in pogodbenimi določili. | The following must also be included or taken into account in the uniform prices of the individual items: - the cost of a works manager for the main contractor, who will also coordinate with subcontractors and other contractors selected by the client and act as site manager; - coordination of the works with other contractors or subcontractors, the designer, the supervisor and the investor in coordinating the organisation of the construction site and the timetable for the works, and in coordinating the production of an installation plan approved by all the participants in the construction; - the costs of coordination, cooperation and coordination with suppliers of technological, laboratory, experimental and all other furniture and multimedia equipment, as well as with all other suppliers or subcontractors on the site; - the cost of drawing up situations; - the cost of insuring the building during the execution of the works and the workers and materials on site during the execution of the works, from the start of the works until the building has been licensed for occupation. The insurance must be taken out with a suitable insurance company for at least the contract value or the legal value (if the insurance for the contract value exceeds the legal value), for the entire duration of the works until the successful handover of the building; - testing the quality of the material to be installed and proving it with certificates or technical approvals; - carrying out all required tests and trials (e.g. pressure tests, thermographic inspections, electromagnetic radiation measurements, noise measurements, etc.), trial operation of the entire building, with emphasis on all installations, and carrying out the required monitoring in accordance with the Environmental Impact Assessment Report (before, during and after construction); - preparation of a fire safety statement, including ongoing monitoring of construction and implementation of fire safety requirements, and preparation of a Fire Safety Order with mandatory annexes; - preparation of a Noise Protection Statement for buildings; - preparation of the Building Energy Performance Report and Energy Performance Certificate; - cooperation with the construction and design supervision contractors and the investor to carry out the technical inspection and prepare the handover, which must include all the required documentation, in particular: declarations of conformity, fire and other statements and mandatory tables, proof of reliability of the building (DZO), certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use and maintenance, and all other documents in accordance with the regulations and the contractual provisions.
0.1.19 | V enotnih cenah posameznih postavk, ki se nanašajo na opremo in posamezne sisteme, mora biti zajeto oz. upoštevano tudi naslednje: - dobava oz. transport, - stroški za vse delovne stroje za dvigovanje bremen in delovne košare za dostope do delovišč; - morebitni stroški povzročeni upravljavcem GJI, ki bi nastali v zvezi s predmetno gradnjo; - montaža, vključno s pomožnim montažnim materialom (vezni, tesnilni in pritrdilni material, sidra, nosilni profili, podkonstrukcije in podobno) in navodili proizvajalca, - odprava vseh kolizij sistemov s stenami in med sistemi, - izvedba vseh potrebnih tesnjenj, - priključitev in nastavitve, vključno z morebitnim kalibriranjem, - zagon, testiranje in meritve, vključno s poročili, - šolanje uporabnikov oz. vzdrževalnega osebja za uporabo in vzdrževanje sistemov, - navodila za obratovanje in vzdrževanje, - vsi potrebni certifikati, izjave o skladnosti oz. potrdila ter - vsa druga pomožna dela in material, da se zagotovi funkcionalnost posamezne postavke popisa. | The following must also be included or taken into account in the uniform prices for individual items relating to equipment and individual systems: - delivery/transport, - the cost of all lifting machines and work baskets for access to work sites; - any costs incurred to the operators of utility infrastructure (GJI) in connection with the subject construction; - installation, including ancillary installation materials (bonding, sealing and fixing materials, anchors, support profiles, substructures, etc.) and manufacturer's instructions, - eliminating all system-to-wall and system-to-system collisions, - all necessary sealing work, - connection and set-up, including calibration if necessary, - commissioning, testing and measurements, including reports, - training users or maintenance staff in the use and maintenance of the systems, - operating and maintenance instructions, - any necessary certificates, declarations of conformity or attestations; and - all other ancillary works and materials to ensure the functionality of each inventory item.
0.1.20 | Vsi odri morajo biti upoštevani v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All scaffolding must be included in the uniform prices of the items listed, except where specifically mentioned.
0.1.21 | Vsi delovni in pomožni odri, lestve in ostala potrebna pomožna sredstva, kot tudi čiščenje vseh elementov po končanih delih, mora biti upoštevano v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All working and auxiliary scaffolding, ladders and other necessary ancillaries, as well as the cleaning of all elements after completion of the works, shall be included in the uniform prices of the items listed, except those specifically mentioned.
0.1.22 | Delavniško dokumentacijo za vse nosilne jeklene konstrukcije in podkonstrukcije izdela izvajalec, strošek izdelave delavniške dokumentacije se upošteva v ponujenih cenah in se ne obračuna posebej. | The cost of the shop drawings for all steelwork and substructures shall be included in the prices quoted and shall not be charged separately.
0.1.23 | V enotnih cenah postavk mora biti vključeno tudi vgrajevanje vseh instalacijskih razvodov v opaže armirano betonskih elementov in izdelava prehodov inštalacij ter dodatno izrezovanje utorov in prebojev v kamnite, zidane ali armirano-betonske stene, ponovno demontiranje in montiranje vseh vrst montažnih sten, vsa dodatna dela za zagotavljanje primernih križanj med posameznimi instalacijskimi vodi, izdelava vseh vrst ojačitev konstrukcij in podobna dela, ki zagotavljajo kakovostno vgradnjo vseh vrst instalacijskih vodov in niso posebej navedena v popisu GOI del. V ponudbi morajo biti upoštevana vsa drobna strojna in elektro instalacijska dela in transporti. | The installation of all installation ducts in the formwork of reinforced concrete elements and the construction of installation penetrations, as well as the additional cutting of grooves and penetrations in stone, masonry or reinforced concrete walls, the reassembly and reinstallation of all types of prefabricated walls, all additional work to ensure adequate crossings between individual installation ducts, the construction of all types of structural reinforcement and similar work to ensure the quality installation of all types of installation ducts and not specifically mentioned in the BoQ of the Construction, installation and finishing works (GOI) shall also be included in the uniform prices of the items. The tender shall take into account all minor mechanical and electrical installation work and transport.
0.1.24 | Vsi kovinski elementi in konstrukcije, ki bi lahko bili izpostavljeni atmosferskim in ostalim korozijskim vplivom, morajo biti ustrezno protikorozijsko zaščiteni. | All metallic elements and structures that could be exposed to atmospheric and other corrosive influences must be adequately protected against corrosion.
0.1.25 | Za vse večje jeklene dele se skladno s predpisi, izdelajo ustrezne ozemljitve, nevidno pritrjene in speljane na splošno ozemljitev objekta. | For all major steel parts, appropriate earth connections shall be made in accordance with the regulations, invisibly attached and connected to the general earth of the building.
0.1.26 | Za vse vidne elemente in serijske elemente je obvezna predhodna uskladitev obdelav, barv in materialov s projektantom na podlagi dostavljenih vzorcev v ustrezni velikosti. Obvezna je preveritev dejanskih mer na licu mesta in posledična prilagoditev elementov in njihove montaže. | For all visible elements and serial elements, it is mandatory to coordinate the finishes, colours and materials with the designer beforehand on the basis of the supplied samples in the appropriate size. It is mandatory to check the actual dimensions on site and to adjust the elements and their installation accordingly.
0.1.27 | Dimenzije obrtniških izdelkov in količine je potrebno pred naročanjem preveriti na objektu. Potrebna je uskladitev vseh elementov (kljuke, okovje, detajlne konstrukcije in obdelave, itd.) s projektantom, nadzornikom in investitorjem. Izvajalec je dolžan pred izdelavo predložiti projektantu v potrditev ustrezne delavniške načrte in detajle. | The dimensions of the workmanship and quantities must be checked on site before ordering. All elements (hooks, fittings, detailed construction and finishes, etc.) must be coordinated with the designer, the supervisor and the investor. The contractor is obliged to submit the relevant workshop plans and details to the designer for approval before manufacture.
0.1.28 | V posameznih postavkah popisa so navedeni proizvajalci in/ali tipi posameznih sistemov, materialov ali opreme, s čimer so zgolj natančno opredeljene zahtevane tehnične lastnosti. Izvajalec del lahko ponudi nadomesten sistem, material ali opremo drugega proizvajalca in tipa, pri čemer morajo biti tehnične lastnosti ponujenega sistema, materiala ali opreme enakovredne ali boljše od opredeljenih v popisu, dimenzijsko pa ne smejo presegati projektiranih dimenzij. Vse funkcijske in tehnične karakteristike nadomestnih sistemov, materialov ali opreme mora izvajalec dokazati z ustrezno dokumentacijo. Vse morebitne posledice zaradi spremembe sistemov, materialov ali opreme vključno z morebitnimi spremembami oz. dopolnitvami BIM modelov in projektne dokumentacije, stroškovno in časovno bremenijo izvajalca. | The individual items of the Inventory shall specify the manufacturers and/or types of the individual systems, materials or equipment, thereby merely specifying the required technical characteristics. The Contractor may offer a substitute system, material or equipment of a different manufacturer and type, provided that the technical characteristics of the offered system, material or equipment shall be equivalent to or better than those specified in the BoQ, and shall not exceed the design dimensions. All functional and technical characteristics of the substitute systems, materials or equipment shall be demonstrated by the Contractor with appropriate documentation. Any consequences resulting from changes to systems, materials or equipment, including any changes or additions to the BIM models and project documentation, shall be borne by the Contractor in terms of cost and time.
0.1.29 | Vsako zamenjavo, uporabo in končni izbor nadomestnih sistemov, materialov, proizvodov in opreme morajo obvezno in pravočasno (pred dobavo in vgradnjo) pisno potrditi projektant (vseh sodelujočih strok), nadzornik in investitor. | Any replacement, use and final selection of alternative systems, materials, products and equipment must be approved in writing by the designer (of all disciplines involved), the supervisor and the investor in a timely manner (prior to delivery and installation).
0.1.30 | Izvajalec mora v ponudbeno ceno vključiti tudi: - ves čas gradnje sprotno beleženje sprememb oz. odstopanj od PZI dokumentacije, vključno z izdelavo tekstualnega opisa sprememb, - pripravo podlog na nivoju PZI, ki so potrebne za posodobitev oz. uskladitev BIM modela z izvedenim stanjem (LOD 500) in izdelavo projektne dokumentacije izvedenih del (PID), - mesečno predajanje potrjenih sprememb opreme in materiala, ki vplivajo na BIM model, v formatu IFC, - vzdrževanje in uporabljanje pri izvedbi zadnje veljavne revizije PZI dokumentacije, vključno z dopolnitvami PZI načrtov, ki so nastali zaradi sprememb med gradnjo. | The contractor must also include in the tender price: - keeping a record of changes or deviations from the construction documentation (PZI) throughout construction, including a textual description of the changes, - preparation of the Detailed Design (PZI) level documents required to update or align the BIM model with the as-built condition (LOD 500) and the preparation of the as-built project documentation for the works (PID), - monthly submission of approved equipment and material changes affecting the BIM model in IFC format, - maintenance and use in the execution of the last valid revision of the construction documentation (PZI), including additions to the construction design documentation (PZI) resulting from changes during construction.

## 0.2_Uvod-DGNB
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
0.2 | SPLOŠNI TEHNIČNI POGOJI ZA PODROČJE DGNB CERTIFICIRANJA | GENERAL TECHNICAL CONDITIONS FOR DGNB CERTIFICATION
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic entity with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
| Splošni pogoji za področje DGNB certificiranja predstavljajo dopolnilo splošnim tehničnim pogojem in ne odpravljajo drugih obveznosti in odgovornosti, ki jih ima izvajalec v skladu s predpisi in pogodbo. | The General Conditions for DGNB Certification are complementary to the General Technical Conditions and do not exclude other obligations and responsibilities that the Contractor has under the Regulations and the Contract.
0.2.1 | Izvajalec mora v svojih ponudbah upoštevati, da se bo objekt certificiral v skladu z zahtevami DGNB sistema certificiranja trajnostne gradnje, ter pravočasno (vsaj 60 dni pred vgradnjo posameznega produkta) dostaviti vso ustrezno dokumentacijo za vse v ponudbi zajete materiale, elemente in opremo. Zahtevana je uporaba materialov, elementov ali opreme, ki so okolju in ljudem prijazni, energetsko učinkoviti in obenem ustrezajo zahtevam DGNB sistema. Zahtevan nivo certifikata je: ZLATI CERTIFIKAT | The Contractor shall take into account in its tenders that the building will be certified in accordance with the requirements of the DGNB Sustainable Building Certification Scheme and shall deliver all relevant documentation for all materials, elements and equipment included in the tender in a timely manner (at least 60 days before the installation of each product). The use of materials, elements or equipment that are environmentally and human friendly, energy efficient and at the same time meet the requirements of the DGNB system is required. The required level of certification is: GOLD CERTIFICATE
0.2.2 | Podrobnejši opis DGNB sistema in navodila za posamezne kriterije so dostopna v dokumentu"DGNB Criteria Set New Construction Buildings, Version 2020 International", ki je na voljo na DGNB spletni strani https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria | A more detailed description of the DGNB system and guidance on the individual criteria is available in the document "DGNB Criteria Set New Construction Buildings, Version 2020 International", available on the DGNB website https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria
0.2.3 | Izvajalec mora v svojih ponudbah upoštevati, da je potrebno skladno z določili DGNB certifikacijskega sistema, pravočasno (pred pričetkom gradnje) dostaviti vso ustrezno dokumentacijo, za vse v ponudbi zajete materiale, elemente in opremo (tehnični list, varnostni list, izjava o lastnostih, tehnična navodila za ravnanje, servisiranje, vzdrževanje,...) v slovenskem jeziku. Vgradnja kakršnihkoli materialov, elementov ali opreme, se izvede zgolj na podlagi predhodne preveritve posredovane dokumentacije in obenem potrditve s strani nadzornika. | The Contractor must take into account in its tenders that, in accordance with the provisions of the DGNB certification system, all relevant documentation for all materials, elements and equipment included in the tender (technical data sheet, safety data sheet, declaration of properties, technical instructions for handling, servicing, maintenance,...) must be delivered on time (prior to the start of construction) in the Slovene language (in accordance with the provisions of the DGNB certification system). The installation of any materials, elements or equipment shall be subject to prior checking of the submitted documentation and, at the same time, to the approval of the Supervisor.
0.2.4 | Izbrani materiali, elementi, naprave, sistemi in oprema morajo prispevati k večji trajnosti stavbe v smeri zagotavljanja energetske učinkovitosti, ekonomičnega in enostavnega vzdrževanja ter čiščenja, dolge življenjske dobe, uporabe okolju prijaznih materialov ipd. | The materials, elements, appliances, systems and equipment chosen must contribute to the sustainability of the building in terms of energy efficiency, economic and easy maintenance and cleaning, long lifetime, use of environmentally friendly materials, etc.
0.2.5 | Predloženi dokumenti za vse uporabljene materiale, elemente in opremo morajo izpolnjevati zahteve najmanj kakovostne stopnje QS3 (zaželeno QS4), iz dokumenta: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001) | The documents submitted for all materials, components and equipment used shall meet the requirements of at least quality level QS3 (preferably QS4) of the document DGNB Quality Grades for Materials, Components and Equipment (JULFS--7X9001)
0.2.6 | V kolikor izbrani materiali oz. elementi, navedeni v posameznih postavkah, ne ustrezajo vsaj kakovostni stopnji QS3 iz seznama: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), je izvajalec dolžan na to opozoriti projektanta, nadzor in investitorja ter podati predlog ustreznega materiala oz. elementa. | If the selected materials or elements listed in the individual items do not meet at least quality level QS3 of the list of DGNB quality classes for materials, elements and equipment (JULFS--7X9001), the Contractor shall draw this to the attention of the Designer, the Supervisor and the Investor, and shall make a proposal for a suitable material or element.
0.2.7 | Izvajalec lahko v svoji ponudbi predlaga alternativne produkte in rešitve glede na predvidene s projektom, pod pogojem, da le-te prav tako izpolnjujejo vse navedene zahteve. Pri morebitnih predlaganih alternativnih produktih oz. rešitvah je potrebno upoštevati najmanj enake ali boljše lastnosti v smislu življenjske dobe, obstojnosti, ter enostavnosti in stroška čiščenja ter vzdrževanja v primerjavi s projektom predpisanimi rešitvami. Za alternativne rešitve izvajalec pridobi soglasje projektanta, nadzornika in investitorja pred pričetkom gradnje. | The Contractor may propose alternative products and solutions to those envisaged by the project in its tender, provided that they also meet all the requirements set out above. Any alternative products or solutions proposed shall have at least the same or better characteristics in terms of service life, durability, and ease and cost of cleaning and maintenance compared to the solutions envisaged by the project. For alternative solutions, the contractor shall obtain the agreement of the designer, the supervisor and the investor before starting construction.
0.2.8 | Izvajalec med gradnjo dnevno beleži vsa eventualna odstopanja od PZI projektne dokumentacije ter podatke pravočasno posreduje naročniku, nadzoru in projektantu. Potrjene spremembe vnese v podlage za izdelavo PID in posodobitev BIM modelov. | During construction, the Contractor shall record on a daily basis any deviations from the Detailed Design documentation (PZI) and shall provide the information to the Client, Supervision and the Designer in a timely manner. Confirmed changes shall be entered into the basis for the As-built documentation (PID) and BIM model updates.
0.2.9 | Izvajalec med gradnjo sproti izpolnjuje Seznam vseh konstrukcijskih sestav s pripadajočimi vgrajenimi gradbenimi materiali in dokumentira naslednje podatke o vgrajenih materialih (v slovenskem jeziku): - Varnostni list - Tehnični list - Izjavo o lastnostih (če je relevantno) - Izkazovanje morebiti obstoječega okoljskega certifikata (Tip I - okoljski znak ali Tip III - okoljska produktna deklaracija /EPD) - Izjavo proizvajalca ali dobavitelja, da produkt ustreza zahtevam ENV1.2 - Tehnična navodila za ravnanje, servisiranje, vzdrževanje oziroma ostale, z zakonom predpisane dokumente in dokumentacijo. | During construction, the Contractor shall keep a List of all structural assemblies with their associated construction materials and document the following information on the materials installed (in Slovene language): - Safety Data Sheet - Technical Data Sheet - Declaration of performance (if applicable) - Demonstration of any existing environmental certification (Type I - Ecolabel or Type III - Environmental Product Declaration /EPD) - A declaration by the manufacturer or supplier that the product complies with the requirements of ENV1.2 - Technical instructions for handling, servicing, maintenance or other documents and documentation required by law.
0.2.10 | Za vse vgrajene bistvene tehnične sisteme mora izvajalec zagotoviti obstoj pooblaščenega servisa, ki deluje na območju Republike Slovenije, da ima investitor možnost skleniti ustrezno pogodbo o vzdrževanju. Med bistvene tehnične sisteme sodijo npr.: sistemi ogrevanja in hlajenja, priprava tehnoloških medijev, prezračevanje in klimatizacija, sistemi detekcije in gašenja požara, sistemi tehničnega varovanja, BMS in CNS sistemi upravljanja stavbe, razsvetljava, komunikacijski in WI-FI sistemi,... | For all installed essential technical systems, the contractor must ensure the existence of an authorised service centre operating in the territory of the Republic of Slovenia, so that the investor has the possibility of concluding an appropriate maintenance contract. The essential technical systems include, for example: heating and cooling systems, technological media preparation, ventilation and air conditioning, fire detection and extinguishing systems, technical security systems, BMS and CNS building management systems, lighting, communication and WI-FI systems,...
0.2.11 | Zaželeno je, da imajo uporabljeni elementi in materiali okoljsko oznako Tip I. (kot npr. ENCODE, BLUE ANGEL, ipd...). | It is preferable that the elements and materials used have a Type I environmental label (such as ENCODE, BLUE ANGEL, etc...).
0.2.12 | Izvajalec bo za elemente iz lesa moral dokazovati izvor z navedbo izvorne države in tipa lesa, FSC / PEFC certifikat z dodatnim pripadajočim potrdilom Chain of custody-trgovski certifikat dobavitelja - ta se dokazuje z dobavnicami, računi ali enakovredno. Za izdelke iz naravnega kamna iz EU držav je potrebna deklaracija, da je izvor in procesiranje teh izdelkov v celoti v EU državah. Za izdelke iz naravnega kamna, ki prihajajo iz držav izven EU, je potrebno predložiti dokazilo o izpolnjevanju ILO konvencije 182, ki vključuje neodvisna inšpekcijska poročila. | For wood elements, the contractor will be required to provide proof of origin, indicating the country of origin and the type of wood, FSC/PEFC certification with an additional Chain of Custody certificate - the supplier's trade certificate - this shall be evidenced by delivery notes, invoices or equivalent. For natural stone products from EU countries, a declaration that the sourcing and processing of these products is entirely in EU countries is required. For natural stone products from non-EU countries, proof of compliance with ILO Convention 182, including independent inspection reports, is required.
0.2.13 | Izobraževanje udeležencev pri gradnji Izvajalec je dolžan vse udeležence pri gradnji podrobneje seznaniti tudi z relevantnimi koncepti, študijami, elaborati, ki opredelujejo trajnostni način gradnje za naslednja področja: - zaščita pred hrupom (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)) - zaščita pred prašenjem - zaščita tal in podzemne vode (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)), Analiza tveganja za onesnaženje vodnega telesa podzemne vode št. 0346-023/2023, maj 2023 (Geološko projektiranje d.o.o.)) - ravnanje z gradbenimi odpadki (Načrt gospodarjenja z gradbenimi odpadki) Izobraževanja se izvajajo skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.1 1.2, 2.2, 3.2 in 4.2 Training for the parties implementing the construction work | Training of construction participants The contractor is also obliged to inform all construction participants in detail about relevant concepts, studies, elaborations defining sustainable construction methods for the following areas: - noise protection (Environmental Impact Assessment Report No 100123-11523, dated 11.5.2023, supplemented on 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.)) - dust protection - protection of soil and groundwater (Environmental Impact Assessment Report No. 100123-11523, dated 11.5.2023, supplemented 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.), Risk analysis for contamination of the groundwater No. 0346-023/2023, May 2023 (Geološko projektiranje d.o.o.)) - construction waste management (Construction Waste Management Plan) The training shall be carried out in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.1 1.2, 2.2, 3.2 and 4.2 Training for the parties implementing the construction work
0.2.14 | Navodila za obratovanje in vzdrževanje objekta Izvajalec pripravi Navodila za obratovanje in vzdrževanje objekta skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilih: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual | Instructions for the operation and maintenance of the facility The Contractor shall prepare the Operation and Maintenance Instructions for the Facility in accordance with the applicable Slovenian legislation and the DGNB System Instructions specified in the Criteria: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual
0.2.15 | Meritve kontrole kakovosti gradnje Izvajalec mora upoštevati, da se bodo po koncu gradnje izvedle naslednje meritve: - meritve zrakotesnosti - meritve s termokamero (termografija) - meritve akustike - meritve zvočne zaščite ovoja stavbe - meritve zvočne zaščite ločilnih elementov med posameznimi prostori različnih namembnosti - meritve udarnega zvoka - meritve vlažnosti vgrajenih elementov, pred vgradnjo finalnih tlakov - test odvoda dima in toplote Meritve morajo opraviti ustrezno usposobljeni preskusni organi ali strokovnjaki ter rezultate oceniti in primerjati z zahtevami. Obseg opravljenih meritev mora biti sorazmeren z velikostjo zgradbe in mora ustrezno odražati cilj preverjanja kakovosti zgradbe. Smiselno je, da izvajalec del tekom gradnje za sprotno kontrolo kakovosti vgrajenih materialov, elementov in opreme, sam izvaja meritve. Končne meritve (ob primopredaji) izvede tretja oseba kot neodvisna potrditev doseganja zahtev. Meritve se izvajajo skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 2. Quality control measurements | Construction quality control measurements The contractor must take into account that the following measurements will be carried out after completion of the construction: - airtightness measurements - thermal camera measurements (thermography) - acoustics measurements - measurements of the sound insulation of the building envelope - measurements of the sound insulation of the separating elements between different rooms of different uses - impact sound measurements - moisture measurements of the installed elements, prior to the installation of the final flooring - smoke and heat extraction test The measurements shall be carried out by suitably qualified test bodies or experts and the results evaluated and compared with the requirements. The extent of the measurements carried out shall be proportionate to the size of the building and shall adequately reflect the objective of the building quality verification. It is reasonable for the contractor to carry out his own measurements during construction to check the quality of the materials, elements and equipment installed. Final measurements (at handover) are carried out by a third party as an independent confirmation of compliance with the requirements. The measurements shall be carried out in accordance with the applicable Slovenian legislation and the DGNB system instructions specified in the benchmark: PRO 2.2 2. Quality control measurements
0.2.16 | Zagotavljanje kakovosti za uporabljene gradbene proizvode Izvajalec mora zagotavljati izvajanje primerjav med definiranim in dejansko uporabljenim materialom, elementom ali opremo skladno seznamom: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), vključno z dokazno dokumentacijo ugotovitev primerjav ter skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 3.1 Quality assurance for the used construction products | Quality assurance for the construction products used The Contractor shall ensure that comparisons are made between the defined and the actual material, element or equipment used in accordance with the list: DGNB Quality Grades of Installed Materials, Elements and Equipment (JULFS--7X9001), including supporting documentation of the findings of the comparisons, and in accordance with the DGNB system instructions defined in the Criterion: PRO 2.2 3.1 Quality assurance for the used construction products
0.2.17 | Zaščita pred vlago Izvajalec predloži dokumentacijo, ki dokazuje, da je bil izveden program prezračevanja, prilagojen stavbi, s čimer se zagotovi pogoje, da so vgrajeni gradbeni elementi ustrezno suhi, skladno z navodili DGNB opredeljenimi v merilu: PRO 2.2 4.1 Mould prevention | Protection against moisture The Contractor shall provide documentation demonstrating that a building-specific ventilation programme has been implemented to ensure that the building elements installed are adequately dry, in accordance with the DGNB guidelines specified in the criteria: PRO 2.2 4.1 Mould prevention
0.2.18 | Preizkusi delovanja sistemov Izvajalec sodeluje pri izvedbi predhodnega in končnega preizkusa delovanja vseh bistvenih tehničnih komponent stavbe in pripravi ustrezne dokazne dokumentacije ter pri usposabljanju vzdrževalcev/upravljalcev stavbe, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators | System performance tests The Contractor shall be involved in the performance of the preliminary and final performance tests of all essential technical components of the building and the preparation of the relevant supporting documentation, as well as in the training of the maintenance/management staff of the building, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators
0.2.19 | Poročilo o zagonu objekta Izvajalec sodeluje pri pripravi končnega poročila o zagonu objekta, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 5.1 Creation of a detailed final report | Commissioning report The Contractor shall be involved in the preparation of the final commissioning report, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 5.1 Creation of a detailed final report
0.2.20 | Koncept celovitega delovanja sistemov v stavbi Izvajalec sodeluje pri procesu implementiranja stalnega nadzora in nastavitev delovanja stavbe ter usposabljanju vzdrževalcev/upravljalcev stavbe. Navedeno se izvede v skladu z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 6.1 Creation and handover of an integral operating concept | The concept of integrated building systems The contractor is involved in the process of implementing the building's continuous monitoring and settings and training the building's maintenance/management staff. This shall be done in accordance with the DGNB system instructions defined in the benchmark: PRO 2.3 6.1 Creation and handover of an integral operating concept
0.2.21 | Prilagoditev nastavitev sistemov po začetni fazi uporabe objekta Izvajalec sodeluje pri ponovnem pregledu delovanja vseh bistvenih tehničnih sistemov ter eventualni ponovni prilagoditvi teh sistemov s strani strokovnjaka oz. (neodvisne) tretje osebe. Postopek se izvede po približno 10–14 mesecih po zaključku gradnje, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 7.1 Readjustment of the system following initial operating phase | Adjusting system settings after the initial phase of use of the building The Contractor shall be involved in the re-examination of the functioning of all essential technical systems and the possible re-adjustment of these systems by an expert or (independent) third party. The procedure shall be carried out approximately 10-14 months after completion of construction, in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.3 7.1 Readjustment of the system following initial operating phase

## 4.10.0_Rekapitulacija
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
| REKAPITULACIJA STROŠKOV STROJNIH DEL | COST SUMMARY OF MECHANICAL WORKS
| 4 NAČRT S PODROČJA STROJNIŠTVA | 4 DOCUMENTATION IN THE FIELD OF MECHANICAL ENGINEERING
| 4/10 Strojno-tehnološki mediji | 4/10 Mechanical-Technological Media
4.10 | STROJNA DELA | MECHANICAL WORKS
4.10.1 | PODSISTEMI HLADILNE IN OGREVNE VODE ZA LABORATORIJE | COOLING AND HEATING WATER SUBSYSTEMS FOR LABORATORIES | 0
4.10.2 | KOMPRIMIRAN ZRAK | COMPRESSED AIR | 0
4.10.3 | TEHNIČNI PLINI | TECHNICAL GAS | 0
0
0 | NEPREDVIDENA DELA | UNFORSEEN WORKS | 0
| SKUPAJ STROJNA DELA: | TOTAL MECHANICAL WORKS: | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT

## 4.10.1_PodsistHvOvLab
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.10 | STROJNA DELA | MECHANICAL WORKS
4.10.1 | PODSISTEMI HLADILNE IN OGREVNE VODE ZA LABORATORIJE | COOLING AND HEATING WATER SUBSYSTEMS FOR LABORATORIES |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
1 | PODSISTEMI HLADILNE IN OGREVNE VODE ZA LABORATORIJE | COOLING AND HEATING WATER SUBSYSTEMS FOR LABORATORIES
| Vse postavke v nadalevanju zajemajo dobavo in montažo (razen tam kjer je to posebej navedeno). | All items below include delivery and installation (except where specifically indicated).
| Podsistem LICEM | LICEM subsystem
1.1 | Ploščni izmenjevalnik toplote, lotana izvedba (nerjavne plošče spojene z bakrenim lotom), PN10, material AISI316 (ali boljši), debeline plošč 0,6mm, tesnila EPDM do 100°C trajne obremenitve, skladnost s PED. Tehnični podatki: | Plate heat exchanger, loted design (stainless steel plates joined by copper lot), PN10, material AISI316 (or better), plate thickness 0,6mm, EPDM seals up to 100°C permanent load, PED compliant. Technical data:
| - hlajenje hladilne vode za laboratorij | - chilled water cooling for the laboratory
| - izmenjana toplota 300 kW - hlajenje | - heat exchanged 300 kW - cooling
| - primar hladna stran P: hladilna voda, temp. vstopa 9°C, temp. izstopa 14°C, pretok 51,57m3/h, padec tlaka do 30kPa | - primary cold side P: cooling water, inlet temp. 9°C, outlet temp. 14°C, flow 51,57m3/h, pressure drop up to 30kPa
| - sekundar topla stran S: hladna voda, temp. vstopa 20°C, temp. izstopa 12°C, pretok 32,29m3/h, padec tlaka do 20kPa | - secondary hot side S: cold water, inlet temp. 20°C, outlet temp. 12°C, flow 32,29m3/h, pressure drop up to 20kPa
| - vsi priključki prirobnični PN10, primar P DN100, sekundar S DN100 | - all connections flanged PN10, primary P DN100, secondary S DN100
| - vključno s podstavkom prenosnika, pritrdilnim in tesnilnim materialom; | - including the laptop base, fixing and sealing materials;
| - dimenzije do: dolžina L x širina W x višina H = 500 x 400 x 1000 mm | - dimensions up to: length L x width W x height H = 500 x 400 x 1000 mm
| - komplet s toplotna parozaporna izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +105°C, debelina 50mm | - complete with thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0.040W/mK according to EN ISO8497, classification B-s3-d0 according to EN13501-1, for temperatures -50 to +105°C, thickness 50mm
| - ustrezen proizvod ALFA LAVAL tip CB210-100AM-F + toplotna izolacija ali enakovredno | - suitable product ALFA LAVAL type CB210-100AM-F + thermal insulation or equivalent
| Oznaka: HE64.100 | Code: HE64.100 | kpl | 1 |  | 0
1.2 | Obtočna črpalka, PN10, z mokrim rotorjem, skladnost z ErP, elektronsko regulirana s PM motorjem in integrairanim frekvenčnim pretvornikom, inegrirano tipalo diferenčnega tlaka in temperature, upravljalnik nastavitev s prikazovalnikom parametrov, z internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, PN10, wet-rotor, ErP-compliant, electronically controlled with PM motor and integrated frequency converter, integrated differential pressure and temperature sensor, setting controller with parameter display, with internal hydraulic, electrical and communication connections, pump material grey cast iron with appropriate sealing for the medium, flanged design, including counter-flanges, fixing and sealing material. Technical data:
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - pretok V= 32,29 m3/h, tlačna višina H= 90kPa, | - flow rate V= 32,29 m3/h, pressure head H= 90kPa,
| - elektro podatki Pel= 1,496kW, 230V /1/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 1,496kW, 230V /1/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip MAGNA3 80-120 F ali enakovredno | - corresponds to GRUNDFOS product type MAGNA3 80-120 F or equivalent
| Oznaka: P64.181 | Code: P64.181 | kpl | 1 |  | 0
1.3 | Temperaturno tipalo, potopno, za merilno območje od 0 do +80°C, potopna dolžina L=100mm, v tulki iz nerjavnega materiala z navojnim priključkom 1/2" (DN15), električni podatki: napajanje 24V, izhod 4-20mA, komplet s pritrdilnim in tesnilnim materialom; | Temperature sensor, immersion, for measuring range from 0 to +80°C, immersion length L=100mm, in stainless steel sleeve with 1/2" (DN15) threaded connection, electrical data: power supply 24V, output 4-20mA, complete with fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - ustreza proizvod ELEKTRONIKA PAHOR, tip CVB ali enakovredno | - corresponds to the product ELEKTRONIKA PAHOR, type CVB or equivalent
| Oznaka: TIC64.111 | Code: TIC64.111 | kpl | 1 |  | 0
1.4 | Tipalo tlaka s pretvornikom, za mertev tlaka v območju od 0 do 6 barg (relativno) ter nastavljivim alarmnim tlakom, navojni priključek 1/2" (DN15), material nerjavno jeklo, električni podatki: napajanje 24V, izhod 4-20mA, kompletno z ventilom za tipalo tlaka 1/2" (DN15) ter tesnilnim in pritrdilnim materialom; | Pressure sensor with transducer, for pressure measurement in the range from 0 to 6 barg (relative) and adjustable alarm pressure, threaded connection 1/2" (DN15), material stainless steel, electrical data: power supply 24V, output 4-20mA, complete with pressure sensor valve 1/2" (DN15) and sealing and fixing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - alarm, če je tlak p < 1,0 barg (nastavitev na tipalu ali programska nastavitev) | - alarm if pressure p < 1.0 barg (sensor setting or software setting)
| - ustreza proizvod ENDRESS+HAUSER tip PTC31B + PZAV ali enakovredno | - corresponds to ENDRESS+HAUSER product type PTC31B + PZAV or equivalent
| Oznaka: PIA64.121 | Code: PIA64.121 | kpl | 1 |  | 0
1.5 | Ekspanzijska posoda za kompenzacijo toplotnih raztezkov medija v sistemu, PN10, skladno z direktivo EU o tlačni opremi PED, pokončna izvedba v obliki diska, membrana po DIN 4807, tlaki do 6 bar, temperature na membrani od 5 do 70°C, vključno s pritrdilnim in tesnilnim materialom; | Expansion vessel for compensation of thermal expansion of the medium in the system, PN10, in compliance with the EU Pressure Equipment Directive PED, upright disc design, diaphragm according to DIN 4807, pressures up to 6 bar, diaphragm temperatures from 5 to 70°C, incl. fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - prostornina ekspanzijske posode 140 litrov | - expansion tank capacity 140 litres
| - dimenzije: premer D x višina H = ø420 x 1280 mm | - dimensions: diameter D x height H = ø420 x 1280 mm
| - z navojnim priključkom 3/4" (DN20), komplet z ventilom s ključavnico 3/4" (DN20) | - with 3/4" (DN20) threaded connection, complete with 3/4" (DN20) keyed valve
| - ustreza proizvod IMI PNEUMATEX tip SU 140.6 + DLV 20 ali enakovredno | - iMI PNEUMATEX product type SU 140.6 + DLV 20 or equivalent
| Oznaka: EP64.101 | Code: EP64.101 | kpl | 1 |  | 0
1.6 | Varnostni ventil po TRD 721, PN16, varnostna funkcija izpusta medija zaradi toplotnih raztezkov v sistemu, vzmetno delovanje, možnost ročnega odzračenja, prostor vzmeti zaščiten z membrano, prirobnična izvedba, vključno s pritrdilnim in tesnilnim materialom; | Safety valve according to TRD 721, PN16, safety function of medium discharge due to thermal expansion in the system, spring operation, manual venting possible, spring space protected by diaphragm, flanged version, including fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - tlak odpiranja 3,0 barg, | - opening pressure 3,0 barg,
| - z navojnima priključkoma DN 40 / 50, komplet z ventilom s ključavnico DN40 | - with threaded connections DN 40/50, complete with valve with lock DN40
| - ustreza proizvod IMI PNEUMATEX tip DSV 40 - 3.0H DGH + dodatna oprema ali enakovredno | - corresponds to IMI PNEUMATEX product type DSV 40 - 3.0H DGH + accessories or equivalent
| Oznaka: VV64.102 | Code: VV64.102 | kpl | 1 |  | 0
1.7 | Regulacijski ventil, prehodni, tlačno neodvisni za hidravlično uravnoteženje z elektromotornim zveznim pogonom, 24V, IP54, PN16, material ventila nikljana medenina, nerjavno jeklo / EPDM, navojna izvedba, komplet z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Control valve, intermediate, pressure independent for hydraulic balancing with electromotor continuous actuator, 24V, IP54, PN16, valve material nickel-plated brass, stainless steel / EPDM, threaded version, complete with threaded Dutch, fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| DN 100, Vv= 23,6 ÷ 59 m3/h - ustreza proizvod DANFOSS tip ventila AB-QM 100 HF, tip pogona AME 435 QM /24V ali enakovredno | DN 100, Vv= 23,6 ÷ 59 m3/h - corresponds to DANFOSS product valve type AB-QM 100 HF, actuator type AME 435 QM /24V or equivalent
| Oznaka: VY64.151 | Code: VY64.151 | kpl | 1 |  | 0
| Podsistem LAT | LAT subsystem
1.8 | Ploščni izmenjevalnik toplote, lotana izvedba (nerjavne plošče spojene z bakrenim lotom), PN10, material AISI316 (ali boljši), debeline plošč 0,6mm, tesnila EPDM do 100°C trajne obremenitve, skladnost s PED. Tehnični podatki: | Plate heat exchanger, loted design (stainless steel plates joined by copper lot), PN10, material AISI316 (or better), plate thickness 0,6mm, EPDM seals up to 100°C permanent load, PED compliant. Technical data:
| - hlajenje hladilne vode za laboratorij | - chilled water cooling for the laboratory
| - izmenjana toplota 70 kW - hlajenje | - heat exchanged 70 kW - cooling
| - primar hladna stran P: hladilna voda, temp. vstopa 9°C, temp. izstopa 14°C, pretok 12,03m3/h, padec tlaka do 30kPa | - primary cold side P: cooling water, inlet temp. 9°C, outlet temp. 14°C, flow rate 12,03m3/h, pressure drop up to 30kPa
| - sekundar topla stran S: hladna voda, temp. vstopa 20°C, temp. izstopa 12°C, pretok 7,53m3/h, padec tlaka do 20kPa | - secondary hot side S: cold water, inlet temp. 20°C, outlet temp. 12°C, flow rate 7,53m3/h, pressure drop up to 20kPa
| - vsi priključki prirobnični PN10, primar P DN50, sekundar S DN50 | - all connections flanged PN10, primary P DN50, secondary S DN50
| - vključno s podstavkom prenosnika, pritrdilnim in tesnilnim materialom; | - including the laptop base, fixing and sealing materials;
| - dimenzije do: dolžina L x širina W x višina H = 300 x 300 x 700 mm | - dimensions up to: length L x width W x height H = 300 x 300 x 700 mm
| - komplet s toplotna parozaporna izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +105°C, debelina 50mm | - complete with thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0.040W/mK according to EN ISO8497, classification B-s3-d0 according to EN13501-1, for temperatures -50 to +105°C, thickness 50mm
| - ustrezen proizvod ALFA LAVAL tip CB110-38M + toplotna izolacija ali enakovredno | - suitable product ALFA LAVAL type CB110-38M + thermal insulation or equivalent
| Oznaka: HE64.200 | Code: HE64.200 | kpl | 1 |  | 0
1.9 | Obtočna črpalka, PN10, z mokrim rotorjem, skladnost z ErP, elektronsko regulirana s PM motorjem in integrairanim frekvenčnim pretvornikom, inegrirano tipalo diferenčnega tlaka in temperature, upravljalnik nastavitev s prikazovalnikom parametrov, z internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, PN10, wet-rotor, ErP-compliant, electronically controlled with PM motor and integrated frequency converter, integrated differential pressure and temperature sensor, setting controller with parameter display, with internal hydraulic, electrical and communication connections, pump material grey cast iron with appropriate sealing for the medium, flanged design, including counter-flanges, fixing and sealing material. Technical data:
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - pretok V= 7,53 m3/h, tlačna višina H= 90kPa, | - flow rate V= 7,53 m3/h, pressure head H= 90kPa,
| - elektro podatki Pel= 0,427kW, 230V /1/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 0,427kW, 230V /1/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip MAGNA3 40-120 F ali enakovredno | - corresponds to GRUNDFOS product type MAGNA3 40-120 F or equivalent
| Oznaka: P64.281 | Code: P64.281 | kpl | 1 |  | 0
1.10 | Temperaturno tipalo, potopno, za merilno območje od 0 do +80°C, potopna dolžina L=100mm, v tulki iz nerjavnega materiala z navojnim priključkom 1/2" (DN15), električni podatki: napajanje 24V, izhod 4-20mA, komplet s pritrdilnim in tesnilnim materialom; | Temperature sensor, immersion, for measuring range from 0 to +80°C, immersion length L=100mm, in stainless steel sleeve with 1/2" (DN15) threaded connection, electrical data: power supply 24V, output 4-20mA, complete with fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - ustreza proizvod ELEKTRONIKA PAHOR, tip CVB ali enakovredno | - corresponds to the product ELEKTRONIKA PAHOR, type CVB or equivalent
| Oznaka: TIC64.211 | Code: TIC64.211 | kpl | 1 |  | 0
1.11 | Tipalo tlaka s pretvornikom, za mertev tlaka v območju od 0 do 6 barg (relativno) ter nastavljivim alarmnim tlakom, navojni priključek 1/2" (DN15), material nerjavno jeklo, električni podatki: napajanje 24V, izhod 4-20mA, kompletno z ventilom za tipalo tlaka 1/2" (DN15) ter tesnilnim in pritrdilnim materialom; | Pressure sensor with transducer, for pressure measurement in the range from 0 to 6 barg (relative) and adjustable alarm pressure, threaded connection 1/2" (DN15), material stainless steel, electrical data: power supply 24V, output 4-20mA, complete with pressure sensor valve 1/2" (DN15) and sealing and fixing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - alarm, če je tlak p < 1,0 barg (nastavitev na tipalu ali programska nastavitev) | - alarm if pressure p < 1.0 barg (sensor setting or software setting)
| - ustreza proizvod ENDRESS+HAUSER tip PTC31B + PZAV ali enakovredno | - corresponds to ENDRESS+HAUSER product type PTC31B + PZAV or equivalent
| Oznaka: PIA64.221 | Code: PIA64.221 | kpl | 1 |  | 0
1.12 | Ekspanzijska posoda za kompenzacijo toplotnih raztezkov medija v sistemu, PN10, skladno z direktivo EU o tlačni opremi PED, pokončna izvedba v obliki diska, membrana po DIN 4807, tlaki do 6 bar, temperature na membrani od 5 do 70°C, vključno s pritrdilnim in tesnilnim materialom; | Expansion vessel for compensation of thermal expansion of the medium in the system, PN10, in compliance with the EU Pressure Equipment Directive PED, upright disc design, diaphragm according to DIN 4807, pressures up to 6 bar, diaphragm temperatures from 5 to 70°C, incl. fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - prostornina ekspanzijske posode 25 litrov | - expansion tank capacity 25 litres
| - dimenzije: premer D x debelina H = ø440 x 250 mm | - dimensions: diameter D x thickness H = ø440 x 250 mm
| - z navojnim priključkom 3/4" (DN20), komplet z ventilom s ključavnico 3/4" (DN20) | - with 3/4" (DN20) threaded connection, complete with 3/4" (DN20) keyed valve
| - ustreza proizvod IMI PNEUMATEX tip SD 25.10 + DLV 20 ali enakovredno | - iMI PNEUMATEX product type SD 25.10 + DLV 20 or equivalent
| Oznaka: EP64.201 | Code: EP64.201 | kpl | 1 |  | 0
1.13 | Varnostni ventil po TRD 721, PN16, varnostna funkcija izpusta medija zaradi toplotnih raztezkov v sistemu, vzmetno delovanje, možnost ročnega odzračenja, prostor vzmeti zaščiten z membrano, prirobnična izvedba, vključno s pritrdilnim in tesnilnim materialom; | Safety valve according to TRD 721, PN16, safety function of medium discharge due to thermal expansion in the system, spring operation, manual venting possible, spring space protected by diaphragm, flanged version, including fastening and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - tlak odpiranja 3,0 barg, | - opening pressure 3,0 barg,
| - z navojnima priključkoma DN 20 / 25, komplet z ventilom s ključavnico 3/4" (DN20) | - with threaded connections DN 20 / 25, complete with 3/4" (DN20) ratchet valve
| - ustreza proizvod IMI PNEUMATEX tip DSV 20 - 3.0 H + DLV 20 ali enakovredno | - iMI PNEUMATEX product type DSV 20 - 3.0 H + DLV 20 or equivalent
| Oznaka: VV64.202 | Code: VV64.202 | kpl | 1 |  | 0
1.14 | Regulacijski ventil, prehodni, tlačno neodvisni za hidravlično uravnoteženje z elektromotornim zveznim pogonom, 24V, IP54, PN16, material ventila nikljana medenina, nerjavno jeklo / EPDM, navojna izvedba, komplet z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Control valve, intermediate, pressure independent for hydraulic balancing with electromotor continuous actuator, 24V, IP54, PN16, valve material nickel-plated brass, stainless steel / EPDM, threaded version, complete with threaded Dutch, fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| DN50, Vv = 5 ÷ 12,5 m3/h - ustreza proizvod DANFOSS tip ventila AB-QM 50, tip pogona AME 435 QM /24V ali enakovredno | DN50, Vv = 5 ÷ 12,5 m3/h - corresponds to DANFOSS product valve type AB-QM 50, actuator type AME 435 QM /24V or equivalent
| Oznaka: VY64.251 | Code: VY64.251 | kpl | 1 |  | 0
| Podsistem LFT | LFT subsystem
1.15 | Ploščni izmenjevalnik toplote, lotana izvedba (nerjavne plošče spojene z bakrenim lotom), PN10, material AISI316 (ali boljši), debeline plošč 0,6mm, tesnila EPDM do 100°C trajne obremenitve, skladnost s PED. Tehnični podatki: | Plate heat exchanger, loted design (stainless steel plates joined by copper lot), PN10, material AISI316 (or better), plate thickness 0,6mm, EPDM seals up to 100°C permanent load, PED compliant. Technical data:
| - hlajenje hladilne vode za laboratorij | - chilled water cooling for the laboratory
| - izmenjana toplota 70 kW - hlajenje | - heat exchanged 70 kW - cooling
| - primar hladna stran P: hladilna voda, temp. vstopa 9°C, temp. izstopa 14°C, pretok 12,03m3/h, padec tlaka do 30kPa | - primary cold side P: cooling water, inlet temp. 9°C, outlet temp. 14°C, flow rate 12,03m3/h, pressure drop up to 30kPa
| - sekundar topla stran S: hladna voda, temp. vstopa 20°C, temp. izstopa 12°C, pretok 7,53m3/h, padec tlaka do 20kPa | - secondary hot side S: cold water, inlet temp. 20°C, outlet temp. 12°C, flow rate 7,53m3/h, pressure drop up to 20kPa
| - vsi priključki prirobnični PN10, primar P DN50, sekundar S DN50 | - all connections flanged PN10, primary P DN50, secondary S DN50
| - vključno s podstavkom prenosnika, pritrdilnim in tesnilnim materialom; | - including the laptop base, fixing and sealing materials;
| - dimenzije do: dolžina L x širina W x višina H = 300 x 300 x 700 mm | - dimensions up to: length L x width W x height H = 300 x 300 x 700 mm
| - komplet s toplotna parozaporna izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +105°C, debelina 50mm | - complete with thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, classification B-s3-d0 according to EN13501-1, for temperatures -50 to +105°C, thickness 50mm
| - ustrezen proizvod ALFA LAVAL tip CB110-38M + toplotna izolacija ali enakovredno | - suitable product ALFA LAVAL type CB110-38M + thermal insulation or equivalent
| Oznaka: HE64.300 | Code: HE64.300 | kpl | 1 |  | 0
1.16 | Obtočna črpalka, PN10, z mokrim rotorjem, skladnost z ErP, elektronsko regulirana s PM motorjem in integrairanim frekvenčnim pretvornikom, inegrirano tipalo diferenčnega tlaka in temperature, upravljalnik nastavitev s prikazovalnikom parametrov, z internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, PN10, wet-rotor, ErP-compliant, electronically controlled with PM motor and integrated frequency converter, integrated differential pressure and temperature sensor, setting control with parameter display, with internal hydraulic, electrical and communication connections, pump material grey cast iron with appropriate sealing for the medium, flanged design, including counter flanges, fixing and sealing material. Technical data:
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - pretok V= 7,53 m3/h, tlačna višina H= 90kPa, | - flow rate V= 7,53 m3/h, pressure head H= 90kPa,
| - elektro podatki Pel= 0,427kW, 230V /1/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 0,427kW, 230V /1/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip MAGNA3 40-120 F ali enakovredno | - corresponds to GRUNDFOS product type MAGNA3 40-120 F or equivalent
| Oznaka: P64.381 | Code: P64.381 | kpl | 1 |  | 0
1.17 | Temperaturno tipalo, potopno, za merilno območje od 0 do +80°C, potopna dolžina L=100mm, v tulki iz nerjavnega materiala z navojnim priključkom 1/2" (DN15), električni podatki: napajanje 24V, izhod 4-20mA, komplet s pritrdilnim in tesnilnim materialom; | Temperature sensor, immersion, for measuring range from 0 to +80°C, immersion length L=100mm, in stainless steel sleeve with 1/2" (DN15) threaded connection, electrical data: power supply 24V, output 4-20mA, complete with fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - ustreza proizvod ELEKTRONIKA PAHOR, tip CVB ali enakovredno | - corresponds to the product ELEKTRONIKA PAHOR, type CVB or equivalent
| Oznaka: TIC64.311 | Code: TIC64.311 | kpl | 1 |  | 0
1.18 | Tipalo tlaka s pretvornikom, za mertev tlaka v območju od 0 do 6 barg (relativno) ter nastavljivim alarmnim tlakom, navojni priključek 1/2" (DN15), material nerjavno jeklo, električni podatki: napajanje 24V, izhod 4-20mA, kompletno z ventilom za tipalo tlaka 1/2" (DN15) ter tesnilnim in pritrdilnim materialom; | Pressure sensor with transducer, for pressure measurement in the range from 0 to 6 barg (relative) and adjustable alarm pressure, threaded connection 1/2" (DN15), material stainless steel, electrical data: power supply 24V, output 4-20mA, complete with pressure sensor valve 1/2" (DN15) and sealing and fixing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - alarm, če je tlak p < 1,0 barg (nastavitev na tipalu ali programska nastavitev) | - alarm if pressure p < 1.0 barg (sensor setting or software setting)
| - ustreza proizvod ENDRESS+HAUSER tip PTC31B + PZAV ali enakovredno | - corresponds to ENDRESS+HAUSER product type PTC31B + PZAV or equivalent
| Oznaka: PIA64.321 | Code: PIA64.321 | kpl | 1 |  | 0
1.19 | Ekspanzijska posoda za kompenzacijo toplotnih raztezkov medija v sistemu, PN10, skladno z direktivo EU o tlačni opremi PED, pokončna izvedba v obliki diska, membrana po DIN 4807, tlaki do 6 bar, temperature na membrani od 5 do 70°C, vključno s pritrdilnim in tesnilnim materialom; | Expansion vessel for compensation of thermal expansion of the medium in the system, PN10, in compliance with the EU Pressure Equipment Directive PED, upright disc design, diaphragm according to DIN 4807, pressures up to 6 bar, diaphragm temperatures from 5 to 70°C, incl. fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - prostornina ekspanzijske posode 25 litrov | - expansion tank capacity 25 litres
| - dimenzije: premer D x debelina H = ø440 x 250 mm | - dimensions: diameter D x thickness H = ø440 x 250 mm
| - z navojnim priključkom 3/4" (DN20), komplet z ventilom s ključavnico 3/4" (DN20) | - with 3/4" (DN20) threaded connection, complete with 3/4" (DN20) keyed valve
| - ustreza proizvod IMI PNEUMATEX tip SD 25.10 + DLV 20 ali enakovredno | - iMI PNEUMATEX product type SD 25.10 + DLV 20 or equivalent
| Oznaka: EP64.301 | Code: EP64.301 | kpl | 1 |  | 0
1.20 | Varnostni ventil po TRD 721, PN16, varnostna funkcija izpusta medija zaradi toplotnih raztezkov v sistemu, vzmetno delovanje, možnost ročnega odzračenja, prostor vzmeti zaščiten z membrano, prirobnična izvedba, vključno s pritrdilnim in tesnilnim materialom; | Safety valve according to TRD 721, PN16, safety function of medium discharge due to thermal expansion in the system, spring operation, manual venting possible, spring space protected by diaphragm, flanged version, including fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - tlak odpiranja 3,0 barg, | - opening pressure 3,0 barg,
| - z navojnima priključkoma DN 20 / 25, komplet z ventilom s ključavnico 3/4" (DN20) | - with threaded connections DN 20 / 25, complete with 3/4" (DN20) ratchet valve
| - ustreza proizvod IMI PNEUMATEX tip DSV 20 - 3.0 H + DLV 20 ali enakovredno | - iMI PNEUMATEX product type DSV 20 - 3.0 H + DLV 20 or equivalent
| Oznaka: VV64.302 | Code: VV64.302 | kpl | 1 |  | 0
1.21 | Regulacijski ventil, prehodni, tlačno neodvisni za hidravlično uravnoteženje z elektromotornim zveznim pogonom, 24V, IP54, PN16, material ventila nikljana medenina, nerjavno jeklo / EPDM, navojna izvedba, komplet z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Control valve, intermediate, pressure independent for hydraulic balancing with electromotor continuous actuator, 24V, IP54, PN16, valve material nickel-plated brass, stainless steel / EPDM, threaded version, complete with threaded Dutch, fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| DN50, Vv = 5 ÷ 12,5 m3/h - ustreza proizvod DANFOSS tip ventila AB-QM 50, tip pogona AME 435 QM /24V ali enakovredno | DN50, Vv = 5 ÷ 12,5 m3/h - corresponds to DANFOSS product valve type AB-QM 50, actuator type AME 435 QM /24V or equivalent
| Oznaka: VY64.351 | Code: VY64.351 | kpl | 1 |  | 0
| Podsistem LADISK | LADISK subsystem
1.22 | Ploščni izmenjevalnik toplote, lotana izvedba (nerjavne plošče spojene z bakrenim lotom), PN10, material AISI316 (ali boljši), debeline plošč 0,6mm, tesnila EPDM do 100°C trajne obremenitve, skladnost s PED. Tehnični podatki: | Plate heat exchanger, loted design (stainless steel plates joined by copper lot), PN10, material AISI316 (or better), plate thickness 0,6mm, EPDM seals up to 100°C permanent load, PED compliant. Technical data:
| - hlajenje hladilne vode za laboratorij | - chilled water cooling for the laboratory
| - izmenjana toplota 20 kW - hlajenje | - heat exchanged 20 kW - cooling
| - primar hladna stran P: hladilna voda, temp. vstopa 9°C, temp. izstopa 14°C, pretok 3,44m3/h, padec tlaka do 30kPa | - primary cold side P: cooling water, inlet temp. 9°C, outlet temp. 14°C, flow rate 3,44m3/h, pressure drop up to 30kPa
| - sekundar topla stran S: hladna voda, temp. vstopa 20°C, temp. izstopa 12°C, pretok 2,15m3/h, padec tlaka do 20kPa | - secondary hot side S: cold water, inlet temp. 20°C, outlet temp. 12°C, flow rate 2,15m3/h, pressure drop up to 20kPa
| - vsi priključki prirobnični PN10, primar P DN25, sekundar S DN25 | - all connections flanged PN10, primary P DN25, secondary S DN25
| - vključno s podstavkom prenosnika, pritrdilnim in tesnilnim materialom; | - including the laptop base, fixing and sealing materials;
| - dimenzije do: dolžina L x širina W x višina H = 300 x 200 x 400 mm | - dimensions up to: length L x width W x height H = 300 x 200 x 400 mm
| - komplet s toplotna parozaporna izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +105°C, debelina 50mm | - complete with thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, classification B-s3-d0 according to EN13501-1, for temperatures -50 to +105°C, thickness 50mm
| - ustrezen proizvod ALFA LAVAL tip CB30-50H + toplotna izolacija ali enakovredno | - suitable product ALFA LAVAL type CB30-50H + thermal insulation or equivalent
| Oznaka: HE64.400 | Code: HE64.400 | kpl | 1 |  | 0
1.23 | Obtočna črpalka, PN10, z mokrim rotorjem, skladnost z ErP, elektronsko regulirana s PM motorjem in integrairanim frekvenčnim pretvornikom, inegrirano tipalo diferenčnega tlaka in temperature, upravljalnik nastavitev s prikazovalnikom parametrov, z internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, PN10, wet-rotor, ErP-compliant, electronically controlled with PM motor and integrated frequency converter, integrated differential pressure and temperature sensor, setting control with parameter display, with internal hydraulic, electrical and communication connections, pump material grey cast iron with appropriate sealing for the medium, flanged design, including counter flanges, fixing and sealing material. Technical data:
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - pretok V= 2,153 m3/h, tlačna višina H= 85kPa, | - flow rate V= 2,153 m3/h, pressure head H= 85kPa,
| - elektro podatki Pel= 0,153kW, 230V /1/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 0,153kW, 230V /1/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip MAGNA3 25-100 ali enakovredno | - corresponds to GRUNDFOS product type MAGNA3 25-100 or equivalent
| Oznaka: P64.481 | Code: P64.481 | kpl | 1 |  | 0
1.24 | Temperaturno tipalo, potopno, za merilno območje od 0 do +80°C, potopna dolžina L=100mm, v tulki iz nerjavnega materiala z navojnim priključkom 1/2" (DN15), električni podatki: napajanje 24V, izhod 4-20mA, komplet s pritrdilnim in tesnilnim materialom; | Temperature sensor, immersion, for measuring range from 0 to +80°C, immersion length L=100mm, in stainless steel sleeve with 1/2" (DN15) threaded connection, electrical data: power supply 24V, output 4-20mA, complete with fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - ustreza proizvod ELEKTRONIKA PAHOR, tip CVB ali enakovredno | - corresponds to the product ELEKTRONIKA PAHOR, type CVB or equivalent
| Oznaka: TIC64.411 | Code: TIC64.411 | kpl | 1 |  | 0
1.25 | Tipalo tlaka s pretvornikom, za mertev tlaka v območju od 0 do 6 barg (relativno) ter nastavljivim alarmnim tlakom, navojni priključek 1/2" (DN15), material nerjavno jeklo, električni podatki: napajanje 24V, izhod 4-20mA, kompletno z ventilom za tipalo tlaka 1/2" (DN15) ter tesnilnim in pritrdilnim materialom; | Pressure sensor with transducer, for pressure measurement in the range from 0 to 6 barg (relative) and adjustable alarm pressure, threaded connection 1/2" (DN15), material stainless steel, electrical data: power supply 24V, output 4-20mA, complete with pressure sensor valve 1/2" (DN15) and sealing and fixing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - alarm, če je tlak p < 1,0 barg (nastavitev na tipalu ali programska nastavitev) | - alarm if pressure p < 1.0 barg (sensor setting or software setting)
| - ustreza proizvod ENDRESS+HAUSER tip PTC31B + PZAV ali enakovredno | - corresponds to ENDRESS+HAUSER product type PTC31B + PZAV or equivalent
| Oznaka: PIA64.421 | Code: PIA64.421 | kpl | 1 |  | 0
1.26 | Ekspanzijska posoda za kompenzacijo toplotnih raztezkov medija v sistemu, PN10, skladno z direktivo EU o tlačni opremi PED, pokončna izvedba v obliki diska, membrana po DIN 4807, tlaki do 6 bar, temperature na membrani od 5 do 70°C, vključno s pritrdilnim in tesnilnim materialom; | Expansion vessel for compensation of thermal expansion of the medium in the system, PN10, in compliance with the EU Pressure Equipment Directive PED, upright disc design, diaphragm according to DIN 4807, pressures up to 6 bar, diaphragm temperatures from 5 to 70°C, incl. fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - prostornina ekspanzijske posode 12 litrov | - expansion tank capacity 12 litres
| - dimenzije: premer D x debelina H = ø360 x 170 mm | - dimensions: diameter D x thickness H = ø360 x 170 mm
| - z navojnim priključkom 1/2" (DN15), komplet z ventilom s ključavnico 1/2" (DN15) | - with threaded connection 1/2" (DN15), complete with valve with lock 1/2" (DN15)
| - ustreza proizvod IMI PNEUMATEX tip SD 12.10 + DLV 15 ali enakovredno | - corresponds to IMI PNEUMATEX product type SD 12.10 + DLV 15 or equivalent
| Oznaka: EP64.401 | Code: EP64.401 | kpl | 1 |  | 0
1.27 | Varnostni ventil po TRD 721, PN16, varnostna funkcija izpusta medija zaradi toplotnih raztezkov v sistemu, vzmetno delovanje, možnost ročnega odzračenja, prostor vzmeti zaščiten z membrano, prirobnična izvedba, vključno s pritrdilnim in tesnilnim materialom; | Safety valve according to TRD 721, PN16, safety function of medium discharge due to thermal expansion in the system, spring operation, manual venting possible, spring space protected by diaphragm, flanged version, including fastening and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - tlak odpiranja 3,0 barg, | - opening pressure 3,0 barg,
| - z navojnima priključkoma DN 15 / 20, komplet z ventilom s ključavnico 1/2" (DN15) | - with threaded connections DN 15 / 20, complete with 1/2" (DN 15) ratchet valve
| - ustreza proizvod IMI PNEUMATEX tip DSV 15 - 3.0 H + DLV 20 ali enakovredno | - iMI PNEUMATEX product type DSV 15 - 3.0 H + DLV 20 or equivalent
| Oznaka: VV64.402 | Code: VV64.402 | kpl | 1 |  | 0
1.28 | Regulacijski ventil, prehodni, tlačno neodvisni za hidravlično uravnoteženje z elektromotornim zveznim pogonom, 24V, IP54, PN16, material ventila nikljana medenina, nerjavno jeklo / EPDM, navojna izvedba, komplet z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Control valve, intermediate, pressure independent for hydraulic balancing with electromotor continuous actuator, 24V, IP54, PN16, valve material nickel-plated brass, stainless steel / EPDM, threaded version, complete with threaded Dutch, fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| DN32, Vv = 0,36 ÷ 3,6 m3/h - ustreza proizvod DANFOSS tip ventila AB-QM 32, tip pogona AME 110/24V NL ali enakovredno | DN32, Vv = 0,36 ÷ 3,6 m3/h - corresponds to DANFOSS product valve type AB-QM 32, actuator type AME 110/24V NL or equivalent
| Oznaka: VY64.451 | Code: VY64.451 | kpl | 1 |  | 0
| Podsistem Lab skupni | Lab Common Subsystem
1.29 | Ploščni izmenjevalnik toplote, lotana izvedba (nerjavne plošče spojene z bakrenim lotom), PN10, material AISI316 (ali boljši), debeline plošč 0,6mm, tesnila EPDM do 100°C trajne obremenitve, skladnost s PED. Tehnični podatki: | Plate heat exchanger, loted design (stainless steel plates joined by copper lot), PN10, material AISI316 (or better), plate thickness 0,6mm, EPDM seals up to 100°C permanent load, PED compliant. Technical data:
| - hlajenje hladilne vode za laboratorij | - chilled water cooling for the laboratory
| - izmenjana toplota 100 kW - hlajenje | - heat exchanged 100 kW - cooling
| - primar hladna stran P: hladilna voda, temp. vstopa 9°C, temp. izstopa 14°C, pretok 17,19m3/h, padec tlaka do 30kPa | - primary cold side P: cooling water, inlet temp. 9°C, outlet temp. 14°C, flow 17,19m3/h, pressure drop up to 30kPa
| - sekundar topla stran S: hladna voda, temp. vstopa 20°C, temp. izstopa 12°C, pretok 10,77m3/h, padec tlaka do 20kPa | - secondary hot side S: cold water, inlet temp. 20°C, outlet temp. 12°C, flow rate 10.77m3/h, pressure drop up to 20kPa
| - vsi priključki prirobnični PN10, primar P DN50, sekundar S DN50 | - all connections flanged PN10, primary P DN50, secondary S DN50
| - vključno s podstavkom prenosnika, pritrdilnim in tesnilnim materialom; | - including the laptop base, fixing and sealing materials;
| - dimenzije do: dolžina L x širina W x višina H = 400 x 300 x 700 mm | - dimensions up to: length L x width W x height H = 400 x 300 x 700 mm
| - komplet s toplotna parozaporna izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +105°C, debelina 50mm | - complete with thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, classification B-s3-d0 according to EN13501-1, for temperatures -50 to +105°C, thickness 50mm
| - ustrezen proizvod ALFA LAVAL tip CB110-55M + toplotna izolacija ali enakovredno | - suitable product ALFA LAVAL type CB110-55M + thermal insulation or equivalent
| Oznaka: HE63.100 | Code: HE63.100 | kpl | 1 |  | 0
1.30 | Obtočna črpalka, PN10, z mokrim rotorjem, skladnost z ErP, elektronsko regulirana s PM motorjem in integrairanim frekvenčnim pretvornikom, inegrirano tipalo diferenčnega tlaka in temperature, upravljalnik nastavitev s prikazovalnikom parametrov, z internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, PN10, wet-rotor, ErP-compliant, electronically controlled with PM motor and integrated frequency converter, integrated differential pressure and temperature sensor, setting controller with parameter display, with internal hydraulic, electrical and communication connections, pump material grey cast iron with appropriate sealing for the medium, flanged design, including counter-flanges, fixing and sealing material. Technical data:
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - pretok V= 10,77 m3/h, tlačna višina H= 85kPa, | - flow rate V= 10,77 m3/h, pressure head H= 85kPa,
| - elektro podatki Pel= 0,427kW, 230V /1/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 0,427kW, 230V /1/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip MAGNA3 40-120 F ali enakovredno | - corresponds to GRUNDFOS product type MAGNA3 40-120 F or equivalent
| Oznaka: P63.181 | Code: P63.181 | kpl | 1 |  | 0
1.31 | Temperaturno tipalo, potopno, za merilno območje od 0 do +80°C, potopna dolžina L=100mm, v tulki iz nerjavnega materiala z navojnim priključkom 1/2" (DN15), električni podatki: napajanje 24V, izhod 4-20mA, komplet s pritrdilnim in tesnilnim materialom; | Temperature sensor, immersion, for measuring range from 0 to +80°C, immersion length L=100mm, in stainless steel sleeve with 1/2" (DN15) threaded connection, electrical data: power supply 24V, output 4-20mA, complete with fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - ustreza proizvod ELEKTRONIKA PAHOR, tip CVB ali enakovredno | - corresponds to the product ELEKTRONIKA PAHOR, type CVB or equivalent
| Oznaka: TIC63.111 | Code: TIC63.111 | kpl | 1 |  | 0
1.32 | Tipalo tlaka s pretvornikom, za mertev tlaka v območju od 0 do 6 barg (relativno) ter nastavljivim alarmnim tlakom, navojni priključek 1/2" (DN15), material nerjavno jeklo, električni podatki: napajanje 24V, izhod 4-20mA, kompletno z ventilom za tipalo tlaka 1/2" (DN15) ter tesnilnim in pritrdilnim materialom; | Pressure sensor with transducer, for pressure measurement in the range from 0 to 6 barg (relative) and adjustable alarm pressure, threaded connection 1/2" (DN15), material stainless steel, electrical data: power supply 24V, output 4-20mA, complete with pressure sensor valve 1/2" (DN15) and sealing and fixing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - alarm, če je tlak p < 1,0 barg (nastavitev na tipalu ali programska nastavitev) | - alarm if pressure p < 1.0 barg (sensor setting or software setting)
| - ustreza proizvod ENDRESS+HAUSER tip PTC31B + PZAV ali enakovredno | - corresponds to ENDRESS+HAUSER product type PTC31B + PZAV or equivalent
| Oznaka: PIA63.121 | Code: PIA63.121 | kpl | 1 |  | 0
1.33 | Ekspanzijska posoda za kompenzacijo toplotnih raztezkov medija v sistemu, PN10, skladno z direktivo EU o tlačni opremi PED, pokončna izvedba v obliki diska, membrana po DIN 4807, tlaki do 6 bar, temperature na membrani od 5 do 70°C, vključno s pritrdilnim in tesnilnim materialom; | Expansion vessel for compensation of thermal expansion of the medium in the system, PN10, in compliance with the EU Pressure Equipment Directive PED, upright disc design, diaphragm according to DIN 4807, pressures up to 6 bar, diaphragm temperatures from 5 to 70°C, incl. fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - prostornina ekspanzijske posode 35 litrov | - expansion tank capacity 35 litres
| - dimenzije: premer D x debelina H = ø490 x 280 mm | - dimensions: diameter D x thickness H = ø490 x 280 mm
| - z navojnim priključkom 3/4" (DN20), komplet z ventilom s ključavnico 3/4" (DN20) | - with 3/4" (DN20) threaded connection, complete with 3/4" (DN20) keyed valve
| - ustreza proizvod IMI PNEUMATEX tip SD 35.10 + DLV 20 ali enakovredno | - corresponds to IMI PNEUMATEX product type SD 35.10 + DLV 20 or equivalent
| Oznaka: EP63.201 | Code: EP63.201 | kpl | 1 |  | 0
1.34 | Varnostni ventil po TRD 721, PN16, varnostna funkcija izpusta medija zaradi toplotnih raztezkov v sistemu, vzmetno delovanje, možnost ročnega odzračenja, prostor vzmeti zaščiten z membrano, prirobnična izvedba, vključno s pritrdilnim in tesnilnim materialom; | Safety valve according to TRD 721, PN16, safety function of medium discharge due to thermal expansion in the system, spring operation, manual venting possible, spring space protected by diaphragm, flanged version, including fastening and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - tlak odpiranja 3,0 barg, | - opening pressure 3,0 barg,
| - z navojnima priključkoma DN 25 / 32, komplet z ventilom s ključavnico 1" (DN25) | - with DN 25 / 32 threaded connections, complete with 1" (DN 25) ratchet valve
| - ustreza proizvod IMI PNEUMATEX tip DSV 25 - 3.0 H + DLV 25 ali enakovredno | - iMI PNEUMATEX product type DSV 25 - 3.0 H + DLV 25 or equivalent
| Oznaka: VV64.302 | Code: VV64.302 | kpl | 1 |  | 0
1.35 | Regulacijski ventil, prehodni, tlačno neodvisni za hidravlično uravnoteženje z elektromotornim zveznim pogonom, 24V, IP54, PN16, material ventila nikljana medenina, nerjavno jeklo / EPDM, navojna izvedba, komplet z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Control valve, intermediate, pressure independent for hydraulic balancing with electromotor continuous actuator, 24V, IP54, PN16, valve material nickel-plated brass, stainless steel / EPDM, threaded version, complete with threaded Dutch, fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| DN65, Vv = 5 ÷ 12,5 m3/h - ustreza proizvod DANFOSS tip ventila AB-QM 65 F, tip pogona AME 435 QM /24V ali enakovredno | DN65, Vv = 5 ÷ 12,5 m3/h - corresponds to DANFOSS product valve type AB-QM 65 F, actuator type AME 435 QM /24V or equivalent
| Oznaka: VY63.151 | Code: VY63.151 | kpl | 1 |  | 0
| Podsistem LAVAR | LAVAR subsystem
1.36 | Ploščni izmenjevalnik toplote, lotana izvedba (nerjavne plošče spojene z bakrenim lotom), PN10, material AISI316 (ali boljši), debeline plošč 0,6mm, tesnila EPDM do 100°C trajne obremenitve, skladnost s PED. Tehnični podatki: | Plate heat exchanger, loted design (stainless steel plates joined by copper lot), PN10, material AISI316 (or better), plate thickness 0,6mm, EPDM seals up to 100°C permanent load, PED compliant. Technical data:
| - hlajenje hladilne vode za laboratorij | - chilled water cooling for the laboratory
| - izmenjana toplota 16 kW - hlajenje | - heat exchanged 16 kW - cooling
| - primar hladna stran P: hladilna voda, temp. vstopa 9°C, temp. izstopa 14°C, pretok 2,75m3/h, padec tlaka do 30kPa | - primary cold side P: cooling water, inlet temp. 9°C, outlet temp. 14°C, flow rate 2,75m3/h, pressure drop up to 30kPa
| - sekundar topla stran S: hladna voda, temp. vstopa 20°C, temp. izstopa 12°C, pretok 1,72m3/h, padec tlaka do 20kPa | - secondary hot side S: cold water, inlet temp. 20°C, outlet temp. 12°C, flow rate 1,72m3/h, pressure drop up to 20kPa
| - vsi priključki prirobnični PN10, primar P DN25, sekundar S DN25 | - all connections flanged PN10, primary P DN25, secondary S DN25
| - vključno s podstavkom prenosnika, pritrdilnim in tesnilnim materialom; | - including the laptop base, fixing and sealing materials;
| - dimenzije do: dolžina L x širina W x višina H = 300 x 200 x 400 mm | - dimensions up to: length L x width W x height H = 300 x 200 x 400 mm
| - komplet s toplotna parozaporna izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +105°C, debelina 50mm | - complete with thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, classification B-s3-d0 according to EN13501-1, for temperatures -50 to +105°C, thickness 50mm
| - ustrezen proizvod ALFA LAVAL tip CB30-50H + toplotna izolacija ali enakovredno | - suitable product ALFA LAVAL type CB30-50H + thermal insulation or equivalent
| Oznaka: HE63.200 | Code: HE63.200 | kpl | 1 |  | 0
1.37 | Obtočna črpalka, PN10, z mokrim rotorjem, skladnost z ErP, elektronsko regulirana s PM motorjem in integrairanim frekvenčnim pretvornikom, inegrirano tipalo diferenčnega tlaka in temperature, upravljalnik nastavitev s prikazovalnikom parametrov, z internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, PN10, wet-rotor, ErP-compliant, electronically controlled with PM motor and integrated frequency converter, integrated differential pressure and temperature sensor, setting controller with parameter display, with internal hydraulic, electrical and communication connections, pump material grey cast iron with appropriate sealing for the medium, flanged design, including counter-flanges, fixing and sealing material. Technical data:
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - pretok V= 1,72 m3/h, tlačna višina H= 85kPa, | - flow rate V= 1,72 m3/h, pressure head H= 85kPa,
| - elektro podatki Pel= 0,153kW, 230V /1/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 0,153kW, 230V /1/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip MAGNA3 25-100 ali enakovredno | - corresponds to GRUNDFOS product type MAGNA3 25-100 or equivalent
| Oznaka: P63.281 | Code: P63.281 | kpl | 1 |  | 0
1.38 | Temperaturno tipalo, potopno, za merilno območje od 0 do +80°C, potopna dolžina L=100mm, v tulki iz nerjavnega materiala z navojnim priključkom 1/2" (DN15), električni podatki: napajanje 24V, izhod 4-20mA, komplet s pritrdilnim in tesnilnim materialom; | Temperature sensor, immersion, for measuring range from 0 to +80°C, immersion length L=100mm, in stainless steel sleeve with 1/2" (DN15) threaded connection, electrical data: power supply 24V, output 4-20mA, complete with fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - ustreza proizvod ELEKTRONIKA PAHOR, tip CVB ali enakovredno | - corresponds to the product ELEKTRONIKA PAHOR, type CVB or equivalent
| Oznaka: TIC63.211 | Code: TIC63.211 | kpl | 1 |  | 0
1.39 | Tipalo tlaka s pretvornikom, za mertev tlaka v območju od 0 do 6 barg (relativno) ter nastavljivim alarmnim tlakom, navojni priključek 1/2" (DN15), material nerjavno jeklo, električni podatki: napajanje 24V, izhod 4-20mA, kompletno z ventilom za tipalo tlaka 1/2" (DN15) ter tesnilnim in pritrdilnim materialom; | Pressure sensor with transducer, for pressure measurement in the range from 0 to 6 barg (relative) and adjustable alarm pressure, threaded connection 1/2" (DN15), material stainless steel, electrical data: power supply 24V, output 4-20mA, complete with pressure sensor valve 1/2" (DN15) and sealing and fixing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - alarm, če je tlak p < 1,0 barg (nastavitev na tipalu ali programska nastavitev) | - alarm if pressure p < 1.0 barg (sensor setting or software setting)
| - ustreza proizvod ENDRESS+HAUSER tip PTC31B + PZAV ali enakovredno | - corresponds to ENDRESS+HAUSER product type PTC31B + PZAV or equivalent
| Oznaka: PIA63.221 | Code: PIA63.221 | kpl | 1 |  | 0
1.40 | Ekspanzijska posoda za kompenzacijo toplotnih raztezkov medija v sistemu, PN10, skladno z direktivo EU o tlačni opremi PED, pokončna izvedba v obliki diska, membrana po DIN 4807, tlaki do 6 bar, temperature na membrani od 5 do 70°C, vključno s pritrdilnim in tesnilnim materialom; | Expansion vessel for compensation of thermal expansion of the medium in the system, PN10, in compliance with the EU Pressure Equipment Directive PED, upright disc design, diaphragm according to DIN 4807, pressures up to 6 bar, diaphragm temperatures from 5 to 70°C, incl. fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - prostornina ekspanzijske posode 12 litrov | - expansion tank capacity 12 litres
| - dimenzije: premer D x debelina H = ø360 x 170 mm | - dimensions: diameter D x thickness H = ø360 x 170 mm
| - z navojnim priključkom 1/2" (DN15), komplet z ventilom s ključavnico 1/2" (DN15) | - with threaded connection 1/2" (DN15), complete with valve with lock 1/2" (DN15)
| - ustreza proizvod IMI PNEUMATEX tip SD 12.10 + DLV 15 ali enakovredno | - corresponds to IMI PNEUMATEX product type SD 12.10 + DLV 15 or equivalent
| Oznaka: EP63.201 | Code: EP63.201 | kpl | 1 |  | 0
1.41 | Varnostni ventil po TRD 721, PN16, varnostna funkcija izpusta medija zaradi toplotnih raztezkov v sistemu, vzmetno delovanje, možnost ročnega odzračenja, prostor vzmeti zaščiten z membrano, prirobnična izvedba, vključno s pritrdilnim in tesnilnim materialom; | Safety valve according to TRD 721, PN16, safety function of medium discharge due to thermal expansion in the system, spring operation, manual venting possible, spring space protected by diaphragm, flanged version, including fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - tlak odpiranja 3,0 barg, | - opening pressure 3,0 barg,
| - z navojnima priključkoma DN 15 / 20, komplet z ventilom s ključavnico 1/2" (DN15) | - with threaded connections DN 15 / 20, complete with 1/2" (DN 15) ratchet valve
| - ustreza proizvod IMI PNEUMATEX tip DSV 15 - 3.0 H + DLV 20 ali enakovredno | - iMI PNEUMATEX product type DSV 15 - 3.0 H + DLV 20 or equivalent
| Oznaka: VV63.202 | Code: VV63.202 | kpl | 1 |  | 0
1.42 | Regulacijski ventil, prehodni, tlačno neodvisni za hidravlično uravnoteženje z elektromotornim zveznim pogonom, 24V, IP54, PN16, material ventila nikljana medenina, nerjavno jeklo / EPDM, navojna izvedba, komplet z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Control valve, intermediate, pressure independent for hydraulic balancing with electromotor continuous actuator, 24V, IP54, PN16, valve material nickel-plated brass, stainless steel / EPDM, threaded version, complete with threaded Dutch, fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| DN32, Vv = 0,36 ÷ 3,6 m3/h - ustreza proizvod DANFOSS tip ventila AB-QM 32, tip pogona AME 110/24V NL ali enakovredno | DN32, Vv = 0,36 ÷ 3,6 m3/h - corresponds to DANFOSS product valve type AB-QM 32, actuator type AME 110/24V NL or equivalent
| Oznaka: VY63.251 | Code: VY63.251 | kpl | 1 |  | 0
| Podsistem LOSK (P1.J2) | LOSK subsystem (P1.J2)
1.43 | Ploščni izmenjevalnik toplote, lotana izvedba (nerjavne plošče spojene z bakrenim lotom), PN10, material AISI316 (ali boljši), debeline plošč 0,6mm, tesnila EPDM do 100°C trajne obremenitve, skladnost s PED. Tehnični podatki: | Plate heat exchanger, loted design (stainless steel plates joined by copper lot), PN10, material AISI316 (or better), plate thickness 0,6mm, EPDM seals up to 100°C permanent load, PED compliant. Technical data:
| - hlajenje hladilne vode za laboratorij | - chilled water cooling for the laboratory
| - izmenjana toplota 15 kW - hlajenje | - heat exchanged 15 kW - cooling
| - primar hladna stran P: hladilna voda, temp. vstopa 9°C, temp. izstopa 14°C, pretok 2,58m3/h, padec tlaka do 30kPa | - primary cold side P: cooling water, inlet temp. 9°C, outlet temp. 14°C, flow rate 2.58m3/h, pressure drop up to 30kPa
| - sekundar topla stran S: hladna voda, temp. vstopa 15°C, temp. izstopa 10°C, pretok 2,58m3/h, padec tlaka do 30kPa | - secondary hot side S: cold water, inlet temp. 15°C, outlet temp. 10°C, flow rate 2,58m3/h, pressure drop up to 30kPa
| - vsi priključki prirobnični PN10, primar P DN32, sekundar S DN32 | - all connections flanged PN10, primary P DN32, secondary S DN32
| - vključno s podstavkom prenosnika, pritrdilnim in tesnilnim materialom; | - including the laptop base, fixing and sealing materials;
| - dimenzije do: dolžina L x širina W x višina H = 300 x 200 x 600 mm | - dimensions up to: length L x width W x height H = 300 x 200 x 600 mm
| - komplet s toplotna parozaporna izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +105°C, debelina 50mm | - complete with thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, classification B-s3-d0 according to EN13501-1, for temperatures -50 to +105°C, thickness 50mm
| - ustrezen proizvod ALFA LAVAL tip CB60-60H + toplotna izolacija ali enakovredno | - suitable product ALFA LAVAL type CB60-60H + thermal insulation or equivalent
| Oznaka: HE63.300 | Code: HE63.300 | kpl | 1 |  | 0
1.44 | Ploščni izmenjevalnik toplote, lotana izvedba (nerjavne plošče spojene z bakrenim lotom), PN10, material AISI316 (ali boljši), debeline plošč 0,6mm, tesnila EPDM do 100°C trajne obremenitve, skladnost s PED. Tehnični podatki: | Plate heat exchanger, loted design (stainless steel plates joined by copper lot), PN10, material AISI316 (or better), plate thickness 0,6mm, EPDM seals up to 100°C permanent load, PED compliant. Technical data:
| - ogrevanje ogrevne vode za laboratorij | - heating water for the laboratory
| - izmenjana toplota 25 kW - ogrevanje | - heat exchanged 25 kW - heating
| - primar hladna stran P: hladilna voda, temp. vstopa 50°C, temp. izstopa 40°C, pretok 2,17m3/h, padec tlaka do 30kPa | - primary cold side P: cooling water, inlet temp 50°C, outlet temp 40°C, flow rate 2.17m3/h, pressure drop up to 30kPa
| - sekundar topla stran S: hladna voda, temp. vstopa 38°C, temp. izstopa 48°C, pretok 2,17m3/h, padec tlaka do 30kPa | - secondary hot side S: cold water, inlet temp. 38°C, outlet temp. 48°C, flow rate 2.17m3/h, pressure drop up to 30kPa
| - vsi priključki prirobnični PN10, primar P DN32, sekundar S DN32 | - all connections flanged PN10, primary P DN32, secondary S DN32
| - vključno s podstavkom prenosnika, pritrdilnim in tesnilnim materialom; | - including the laptop base, fixing and sealing materials;
| - dimenzije do: dolžina L x širina W x višina H = 300 x 200 x 600 mm | - dimensions up to: length L x width W x height H = 300 x 200 x 600 mm
| - komplet s toplotna parozaporna izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +105°C, debelina 50mm | - complete with thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, classification B-s3-d0 according to EN13501-1, for temperatures -50 to +105°C, thickness 50mm
| - ustrezen proizvod ALFA LAVAL tip CB60-60H + toplotna izolacija ali enakovredno | - suitable product ALFA LAVAL type CB60-60H + thermal insulation or equivalent
| Oznaka: HE53.300 | Code: HE53.300 | kpl | 1 |  | 0
1.45 | Obtočna črpalka, PN10, z mokrim rotorjem, skladnost z ErP, elektronsko regulirana s PM motorjem in integrairanim frekvenčnim pretvornikom, inegrirano tipalo diferenčnega tlaka in temperature, upravljalnik nastavitev s prikazovalnikom parametrov, z internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, PN10, wet-rotor, ErP-compliant, electronically controlled with PM motor and integrated frequency converter, integrated differential pressure and temperature sensor, setting control with parameter display, with internal hydraulic, electrical and communication connections, pump material grey cast iron with appropriate sealing for the medium, flanged design, including counter flanges, fixing and sealing material. Technical data:
| - za obtok hladilne vode laboratorija 10/15°C | - for laboratory cooling water circulation 10/15°C
| - pretok V= 2,58 m3/h, tlačna višina H= 95kPa, | - flow rate V= 2,58 m3/h, pressure head H= 95kPa,
| - elektro podatki Pel= 0,153kW, 230V /1/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 0,153kW, 230V /1/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip MAGNA3 25-100 ali enakovredno | - corresponds to GRUNDFOS product type MAGNA3 25-100 or equivalent
| Oznaka: P63.381 | Code: P63.381 | kpl | 1 |  | 0
1.46 | Obtočna črpalka, PN10, z mokrim rotorjem, skladnost z ErP, elektronsko regulirana s PM motorjem in integrairanim frekvenčnim pretvornikom, inegrirano tipalo diferenčnega tlaka in temperature, upravljalnik nastavitev s prikazovalnikom parametrov, z internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, PN10, wet-rotor, ErP-compliant, electronically controlled with PM motor and integrated frequency converter, integrated differential pressure and temperature sensor, setting control with parameter display, with internal hydraulic, electrical and communication connections, pump material grey cast iron with appropriate sealing for the medium, flanged design, including counter flanges, fixing and sealing material. Technical data:
| - za obtok ogrevne vode laboratorija 48/38°C | - for laboratory heating water circulation 48/38°C
| - pretok V= 2,17 m3/h, tlačna višina H= 95kPa, | - flow rate V= 2,17 m3/h, pressure head H= 95kPa,
| - elektro podatki Pel= 0,153kW, 230V /1/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 0,153kW, 230V /1/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip MAGNA3 25-100 ali enakovredno | - corresponds to GRUNDFOS product type MAGNA3 25-100 or equivalent
| Oznaka: P53.381 | Code: P53.381 | kpl | 1 |  | 0
1.47 | Temperaturno tipalo, potopno, za merilno območje od 0 do +80°C, potopna dolžina L=100mm, v tulki iz nerjavnega materiala z navojnim priključkom 1/2" (DN15), električni podatki: napajanje 24V, izhod 4-20mA, komplet s pritrdilnim in tesnilnim materialom; | Temperature sensor, immersion, for measuring range from 0 to +80°C, immersion length L=100mm, in stainless steel sleeve with 1/2" (DN15) threaded connection, electrical data: power supply 24V, output 4-20mA, complete with fixing and sealing material;
| - hladilna voda za laboratorij 10/15°C | - laboratory cooling water 10/15°C
| - ogrevna voda za laboratorij 48/38°C | - laboratory heating water 48/38°C
| - ustreza proizvod ELEKTRONIKA PAHOR, tip CVB ali enakovredno | - corresponds to the product ELEKTRONIKA PAHOR, type CVB or equivalent
| Oznaka: TIC63.311, TIC53.311 | Code: TIC63.311, TIC53.311 | kpl | 2 |  | 0
1.48 | Tipalo tlaka s pretvornikom, za mertev tlaka v območju od 0 do 6 barg (relativno) ter nastavljivim alarmnim tlakom, navojni priključek 1/2" (DN15), material nerjavno jeklo, električni podatki: napajanje 24V, izhod 4-20mA, kompletno z ventilom za tipalo tlaka 1/2" (DN15) ter tesnilnim in pritrdilnim materialom; | Pressure sensor with transducer, for pressure measurement in the range from 0 to 6 barg (relative) and adjustable alarm pressure, threaded connection 1/2" (DN15), material stainless steel, electrical data: power supply 24V, output 4-20mA, complete with pressure sensor valve 1/2" (DN15) and sealing and fixing material;
| - hladilna voda za laboratorij 10/15°C | - laboratory cooling water 10/15°C
| - ogrevna voda za laboratorij 48/38°C | - laboratory heating water 48/38°C
| - alarm, če je tlak p < 1,0 barg (nastavitev na tipalu ali programska nastavitev) | - alarm if pressure p < 1.0 barg (sensor setting or software setting)
| - ustreza proizvod ENDRESS+HAUSER tip PTC31B + PZAV ali enakovredno | - corresponds to ENDRESS+HAUSER product type PTC31B + PZAV or equivalent
| Oznaka: PIA63.321, PIA53.321 | Code: PIA63.321, PIA53.321 | kpl | 2 |  | 0
1.49 | Ekspanzijska posoda za kompenzacijo toplotnih raztezkov medija v sistemu, PN10, skladno z direktivo EU o tlačni opremi PED, pokončna izvedba v obliki diska, membrana po DIN 4807, tlaki do 6 bar, temperature na membrani od 5 do 70°C, vključno s pritrdilnim in tesnilnim materialom; | Expansion vessel for compensation of thermal expansion of the medium in the system, PN10, in compliance with the EU Pressure Equipment Directive PED, upright disc design, diaphragm according to DIN 4807, pressures up to 6 bar, diaphragm temperatures from 5 to 70°C, incl. fixing and sealing material;
| - hladilna voda za laboratorij 10/15°C | - laboratory cooling water 10/15°C
| - ogrevna voda za laboratorij 48/38°C | - laboratory heating water 48/38°C
| - prostornina ekspanzijske posode 12 litrov | - expansion tank capacity 12 litres
| - dimenzije: premer D x debelina H = ø360 x 170 mm | - dimensions: diameter D x thickness H = ø360 x 170 mm
| - z navojnim priključkom 1/2" (DN15), komplet z ventilom s ključavnico 1/2" (DN15) | - with threaded connection 1/2" (DN15), complete with valve with lock 1/2" (DN15)
| - ustreza proizvod IMI PNEUMATEX tip SD 12.10 + DLV 15 ali enakovredno | - corresponds to IMI PNEUMATEX product type SD 12.10 + DLV 15 or equivalent
| Oznaka: EP63.301, EP53.301 | Code: EP63.301, EP53.301 | kpl | 2 |  | 0
1.50 | Varnostni ventil po TRD 721, PN16, varnostna funkcija izpusta medija zaradi toplotnih raztezkov v sistemu, vzmetno delovanje, možnost ročnega odzračenja, prostor vzmeti zaščiten z membrano, prirobnična izvedba, vključno s pritrdilnim in tesnilnim materialom; | Safety valve according to TRD 721, PN16, safety function of medium discharge due to thermal expansion in the system, spring operation, manual venting possible, spring space protected by diaphragm, flanged version, including fastening and sealing material;
| - hladilna voda za laboratorij 10/15°C | - laboratory cooling water 10/15°C
| - ogrevna voda za laboratorij 48/38°C | - laboratory heating water 48/38°C
| - tlak odpiranja 3,0 barg, | - opening pressure 3,0 barg,
| - z navojnima priključkoma DN 15 / 20, komplet z ventilom s ključavnico 1/2" (DN15) | - with threaded connections DN 15 / 20, complete with 1/2" (DN 15) ratchet valve
| - ustreza proizvod IMI PNEUMATEX tip DSV 15 - 3.0 H + DLV 20 ali enakovredno | - iMI PNEUMATEX product type DSV 15 - 3.0 H + DLV 20 or equivalent
| Oznaka: VV63.302, VV53.302 | Code: VV63.302, VV53.302 | kpl | 1 |  | 0
1.51 | Regulacijski ventil, prehodni, tlačno neodvisni za hidravlično uravnoteženje z elektromotornim zveznim pogonom, 24V, IP54, PN16, material ventila nikljana medenina, nerjavno jeklo / EPDM, navojna izvedba, komplet z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Control valve, intermediate, pressure independent for hydraulic balancing with electromotor continuous actuator, 24V, IP54, PN16, valve material nickel-plated brass, stainless steel / EPDM, threaded version, complete with threaded Dutch, fixing and sealing material;
| - hladilna voda za laboratorij 10/15°C | - laboratory cooling water 10/15°C
| - ogrevna voda za laboratorij 48/38°C | - laboratory heating water 48/38°C
| DN32, Vv = 0,36 ÷ 3,6 m3/h - ustreza proizvod DANFOSS tip ventila AB-QM 32, tip pogona AME 110/24V NL ali enakovredno | DN32, Vv = 0,36 ÷ 3,6 m3/h - corresponds to DANFOSS product valve type AB-QM 32, actuator type AME 110/24V NL or equivalent
| Oznaka: VY63.351, VY53.351 | Code: VY63.351, VY53.351 | kpl | 2 |  | 0
| Podsistem LASEM LAVEK | LASEM LAVEK subsystem
1.52 | Ploščni izmenjevalnik toplote, lotana izvedba (nerjavne plošče spojene z bakrenim lotom), PN10, material AISI316 (ali boljši), debeline plošč 0,6mm, tesnila EPDM do 100°C trajne obremenitve, skladnost s PED. Tehnični podatki: | Plate heat exchanger, loted design (stainless steel plates joined by copper lot), PN10, material AISI316 (or better), plate thickness 0,6mm, EPDM seals up to 100°C permanent load, PED compliant. Technical data:
| - hlajenje hladilne vode za laboratorij | - cooling water for the laboratory
| - izmenjana toplota 20 kW - hlajenje | - heat exchanged 20 kW - cooling
| - primar hladna stran P: hladilna voda, temp. vstopa 9°C, temp. izstopa 14°C, pretok 3,44m3/h, padec tlaka do 30kPa | - primary cold side P: cooling water, inlet temp. 9°C, outlet temp. 14°C, flow rate 3,44m3/h, pressure drop up to 30kPa
| - sekundar topla stran S: hladna voda, temp. vstopa 20°C, temp. izstopa 12°C, pretok 2,15m3/h, padec tlaka do 20kPa | - secondary hot side S: cold water, inlet temp. 20°C, outlet temp. 12°C, flow rate 2,15m3/h, pressure drop up to 20kPa
| - vsi priključki prirobnični PN10, primar P DN25, sekundar S DN25 | - all connections flanged PN10, primary P DN25, secondary S DN25
| - vključno s podstavkom prenosnika, pritrdilnim in tesnilnim materialom; | - including the laptop base, fixing and sealing materials;
| - dimenzije do: dolžina L x širina W x višina H = 300 x 200 x 400 mm | - dimensions up to: length L x width W x height H = 300 x 200 x 400 mm
| - komplet s toplotna parozaporna izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +105°C, debelina 50mm | - complete with thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0.040W/mK according to EN ISO8497, classification B-s3-d0 according to EN13501-1, for temperatures -50 to +105°C, thickness 50mm
| - ustrezen proizvod ALFA LAVAL tip CB30-50H + toplotna izolacija ali enakovredno | - suitable product ALFA LAVAL type CB30-50H + thermal insulation or equivalent
| Oznaka: HE62.100 | Code: HE62.100 | kpl | 1 |  | 0
1.53 | Obtočna črpalka, PN10, z mokrim rotorjem, skladnost z ErP, elektronsko regulirana s PM motorjem in integrairanim frekvenčnim pretvornikom, inegrirano tipalo diferenčnega tlaka in temperature, upravljalnik nastavitev s prikazovalnikom parametrov, z internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, PN10, wet-rotor, ErP-compliant, electronically controlled with PM motor and integrated frequency converter, integrated differential pressure and temperature sensor, setting control with parameter display, with internal hydraulic, electrical and communication connections, pump material grey cast iron with appropriate sealing for the medium, flanged design, including counter flanges, fixing and sealing material. Technical data:
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - pretok V= 2,15 m3/h, tlačna višina H= 85kPa, | - flow rate V= 2,15 m3/h, pressure head H= 85kPa,
| - elektro podatki Pel= 0,153kW, 230V /1/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 0,153kW, 230V /1/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip MAGNA3 25-100 ali enakovredno | - corresponds to GRUNDFOS product type MAGNA3 25-100 or equivalent
| Oznaka: P62.181 | Code: P62.181 | kpl | 1 |  | 0
1.54 | Temperaturno tipalo, potopno, za merilno območje od 0 do +80°C, potopna dolžina L=100mm, v tulki iz nerjavnega materiala z navojnim priključkom 1/2" (DN15), električni podatki: napajanje 24V, izhod 4-20mA, komplet s pritrdilnim in tesnilnim materialom; | Temperature sensor, immersion, for measuring range from 0 to +80°C, immersion length L=100mm, in stainless steel sleeve with 1/2" (DN15) threaded connection, electrical data: power supply 24V, output 4-20mA, complete with fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - ustreza proizvod ELEKTRONIKA PAHOR, tip CVB ali enakovredno | - corresponds to the product ELEKTRONIKA PAHOR, type CVB or equivalent
| Oznaka: TIC62.111 | Code: TIC62.111 | kpl | 1 |  | 0
1.55 | Tipalo tlaka s pretvornikom, za mertev tlaka v območju od 0 do 6 barg (relativno) ter nastavljivim alarmnim tlakom, navojni priključek 1/2" (DN15), material nerjavno jeklo, električni podatki: napajanje 24V, izhod 4-20mA, kompletno z ventilom za tipalo tlaka 1/2" (DN15) ter tesnilnim in pritrdilnim materialom; | Pressure sensor with transducer, for pressure measurement in the range from 0 to 6 barg (relative) and adjustable alarm pressure, threaded connection 1/2" (DN15), material stainless steel, electrical data: power supply 24V, output 4-20mA, complete with pressure sensor valve 1/2" (DN15) and sealing and fixing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - alarm, če je tlak p < 1,0 barg (nastavitev na tipalu ali programska nastavitev) | - alarm if pressure p < 1.0 barg (sensor setting or software setting)
| - ustreza proizvod ENDRESS+HAUSER tip PTC31B + PZAV ali enakovredno | - corresponds to ENDRESS+HAUSER product type PTC31B + PZAV or equivalent
| Oznaka: PIA62.121 | Code: PIA62.121 | kpl | 1 |  | 0
1.56 | Ekspanzijska posoda za kompenzacijo toplotnih raztezkov medija v sistemu, PN10, skladno z direktivo EU o tlačni opremi PED, pokončna izvedba v obliki diska, membrana po DIN 4807, tlaki do 6 bar, temperature na membrani od 5 do 70°C, vključno s pritrdilnim in tesnilnim materialom; | Expansion vessel for compensation of thermal expansion of the medium in the system, PN10, in compliance with the EU Pressure Equipment Directive PED, upright disc design, diaphragm according to DIN 4807, pressures up to 6 bar, diaphragm temperatures from 5 to 70°C, incl. fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - prostornina ekspanzijske posode 12 litrov | - expansion tank capacity 12 litres
| - dimenzije: premer D x debelina H = ø360 x 170 mm | - dimensions: diameter D x thickness H = ø360 x 170 mm
| - z navojnim priključkom 1/2" (DN15), komplet z ventilom s ključavnico 1/2" (DN15) | - with threaded connection 1/2" (DN15), complete with valve with lock 1/2" (DN15)
| - ustreza proizvod IMI PNEUMATEX tip SD 12.10 + DLV 15 ali enakovredno | - corresponds to IMI PNEUMATEX product type SD 12.10 + DLV 15 or equivalent
| Oznaka: EP62.101 | Code: EP62.101 | kpl | 1 |  | 0
1.57 | Varnostni ventil po TRD 721, PN16, varnostna funkcija izpusta medija zaradi toplotnih raztezkov v sistemu, vzmetno delovanje, možnost ročnega odzračenja, prostor vzmeti zaščiten z membrano, prirobnična izvedba, vključno s pritrdilnim in tesnilnim materialom; | Safety valve according to TRD 721, PN16, safety function of medium discharge due to thermal expansion in the system, spring operation, manual venting possible, spring space protected by diaphragm, flanged version, including fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - tlak odpiranja 3,0 barg, | - opening pressure 3,0 barg,
| - z navojnima priključkoma DN 15 / 20, komplet z ventilom s ključavnico 1/2" (DN15) | - with threaded connections DN 15 / 20, complete with 1/2" (DN 15) ratchet valve
| - ustreza proizvod IMI PNEUMATEX tip DSV 15 - 3.0 H + DLV 20 ali enakovredno | - iMI PNEUMATEX product type DSV 15 - 3.0 H + DLV 20 or equivalent
| Oznaka: VV62.102 | Code: VV62.102 | kpl | 1 |  | 0
1.58 | Regulacijski ventil, prehodni, tlačno neodvisni za hidravlično uravnoteženje z elektromotornim zveznim pogonom, 24V, IP54, PN16, material ventila nikljana medenina, nerjavno jeklo / EPDM, navojna izvedba, komplet z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Control valve, intermediate, pressure independent for hydraulic balancing with electromotor continuous actuator, 24V, IP54, PN16, valve material nickel-plated brass, stainless steel / EPDM, threaded version, complete with threaded Dutch, fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| DN32, Vv = 0,36 ÷ 3,6 m3/h - ustreza proizvod DANFOSS tip ventila AB-QM 32, tip pogona AME 110/24V NL ali enakovredno | DN32, Vv = 0,36 ÷ 3,6 m3/h - corresponds to DANFOSS product valve type AB-QM 32, actuator type AME 110/24V NL or equivalent
| Oznaka: VY62.151 | Code: VY62.151 | kpl | 1 |  | 0
| Podsistem LAHDE | LAHDE subsystem
1.59 | Ploščni izmenjevalnik toplote, lotana izvedba (nerjavne plošče spojene z bakrenim lotom), PN10, material AISI316 (ali boljši), debeline plošč 0,6mm, tesnila EPDM do 100°C trajne obremenitve, skladnost s PED. Tehnični podatki: | Plate heat exchanger, loted design (stainless steel plates joined by copper lot), PN10, material AISI316 (or better), plate thickness 0,6mm, EPDM seals up to 100°C permanent load, PED compliant. Technical data:
| - hlajenje hladilne vode za laboratorij | - cooling water for the laboratory
| - izmenjana toplota 24 kW - hlajenje | - heat exchanged 24 kW - cooling
| - primar hladna stran P: hladilna voda, temp. vstopa 9°C, temp. izstopa 14°C, pretok 4,13m3/h, padec tlaka do 30kPa | - primary cold side P: cooling water, inlet temp. 9°C, outlet temp. 14°C, flow rate 4,13m3/h, pressure drop up to 30kPa
| - sekundar topla stran S: hladna voda, temp. vstopa 20°C, temp. izstopa 12°C, pretok 2,58m3/h, padec tlaka do 20kPa | - secondary hot side S: cold water, inlet temp. 20°C, outlet temp. 12°C, flow rate 2,58m3/h, pressure drop up to 20kPa
| - vsi priključki prirobnični PN10, primar P DN25, sekundar S DN25 | - all connections flanged PN10, primary P DN25, secondary S DN25
| - vključno s podstavkom prenosnika, pritrdilnim in tesnilnim materialom; | - including the laptop base, fixing and sealing materials;
| - dimenzije do: dolžina L x širina W x višina H = 300 x 200 x 400 mm | - dimensions up to: length L x width W x height H = 300 x 200 x 400 mm
| - komplet s toplotna parozaporna izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +105°C, debelina 50mm | - complete with thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, classification B-s3-d0 according to EN13501-1, for temperatures -50 to +105°C, thickness 50mm
| - ustrezen proizvod ALFA LAVAL tip CB30-50H + toplotna izolacija ali enakovredno | - suitable product ALFA LAVAL type CB30-50H + thermal insulation or equivalent
| Oznaka: HE62.200 | Code: HE62.200 | kpl | 1 |  | 0
1.60 | Obtočna črpalka, PN10, z mokrim rotorjem, skladnost z ErP, elektronsko regulirana s PM motorjem in integrairanim frekvenčnim pretvornikom, inegrirano tipalo diferenčnega tlaka in temperature, upravljalnik nastavitev s prikazovalnikom parametrov, z internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, PN10, wet-rotor, ErP-compliant, electronically controlled with PM motor and integrated frequency converter, integrated differential pressure and temperature sensor, setting control with parameter display, with internal hydraulic, electrical and communication connections, pump material grey cast iron with appropriate sealing for the medium, flanged design, including counter flanges, fixing and sealing material. Technical data:
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - pretok V= 2,58 m3/h, tlačna višina H= 85kPa, | - flow rate V= 2,58 m3/h, pressure head H= 85kPa,
| - elektro podatki Pel= 0,153kW, 230V /1/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 0,153kW, 230V /1/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip MAGNA3 25-100 ali enakovredno | - corresponds to GRUNDFOS product type MAGNA3 25-100 or equivalent
| Oznaka: P62.281 | Code: P62.281 | kpl | 1 |  | 0
1.61 | Temperaturno tipalo, potopno, za merilno območje od 0 do +80°C, potopna dolžina L=100mm, v tulki iz nerjavnega materiala z navojnim priključkom 1/2" (DN15), električni podatki: napajanje 24V, izhod 4-20mA, komplet s pritrdilnim in tesnilnim materialom; | Temperature sensor, immersion, for measuring range from 0 to +80°C, immersion length L=100mm, in stainless steel sleeve with 1/2" (DN15) threaded connection, electrical data: power supply 24V, output 4-20mA, complete with fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - ustreza proizvod ELEKTRONIKA PAHOR, tip CVB ali enakovredno | - corresponds to the product ELEKTRONIKA PAHOR, type CVB or equivalent
| Oznaka: TIC62.211 | Code: TIC62.211 | kpl | 1 |  | 0
1.62 | Tipalo tlaka s pretvornikom, za mertev tlaka v območju od 0 do 6 barg (relativno) ter nastavljivim alarmnim tlakom, navojni priključek 1/2" (DN15), material nerjavno jeklo, električni podatki: napajanje 24V, izhod 4-20mA, kompletno z ventilom za tipalo tlaka 1/2" (DN15) ter tesnilnim in pritrdilnim materialom; | Pressure sensor with transducer, for pressure measurement in the range from 0 to 6 barg (relative) and adjustable alarm pressure, threaded connection 1/2" (DN15), material stainless steel, electrical data: power supply 24V, output 4-20mA, complete with pressure sensor valve 1/2" (DN15) and sealing and fixing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - alarm, če je tlak p < 1,0 barg (nastavitev na tipalu ali programska nastavitev) | - alarm if pressure p < 1.0 barg (sensor setting or software setting)
| - ustreza proizvod ENDRESS+HAUSER tip PTC31B + PZAV ali enakovredno | - corresponds to ENDRESS+HAUSER product type PTC31B + PZAV or equivalent
| Oznaka: PIA62.221 | Code: PIA62.221 | kpl | 1 |  | 0
1.63 | Ekspanzijska posoda za kompenzacijo toplotnih raztezkov medija v sistemu, PN10, skladno z direktivo EU o tlačni opremi PED, pokončna izvedba v obliki diska, membrana po DIN 4807, tlaki do 6 bar, temperature na membrani od 5 do 70°C, vključno s pritrdilnim in tesnilnim materialom; | Expansion vessel for compensation of thermal expansion of the medium in the system, PN10, in compliance with the EU Pressure Equipment Directive PED, upright disc design, diaphragm according to DIN 4807, pressures up to 6 bar, diaphragm temperatures from 5 to 70°C, incl. fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - prostornina ekspanzijske posode 12 litrov | - expansion tank capacity 12 litres
| - dimenzije: premer D x debelina H = ø360 x 170 mm | - dimensions: diameter D x thickness H = ø360 x 170 mm
| - z navojnim priključkom 1/2" (DN15), komplet z ventilom s ključavnico 1/2" (DN15) | - with threaded connection 1/2" (DN15), complete with valve with lock 1/2" (DN15)
| - ustreza proizvod IMI PNEUMATEX tip SD 12.10 + DLV 15 ali enakovredno | - corresponds to IMI PNEUMATEX product type SD 12.10 + DLV 15 or equivalent
| Oznaka: EP62.201 | Code: EP62.201 | kpl | 1 |  | 0
1.64 | Varnostni ventil po TRD 721, PN16, varnostna funkcija izpusta medija zaradi toplotnih raztezkov v sistemu, vzmetno delovanje, možnost ročnega odzračenja, prostor vzmeti zaščiten z membrano, prirobnična izvedba, vključno s pritrdilnim in tesnilnim materialom; | Safety valve according to TRD 721, PN16, safety function of medium discharge due to thermal expansion in the system, spring operation, manual venting possible, spring space protected by diaphragm, flanged version, including fastening and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - tlak odpiranja 3,0 barg, | - opening pressure 3,0 barg,
| - z navojnima priključkoma DN 15 / 20, komplet z ventilom s ključavnico 1/2" (DN15) | - with threaded connections DN 15 / 20, complete with 1/2" (DN 15) ratchet valve
| - ustreza proizvod IMI PNEUMATEX tip DSV 15 - 3.0 H + DLV 20 ali enakovredno | - iMI PNEUMATEX product type DSV 15 - 3.0 H + DLV 20 or equivalent
| Oznaka: VV62.202 | Code: VV62.202 | kpl | 1 |  | 0
1.65 | Regulacijski ventil, prehodni, tlačno neodvisni za hidravlično uravnoteženje z elektromotornim zveznim pogonom, 24V, IP54, PN16, material ventila nikljana medenina, nerjavno jeklo / EPDM, navojna izvedba, komplet z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Control valve, intermediate, pressure independent for hydraulic balancing with electromotor continuous actuator, 24V, IP54, PN16, valve material nickel-plated brass, stainless steel / EPDM, threaded version, complete with threaded Dutch, fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| DN32, Vv = 0,36 ÷ 3,6 m3/h - ustreza proizvod DANFOSS tip ventila AB-QM 32, tip pogona AME 110/24V NL ali enakovredno | DN32, Vv = 0,36 ÷ 3,6 m3/h - corresponds to DANFOSS product valve type AB-QM 32, actuator type AME 110/24V NL or equivalent
| Oznaka: VY62.251 | Code: VY62.251 | kpl | 1 |  | 0
| Podsistem LOSK (P1.J3) | LOSK subsystem (P1.J3)
1.66 | Ploščni izmenjevalnik toplote, lotana izvedba (nerjavne plošče spojene z bakrenim lotom), PN10, material AISI316 (ali boljši), debeline plošč 0,6mm, tesnila EPDM do 100°C trajne obremenitve, skladnost s PED. Tehnični podatki: | Plate heat exchanger, loted design (stainless steel plates joined by copper lot), PN10, material AISI316 (or better), plate thickness 0,6mm, EPDM seals up to 100°C permanent load, PED compliant. Technical data:
| - hlajenje hladilne vode za laboratorij | - chilled water cooling for the laboratory
| - izmenjana toplota 30 kW - hlajenje | - heat exchanged 30 kW - cooling
| - primar hladna stran P: hladilna voda, temp. vstopa 9°C, temp. izstopa 14°C, pretok 5,16m3/h, padec tlaka do 30kPa | - primary cold side P: cooling water, inlet temp. 9°C, outlet temp. 14°C, flow rate 5,16m3/h, pressure drop up to 30kPa
| - sekundar topla stran S: hladna voda, temp. vstopa 15°C, temp. izstopa 10°C, pretok 5,16m3/h, padec tlaka do 30kPa | - secondary hot side S: cold water, inlet temp. 15°C, outlet temp. 10°C, flow rate 5,16m3/h, pressure drop up to 30kPa
| - vsi priključki prirobnični PN10, primar P DN32, sekundar S DN32 | - all connections flanged PN10, primary P DN32, secondary S DN32
| - vključno s podstavkom prenosnika, pritrdilnim in tesnilnim materialom; | - including the laptop base, fixing and sealing materials;
| - dimenzije do: dolžina L x širina W x višina H = 400 x 200 x 600 mm | - dimensions up to: length L x width W x height H = 400 x 200 x 600 mm
| - komplet s toplotna parozaporna izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +105°C, debelina 50mm | - complete with thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0.040W/mK according to EN ISO8497, classification B-s3-d0 according to EN13501-1, for temperatures -50 to +105°C, thickness 50mm
| - ustrezen proizvod ALFA LAVAL tip CB60-100H + toplotna izolacija ali enakovredno | - suitable product ALFA LAVAL type CB60-100H + thermal insulation or equivalent
| Oznaka: HE62.300 | Code: HE62.300 | kpl | 1 |  | 0
1.67 | Ploščni izmenjevalnik toplote, lotana izvedba (nerjavne plošče spojene z bakrenim lotom), PN10, material AISI316 (ali boljši), debeline plošč 0,6mm, tesnila EPDM do 100°C trajne obremenitve, skladnost s PED. Tehnični podatki: | Plate heat exchanger, loted design (stainless steel plates joined by copper lot), PN10, material AISI316 (or better), plate thickness 0,6mm, EPDM seals up to 100°C permanent load, PED compliant. Technical data:
| - ogrevanje ogrevne vode za laboratorij | - heating water for the laboratory
| - izmenjana toplota 50 kW - ogrevanje | - heat exchanged 50 kW - heating
| - primar hladna stran P: hladilna voda, temp. vstopa 50°C, temp. izstopa 40°C, pretok 4,35m3/h, padec tlaka do 30kPa | - primary cold side P: cooling water, inlet temp 50°C, outlet temp 40°C, flow rate 4.35m3/h, pressure drop up to 30kPa
| - sekundar topla stran S: hladna voda, temp. vstopa 38°C, temp. izstopa 48°C, pretok 4,35m3/h, padec tlaka do 30kPa | - secondary hot side S: cold water, inlet temp. 38°C, outlet temp. 48°C, flow rate 4,35m3/h, pressure drop up to 30kPa
| - vsi priključki prirobnični PN10, primar P DN32, sekundar S DN32 | - all connections flanged PN10, primary P DN32, secondary S DN32
| - vključno s podstavkom prenosnika, pritrdilnim in tesnilnim materialom; | - including the laptop base, fixing and sealing materials;
| - dimenzije do: dolžina L x širina W x višina H = 400 x 200 x 600 mm | - dimensions up to: length L x width W x height H = 400 x 200 x 600 mm
| - komplet s toplotna parozaporna izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +105°C, debelina 50mm | - complete with thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0.040W/mK according to EN ISO8497, classification B-s3-d0 according to EN13501-1, for temperatures -50 to +105°C, thickness 50mm
| - ustrezen proizvod ALFA LAVAL tip CB60-100H + toplotna izolacija ali enakovredno | - suitable product ALFA LAVAL type CB60-100H + thermal insulation or equivalent
| Oznaka: HE52.300 | Code: HE52.300 | kpl | 1 |  | 0
1.68 | Obtočna črpalka, PN10, z mokrim rotorjem, skladnost z ErP, elektronsko regulirana s PM motorjem in integrairanim frekvenčnim pretvornikom, inegrirano tipalo diferenčnega tlaka in temperature, upravljalnik nastavitev s prikazovalnikom parametrov, z internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, PN10, wet-rotor, ErP-compliant, electronically controlled with PM motor and integrated frequency converter, integrated differential pressure and temperature sensor, setting control with parameter display, with internal hydraulic, electrical and communication connections, pump material grey cast iron with appropriate sealing for the medium, flanged design, including counter flanges, fixing and sealing material. Technical data:
| - za obtok hladilne vode laboratorija 10/15°C | - for laboratory cooling water circulation 10/15°C
| - pretok V= 5,16 m3/h, tlačna višina H= 95kPa, | - flow rate V= 5,16 m3/h, pressure head H= 95kPa,
| - elektro podatki Pel= 0,153kW, 230V /1/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 0,153kW, 230V /1/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip MAGNA3 32-120 F ali enakovredno | - corresponds to GRUNDFOS product type MAGNA3 32-120 F or equivalent
| Oznaka: P62.381 | Code: P62.381 | kpl | 1 |  | 0
1.69 | Obtočna črpalka, PN10, z mokrim rotorjem, skladnost z ErP, elektronsko regulirana s PM motorjem in integrairanim frekvenčnim pretvornikom, inegrirano tipalo diferenčnega tlaka in temperature, upravljalnik nastavitev s prikazovalnikom parametrov, z internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, PN10, wet-rotor, ErP-compliant, electronically controlled with PM motor and integrated frequency converter, integrated differential pressure and temperature sensor, setting control with parameter display, with internal hydraulic, electrical and communication connections, pump material grey cast iron with appropriate sealing for the medium, flanged design, including counter flanges, fixing and sealing material. Technical data:
| - za obtok ogrevne vode laboratorija 48/38°C | - for laboratory heating water circulation 48/38°C
| - pretok V= 4,35 m3/h, tlačna višina H= 95kPa, | - flow rate V= 4,35 m3/h, pressure head H= 95kPa,
| - elektro podatki Pel= 0,153kW, 230V /1/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 0,153kW, 230V /1/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip MAGNA3 32-120 F ali enakovredno | - corresponds to GRUNDFOS product type MAGNA3 32-120 F or equivalent
| Oznaka: P52.381 | Code: P52.381 | kpl | 1 |  | 0
1.70 | Temperaturno tipalo, potopno, za merilno območje od 0 do +80°C, potopna dolžina L=100mm, v tulki iz nerjavnega materiala z navojnim priključkom 1/2" (DN15), električni podatki: napajanje 24V, izhod 4-20mA, komplet s pritrdilnim in tesnilnim materialom; | Temperature sensor, immersion, for measuring range from 0 to +80°C, immersion length L=100mm, in stainless steel sleeve with 1/2" (DN15) threaded connection, electrical data: power supply 24V, output 4-20mA, complete with fixing and sealing material;
| - hladilna voda za laboratorij 10/15°C | - laboratory cooling water 10/15°C
| - ogrevna voda za laboratorij 48/38°C | - laboratory heating water 48/38°C
| - ustreza proizvod ELEKTRONIKA PAHOR, tip CVB ali enakovredno | - corresponds to the product ELEKTRONIKA PAHOR, type CVB or equivalent
| Oznaka: TIC62.311, TIC52.311 | Code: TIC62.311, TIC52.311 | kpl | 2 |  | 0
1.71 | Tipalo tlaka s pretvornikom, za mertev tlaka v območju od 0 do 6 barg (relativno) ter nastavljivim alarmnim tlakom, navojni priključek 1/2" (DN15), material nerjavno jeklo, električni podatki: napajanje 24V, izhod 4-20mA, kompletno z ventilom za tipalo tlaka 1/2" (DN15) ter tesnilnim in pritrdilnim materialom; | Pressure sensor with transducer, for pressure measurement in the range from 0 to 6 barg (relative) and adjustable alarm pressure, threaded connection 1/2" (DN15), material stainless steel, electrical data: power supply 24V, output 4-20mA, complete with pressure sensor valve 1/2" (DN15) and sealing and fixing material;
| - hladilna voda za laboratorij 10/15°C | - laboratory cooling water 10/15°C
| - ogrevna voda za laboratorij 48/38°C | - laboratory heating water 48/38°C
| - alarm, če je tlak p < 1,0 barg (nastavitev na tipalu ali programska nastavitev) | - alarm if pressure p < 1.0 barg (sensor setting or software setting)
| - ustreza proizvod ENDRESS+HAUSER tip PTC31B + PZAV ali enakovredno | - corresponds to ENDRESS+HAUSER product type PTC31B + PZAV or equivalent
| Oznaka: PIA62.321, PIA52.321 | Code: PIA62.321, PIA52.321 | kpl | 2 |  | 0
1.72 | Ekspanzijska posoda za kompenzacijo toplotnih raztezkov medija v sistemu, PN10, skladno z direktivo EU o tlačni opremi PED, pokončna izvedba v obliki diska, membrana po DIN 4807, tlaki do 6 bar, temperature na membrani od 5 do 70°C, vključno s pritrdilnim in tesnilnim materialom; | Expansion vessel for compensation of thermal expansion of the medium in the system, PN10, in compliance with the EU Pressure Equipment Directive PED, upright disc design, diaphragm according to DIN 4807, pressures up to 6 bar, diaphragm temperatures from 5 to 70°C, incl. fixing and sealing material;
| - hladilna voda za laboratorij 10/15°C | - laboratory cooling water 10/15°C
| - ogrevna voda za laboratorij 48/38°C | - laboratory heating water 48/38°C
| - prostornina ekspanzijske posode 12 litrov | - expansion tank capacity 12 litres
| - dimenzije: premer D x debelina H = ø360 x 170 mm | - dimensions: diameter D x thickness H = ø360 x 170 mm
| - z navojnim priključkom 1/2" (DN15), komplet z ventilom s ključavnico 1/2" (DN15) | - with threaded connection 1/2" (DN15), complete with valve with lock 1/2" (DN15)
| - ustreza proizvod IMI PNEUMATEX tip SD 12.10 + DLV 15 ali enakovredno | - corresponds to IMI PNEUMATEX product type SD 12.10 + DLV 15 or equivalent
| Oznaka: EP62.301, EP52.301 | Code: EP62.301, EP52.301 | kpl | 2 |  | 0
1.73 | Varnostni ventil po TRD 721, PN16, varnostna funkcija izpusta medija zaradi toplotnih raztezkov v sistemu, vzmetno delovanje, možnost ročnega odzračenja, prostor vzmeti zaščiten z membrano, prirobnična izvedba, vključno s pritrdilnim in tesnilnim materialom; | Safety valve according to TRD 721, PN16, safety function of medium discharge due to thermal expansion in the system, spring operation, manual venting possible, spring space protected by diaphragm, flanged version, including fastening and sealing material;
| - hladilna voda za laboratorij 10/15°C | - laboratory cooling water 10/15°C
| - ogrevna voda za laboratorij 48/38°C | - laboratory heating water 48/38°C
| - tlak odpiranja 3,0 barg, | - opening pressure 3,0 barg,
| - z navojnima priključkoma DN 15 / 20, komplet z ventilom s ključavnico 1/2" (DN15) | - with threaded connections DN 15 / 20, complete with 1/2" (DN 15) ratchet valve
| - ustreza proizvod IMI PNEUMATEX tip DSV 15 - 3.0 H + DLV 20 ali enakovredno | - iMI PNEUMATEX product type DSV 15 - 3.0 H + DLV 20 or equivalent
| Oznaka: VV62.302, VV52.302 | Code: VV62.302, VV52.302 | kpl | 1 |  | 0
1.74 | Regulacijski ventil, prehodni, tlačno neodvisni za hidravlično uravnoteženje z elektromotornim zveznim pogonom, 24V, IP54, PN16, material ventila nikljana medenina, nerjavno jeklo / EPDM, navojna izvedba, komplet z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Control valve, intermediate, pressure independent for hydraulic balancing with electromotor continuous actuator, 24V, IP54, PN16, valve material nickel-plated brass, stainless steel / EPDM, threaded version, complete with threaded Dutch, fixing and sealing material;
| - hladilna voda za laboratorij 10/15°C | - laboratory cooling water 10/15°C
| - ogrevna voda za laboratorij 48/38°C | - laboratory heating water 48/38°C
| DN32, Vv = 0,36 ÷ 3,6 m3/h - ustreza proizvod DANFOSS tip ventila AB-QM 32, tip pogona AME 110/24V NL ali enakovredno | DN32, Vv = 0,36 ÷ 3,6 m3/h - corresponds to DANFOSS product valve type AB-QM 32, actuator type AME 110/24V NL or equivalent
| Oznaka: VY62.351, VY52.351 | Code: VY62.351, VY52.351 | kpl | 2 |  | 0
| Podsistem LASTEH | LASTEH subsystem
1.75 | Ploščni izmenjevalnik toplote, lotana izvedba (nerjavne plošče spojene z bakrenim lotom), PN10, material AISI316 (ali boljši), debeline plošč 0,6mm, tesnila EPDM do 100°C trajne obremenitve, skladnost s PED. Tehnični podatki: | Plate heat exchanger, loted design (stainless steel plates joined by copper lot), PN10, material AISI316 (or better), plate thickness 0,6mm, EPDM seals up to 100°C permanent load, PED compliant. Technical data:
| - hlajenje hladilne vode za laboratorij | - chilled water cooling for the laboratory
| - izmenjana toplota 20 kW - hlajenje | - heat exchanged 20 kW - cooling
| - primar hladna stran P: hladilna voda, temp. vstopa 9°C, temp. izstopa 14°C, pretok 3,44m3/h, padec tlaka do 30kPa | - primary cold side P: cooling water, inlet temp. 9°C, outlet temp. 14°C, flow rate 3,44m3/h, pressure drop up to 30kPa
| - sekundar topla stran S: hladna voda, temp. vstopa 20°C, temp. izstopa 12°C, pretok 2,15m3/h, padec tlaka do 20kPa | - secondary hot side S: cold water, inlet temp. 20°C, outlet temp. 12°C, flow rate 2,15m3/h, pressure drop up to 20kPa
| - vsi priključki prirobnični PN10, primar P DN25, sekundar S DN25 | - all connections flanged PN10, primary P DN25, secondary S DN25
| - vključno s podstavkom prenosnika, pritrdilnim in tesnilnim materialom; | - including the laptop base, fixing and sealing materials;
| - dimenzije do: dolžina L x širina W x višina H = 300 x 200 x 400 mm | - dimensions up to: length L x width W x height H = 300 x 200 x 400 mm
| - komplet s toplotna parozaporna izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +105°C, debelina 50mm | - complete with thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, classification B-s3-d0 according to EN13501-1, for temperatures -50 to +105°C, thickness 50mm
| - ustrezen proizvod ALFA LAVAL tip CB30-50H + toplotna izolacija ali enakovredno | - suitable product ALFA LAVAL type CB30-50H + thermal insulation or equivalent
| Oznaka: HE62.400 | Code: HE62.400 | kpl | 1 |  | 0
1.76 | Obtočna črpalka, PN10, z mokrim rotorjem, skladnost z ErP, elektronsko regulirana s PM motorjem in integrairanim frekvenčnim pretvornikom, inegrirano tipalo diferenčnega tlaka in temperature, upravljalnik nastavitev s prikazovalnikom parametrov, z internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, PN10, wet-rotor, ErP-compliant, electronically controlled with PM motor and integrated frequency converter, integrated differential pressure and temperature sensor, setting control with parameter display, with internal hydraulic, electrical and communication connections, pump material grey cast iron with appropriate sealing for the medium, flanged design, including counter flanges, fixing and sealing material. Technical data:
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - pretok V= 2,15 m3/h, tlačna višina H= 85kPa, | - flow rate V= 2,15 m3/h, pressure head H= 85kPa,
| - elektro podatki Pel= 0,153kW, 230V /1/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 0,153kW, 230V /1/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip MAGNA3 25-100 ali enakovredno | - corresponds to GRUNDFOS product type MAGNA3 25-100 or equivalent
| Oznaka: P62.481 | Code: P62.481 | kpl | 1 |  | 0
1.77 | Temperaturno tipalo, potopno, za merilno območje od 0 do +80°C, potopna dolžina L=100mm, v tulki iz nerjavnega materiala z navojnim priključkom 1/2" (DN15), električni podatki: napajanje 24V, izhod 4-20mA, komplet s pritrdilnim in tesnilnim materialom; | Temperature sensor, immersion, for measuring range from 0 to +80°C, immersion length L=100mm, in stainless steel sleeve with 1/2" (DN15) threaded connection, electrical data: power supply 24V, output 4-20mA, complete with fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - ustreza proizvod ELEKTRONIKA PAHOR, tip CVB ali enakovredno | - corresponds to the product ELEKTRONIKA PAHOR, type CVB or equivalent
| Oznaka: TIC62.411 | Code: TIC62.411 | kpl | 1 |  | 0
1.78 | Tipalo tlaka s pretvornikom, za mertev tlaka v območju od 0 do 6 barg (relativno) ter nastavljivim alarmnim tlakom, navojni priključek 1/2" (DN15), material nerjavno jeklo, električni podatki: napajanje 24V, izhod 4-20mA, kompletno z ventilom za tipalo tlaka 1/2" (DN15) ter tesnilnim in pritrdilnim materialom; | Pressure sensor with transducer, for pressure measurement in the range from 0 to 6 barg (relative) and adjustable alarm pressure, threaded connection 1/2" (DN15), material stainless steel, electrical data: power supply 24V, output 4-20mA, complete with pressure sensor valve 1/2" (DN15) and sealing and fixing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - alarm, če je tlak p < 1,0 barg (nastavitev na tipalu ali programska nastavitev) | - alarm if pressure p < 1.0 barg (sensor setting or software setting)
| - ustreza proizvod ENDRESS+HAUSER tip PTC31B + PZAV ali enakovredno | - corresponds to ENDRESS+HAUSER product type PTC31B + PZAV or equivalent
| Oznaka: PIA62.421 | Code: PIA62.421 | kpl | 1 |  | 0
1.79 | Ekspanzijska posoda za kompenzacijo toplotnih raztezkov medija v sistemu, PN10, skladno z direktivo EU o tlačni opremi PED, pokončna izvedba v obliki diska, membrana po DIN 4807, tlaki do 6 bar, temperature na membrani od 5 do 70°C, vključno s pritrdilnim in tesnilnim materialom; | Expansion vessel for compensation of thermal expansion of the medium in the system, PN10, in compliance with the EU Pressure Equipment Directive PED, upright disc design, diaphragm according to DIN 4807, pressures up to 6 bar, diaphragm temperatures from 5 to 70°C, incl. fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - prostornina ekspanzijske posode 12 litrov | - expansion tank capacity 12 litres
| - dimenzije: premer D x debelina H = ø360 x 170 mm | - dimensions: diameter D x thickness H = ø360 x 170 mm
| - z navojnim priključkom 1/2" (DN15), komplet z ventilom s ključavnico 1/2" (DN15) | - with threaded connection 1/2" (DN15), complete with valve with lock 1/2" (DN15)
| - ustreza proizvod IMI PNEUMATEX tip SD 12.10 + DLV 15 ali enakovredno | - corresponds to IMI PNEUMATEX product type SD 12.10 + DLV 15 or equivalent
| Oznaka: EP62.401 | Code: EP62.401 | kpl | 1 |  | 0
1.80 | Varnostni ventil po TRD 721, PN16, varnostna funkcija izpusta medija zaradi toplotnih raztezkov v sistemu, vzmetno delovanje, možnost ročnega odzračenja, prostor vzmeti zaščiten z membrano, prirobnična izvedba, vključno s pritrdilnim in tesnilnim materialom; | Safety valve according to TRD 721, PN16, safety function of medium discharge due to thermal expansion in the system, spring operation, manual venting possible, spring space protected by diaphragm, flanged version, including fastening and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - tlak odpiranja 3,0 barg, | - opening pressure 3,0 barg,
| - z navojnima priključkoma DN 15 / 20, komplet z ventilom s ključavnico 1/2" (DN15) | - with threaded connections DN 15 / 20, complete with 1/2" (DN 15) ratchet valve
| - ustreza proizvod IMI PNEUMATEX tip DSV 15 - 3.0 H + DLV 20 ali enakovredno | - iMI PNEUMATEX product type DSV 15 - 3.0 H + DLV 20 or equivalent
| Oznaka: VV62.402 | Code: VV62.402 | kpl | 1 |  | 0
1.81 | Regulacijski ventil, prehodni, tlačno neodvisni za hidravlično uravnoteženje z elektromotornim zveznim pogonom, 24V, IP54, PN16, material ventila nikljana medenina, nerjavno jeklo / EPDM, navojna izvedba, komplet z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Control valve, intermediate, pressure independent for hydraulic balancing with electromotor continuous actuator, 24V, IP54, PN16, valve material nickel-plated brass, stainless steel / EPDM, threaded version, complete with threaded Dutch, fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| DN32, Vv = 0,36 ÷ 3,6 m3/h - ustreza proizvod DANFOSS tip ventila AB-QM 32, tip pogona AME 110/24V NL ali enakovredno | DN32, Vv = 0,36 ÷ 3,6 m3/h - corresponds to DANFOSS product valve type AB-QM 32, actuator type AME 110/24V NL or equivalent
| Oznaka: VY62.451 | Code: VY62.451 | kpl | 1 |  | 0
| Podsistem LASIM | LASIM subsystem
1.82 | Ploščni izmenjevalnik toplote, lotana izvedba (nerjavne plošče spojene z bakrenim lotom), PN10, material AISI316 (ali boljši), debeline plošč 0,6mm, tesnila EPDM do 100°C trajne obremenitve, skladnost s PED. Tehnični podatki: | Plate heat exchanger, loted design (stainless steel plates joined by copper lot), PN10, material AISI316 (or better), plate thickness 0,6mm, EPDM seals up to 100°C permanent load, PED compliant. Technical data:
| - hlajenje hladilne vode za laboratorij | - chilled water cooling for the laboratory
| - izmenjana toplota 17 kW - hlajenje | - heat exchanged 17 kW - cooling
| - primar hladna stran P: hladilna voda, temp. vstopa 9°C, temp. izstopa 14°C, pretok 2,92m3/h, padec tlaka do 30kPa | - primary cold side P: cooling water, inlet temp. 9°C, outlet temp. 14°C, flow rate 2,92m3/h, pressure drop up to 30kPa
| - sekundar topla stran S: hladna voda, temp. vstopa 20°C, temp. izstopa 12°C, pretok 1,83m3/h, padec tlaka do 20kPa | - secondary hot side S: cold water, inlet temp. 20°C, outlet temp. 12°C, flow rate 1,83m3/h, pressure drop up to 20kPa
| - vsi priključki prirobnični PN10, primar P DN25, sekundar S DN25 | - all connections flanged PN10, primary P DN25, secondary S DN25
| - vključno s podstavkom prenosnika, pritrdilnim in tesnilnim materialom; | - including the laptop base, fixing and sealing materials;
| - dimenzije do: dolžina L x širina W x višina H = 300 x 200 x 400 mm | - dimensions up to: length L x width W x height H = 300 x 200 x 400 mm
| - komplet s toplotna parozaporna izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +105°C, debelina 50mm | - complete with thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, classification B-s3-d0 according to EN13501-1, for temperatures -50 to +105°C, thickness 50mm
| - ustrezen proizvod ALFA LAVAL tip CB30-50H + toplotna izolacija ali enakovredno | - suitable product ALFA LAVAL type CB30-50H + thermal insulation or equivalent
| Oznaka: HE62.500 | Code: HE62.500 | kpl | 1 |  | 0
1.83 | Obtočna črpalka, PN10, z mokrim rotorjem, skladnost z ErP, elektronsko regulirana s PM motorjem in integrairanim frekvenčnim pretvornikom, inegrirano tipalo diferenčnega tlaka in temperature, upravljalnik nastavitev s prikazovalnikom parametrov, z internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, PN10, wet-rotor, ErP-compliant, electronically controlled with PM motor and integrated frequency converter, integrated differential pressure and temperature sensor, setting control with parameter display, with internal hydraulic, electrical and communication connections, pump material grey cast iron with appropriate sealing for the medium, flanged design, including counter flanges, fixing and sealing material. Technical data:
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - pretok V= 1,83 m3/h, tlačna višina H= 85kPa, | - flow rate V= 1,83 m3/h, pressure head H= 85kPa,
| - elektro podatki Pel= 0,153kW, 230V /1/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 0,153kW, 230V /1/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip MAGNA3 25-100 ali enakovredno | - corresponds to GRUNDFOS product type MAGNA3 25-100 or equivalent
| Oznaka: P62.581 | Code: P62.581 | kpl | 1 |  | 0
1.84 | Temperaturno tipalo, potopno, za merilno območje od 0 do +80°C, potopna dolžina L=100mm, v tulki iz nerjavnega materiala z navojnim priključkom 1/2" (DN15), električni podatki: napajanje 24V, izhod 4-20mA, komplet s pritrdilnim in tesnilnim materialom; | Temperature sensor, immersion, for measuring range from 0 to +80°C, immersion length L=100mm, in stainless steel sleeve with 1/2" (DN15) threaded connection, electrical data: power supply 24V, output 4-20mA, complete with fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - ustreza proizvod ELEKTRONIKA PAHOR, tip CVB ali enakovredno | - corresponds to the product ELEKTRONIKA PAHOR, type CVB or equivalent
| Oznaka: TIC62.511 | Code: TIC62.511 | kpl | 1 |  | 0
1.85 | Tipalo tlaka s pretvornikom, za mertev tlaka v območju od 0 do 6 barg (relativno) ter nastavljivim alarmnim tlakom, navojni priključek 1/2" (DN15), material nerjavno jeklo, električni podatki: napajanje 24V, izhod 4-20mA, kompletno z ventilom za tipalo tlaka 1/2" (DN15) ter tesnilnim in pritrdilnim materialom; | Pressure sensor with transducer, for pressure measurement in the range from 0 to 6 barg (relative) and adjustable alarm pressure, threaded connection 1/2" (DN15), material stainless steel, electrical data: power supply 24V, output 4-20mA, complete with pressure sensor valve 1/2" (DN15) and sealing and fixing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - alarm, če je tlak p < 1,0 barg (nastavitev na tipalu ali programska nastavitev) | - alarm if pressure p < 1.0 barg (sensor setting or software setting)
| - ustreza proizvod ENDRESS+HAUSER tip PTC31B + PZAV ali enakovredno | - corresponds to ENDRESS+HAUSER product type PTC31B + PZAV or equivalent
| Oznaka: PIA62.521 | Code: PIA62.521 | kpl | 1 |  | 0
1.86 | Ekspanzijska posoda za kompenzacijo toplotnih raztezkov medija v sistemu, PN10, skladno z direktivo EU o tlačni opremi PED, pokončna izvedba v obliki diska, membrana po DIN 4807, tlaki do 6 bar, temperature na membrani od 5 do 70°C, vključno s pritrdilnim in tesnilnim materialom; | Expansion vessel for compensation of thermal expansion of the medium in the system, PN10, in compliance with the EU Pressure Equipment Directive PED, upright disc design, diaphragm according to DIN 4807, pressures up to 6 bar, diaphragm temperatures from 5 to 70°C, incl. fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - prostornina ekspanzijske posode 12 litrov | - expansion tank capacity 12 litres
| - dimenzije: premer D x debelina H = ø360 x 170 mm | - dimensions: diameter D x thickness H = ø360 x 170 mm
| - z navojnim priključkom 1/2" (DN15), komplet z ventilom s ključavnico 1/2" (DN15) | - with threaded connection 1/2" (DN15), complete with valve with lock 1/2" (DN15)
| - ustreza proizvod IMI PNEUMATEX tip SD 12.10 + DLV 15 ali enakovredno | - corresponds to IMI PNEUMATEX product type SD 12.10 + DLV 15 or equivalent
| Oznaka: EP62.501 | Code: EP62.501 | kpl | 1 |  | 0
1.87 | Varnostni ventil po TRD 721, PN16, varnostna funkcija izpusta medija zaradi toplotnih raztezkov v sistemu, vzmetno delovanje, možnost ročnega odzračenja, prostor vzmeti zaščiten z membrano, prirobnična izvedba, vključno s pritrdilnim in tesnilnim materialom; | Safety valve according to TRD 721, PN16, safety function of medium discharge due to thermal expansion in the system, spring operation, manual venting possible, spring space protected by diaphragm, flanged version, including fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - tlak odpiranja 3,0 barg, | - opening pressure 3,0 barg,
| - z navojnima priključkoma DN 15 / 20, komplet z ventilom s ključavnico 1/2" (DN15) | - with threaded connections DN 15 / 20, complete with 1/2" (DN 15) ratchet valve
| - ustreza proizvod IMI PNEUMATEX tip DSV 15 - 3.0 H + DLV 20 ali enakovredno | - iMI PNEUMATEX product type DSV 15 - 3.0 H + DLV 20 or equivalent
| Oznaka: VV62.502 | Code: VV62.502 | kpl | 1 |  | 0
1.88 | Regulacijski ventil, prehodni, tlačno neodvisni za hidravlično uravnoteženje z elektromotornim zveznim pogonom, 24V, IP54, PN16, material ventila nikljana medenina, nerjavno jeklo / EPDM, navojna izvedba, komplet z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Control valve, intermediate, pressure independent for hydraulic balancing with electromotor continuous actuator, 24V, IP54, PN16, valve material nickel-plated brass, stainless steel / EPDM, threaded version, complete with threaded Dutch, fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| DN32, Vv = 0,36 ÷ 3,6 m3/h - ustreza proizvod DANFOSS tip ventila AB-QM 32, tip pogona AME 110/24V NL ali enakovredno | DN32, Vv = 0,36 ÷ 3,6 m3/h - corresponds to DANFOSS product valve type AB-QM 32, actuator type AME 110/24V NL or equivalent
| Oznaka: VY62.551 | Code: VY62.551 | kpl | 1 |  | 0
| Podsistem LASIN | LASIN subsystem
1.89 | Ploščni izmenjevalnik toplote, lotana izvedba (nerjavne plošče spojene z bakrenim lotom), PN10, material AISI316 (ali boljši), debeline plošč 0,6mm, tesnila EPDM do 100°C trajne obremenitve, skladnost s PED. Tehnični podatki: | Plate heat exchanger, loted design (stainless steel plates joined by copper lot), PN10, material AISI316 (or better), plate thickness 0,6mm, EPDM seals up to 100°C permanent load, PED compliant. Technical data:
| - hlajenje hladilne vode za laboratorij | - chilled water cooling for the laboratory
| - izmenjana toplota 15 kW - hlajenje | - heat exchanged 15 kW - cooling
| - primar hladna stran P: hladilna voda, temp. vstopa 9°C, temp. izstopa 14°C, pretok 2,58m3/h, padec tlaka do 30kPa | - primary cold side P: cooling water, inlet temp. 9°C, outlet temp. 14°C, flow rate 2.58m3/h, pressure drop up to 30kPa
| - sekundar topla stran S: hladna voda, temp. vstopa 20°C, temp. izstopa 12°C, pretok 1,62m3/h, padec tlaka do 20kPa | - secondary hot side S: cold water, inlet temp. 20°C, outlet temp. 12°C, flow rate 1.62m3/h, pressure drop up to 20kPa
| - vsi priključki prirobnični PN10, primar P DN25, sekundar S DN25 | - all connections flanged PN10, primary P DN25, secondary S DN25
| - vključno s podstavkom prenosnika, pritrdilnim in tesnilnim materialom; | - including the laptop base, fixing and sealing materials;
| - dimenzije do: dolžina L x širina W x višina H = 300 x 200 x 400 mm | - dimensions up to: length L x width W x height H = 300 x 200 x 400 mm
| - komplet s toplotna parozaporna izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +105°C, debelina 50mm | - complete with thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, classification B-s3-d0 according to EN13501-1, for temperatures -50 to +105°C, thickness 50mm
| - ustrezen proizvod ALFA LAVAL tip CB30-50H + toplotna izolacija ali enakovredno | - suitable product ALFA LAVAL type CB30-50H + thermal insulation or equivalent
| Oznaka: HE61.100 | Code: HE61.100 | kpl | 1 |  | 0
1.90 | Obtočna črpalka, PN10, z mokrim rotorjem, skladnost z ErP, elektronsko regulirana s PM motorjem in integrairanim frekvenčnim pretvornikom, inegrirano tipalo diferenčnega tlaka in temperature, upravljalnik nastavitev s prikazovalnikom parametrov, z internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, PN10, wet-rotor, ErP-compliant, electronically controlled with PM motor and integrated frequency converter, integrated differential pressure and temperature sensor, setting control with parameter display, with internal hydraulic, electrical and communication connections, pump material grey cast iron with appropriate sealing for the medium, flanged design, including counter flanges, fixing and sealing material. Technical data:
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - pretok V= 1,62 m3/h, tlačna višina H= 85kPa, | - flow rate V= 1,62 m3/h, pressure head H= 85kPa,
| - elektro podatki Pel= 0,153kW, 230V /1/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 0,153kW, 230V /1/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip MAGNA3 25-100 ali enakovredno | - corresponds to GRUNDFOS product type MAGNA3 25-100 or equivalent
| Oznaka: P61.181 | Code: P61.181 | kpl | 1 |  | 0
1.91 | Temperaturno tipalo, potopno, za merilno območje od 0 do +80°C, potopna dolžina L=100mm, v tulki iz nerjavnega materiala z navojnim priključkom 1/2" (DN15), električni podatki: napajanje 24V, izhod 4-20mA, komplet s pritrdilnim in tesnilnim materialom; | Temperature sensor, immersion, for measuring range from 0 to +80°C, immersion length L=100mm, in stainless steel sleeve with 1/2" (DN15) threaded connection, electrical data: power supply 24V, output 4-20mA, complete with fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - ustreza proizvod ELEKTRONIKA PAHOR, tip CVB ali enakovredno | - corresponds to the product ELEKTRONIKA PAHOR, type CVB or equivalent
| Oznaka: TIC61.111 | Code: TIC61.111 | kpl | 1 |  | 0
1.92 | Tipalo tlaka s pretvornikom, za mertev tlaka v območju od 0 do 6 barg (relativno) ter nastavljivim alarmnim tlakom, navojni priključek 1/2" (DN15), material nerjavno jeklo, električni podatki: napajanje 24V, izhod 4-20mA, kompletno z ventilom za tipalo tlaka 1/2" (DN15) ter tesnilnim in pritrdilnim materialom; | Pressure sensor with transducer, for pressure measurement in the range from 0 to 6 barg (relative) and adjustable alarm pressure, threaded connection 1/2" (DN15), material stainless steel, electrical data: power supply 24V, output 4-20mA, complete with pressure sensor valve 1/2" (DN15) and sealing and fixing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - alarm, če je tlak p < 1,0 barg (nastavitev na tipalu ali programska nastavitev) | - alarm if pressure p < 1.0 barg (sensor setting or software setting)
| - ustreza proizvod ENDRESS+HAUSER tip PTC31B + PZAV ali enakovredno | - corresponds to ENDRESS+HAUSER product type PTC31B + PZAV or equivalent
| Oznaka: PIA61.121 | Code: PIA61.121 | kpl | 1 |  | 0
1.93 | Ekspanzijska posoda za kompenzacijo toplotnih raztezkov medija v sistemu, PN10, skladno z direktivo EU o tlačni opremi PED, pokončna izvedba v obliki diska, membrana po DIN 4807, tlaki do 6 bar, temperature na membrani od 5 do 70°C, vključno s pritrdilnim in tesnilnim materialom; | Expansion vessel for compensation of thermal expansion of the medium in the system, PN10, in compliance with the EU Pressure Equipment Directive PED, upright disc design, diaphragm according to DIN 4807, pressures up to 6 bar, diaphragm temperatures from 5 to 70°C, incl. fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - prostornina ekspanzijske posode 12 litrov | - expansion tank capacity 12 litres
| - dimenzije: premer D x debelina H = ø360 x 170 mm | - dimensions: diameter D x thickness H = ø360 x 170 mm
| - z navojnim priključkom 1/2" (DN15), komplet z ventilom s ključavnico 1/2" (DN15) | - with threaded connection 1/2" (DN15), complete with valve with lock 1/2" (DN15)
| - ustreza proizvod IMI PNEUMATEX tip SD 12.10 + DLV 15 ali enakovredno | - corresponds to IMI PNEUMATEX product type SD 12.10 + DLV 15 or equivalent
| Oznaka: EP61.101 | Code: EP61.101 | kpl | 1 |  | 0
1.94 | Varnostni ventil po TRD 721, PN16, varnostna funkcija izpusta medija zaradi toplotnih raztezkov v sistemu, vzmetno delovanje, možnost ročnega odzračenja, prostor vzmeti zaščiten z membrano, prirobnična izvedba, vključno s pritrdilnim in tesnilnim materialom; | Safety valve according to TRD 721, PN16, safety function of medium discharge due to thermal expansion in the system, spring operation, manual venting possible, spring space protected by diaphragm, flanged version, including fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - tlak odpiranja 3,0 barg, | - opening pressure 3,0 barg,
| - z navojnima priključkoma DN 15 / 20, komplet z ventilom s ključavnico 1/2" (DN15) | - with threaded connections DN 15 / 20, complete with 1/2" (DN 15) ratchet valve
| - ustreza proizvod IMI PNEUMATEX tip DSV 15 - 3.0 H + DLV 20 ali enakovredno | - iMI PNEUMATEX product type DSV 15 - 3.0 H + DLV 20 or equivalent
| Oznaka: VV61.102 | Code: VV61.102 | kpl | 1 |  | 0
1.95 | Regulacijski ventil, prehodni, tlačno neodvisni za hidravlično uravnoteženje z elektromotornim zveznim pogonom, 24V, IP54, PN16, material ventila nikljana medenina, nerjavno jeklo / EPDM, navojna izvedba, komplet z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Control valve, intermediate, pressure independent for hydraulic balancing with electromotor continuous actuator, 24V, IP54, PN16, valve material nickel-plated brass, stainless steel / EPDM, threaded version, complete with threaded Dutch, fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| DN32, Vv = 0,36 ÷ 3,6 m3/h - ustreza proizvod DANFOSS tip ventila AB-QM 32, tip pogona AME 110/24V NL ali enakovredno | DN32, Vv = 0,36 ÷ 3,6 m3/h - corresponds to DANFOSS product valve type AB-QM 32, actuator type AME 110/24V NL or equivalent
| Oznaka: VY61.151 | Code: VY61.151 | kpl | 1 |  | 0
| Podsistem LECAD | LECAD subsystem
1.96 | Ploščni izmenjevalnik toplote, lotana izvedba (nerjavne plošče spojene z bakrenim lotom), PN10, material AISI316 (ali boljši), debeline plošč 0,6mm, tesnila EPDM do 100°C trajne obremenitve, skladnost s PED. Tehnični podatki: | Plate heat exchanger, loted design (stainless steel plates joined by copper lot), PN10, material AISI316 (or better), plate thickness 0,6mm, EPDM seals up to 100°C permanent load, PED compliant. Technical data:
| - hlajenje hladilne vode za laboratorij | - chilled water cooling for the laboratory
| - izmenjana toplota 12 kW - hlajenje | - heat exchanged 12 kW - cooling
| - primar hladna stran P: hladilna voda, temp. vstopa 9°C, temp. izstopa 14°C, pretok 2,07m3/h, padec tlaka do 30kPa | - primary cold side P: cooling water, inlet temp. 9°C, outlet temp. 14°C, flow rate 2.07m3/h, pressure drop up to 30kPa
| - sekundar topla stran S: hladna voda, temp. vstopa 20°C, temp. izstopa 12°C, pretok 1,30m3/h, padec tlaka do 20kPa | - secondary hot side S: cold water, inlet temp. 20°C, outlet temp. 12°C, flow rate 1,30m3/h, pressure drop up to 20kPa
| - vsi priključki prirobnični PN10, primar P DN25, sekundar S DN25 | - all connections flanged PN10, primary P DN25, secondary S DN25
| - vključno s podstavkom prenosnika, pritrdilnim in tesnilnim materialom; | - including the laptop base, fixing and sealing materials;
| - dimenzije do: dolžina L x širina W x višina H = 300 x 200 x 400 mm | - dimensions up to: length L x width W x height H = 300 x 200 x 400 mm
| - komplet s toplotna parozaporna izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +105°C, debelina 50mm | - complete with thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, classification B-s3-d0 according to EN13501-1, for temperatures -50 to +105°C, thickness 50mm
| - ustrezen proizvod ALFA LAVAL tip CB30-50H + toplotna izolacija ali enakovredno | - suitable product ALFA LAVAL type CB30-50H + thermal insulation or equivalent
| Oznaka: HE65.100 | Code: HE65.100 | kpl | 1 |  | 0
1.97 | Obtočna črpalka, PN10, z mokrim rotorjem, skladnost z ErP, elektronsko regulirana s PM motorjem in integrairanim frekvenčnim pretvornikom, inegrirano tipalo diferenčnega tlaka in temperature, upravljalnik nastavitev s prikazovalnikom parametrov, z internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, PN10, wet-rotor, ErP-compliant, electronically controlled with PM motor and integrated frequency converter, integrated differential pressure and temperature sensor, setting control with parameter display, with internal hydraulic, electrical and communication connections, pump material grey cast iron with appropriate sealing for the medium, flanged design, including counter flanges, fixing and sealing material. Technical data:
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - pretok V= 1,30 m3/h, tlačna višina H= 80kPa, | - flow rate V= 1,30 m3/h, pressure head H= 80kPa,
| - elektro podatki Pel= 0,153kW, 230V /1/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 0,153kW, 230V /1/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip MAGNA3 25-100 ali enakovredno | - corresponds to GRUNDFOS product type MAGNA3 25-100 or equivalent
| Oznaka: P65.181 | Code: P65.181 | kpl | 1 |  | 0
1.98 | Temperaturno tipalo, potopno, za merilno območje od 0 do +80°C, potopna dolžina L=100mm, v tulki iz nerjavnega materiala z navojnim priključkom 1/2" (DN15), električni podatki: napajanje 24V, izhod 4-20mA, komplet s pritrdilnim in tesnilnim materialom; | Temperature sensor, immersion, for measuring range from 0 to +80°C, immersion length L=100mm, in stainless steel sleeve with 1/2" (DN15) threaded connection, electrical data: power supply 24V, output 4-20mA, complete with fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - ustreza proizvod ELEKTRONIKA PAHOR, tip CVB ali enakovredno | - corresponds to the product ELEKTRONIKA PAHOR, type CVB or equivalent
| Oznaka: TIC65.111 | Code: TIC65.111 | kpl | 1 |  | 0
1.99 | Tipalo tlaka s pretvornikom, za mertev tlaka v območju od 0 do 6 barg (relativno) ter nastavljivim alarmnim tlakom, navojni priključek 1/2" (DN15), material nerjavno jeklo, električni podatki: napajanje 24V, izhod 4-20mA, kompletno z ventilom za tipalo tlaka 1/2" (DN15) ter tesnilnim in pritrdilnim materialom; | Pressure sensor with transducer, for pressure measurement in the range from 0 to 6 barg (relative) and adjustable alarm pressure, threaded connection 1/2" (DN15), material stainless steel, electrical data: power supply 24V, output 4-20mA, complete with pressure sensor valve 1/2" (DN15) and sealing and fixing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - alarm, če je tlak p < 1,0 barg (nastavitev na tipalu ali programska nastavitev) | - alarm if pressure p < 1.0 barg (sensor setting or software setting)
| - ustreza proizvod ENDRESS+HAUSER tip PTC31B + PZAV ali enakovredno | - corresponds to ENDRESS+HAUSER product type PTC31B + PZAV or equivalent
| Oznaka: PIA65.121 | Code: PIA65.121 | kpl | 1 |  | 0
1.100 | Ekspanzijska posoda za kompenzacijo toplotnih raztezkov medija v sistemu, PN10, skladno z direktivo EU o tlačni opremi PED, pokončna izvedba v obliki diska, membrana po DIN 4807, tlaki do 6 bar, temperature na membrani od 5 do 70°C, vključno s pritrdilnim in tesnilnim materialom; | Expansion vessel for compensation of thermal expansion of the medium in the system, PN10, in compliance with the EU Pressure Equipment Directive PED, upright disc design, diaphragm according to DIN 4807, pressures up to 6 bar, diaphragm temperatures from 5 to 70°C, incl. fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - prostornina ekspanzijske posode 12 litrov | - expansion tank capacity 12 litres
| - dimenzije: premer D x debelina H = ø360 x 170 mm | - dimensions: diameter D x thickness H = ø360 x 170 mm
| - z navojnim priključkom 1/2" (DN15), komplet z ventilom s ključavnico 1/2" (DN15) | - with threaded connection 1/2" (DN15), complete with valve with lock 1/2" (DN15)
| - ustreza proizvod IMI PNEUMATEX tip SD 12.10 + DLV 15 ali enakovredno | - corresponds to IMI PNEUMATEX product type SD 12.10 + DLV 15 or equivalent
| Oznaka: EP65.101 | Code: EP65.101 | kpl | 1 |  | 0
1.101 | Varnostni ventil po TRD 721, PN16, varnostna funkcija izpusta medija zaradi toplotnih raztezkov v sistemu, vzmetno delovanje, možnost ročnega odzračenja, prostor vzmeti zaščiten z membrano, prirobnična izvedba, vključno s pritrdilnim in tesnilnim materialom; | Safety valve according to TRD 721, PN16, safety function of medium discharge due to thermal expansion in the system, spring operation, manual venting possible, spring space protected by diaphragm, flanged version, including fastening and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - tlak odpiranja 3,0 barg, | - opening pressure 3,0 barg,
| - z navojnima priključkoma DN 15 / 20, komplet z ventilom s ključavnico 1/2" (DN15) | - with threaded connections DN 15 / 20, complete with 1/2" (DN 15) ratchet valve
| - ustreza proizvod IMI PNEUMATEX tip DSV 15 - 3.0 H + DLV 20 ali enakovredno | - iMI PNEUMATEX product type DSV 15 - 3.0 H + DLV 20 or equivalent
| Oznaka: VV65.102 | Code: VV65.102 | kpl | 1 |  | 0
1.102 | Regulacijski ventil, prehodni, tlačno neodvisni za hidravlično uravnoteženje z elektromotornim zveznim pogonom, 24V, IP54, PN16, material ventila nikljana medenina, nerjavno jeklo / EPDM, navojna izvedba, komplet z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Control valve, intermediate, pressure independent for hydraulic balancing with electromotor continuous actuator, 24V, IP54, PN16, valve material nickel-plated brass, stainless steel / EPDM, threaded version, complete with threaded Dutch, fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| DN25, Vv = 0,22 ÷ 2,2 m3/h - ustreza proizvod DANFOSS tip ventila AB-QM 25, tip pogona AME 110/24V NL ali enakovredno | DN25, Vv = 0,22 ÷ 2,2 m3/h - corresponds to DANFOSS product valve type AB-QM 25, actuator type AME 110/24V NL or equivalent
| Oznaka: VY65.151 | Code: VY65.151 | kpl | 1 |  | 0
| Podsistem FOLAS | FOLAS subsystem
1.103 | Ploščni izmenjevalnik toplote, lotana izvedba (nerjavne plošče spojene z bakrenim lotom), PN10, material AISI316 (ali boljši), debeline plošč 0,6mm, tesnila EPDM do 100°C trajne obremenitve, skladnost s PED. Tehnični podatki: | Plate heat exchanger, loted design (stainless steel plates joined by copper lot), PN10, material AISI316 (or better), plate thickness 0,6mm, EPDM seals up to 100°C permanent load, PED compliant. Technical data:
| - hlajenje hladilne vode za laboratorij | - cooling water for the laboratory
| - izmenjana toplota 20 kW - hlajenje | - heat exchanged 20 kW - cooling
| - primar hladna stran P: hladilna voda, temp. vstopa 9°C, temp. izstopa 14°C, pretok 3,44m3/h, padec tlaka do 30kPa | - primary cold side P: cooling water, inlet temp. 9°C, outlet temp. 14°C, flow rate 3,44m3/h, pressure drop up to 30kPa
| - sekundar topla stran S: hladna voda, temp. vstopa 20°C, temp. izstopa 12°C, pretok 2,15m3/h, padec tlaka do 20kPa | - secondary hot side S: cold water, inlet temp. 20°C, outlet temp. 12°C, flow rate 2,15m3/h, pressure drop up to 20kPa
| - vsi priključki prirobnični PN10, primar P DN25, sekundar S DN25 | - all connections flanged PN10, primary P DN25, secondary S DN25
| - vključno s podstavkom prenosnika, pritrdilnim in tesnilnim materialom; | - including the laptop base, fixing and sealing materials;
| - dimenzije do: dolžina L x širina W x višina H = 300 x 200 x 400 mm | - dimensions up to: length L x width W x height H = 300 x 200 x 400 mm
| - komplet s toplotna parozaporna izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +105°C, debelina 50mm | - complete with thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, classification B-s3-d0 according to EN13501-1, for temperatures -50 to +105°C, thickness 50mm
| - ustrezen proizvod ALFA LAVAL tip CB30-50H + toplotna izolacija ali enakovredno | - suitable product ALFA LAVAL type CB30-50H + thermal insulation or equivalent
| Oznaka: HE65.200 | Code: HE65.200 | kpl | 1 |  | 0
1.104 | Obtočna črpalka, PN10, z mokrim rotorjem, skladnost z ErP, elektronsko regulirana s PM motorjem in integrairanim frekvenčnim pretvornikom, inegrirano tipalo diferenčnega tlaka in temperature, upravljalnik nastavitev s prikazovalnikom parametrov, z internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, PN10, wet-rotor, ErP-compliant, electronically controlled with PM motor and integrated frequency converter, integrated differential pressure and temperature sensor, setting controller with parameter display, with internal hydraulic, electrical and communication connections, pump material grey cast iron with appropriate sealing for the medium, flanged design, including counter flanges, fixing and sealing material. Technical data:
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - pretok V= 2,15 m3/h, tlačna višina H= 85kPa, | - flow rate V= 2,15 m3/h, pressure head H= 85kPa,
| - elektro podatki Pel= 0,153kW, 230V /1/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 0,153kW, 230V /1/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip MAGNA3 25-100 ali enakovredno | - corresponds to GRUNDFOS product type MAGNA3 25-100 or equivalent
| Oznaka: P65.281 | Code: P65.281 | kpl | 1 |  | 0
1.105 | Temperaturno tipalo, potopno, za merilno območje od 0 do +80°C, potopna dolžina L=100mm, v tulki iz nerjavnega materiala z navojnim priključkom 1/2" (DN15), električni podatki: napajanje 24V, izhod 4-20mA, komplet s pritrdilnim in tesnilnim materialom; | Temperature sensor, immersion, for measuring range from 0 to +80°C, immersion length L=100mm, in stainless steel sleeve with 1/2" (DN15) threaded connection, electrical data: power supply 24V, output 4-20mA, complete with fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - ustreza proizvod ELEKTRONIKA PAHOR, tip CVB ali enakovredno | - corresponds to the product ELEKTRONIKA PAHOR, type CVB or equivalent
| Oznaka: TIC65.211 | Code: TIC65.211 | kpl | 1 |  | 0
1.106 | Tipalo tlaka s pretvornikom, za mertev tlaka v območju od 0 do 6 barg (relativno) ter nastavljivim alarmnim tlakom, navojni priključek 1/2" (DN15), material nerjavno jeklo, električni podatki: napajanje 24V, izhod 4-20mA, kompletno z ventilom za tipalo tlaka 1/2" (DN15) ter tesnilnim in pritrdilnim materialom; | Pressure sensor with transducer, for pressure measurement in the range from 0 to 6 barg (relative) and adjustable alarm pressure, threaded connection 1/2" (DN15), material stainless steel, electrical data: power supply 24V, output 4-20mA, complete with pressure sensor valve 1/2" (DN15) and sealing and fixing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - alarm, če je tlak p < 1,0 barg (nastavitev na tipalu ali programska nastavitev) | - alarm if pressure p < 1.0 barg (sensor setting or software setting)
| - ustreza proizvod ENDRESS+HAUSER tip PTC31B + PZAV ali enakovredno | - corresponds to ENDRESS+HAUSER product type PTC31B + PZAV or equivalent
| Oznaka: PIA65.221 | Code: PIA65.221 | kpl | 1 |  | 0
1.107 | Ekspanzijska posoda za kompenzacijo toplotnih raztezkov medija v sistemu, PN10, skladno z direktivo EU o tlačni opremi PED, pokončna izvedba v obliki diska, membrana po DIN 4807, tlaki do 6 bar, temperature na membrani od 5 do 70°C, vključno s pritrdilnim in tesnilnim materialom; | Expansion vessel for compensation of thermal expansion of the medium in the system, PN10, in compliance with the EU Pressure Equipment Directive PED, upright disc design, diaphragm according to DIN 4807, pressures up to 6 bar, diaphragm temperatures from 5 to 70°C, incl. fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - prostornina ekspanzijske posode 12 litrov | - expansion tank capacity 12 litres
| - dimenzije: premer D x debelina H = ø360 x 170 mm | - dimensions: diameter D x thickness H = ø360 x 170 mm
| - z navojnim priključkom 1/2" (DN15), komplet z ventilom s ključavnico 1/2" (DN15) | - with threaded connection 1/2" (DN15), complete with valve with lock 1/2" (DN15)
| - ustreza proizvod IMI PNEUMATEX tip SD 12.10 + DLV 15 ali enakovredno | - corresponds to IMI PNEUMATEX product type SD 12.10 + DLV 15 or equivalent
| Oznaka: EP65.201 | Code: EP65.201 | kpl | 1 |  | 0
1.108 | Varnostni ventil po TRD 721, PN16, varnostna funkcija izpusta medija zaradi toplotnih raztezkov v sistemu, vzmetno delovanje, možnost ročnega odzračenja, prostor vzmeti zaščiten z membrano, prirobnična izvedba, vključno s pritrdilnim in tesnilnim materialom; | Safety valve according to TRD 721, PN16, safety function of medium discharge due to thermal expansion in the system, spring operation, manual venting possible, spring space protected by diaphragm, flanged version, including fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| - tlak odpiranja 3,0 barg, | - opening pressure 3,0 barg,
| - z navojnima priključkoma DN 15 / 20, komplet z ventilom s ključavnico 1/2" (DN15) | - with threaded connections DN 15 / 20, complete with 1/2" (DN 15) ratchet valve
| - ustreza proizvod IMI PNEUMATEX tip DSV 15 - 3.0 H + DLV 20 ali enakovredno | - iMI PNEUMATEX product type DSV 15 - 3.0 H + DLV 20 or equivalent
| Oznaka: VV65.202 | Code: VV65.202 | kpl | 1 |  | 0
1.109 | Regulacijski ventil, prehodni, tlačno neodvisni za hidravlično uravnoteženje z elektromotornim zveznim pogonom, 24V, IP54, PN16, material ventila nikljana medenina, nerjavno jeklo / EPDM, navojna izvedba, komplet z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Control valve, intermediate, pressure independent for hydraulic balancing with electromotor continuous actuator, 24V, IP54, PN16, valve material nickel-plated brass, stainless steel / EPDM, threaded version, complete with threaded Dutch, fixing and sealing material;
| - hladilna voda za laboratorij 12/20°C | - laboratory cooling water 12/20°C
| DN32, Vv = 0,36 ÷ 3,6 m3/h - ustreza proizvod DANFOSS tip ventila AB-QM 32, tip pogona AME 110/24V NL ali enakovredno | DN32, Vv = 0,36 ÷ 3,6 m3/h - corresponds to DANFOSS product valve type AB-QM 32, actuator type AME 110/24V NL or equivalent
| Oznaka: VY65.251 | Code: VY65.251 | kpl | 1 |  | 0
1.110 | Krogelni ventil s priklučkom za praznenje oz. polnenje, navojna izvedba, PN16, z ročico, material medenina / PTFE, vključno s pritrdilnim in tesnilnim materialom: | Ball valve with union for emptying or filling, threaded version, PN16, with handle, material brass/PTFE, incl. fitting and sealing material:
| - ustreza proizvod KOVINA ali END ARMATUREN ali enakovredno | - corresponds to the product METAL or END ARMATUREN or equivalent
| DN 15 | DN 15 | kos | 120 |  | 0
1.111 | Krogelni ventil, navojna izvedba, PN16, z ročico, material medenina / PTFE, vključno s pritrdilnim in tesnilnim materialom: | Ball valve, threaded version, PN16, with lever, material brass/PTFE, incl. mounting and sealing material:
| - ustreza proizvod KOVINA ali END ARMATUREN ali enakovredno | - corresponds to the product METAL or END ARMATUREN or equivalent
| DN 15 | DN 15 | kos | 152 |  | 0
| DN 20 | DN 20 | kos | 12 |  | 0
| DN 25 | DN 25 | kos | 12 |  | 0
| DN 32 | DN 32 | kos | 58 |  | 0
| DN 40 | DN 40 | kos | 18 |  | 0
| DN 50 | DN 50 | kos | 20 |  | 0
1.112 | Zaporna loputa, prirobnična izvedba, mehko tesnenje, PN16, z ročnim pogonom z ročico do vključno DN100 oziroma z ročnim polžnim pogonom nad vključno DN125, material nodularna litina / EPDM, za vgradnjo med prirobnice, komplet s protiprirobnicama, vijačnim in tesnilnim materialom; | Butterfly valve, flanged version, soft sealing, PN16, with manual lever actuator up to and including DN100 or with manual screw actuator up to and including DN125, material ductile iron / EPDM, for installation between flanges, complete with two anti-seize fittings, screwing and sealing material;
| - ustreza proizvod IMP ARMATURE ali enakovredno | - iMP ARMATURE or equivalent
| DN 65 | DN 65 | kpl | 4 |  | 0
| DN 80 | DN 80 | kpl | 5 |  | 0
| DN 100 | DN 100 | kpl | 4 |  | 0
1.113 | Lovilnik nesnage, navojna izvedba, z normalnim sitom, PN16, material siva litina, sito nerjavno jeklo, komplet s krogelnim ventilom DN15 za praznenje in izpiranje, vključno z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Debris trap, threaded version, with normal sieve, PN16, material grey cast iron, sieve stainless steel, complete with ball valve DN15 for emptying and flushing, incl. two threaded Hollanders, fixing and sealing material;
| - ustreza proizvod IMP ARMATURE ali enakovredno | - iMP ARMATURE or equivalent
| DN 32 | DN 32 | kpl | 8 |  | 0
| DN 40 | DN 40 | kpl | 3 |  | 0
| DN 50 | DN 50 | kpl | 4 |  | 0
1.114 | Lovilnik nesnage, prirobnična izvedba, z normalnim sitom, PN16, material siva litina, sito nerjavno jeklo, komplet s krogelnim ventilom DN15 za praznenje in izpiranje, vključno s protiprirobnicama, vijačnim in tesnilnim materialom; | Debris trap, flanged version, with normal sieve, PN16, material grey cast iron, sieve stainless steel, complete with ball valve DN15 for emptying and flushing, incl. counter flanges, screwing and sealing material;
| - ustreza proizvod IMP ARMATURE ali enakovredno | - iMP ARMATURE or equivalent
| DN 65 | DN 65 | kpl | 1 |  | 0
| DN 100 | DN 100 | kpl | 1 |  | 0
1.115 | Ventil za hidravlično uravnoteženje, nastavitev pretoka, navojna izvedba, PN16, s priključkoma za priklop naprave za merjenje pretoka, z zaporno funkcijo brez prenastavitve pretoka, material siva litina, nerjavno jeklo, EPDM, PTFE, vključno z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Hydraulic balancing valve, flow adjustment, threaded version, PN16, with two connections for connection of flow measuring device, with shut-off function without flow reset, material grey cast iron, stainless steel, EPDM, PTFE, incl. threaded plugs, fastening and sealing material;
| - ustreza proizvod IMI TA tip STAD ali enakovredno | - the product conforms to IMI TA type STAD or equivalent
| DN 15 | DN 15 | kpl | 1 |  | 0
| DN 20 | DN 20 | kpl | 3 |  | 0
| DN 25 | DN 25 | kpl | 7 |  | 0
| DN 32 | DN 32 | kpl | 11 |  | 0
| DN 40 | DN 40 | kos | 5 |  | 0
| DN 50 | DN 50 | kos | 1 |  | 0
1.116 | Ventil za hidravlično uravnoteženje, nastavitev pretoka, prirobnična izvedba, PN16, s priključkoma za priklop naprave za merjenje pretoka, z zaporno funkcijo brez prenastavitve pretoka, material siva litina, nerjavno jeklo, EPDM, PTFE, vključno s protiprirobnicama, vijačnim in tesnilnim materialom; | Hydraulic balancing valve, flow adjustable, flanged version, PN16, with two connections for connection of a flow measuring device, with shut-off function without flow reset, material grey cast iron, stainless steel, EPDM, PTFE, incl. anti-seize, screwing and sealing material;
| - ustreza proizvod IMI TA tip STAF ali enakovredno | - corresponds to IMI TA type STAF or equivalent
| DN 80 | DN 80 | kpl | 5 |  | 0
1.117 | Prelivni regulator, regulator diferenčnega tlaka (prestrujni ventil), odpiranje pretoka pri nastavljenem diferenčnem tlaku, navojna izvedba, PN10, material medenina, nerjavno jeklo, EPDM, NBR, vključno z dvema impulznima cevkama in spojkama, navojnima holandcema, pritrdilnim in tesnilnim materialom; | Overflow regulator, differential pressure regulator (pressure relief valve), flow opening at set differential pressure, threaded version, PN10, material brass, stainless steel, EPDM, NBR, incl. two impulse tubes and couplings, threaded Hollanders, fastening and sealing material;
| - diferenčni tlak nastavljiv 10 ÷ 120 kPa | - differential pressure adjustable 10 ÷ 120 kPa
| - ustreza proizvod DANOSS tip AVDA ali enakovredno | - corresponds to DANOSS product type AVDA or equivalent
| DN 15 | DN 15 | kpl | 13 |  | 0
| DN 20 | DN 20 | kpl | 3 |  | 0
| DN 25 | DN 25 | kpl | 1 |  | 0
1.118 | Kompenzator vibracij in prenosa hrupa iz strojne opreme na cevovod ali iz hrupnega prostora po cevovodu v sosednji prostor, navojna izvedba, PN16, material nerjavno jeklo, EPDM, vključno z nerjavnima navojnima holandcema, pritrdilnim in tesnilnim materialom; | Vibration and noise compensator for noise transmission from machinery to pipeline or from noise room through pipeline to adjacent room, threaded version, PN16, material stainless steel, EPDM, incl. stainless steel threaded dutch, fastening and sealing material;
| - ustreza proizvod END ARMATUREN tip KP ali enakovredno | - corresponds to END ARMATUREN type KP or equivalent
| DN 25 | DN 25 | kpl | 22 |  | 0
| DN 32 | DN 32 | kpl | 4 |  | 0
| DN 40 | DN 40 | kpl | 6 |  | 0
1.119 | Kompenzator vibracij in prenosa hrupa iz strojne opreme na cevovod ali iz hrupnega prostora po cevovodu v sosednji prostor, prirobnična izvedba, PN16, material nerjavno jeklo, EPDM, vključno z nerjavnima protiprirobnicama, vijačnim in tesnilnim materialom; | Vibration and noise compensator for noise transmission from machinery to pipeline or from noise room through pipeline to adjacent room, flanged version, PN16, material stainless steel, EPDM, incl. stainless steel counter flanges, screwing and sealing material;
| - ustreza proizvod END ARMATUREN tip KP ali enakovredno | - corresponds to END ARMATUREN type KP or equivalent
| DN 80 | DN 80 | kpl | 6 |  | 0
| DN 100 | DN 100 | kpl | 4 |  | 0
1.120 | Termometer, tekočinski, dolžina skale 100mm, kotni 90°, potopna dolžina 40mm, v zaščitni cevi - tulki, klasa točnosti 1%, navojni priključek 1/2" (DN15), material medenina, aluminij, steklo, nerjavno jeklo, vključno s pritrdilnim in tesnilnim materialom; | Thermometer, liquid, scale length 100mm, angle 90°, immersion length 40mm, in protective tube - sleeves, accuracy class 1%, threaded connection 1/2" (DN15), material brass, aluminium, glass, stainless steel, incl. fixing and sealing material;
| - ustreza proizvod INOL ali enakovredno | - corresponds to INOL or equivalent
| - območjem merjenja: 0 do 100°C | - measuring range: 0 to 100°C | kpl | 116 |  | 0
1.121 | Manometer ø 68 mm, klasa točnosti 1,6% po EN837-1, navojni radialni priključek, material medenina, nerjavno jeklo, steklo / EPDM, komplet z manometrskim ventilom DN15 (1/2"), vključno s pritrdilnim in tesnilnim materialom; | Pressure gauge ø 68 mm, accuracy class 1.6% according to EN837-1, threaded radial connection, material brass, stainless steel, glass / EPDM, complete with pressure gauge valve DN15 (1/2"), including fitting and sealing material;
| - ustreza proizvod INOL ali enakovredno | - corresponds to INOL or equivalent
| - območjem merjenja: 0 do 10 bar | - measuring range: 0 to 10 bar | kpl | 116 |  | 0
1.122 | Avtomatski odzračevalnik, z zapornim in ročno odzračevalnim ventilom PN10 material medenina / PTFE, vključno z navojnim holandcem in tesnilnim materialom; | Automatic venting valve, with shut-off and manual venting valve PN10 material brass/PTFE, including threaded Dutchman and sealing material;
| DN25 - ustreza proizvod IMI PNEUMATEX tip ZUTX 25 ali enakovredno | DN25 - corresponds to IMI PNEUMATEX product type ZUTX 25 or equivalent | kpl | 124 |  | 0
1.123 | Jeklene nerjavne cevi za precizno uporabo, zatisni press sistem, PN10 ali več, izdelava in skladnost po EN10088, EN10312, material nerjavno jeklo 1.4520 ali 1.4404 ali boljši, vključno s spojnimi in oblikovnimi zatisnimi press kosi (90°loki, T kosi, redukcije, ...), spojnim in tesnilnim materialom, zatiskanje z originalnim press orodjem proizvajalca, komplet s prehodnimi navojnimi in prirobnični oblikovnimi kosi, ustreza proizvod VIEGA ali KANTHERM ali enakovredno; | Stainless steel tubes for precision applications, press fitting system, PN10 or higher, manufacture and conformity to EN10088, EN10312, material stainless steel 1.4520 or 1.4404 or better, including coupling and press fitting shapes (90°bends, T-pieces, reducers, etc.), coupling and sealing material, press fitting with original manufacturer's press tool, complete with threaded and flanged transition shapes, corresponding to VIEGA or KANTHERM product or equivalent;
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and hose clamps with noise damping lining, suitable for HILTI or SIKLA, or equivalent;
| DN 15, ø 18 x 1,2 | DN 15, ø 18 x 1,2 | m | 120 |  | 0
| DN 20, ø 22 x 1,5 | DN 20, ø 22 x 1,5 | m | 60 |  | 0
| DN 25, ø 28 x 1,5 | DN 25, ø 28 x 1,5 | m | 60 |  | 0
| DN 32, ø 35 x 1,5 | DN 32, ø 35 x 1,5 | m | 300 |  | 0
| DN 40, ø 42 x 1,5 | DN 40, ø 42 x 1,5 | m | 60 |  | 0
| DN 50, ø 54 x 1,5 | DN 50, ø 54 x 1,5 | m | 150 |  | 0
| DN 65, ø 76,1 x 2 | DN 65, ø 76,1 x 2 | m | 30 |  | 0
| DN 80, ø 88,9 x 2 | DN 80, ø 88,9 x 2 | m | 90 |  | 0
| DN 100, ø 108 x 2 | DN 100, ø 108 x 2 | m | 120 |  | 0
| 90°lok DN 15, ø 18 x 1,2 | 90°lok DN 15, ø 18 x 1,2 | kos | 32 |  | 0
| 90°lok DN 20, ø 22 x 1,5 | 90°lok DN 20, ø 22 x 1,5 | kos | 16 |  | 0
| 90°lok DN 25, ø 28 x 1,5 | 90°lok DN 25, ø 28 x 1,5 | kos | 16 |  | 0
| 90°lok DN 32, ø 35 x 1,5 | 90°lok DN 32, ø 35 x 1,5 | kos | 76 |  | 0
| 90°lok DN 40, ø 42 x 1,5 | 90°lok DN 40, ø 42 x 1,5 | kos | 16 |  | 0
| 90°lok DN 50, ø 54 x 1,5 | 90°lok DN 50, ø 54 x 1,5 | kos | 38 |  | 0
| 90°lok DN 65, ø 76,1 x 2 | 90°lok DN 65, ø 76,1 x 2 | kos | 8 |  | 0
| 90°lok DN 80, ø 88,9 x 2 | 90°lok DN 80, ø 88,9 x 2 | kos | 24 |  | 0
| 90°lok DN 100, ø 108 x 2 | 90°lok DN 100, ø 108 x 2 | kos | 30 |  | 0
| T kos DN 25 / odcep DN 15 | T piece DN 25 / branch DN 15 | kos | 20 |  | 0
| T kos DN 25 / odcep DN 20 | T piece DN 25 / branch DN 20 | kos | 10 |  | 0
| T kos DN 32 / odcep DN 25 | T piece DN 32 / branch DN 25 | kos | 40 |  | 0
| T kos DN 40 / odcep DN 15 | T piece DN 40 / branch DN 15 | kos | 4 |  | 0
| T kos DN 40 / odcep DN 32 | T piece DN 40 / branch DN 32 | kos | 8 |  | 0
| T kos DN 50 / odcep DN 15 | T piece DN 50 / branch DN 15 | kos | 4 |  | 0
| T kos DN 50 / odcep DN 25 | T piece DN 50 / branch DN 25 | kos | 2 |  | 0
| T kos DN 50 / odcep DN 40 | T piece DN 50 / branch DN 40 | kos | 4 |  | 0
| T kos DN 65 / odcep DN 50 | T piece DN 65 / branch DN 50 | kos | 2 |  | 0
| T kos DN 100 / odcep DN 80 | T piece DN 100 / branch DN 80 | kos | 10 |  | 0
| redukcija DN 20 / DN 15 | dN 20 / DN 15 reduction | kos | 2 |  | 0
| redukcija DN 25 / DN 20 | dN 25 / DN 20 reduction | kos | 8 |  | 0
| redukcija DN 32 / DN 15 | reduction DN 32 / DN 15 | kos | 24 |  | 0
| redukcija DN 32 / DN 25 | dN 32 / DN 25 reduction | kos | 16 |  | 0
| redukcija DN 40 / DN 32 | dN 40 / DN 32 reduction | kos | 4 |  | 0
| redukcija DN 50 / DN 32 | dN 50 / DN 32 reduction | kos | 4 |  | 0
| redukcija DN 50 / DN 20 | dN 50 / DN 20 reduction | kos | 2 |  | 0
| redukcija DN 50 / DN 40 | dN 50 / DN 40 reduction | kos | 2 |  | 0
| redukcija DN 65 / DN 20 | dN 65 / DN 20 reduction | kos | 2 |  | 0
| redukcija DN 65 / DN 40 | dN 65 / DN 40 reduction | kos | 2 |  | 0
| redukcija DN 100 / DN 25 | dN 100 / DN 25 reduction | kos | 2 |  | 0
| redukcija DN 100 / DN 80 | dN 100 / DN 80 reduction | kos | 2 |  | 0
| prirobnica DN 32 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 32 to EN1092, PN16, including bolting and sealing material | kpl | 24 |  | 0
| prirobnica DN 40 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 40 to EN1092, PN16, including bolting and sealing material | kpl | 12 |  | 0
| prirobnica DN 50 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 50 to EN1092, PN16, including bolting and sealing material | kpl | 8 |  | 0
| prirobnica DN 65 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 65 to EN1092, PN16, including bolting and sealing material | kpl | 4 |  | 0
| prirobnica DN 80 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 80 to EN1092, PN16, including bolting and sealing material | kpl | 16 |  | 0
| prirobnica DN 100 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 100 to EN1092, PN16, including bolting and sealing material | kpl | 4 |  | 0
1.124 | Toplotna izolacija cevovodov in cevnih armatur s parozaporno izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z naslednjimi lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, požarna klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +110°C, lepljeno na cevovode in armature z originalnim lepilom proizvajalca, vključno s trakovi za šive; | Thermal insulation of pipelines and pipe fittings with vapour barrier insulation made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, fire classification B-s3-d0 according to EN13501-1, for temperatures from -50 to +110°C, bonded to pipelines and fittings with the original manufacturer's adhesive, including seam tapes;
| - ustreza proizvod ARMACELL tip Armaflex ACE Plus ali enakovredno | - corresponds to ARMACELL product type Armaflex ACE Plus or equivalent
| DN 15, ø 18 ; debelina 13 mm | DN 15, ø 18; thickness 13 mm | m | 160 |  | 0
| DN 20, ø 22 ; debelina 19 mm | DN 20, ø 22 ; thickness 19 mm | m | 80 |  | 0
| DN 25, ø 28 ; debelina 19 mm | DN 25, ø 28 ; thickness 19 mm | m | 80 |  | 0
| DN 32, ø 35 ; debelina 25 mm | DN 32, ø 35 ; thickness 25 mm | m | 400 |  | 0
| DN 40, ø 42 ; debelina 25 mm | DN 40, ø 42 ; thickness 25 mm | m | 80 |  | 0
| DN 50, ø 53 ; debelina 40 mm | DN 50, ø 53 ; thickness 40 mm | m | 200 |  | 0
| DN 65, ø 76,1 ; debelina 40 mm | DN 65, ø 76,1 ; thickness 40 mm | m | 40 |  | 0
| DN 80, ø 88,9 ; debelina 40 mm | DN 80, ø 88,9 ; thickness 40 mm | m | 120 |  | 0
| DN 100, ø108 ; debelina 40 mm | DN 100, ø108 ; thickness 40 mm | m | 160 |  | 0
1.125 | Tlačni preskus trdnosti in tesnenja sistema cevovodov, skladeno z opisom v "IZS Priročnik tlačnih preizkusov strojnih inštalacij", vključno s potrebnim materialom za izvedbo preizkusa, ter izdelavo pisnega poročila o uspešno opravljenem tlačnem preizkusu; | Pressure test of the strength and tightness of the piping system, as described in the "IZS Manual for Pressure Testing of Mechanical Installations", including the necessary materials for the test, and the production of a written report on the successful completion of the pressure test;
| preskusni tlak = 4,5 barg | test pressure = 4,5 barg | kpl | 1 |  | 0
1.126 | Izpiranje cevovodov s sanitarno hladno vodo v celotnem sistemu novoinstaliranih razvodov z namenom odstranjevanja nečistoč v sistemu cevovodov, vključno s čiščenjem lovilnikov nesnage in drugih elementov; | Flushing of sanitary cold water piping throughout the newly installed piping system to remove impurities in the piping system, including cleaning of debris traps and other elements;
| - vsi podsistemi | - all subsystems | kpl | 1 |  | 0
1.127 | Ognjeodporna tesnilna masa, vgradnja na prehodu cevovodov skozi zid med požarnima sektortjema, požarna odpornost 90 minut, ustreza proizvod HILTI ali enakovredno. | Fire-resistant sealant, for installation at the transition of pipelines through the wall between the two fire sectors, fire resistance 90 minutes, equivalent to HILTI or equivalent.
| Vsak prehod mora biti označen z nalepko ali tablico z osnovnimi požarnimi podatki; | Each passageway must be marked with a sticker or placard with basic fire information; | kpl | 1 |  | 0
1.128 | Preizkusno obratovanje delovanja sistema v obsegu: | Operational test of the system in scope:
| - pregled opreme, instalacije in armatur, | - inspection of equipment, plumbing and fittings,
| - pregled delovanja naprav, elementov regulacije in nastavitve parametrov, | - overview of the operation of the devices, control elements and parameter settings,
| - cirkulacija hladilne vode oziroma ogrevne vode, | - circulation of cooling water and heating water respectively,
| - kontrola predpisanih parametrov hladilne vode oziroma ogrevne vode. | - checking the prescribed parameters for cooling water and heating water respectively.
| Preizkusno obratovanje traja neprekinjeno 72 ur. | The test operation shall be continuous for 72 hours. | kpl | 1 |  | 0
1.129 | Napisne ploščice iz nerjavne pločevine z vgravirano oznako po shemi za opremo in armature, kompletno z jekleno pritrdilno žico ali visoko kvalotetne nalepke; visoko trajanje H (več kot 15 let) | Stainless steel nameplates with engraved marking according to the scheme for fittings and fixtures, complete with steel fixing wire or high quality labels; high durability H (more than 15 years) | kpl | 1 |  | 0
1.130 | Samolepilne puščice za označitev smeri pretoka ter z napisom vrste medija; visoko trajanje H (več kot 15 let) | Self-adhesive arrows to indicate direction of flow and type of media; high H lifetime (more than 15 years) | kpl | 1 |  | 0
1.131 | Izdelava montažnih risb za izvedbo inštalacij med gradnjo objekta, kot so: detajli priključkov, montažne skice, montažni detajli, ipd. | Preparation of assembly drawings for the installation of services during the construction of the building, such as: connection details, assembly sketches, assembly details, etc. | kpl | 1 |  | 0
1.132 | Kvalifikacije montaže IQ-pregledi (instalation qualification) po GEP Commissioning protokolu in dokumentiranje kvalifikacije montaže, vključno z odpravo prvotnih napak montaže; | Installation qualification IQ-checks (installation qualification) according to the GEP Commissioning Protocol and documentation of installation qualification, including correction of original installation faults; | kpl | 1 |  | 0
1.133 | Meritve delovanja OQ-kvalifikacija (operation qualification) ter dokumentiranje meritev delovanja, vključno z nastavitvijo parametrov; | OQ (operation qualification) measurements and documentation of performance measurements, including parameter settings; | kpl | 1 |  | 0
1.134 | Posnetki izvedenega stanja, sprotno beleženje vseh sprememb nastalih med izvedbo, vrisovanje in vpisovanje v PZI projektno dokumentacijo; | Recording of the as-built condition, keeping a running record of any changes made during execution, plotting and entering into the PZI project documentation; | kpl | 1 |  | 0
1.135 | Stenska shema sistema, vloženo v zaščitni okvir s prosojnim umetnim steklomo (plastika) ali plastificirano, vključno s pritrditvijo na notranjo steno v strojnici objekta; | Wall diagram of the system, enclosed in a protective frame with transparent plastic or plasticised glass, including fixing to an internal wall in the mechanical room of the building; | kpl | 1 |  | 0
1.136 | Primopredajna dokumentacija, ki mora vsebovati: izjave, dokazilo o zanesljivosti objekta, certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo, obratovanje in vzdrževanje ter ostalo primopredajno dokumantacijo. Predaja se v dveh mapiranih izvodih ter en izvod v elektronski obliki; | The handover documentation, which shall include: declarations, proof of the reliability of the facility, certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use, operation and maintenance, and other handover documentation. It shall be handed over in two mapped copies and one copy in electronic form; | kpl | 1 |  | 0
| PODSISTEMI HLADILNE IN OGREVNE VODE ZA LABORATORIJE | COOLING AND HEATING WATER SUBSYSTEMS FOR LABORATORIES |  |  |  | 0

## 4.10.2_KomprimZrak
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.10 | STROJNA DELA | MECHANICAL WORKS
4.10.2 | KOMPRIMIRAN ZRAK | COMPRESSED AIR |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
2 | KOMPRIMIRAN ZRAK | COMPRESSED AIR
| Vse postavke v nadalevanju zajemajo dobavo in montažo (razen tam kjer je to posebej navedeno). | All items below include delivery and installation (except where specifically indicated).
2.1 | Zračni brezoljni kompresor, vodno hlajen z zveznim frekvenčno vodenim delovanjem, z vgrajenim sušilnikom zraka ter z avtomatskim elektronskim odvajalnikom kondenzata, obratovalni tlak 7 bar z možnostjo nastavitve do 8,6 bar, FAD = 131 l/s po ISO1217 aneks C (pri 1 bar in 20°C) = 471,6 Nm3/h = 7,86 Nm3/min, točka rosišča -20°C, z vijačnim kompresorjem z modularnim sistemom, vključno z elektro krmilno omaro in krmilnikom za regulacjo delovanja z povezavo na CNS, dobavljeno kot kompaktna naprava z blažilniki vibracij in hrupa. Tehnični podatki: | Oil-free air compressor, water-cooled with continuous frequency-controlled operation, with integrated air dryer and automatic electronic condensate drain, operating pressure 7 bar adjustable up to 8,6 bar, FAD = 131 l/s according to ISO1217 Annex C (at 1 bar and 20°C) = 471,6 Nm3/h = 7,86 Nm3/min, dew point -20°C, with screw compressor with modular system, including electrical control cabinet and operation control controller with connection to CNS, supplied as a compact unit with vibration and noise dampers. Technical data:
| - električni podatki: 55 kW / 3x400 V / 50 Hz | - electrical data: 55 kW / 3x400 V / 50 Hz
| - zvočni tlačni nivo: do 70 db(A) na 1m po ISO2151 in ISO9614, | - sound pressure level: up to 70 db(A) at 1m according to ISO2151 and ISO9614,
| - dimenzije do: L x W x H = 2500 x 1450 x 2200 mm, teža do: 1900kg, | - dimensions up to: L x W x H = 2500 x 1450 x 2200 mm, weight up to: 1900kg,
| - z avtomatskim zapornim ventilom na hladilni vodi | - with automatic shut-off valve on the cooling water
| - zvezno voden od 30 do 100% | - federally controlled from 30 to 100%
| - ustreza proizvod ATLAS COPCO tip ZR 55 FF - VSD - IMD 8.6bar - 50Hz ali enakovredno | - corresponds to ATLAS COPCO product type ZR 55 FF - VSD - IMD 8.6bar - 50Hz or equivalent
| Oznaka: KS90.11, KS90.12 | Code: KS90.11, KS90.12 | kpl | 1 |  | 0
2.2 | Tačna posoda za akumulacijo komprimiraneja zraka kapacitete 5000 litrov za obratovalni tlak do 13 bar, vertikalna izvedba z revizijsko odprtino, material nerjavno jeklo AISI304 ali boljše, notranja površinska hrapavost Ra≤1,6µm, postavljeno na jeklenih nogah 300mm od tal, komplet z dodatno opremo: varnostni ventil DN50 s tlakom odpiranja pn=10bar, manometer 0 do 10 barg. Certifikat o skladnosti po direktivo o tlačni opremi PED ter CE certifikat. Tehnični podatki: | Compressed air storage tank with a capacity of 5000 litres for operating pressures up to 13 bar, vertical design with inspection opening, material stainless steel AISI304 or better, internal surface roughness Ra≤1.6µm, mounted on steel legs 300mm from the floor, complete with accessories: safety valve DN50 with opening pressure pn=10bar, pressure gauge 0 to 10 barg. Certificate of conformity according to the Pressure Equipment Directive (PED) and CE certificate. Technical data:
| - dimenzije D x H = Ø1400mm x 4000mm | - dimensions L x H = Ø1400mm x 4000mm
| - priključki po ISO1127, prirobnični: 4x DN80 (ø88,9x2,3), 1x DN50 (ø60,3x2), 1x DN25 (ø33,7x2), 1x DN15 (ø21,3x1,6) | - iSO1127, flanged connections: 4x DN80 (ø88,9x2,3), 1x DN50 (ø60,3x2), 1x DN25 (ø33,7x2), 1x DN15 (ø21,3x1,6)
| - ustreza proizvod OMEGA AIR tip TP PED 5000 AISI 304 vertikalna izvedba ali enakovredno | - corresponds to OMEGA AIR product type TP PED 5000 AISI 304 vertical version or equivalent
| Oznaka: T90.13 | Code: T90.13 | kpl | 1 |  | 0
2.3 | Filter komprimiranega zraka sestavljen iz ohišja in filtrnega vložka s filtracijo vodnih in oljnih aerosolov 0,01mg/m3 (0,01ppm) ter prašnih delcev nad 0,01 µm, PN16, FAD= 300 l/s po ISO1217 aneks C (pri 1 bar in 20°C) = 1080 Nm3/h = 18 Nm3/min, komplet z dodatno opremo prikazovalnik zamazanosti, električnim kontaktom 230V / alarm in avtomatskim odvodom kondenzata. Tehnični podatki: | Compressed air filter consisting of housing and filter cartridge with filtration of water and oil aerosols 0,01mg/m3 (0,01ppm) and dust particles above 0,01 µm, PN16, FAD= 300 l/s according to ISO1217 annex C (at 1 bar and 20°C) = 1080 Nm3/h = 18 Nm3/min, complete with accessories: turbidity display, 230V electrical contact/alarm and automatic condensate drain. Technical data:
| - dimenzije B x H = 230mm x 830mm | - dimensions B x H = 230mm x 830mm
| - ustreza proizvod ATLAS COPCO tip PD+300 ali enakovredno | - corresponds to ATLAS COPCO product type PD+300 or equivalent
| Oznaka: F90.15. F90.16 | Code: F90.15. F90.16 | kpl | 2 |  | 0
2.4 | Avtomatski elektronski odvajalnika kondenzata iz komprimiranega zraka, G1/2, kapaciteta 330 l/s, električno napajanje 230V /50Hz, vključno s pritrdilnim in tesnilnim materialom; | Automatic electronic compressed air condensate drain, G1/2, capacity 330 l/s, electric power supply 230V/50Hz, incl. fixing and sealing material;
| - ustreza proizvod ATLAS COPCO tip EWD 330 C ali enakovredno | - corresponds to ATLAS COPCO product type EWD 330 C or equivalent
| Oznaka: Z90.14 | Code: Z90.14 | kpl | 1 |  | 0
2.5 | Tipalo tlaka komprimiranega zraka, za območje 0 do 10 bar, material nerjavno jeklo, navojni priključek 1/2", PN16, elektični podatki: napajanje 24VAC, izhod 4-20mA, kompletno z ventilom za tipalo tlaka 1/2" ter tesnilnim in pritrdilnim materialom; | Compressed air pressure sensor, for range 0 to 10 bar, material stainless steel, threaded connection 1/2", PN16, electrical data: power supply 24VAC, output 4-20mA, complete with pressure sensor valve 1/2" and sealing and fixing material;
| - ustreza proizvod ENDRESS+HAUSER tip PMC51 + PZAV ali enakovredno | - corresponds to ENDRESS+HAUSER product type PMC51 + PZAV or equivalent
| Oznaka: PIA90.001 | Code: PIA90.001 | kpl | 1 |  | 0
2.6 | Tipalo točke rosišča (dew point) in absolutne vlažnosti (mixing ratio) komprimiranega zraka, za merilno območje: "dewpoint" -50 do +50°C in "mixing ratio" 0 do 30 g/kg, potopna dolžina 120mm, senzibilna dolžina 41mm, material nerjavno jeklo, navojni priključek 1/2", PN16, elektični podatki: napajanje 24VAC, izhod 4-20mA, kabel 2m, pretvornik vgrajen na zid, komplet s pritrdilnim in tesnilnim materialom; | Dew point and mixing ratio sensor for compressed air, for measuring range: dew point -50 to +50°C and mixing ratio 0 to 30 g/kg, immersion length 120mm, sensing length 41mm, material stainless steel, threaded connection 1/2", PN16, electrical data: power supply 24VAC, output 4-20mA, cable 2m, wall-mounted transducer, complete with fixing and sealing material;
| - ustreza proizvod VAISALA tip DMT344 ali enakovredno | - corresponds to VAISALA product type DMT344 or equivalent
| Oznaka: MIA90.002 | Code: MIA90.002 | kpl | 1 |  | 0
2.7 | Varnostni ventil na vzmet, za komprimiran zrak, z navojnimi priključki, kapaciteta 200 l/s (pri 1 bar in 20°C), nastavljen na tlak odpiranja 10 barg, vključno s pritrdilnim in tesnilnim materialom; | Spring-loaded safety valve for compressed air, with threaded connections, capacity 200 l/s (at 1 bar and 20°C), set to an opening pressure of 10 barg, incl. fixing and sealing material;
| - ustreza proizvod SPIRAX SARCO tip SV615AS DN20/32 ali enakovredno | - corresponds to SPIRAX SARCO product type SV615AS DN20/32 or equivalent
| Oznaka: VV90.18, VV90.19 | Code: VV90.18, VV90.19 | kpl | 2 |  | 0
2.8 | Kompenzator vibracij in prenosa hrupa iz strojne opreme na cevovod ali iz hrupnega prostora po cevovodu v sosednji prostor, navojna izvedba, PN16, material nerjavno jeklo, EPDM, vključno z nerjavnima navojnima holandcema, pritrdilnim in tesnilnim materialom; | Vibration and noise compensator for noise transmission from machinery to pipeline or from noise room through pipeline to adjacent room, threaded version, PN16, material stainless steel, EPDM, incl. stainless steel threaded dutch, fastening and sealing material;
| - ustreza proizvod END ARMATUREN tip KP ali enakovredno | - corresponds to END ARMATUREN type KP or equivalent
| DN 15, ø 21,3 x 1,6 | DN 15, ø 21,3 x 1,6 | kos | 4 |  | 0
| DN 20, ø 26,9 x 1,6 | DN 20, ø 26,9 x 1,6 | kos | 4 |  | 0
| DN 25, ø 33,7 x 2,0 | DN 25, ø 33,7 x 2,0 | kos | 4 |  | 0
| DN 32, ø 42,4 x 2,0 | DN 32, ø 42,4 x 2,0 | kos | 8 |  | 0
| DN 40, ø 48,3 x 2,0 | DN 40, ø 48,3 x 2,0 | kos | 2 |  | 0
| DN 50, ø 60,3 x 2,0 | DN 50, ø 60,3 x 2,0 | kos | 4 |  | 0
| DN 65, ø 76,1 x 2,0 | DN 65, ø 76,1 x 2,0 | kos | 4 |  | 0
2.9 | Razdelilnik komprimiranega zraka PN16 v skaladu z direktivo o tlačni opremi PED, izdelan iz jeklenih nerjavnih cevi AISI304 po ISO1127 iz materiala AISI304, notranja površinska hrapavost Ra≤1,6µm, vključno z varilnim materialom, varjenje TIG pod inertnim plinom; | Compressed air manifold PN16 in compliance with the Pressure Equipment Directive PED, made of stainless steel tubes AISI304 according to ISO1127, material AISI304, internal surface roughness Ra≤1,6µm, including welding material, TIG welding under inert gas;
| Razdelilnik DN200 (ø219,1x2,6) dolžina 1500 mm na obeh straneh zaključen s prirobnicama in s slepima prirobnicama po EN1092: 2x DN200, vključno z vijačnim in tesnilnim materalom; | Manifold DN200 (ø219,1x2,6) length 1500 mm on both sides, terminated with flanges and blind flanges according to EN1092: 2x DN200, incl. screwing and sealing material;
| Predvideni priključki po obodu: prirobnični | Perimeter connections: flanged
| - prirobnični zgoraj: 5x DN80 | - flange above: 5x DN80
| - varjeni oz. navojni na obodu za PIA in MIA | - welded or threaded on the circumference for PIA and MIA
| - varjeni oz. navojni spodaj: 2x DN15 | - welded or threaded below: 2x DN15
| - izdelava delavniške risbe | - drawing up a workshop drawing
| Oznaka: RZ90.17 | Code: RZ90.17 | kpl | 1 |  | 0
2.10 | Manometer za komprimiran zraka za območje merjanja od 0 do 10 bar, premer skale ø 63 mm, izdelan iz materiala nerjavno jeklo AISI 316L / EPDM, polnjen z glicerinom, klasa I, s triclamp priključkom 1", F=ø50,5mm, pritrdilnim in tesnilnim materialom; | Compressed air pressure gauge for measuring range from 0 to 10 bar, scale diameter ø 63 mm, made of stainless steel AISI 316L/EPDM, filled with glycerine, class I, with triclamp connection 1", F=ø50,5mm, fixing and sealing material;
| - ustreza proizvod WIKA tip 233.50 ali enakovredno | - corresponds to WIKA product type 233.50 or equivalent | kpl | 3 |  | 0
2.11 | Krogelni ventil iz nerjavnega jekla, PN16, material AISI 304 (ali boljši) / PTFE, tridelno telo ventila, ročica z možnostjo zaklepanja položaja ventila (odprto ali zaprto), varjeni priključki dimenzije po ISO1127, vključno z varilnim materialom, varjenje TIG pod inertnim plinom; | Stainless steel ball valve, PN16, material AISI 304 (or better) / PTFE, three-piece valve body, lever with locking valve position (open or closed), welded connections dimensions according to ISO1127, including welding material, TIG welding under inert gas;
| - ustreza proizvod END ARMATUREN ali enakovredno | - eND ARMATUREN or equivalent
| DN 10, ø 17,2 x 1,6 | DN 10, ø 17,2 x 1,6 | kos | 8 |  | 0
| DN 15, ø 21,3 x 1,6 | DN 15, ø 21,3 x 1,6 | kos | 460 |  | 0
| DN 20, ø 26,9 x 1,6 | DN 20, ø 26,9 x 1,6 | kos | 16 |  | 0
| DN 25, ø 33,7 x 2,0 | DN 25, ø 33,7 x 2,0 | kos | 28 |  | 0
| DN 32, ø 42,4 x 2,0 | DN 32, ø 42,4 x 2,0 | kos | 26 |  | 0
| DN 40, ø 48,3 x 2,0 | DN 40, ø 48,3 x 2,0 | kos | 14 |  | 0
| DN 50, ø 60,3 x 2,0 | DN 50, ø 60,3 x 2,0 | kos | 4 |  | 0
| DN 65, ø 76,1 x 2,0 | DN 65, ø 76,1 x 2,0 | kos | 6 |  | 0
| DN 80, ø 88,9 x 2,3 | DN 80, ø 88,9 x 2,3 | kos | 12 |  | 0
2.12 | Jeklene nerjavne cevi, izdelane po ISO1127, material AISI304, notranja površinska hrapavost Ra≤1,6µm, vključno s pripadajočimi oblikovnimi kosi (loki, redukcije, T kosi, ...) in varilnim materialom, varjenje TIG pod inertnim plinom; | Stainless steel tubes, manufactured to ISO1127, material AISI304, internal surface roughness Ra≤1,6µm, including related shaping pieces (arcs, reducers, T-pieces, etc.) and welding consumables, TIG welding under inert gas;
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and pipe clamps with noise damping lining, suitable for HILTI or SIKLA, or equivalent;
| DN 10, ø 17,2 x 1,6 | DN 10, ø 17,2 x 1,6 | m | 30 |  | 0
| DN 15, ø 21,3 x 1,6 | DN 15, ø 21,3 x 1,6 | m | 1480 |  | 0
| DN 20, ø 26,9 x 1,6 | DN 20, ø 26,9 x 1,6 | m | 260 |  | 0
| DN 25, ø 33,7 x 2,0 | DN 25, ø 33,7 x 2,0 | m | 940 |  | 0
| DN 32, ø 42,4 x 2,0 | DN 32, ø 42,4 x 2,0 | m | 450 |  | 0
| DN 40, ø 48,3 x 2,0 | DN 40, ø 48,3 x 2,0 | m | 180 |  | 0
| DN 50, ø 60,3 x 2,0 | DN 50, ø 60,3 x 2,0 | m | 290 |  | 0
| DN 65, ø 76,1 x 2,0 | DN 65, ø 76,1 x 2,0 | m | 470 |  | 0
| DN 80, ø 88,9 x 2,3 | DN 80, ø 88,9 x 2,3 | m | 600 |  | 0
| 90°lok DN 10, ø 17,2 x 1,6 | 90°lok DN 10, ø 17,2 x 1,6 | kos | 10 |  | 0
| 90°lok DN 15, ø 21,3 x 1,6 | 90°lok DN 15, ø 21,3 x 1,6 | kos | 370 |  | 0
| 90°lok DN 20, ø 26,9 x 1,6 | 90°lok DN 20, ø 26,9 x 1,6 | kos | 60 |  | 0
| 90°lok DN 25, ø 33,7 x 2,0 | 90°lok DN 25, ø 33,7 x 2,0 | kos | 230 |  | 0
| 90°lok DN 32, ø 42,4 x 2,0 | 90°lok DN 32, ø 42,4 x 2,0 | kos | 120 |  | 0
| 90°lok DN 40, ø 48,3 x 2,0 | 90°block DN 40, ø 48,3 x 2,0 | kos | 50 |  | 0
| 90°lok DN 50, ø 60,3 x 2,0 | 90°lok DN 50, ø 60,3 x 2,0 | kos | 80 |  | 0
| 90°lok DN 65, ø 76,1 x 2,0 | 90°block DN 65, ø 76,1 x 2,0 | kos | 120 |  | 0
| 90°lok DN 80, ø 88,9 x 2,3 | 90°lok DN 80, ø 88,9 x 2,3 | kos | 150 |  | 0
| T kos DN 15 / odcep DN 10 | T piece DN 15 / branch DN 10 | kos | 2 |  | 0
| T kos DN 15 / odcep DN 15 | T piece DN 15 / branch DN 15 | kos | 60 |  | 0
| T kos DN 20 / odcep DN 15 | T piece DN 20 / branch DN 15 | kos | 16 |  | 0
| T kos DN 20 / odcep DN 20 | T piece DN 20 / branch DN 20 | kos | 8 |  | 0
| T kos DN 25 / odcep DN 15 | T piece DN 25 / branch DN 15 | kos | 24 |  | 0
| T kos DN 25 / odcep DN 20 | T piece DN 25 / branch DN 20 | kos | 16 |  | 0
| T kos DN 25 / odcep DN 25 | T piece DN 25 / branch DN 25 | kos | 32 |  | 0
| T kos DN 32 / odcep DN 15 | T piece DN 32 / branch DN 15 | kos | 24 |  | 0
| T kos DN 32 / odcep DN 32 | T piece DN 32 / branch DN 32 | kos | 12 |  | 0
| T kos DN 40 / odcep DN 32 | T piece DN 40 / branch DN 32 | kos | 8 |  | 0
| T kos DN 50 / odcep DN 20 | T piece DN 50 / branch DN 20 | kos | 8 |  | 0
| T kos DN 50 / odcep DN 20 | T piece DN 50 / branch DN 20 | kos | 6 |  | 0
| T kos DN 50 / odcep DN 25 | T piece DN 50 / branch DN 25 | kos | 8 |  | 0
| T kos DN 50 / odcep DN 32 | T piece DN 50 / branch DN 32 | kos | 8 |  | 0
| T kos DN 50 / odcep DN 50 | T piece DN 50 / branch DN 50 | kos | 4 |  | 0
| T kos DN 65 / odcep DN 15 | T piece DN 65 / branch DN 15 | kos | 1 |  | 0
| T kos DN 65 / odcep DN 20 | T piece DN 65 / branch DN 20 | kos | 12 |  | 0
| T kos DN 65 / odcep DN 20 | T piece DN 65 / branch DN 20 | kos | 8 |  | 0
| T kos DN 65 / odcep DN 25 | T piece DN 65 / branch DN 25 | kos | 12 |  | 0
| T kos DN 65 / odcep DN 32 | T piece DN 65 / branch DN 32 | kos | 16 |  | 0
| T kos DN 65 / odcep DN 50 | T piece DN 65 / branch DN 50 | kos | 4 |  | 0
| T kos DN 65 / odcep DN 65 | T piece DN 65 / branch DN 65 | kos | 2 |  | 0
| T kos DN 80 / odcep DN 20 | T piece DN 80 / branch DN 20 | kos | 2 |  | 0
| T kos DN 80 / odcep DN 25 | T piece DN 80 / branch DN 25 | kos | 8 |  | 0
| T kos DN 80 / odcep DN 32 | T piece DN 80 / branch DN 32 | kos | 8 |  | 0
| T kos DN 80 / odcep DN 40 | T piece DN 80 / branch DN 40 | kos | 4 |  | 0
| T kos DN 80 / odcep DN 50 | T piece DN 80 / branch DN 50 | kos | 4 |  | 0
| T kos DN 80 / odcep DN 65 | T piece DN 80 / branch DN 65 | kos | 2 |  | 0
| T kos DN 80 / odcep DN 80 | T piece DN 80 / branch DN 80 | kos | 6 |  | 0
| redukcija DN 15 / DN 10 | reduction DN 15 / DN 10 | kos | 2 |  | 0
| redukcija DN 20 / DN 15 | reduction DN 20 / DN 15 | kos | 72 |  | 0
| redukcija DN 25 / DN 20 | dN 25 / DN 20 reduction | kos | 48 |  | 0
| redukcija DN 40 / DN 32 | dN 40 / DN 32 reduction | kos | 32 |  | 0
| redukcija DN 40 / DN 32 | dN 40 / DN 32 reduction | kos | 16 |  | 0
| redukcija DN 50 / DN 40 | dN 50 / DN 40 reduction | kos | 8 |  | 0
| redukcija DN 65 / DN 50 | dN 65 / DN 50 reduction | kos | 2 |  | 0
| redukcija DN 80 / DN 65 | dN 80 / DN 65 reduction | kos | 2 |  | 0
| prirobnica DN 50 po EN1092, PN16, z vijačnim in tesnilnim materialom | flange DN 50 to EN1092, PN16, with bolting and sealing material | kpl | 8 |  | 0
| prirobnica DN 65 po EN1092, PN16, z vijačnim in tesnilnim materialom | flange DN 65 to EN1092, PN16, with bolting and sealing material | kpl | 2 |  | 0
| prirobnica DN 80 po EN1092, PN16, z vijačnim in tesnilnim materialom | flange DN 80 to EN1092, PN16, with bolting and sealing material | kpl | 10 |  | 0
| slepa prirobnica DN 80 po EN1092, PN16, z vijačnim in tesnilnim materialom | blind flange DN 80 to EN1092, PN16, with screw and sealing material | kpl | 2 |  | 0
2.13 | Tlačni preskus trdnosti in tesnenja sistema cevovodov, skladeno z opisom v "IZS Priročnik tlačnih preizkusov strojnih inštalacij", vključno s potrebnim materialom za izvedbo preizkusa, ter izdelavo pisnega poročila o uspešno opravljenem tlačnem preizkusu; | Pressure test of the strength and tightness of the piping system, as described in the "IZS Manual for Pressure Testing of Mechanical Installations", including the necessary materials for the test, and the production of a written report on the successful completion of the pressure test;
| preskusni tlak = 1,1 x najvišji delovni tlak = 9,5 barg | test pressure = 1,1 x maximum working pressure = 9,5 barg | kpl | 1 |  | 0
2.14 | Izpihovanje cevovodov z komprimiranim zrakom ali inertnim plinom (na primer dušik) v celotnem sistemu z namenom odstranjevanja nečistoč; | Blowing out the piping with compressed air or an inert gas (e.g. nitrogen) throughout the system to remove impurities; | kpl | 1 |  | 0
2.15 | Kvalifikacija zvarov ter izdelava dokumentacije o zvarih: | Weld qualification and documentation of welds:
| - zvare lahko izvajajo samo varilci s certifikatom pooblaščenih organizacij, | - welding can only be carried out by welders certified by approved organisations,
| - postopek vizualne kontrole zvarov, kontrolirajo se vsi zvari - 100% zvarov, | - visual weld inspection procedure, all welds are inspected - 100% of welds,
| - postopek kontrole s snemanja zvarov - 10% zvarov, kjer so enakomerno zastopani vsi premeri, | - weld stripping inspection procedure - 10% of welds where all diameters are equally represented,
| - označevanje zvarov, izdelava dokumentacije z dokazili o ustreznosti ter slikovnim materialom; | - marking welds, producing documentation with proof of conformity and pictorial material; | kpl | 1 |  | 0
| Podsistem vodnega hlajenja kompresorjev | Compressor water-cooling subsystem
2.16 | Ploščni izmenjevalnik toplote, sestavljive vijačene izvedbe, PN10, material AISI316 (ali boljši), debeline plošč 0,6mm, tesnila EPDM do 100°C trajne obremenitve, skladnost s PED. Tehnični podatki: | Plate heat exchanger, bolted design, PN10, material AISI316 (or better), plate thickness 0,6mm, EPDM seals up to 100°C permanent load, PED compliant. Technical data:
| - hlajenje hladilne vode za hlajenje kompresorjev | - cooling water for compressor cooling
| - izmenjana toplota 110 kW - hlajenje | - heat exchanged 110 kW - cooling
| - primar hladna stran P: hladilna voda, temp. vstopa 9°C, temp. izstopa 14°C, pretok 18,91m3/h, padec tlaka do 30kPa | - primary cold side P: cooling water, inlet temp. 9°C, outlet temp. 14°C, flow 18,91m3/h, pressure drop up to 30kPa
| - sekundar topla stran S: hladna voda, temp. vstopa 30°C, temp. izstopa 15°C, pretok 6,33m3/h, padec tlaka do 20kPa | - secondary hot side S: cold water, inlet temp. 30°C, outlet temp. 15°C, flow rate 6,33m3/h, pressure drop up to 20kPa
| - vsi priključki prirobnični PN10, primar P DN50, sekundar S DN50 | - all connections flanged PN10, primary P DN50, secondary S DN50
| - vključno s podstavkom prenosnika, pritrdilnim in tesnilnim materialom; | - including the laptop base, fixing and sealing materials;
| - dimenzije do: dolžina L x širina W x višina H = 500 x 400 x 1000 mm | - dimensions up to: length L x width W x height H = 500 x 400 x 1000 mm
| - komplet s toplotna parozaporna izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +105°C, debelina 50mm | - complete with thermal vapour barrier made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, classification B-s3-d0 according to EN13501-1, for temperatures -50 to +105°C, thickness 50mm
| - ustrezen proizvod IPROS HEX tip NT50M CDH-10 + toplotna izolacija ali enakovredno | - suitable product IPROS HEX type NT50M CDH-10 + thermal insulation or equivalent
| Oznaka: HE91.11 | Code: HE91.11 | kpl | 1 |  | 0
2.17 | Obtočna črpalka, dvojna izvedba PN10, z mokrim rotorjem, skladnost z ErP, elektronsko regulirana s PM motorjem in integrairanim frekvenčnim pretvornikom, inegrirano tipalo diferenčnega tlaka in temperature, upravljalnik nastavitev s prikazovalnikom parametrov, z internimi hidravličnimi, električnimi in komunikacijskimi povezavami, material črpalke siva litina z ustreznim tesnenjem za medij, prirobnična izvedba, vključno s protiprirobnicami, pritrdilnim in tesnilnim materialom. Tehnični podatki: | Circulation pump, double PN10 version, wet rotor, ErP compliant, electronically regulated with PM motor and integrated frequency converter, integrated differential pressure and temperature sensor, setting control with parameter display, with internal hydraulic, electrical and communication connections, pump material grey cast iron with suitable medium seal, flanged version, including counter flanges, fixing and sealing material. Technical data:
| - za obtok hladilne vode za kompresorje 15/30°C | - for cooling water circulation for compressors 15/30°C
| - deluje ena črpalka, druga rezerva, parametri za delovanje ene črpalke: pretok V= 6,4 m3/h, tlačna višina H= 80kPa, | - one pump in operation, another in reserve, parameters for operation of one pump: flow rate V= 6,4 m3/h, pressure head H= 80kPa,
| - elektro podatki Pel= 2x 0,34kW, 230V /1/ 50Hz, IP55, IE3 ali boljše | - electrical data Pel= 2x 0,34kW, 230V /1/ 50Hz, IP55, IE3 or better
| - ustreza proizvod GRUNDFOS tip MAGNA3 D 32-120 F ali enakovredno | - corresponds to GRUNDFOS product type MAGNA3 D 32-120 F or equivalent
| Oznaka: P91.081 | Code: P91.081 | kpl | 1 |  | 0
2.18 | Tipalo tlaka s pretvornikom, za mertev tlaka v območju od 0 do 6 barg (relativno) ter nastavljivim alarmnim tlakom, navojni priključek 1/2" (DN15), material nerjavno jeklo, električni podatki: napajanje 24V, izhod 4-20mA, kompletno z ventilom za tipalo tlaka 1/2" (DN15) ter tesnilnim in pritrdilnim materialom; | Pressure sensor with transducer, for pressure measurement in the range from 0 to 6 barg (relative) and adjustable alarm pressure, threaded connection 1/2" (DN15), material stainless steel, electrical data: power supply 24V, output 4-20mA, complete with pressure sensor valve 1/2" (DN15) and sealing and fixing material;
| - hladilna voda za kompresorje 15/30°C | - compressor cooling water 15/30°C
| - alarm, če je tlak p < 1,1 barg (nastavitev na tipalu ali programska nastavitev) | - alarm if pressure p < 1.1 barg (sensor setting or software setting)
| - ustreza proizvod ENDRESS+HAUSER tip PTC31B + PZAV ali enakovredno | - corresponds to ENDRESS+HAUSER product type PTC31B + PZAV or equivalent
| Oznaka: PIA91.011 | Code: PIA91.011 | kpl | 1 |  | 0
2.19 | Temperaturno tipalo, potopno, za merilno območje od 0 do +50°C, potopna dolžina L=100mm, v tulki iz nerjavnega materiala z navojnim priključkom 1/2" (DN15), električni podatki: napajanje 24V, izhod 4-20mA, komplet s pritrdilnim in tesnilnim materialom; | Temperature sensor, immersion, for measuring range 0 to +50°C, immersion length L=100mm, in stainless steel sleeve with threaded connection 1/2" (DN15), electrical data: power supply 24V, output 4-20mA, complete with fixing and sealing material;
| - hladilna voda za kompresorje 15/30°C | - compressor cooling water 15/30°C
| - ustreza proizvod ELEKTRONIKA PAHOR, tip CVB ali enakovredno | - corresponds to the product ELEKTRONIKA PAHOR, type CVB or equivalent
| Oznaka: TIC91.001, TI91.002 | Code: TIC91.001, TI91.002 | kpl | 2 |  | 0
2.20 | Ekspanzijska posoda za kompenzacijo toplotnih raztezkov medija v sistemu, PN10, skladno z direktivo EU o tlačni opremi PED, pokončna izvedba v obliki diska, membrana po DIN 4807, tlaki do 6 bar, temperature na membrani od 5 do 70°C, vključno s pritrdilnim in tesnilnim materialom; | Expansion vessel for compensation of thermal expansion of the medium in the system, PN10, in compliance with the EU Pressure Equipment Directive PED, upright disc design, diaphragm according to DIN 4807, pressures up to 6 bar, diaphragm temperatures from 5 to 70°C, incl. fixing and sealing material;
| - hladilna voda za kompresorje 15/30°C | - compressor cooling water 15/30°C
| - prostornina ekspanzijske posode 50 litrov | - expansion tank capacity 50 litres
| - dimenzije: premer D x debelina H = ø540 x 320 mm | - dimensions: diameter D x thickness H = ø540 x 320 mm
| - z navojnim priključkom 3/4" (DN20), komplet z ventilom s ključavnico 3/4" (DN20) | - with 3/4" (DN20) threaded connection, complete with 3/4" (DN20) keyed valve
| - ustreza proizvod IMI PNEUMATEX tip SD 50.10 + DLV 20 ali enakovredno | - iMI PNEUMATEX product type SD 50.10 + DLV 20 or equivalent
| Oznaka: EPS 91.12 | Code: EPS 91.12 | kpl | 1 |  | 0
2.21 | Varnostni ventil po TRD 721, PN16, varnostna funkcija izpusta medija zaradi toplotnih raztezkov v sistemu, vzmetno delovanje, možnost ročnega odzračenja, prostor vzmeti zaščiten z membrano, prirobnična izvedba, vključno s pritrdilnim in tesnilnim materialom; | Safety valve according to TRD 721, PN16, safety function of medium discharge due to thermal expansion in the system, spring operation, manual venting possible, spring space protected by diaphragm, flanged version, including fixing and sealing material;
| - hladilna voda za kompresorje 15/30°C | - compressor cooling water 15/30°C
| - tlak odpiranja 5,0 barg, | - opening pressure 5,0 barg,
| - z navojnima priključkoma DN 20 / 32, komplet z ventilom s ključavnico 3/4" (DN20) | - with threaded connections DN 20 / 32, complete with 3/4" (DN20) ratchet valve
| - ustreza proizvod IMI PNEUMATEX tip DSV 20 - 5.0 DGH + DLV 20 ali enakovredno | - iMI PNEUMATEX product type DSV 20 - 5.0 DGH + DLV 20 or equivalent
| Oznaka: VV91.13, VV91.14 | Code: VV91.13, VV91.14 | kpl | 2 |  | 0
2.22 | Regulacijski ventil, prehodni, z elektromotornim zveznim pogonom, 24V, IP54, PN16, material ventila nikljana medenina, nerjavno jeklo / EPDM, navojna izvedba, komplet z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Control valve, intermediate, with continuous electromotor drive, 24V, IP54, PN16, valve material nickel-plated brass, stainless steel / EPDM, threaded version, complete with two threaded Dutchmen, fixing and sealing material;
| - hladilna voda za kompresorje 15/30°C | - compressor cooling water 15/30°C
| DN 50, kvs= 40 m3/h - ustreza proizvod BELIMO tip R2050-40-S4 +SR24A-SR ali enakovredno Oznaka: VY91.051 | DN 50, kvs= 40 m3/h - corresponds to BELIMO product type R2050-40-S4 +SR24A-SR or equivalent Code: VY91.051 | kpl | 1 |  | 0
2.23 | Krogelni ventil s priklučkom za praznenje oz. polnenje, navojna izvedba, PN16, z ročico, material medenina / PTFE, vključno s pritrdilnim in tesnilnim materialom: | Ball valve with union for emptying or filling, threaded version, PN16, with handle, material brass/PTFE, incl. fitting and sealing material:
| - hladilna voda za kompresorje 15/30°C | - compressor cooling water 15/30°C
| - ustreza proizvod KOVINA ali END ARMATUREN ali enakovredno | - corresponds to the product METAL or END ARMATUREN or equivalent
| DN 15 | DN 15 | kos | 10 |  | 0
2.24 | Krogelni ventil, navojna izvedba, PN16, z ročico, material medenina / PTFE, vključno s pritrdilnim in tesnilnim materialom: | Ball valve, threaded version, PN16, with lever, material brass/PTFE, incl. mounting and sealing material:
| - hladilna voda za kompresorje 15/30°C | - compressor cooling water 15/30°C
| - ustreza proizvod KOVINA ali END ARMATUREN ali enakovredno | - corresponds to the product METAL or END ARMATUREN or equivalent
| DN 40 | DN 40 | kos | 4 |  | 0
| DN 50 | DN 50 | kos | 3 |  | 0
2.25 | Nepovratni ventil, z vmetjo, navojna izvedba, PN16, material medenina, vzmet nerjavno jeklo / NBR, vključno s pritrdilnim in tesnilnim materialom | Non-return valve, with spout, threaded version, PN16, material brass, spring stainless steel/NBR, incl. mounting and sealing material
| - hladilna voda za kompresorje 15/30°C | - compressor cooling water 15/30°C
| - ustreza proizvod KOVINA ali END ARMATUREN ali enakovredno | - corresponds to the product METAL or END ARMATUREN or equivalent
| DN 40 | DN 40 | kos | 2 |  | 0
2.26 | Izločevalnika nečistoč in magnetita, ciklonsko izločanje, P10, skladno s PED, material medenina, navojni priključki, s krogelnim ventilom DN15 za izpust nečistoč, vključno z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Impurity and magnetite eliminators, cyclone elimination, P10, PED-compliant, material brass, threaded connections, with DN15 ball valve for impurity discharge, incl. threaded dutch, fixing and sealing material;
| - hladilna voda za kompresorje 15/30°C | - compressor cooling water 15/30°C
| DN 50 - ustreza proizvod IMI PMEUMATEX tip Zeparo Cyclone ZCD ali enakovredno | DN 50 - corresponds to IMI PMEUMATEX product type Zeparo Cyclone ZCD or equivalent | kpl | 1 |  | 0
2.27 | Ventil za hidravlično uravnoteženje, nastavitev pretoka, navojna izvedba, PN16, s priključkoma za priklop naprave za merjenje pretoka, z zaporno funkcijo brez prenastavitve pretoka, material siva litina, nerjavno jeklo, EPDM, PTFE, vključno z navojnima holandcema, pritrdilnim in tesnilnim materialom; | Hydraulic balancing valve, flow adjustment, threaded version, PN16, with two connections for connection of flow measuring device, with shut-off function without flow reset, material grey cast iron, stainless steel, EPDM, PTFE, incl. threaded plugs, fastening and sealing material;
| - hladilna voda za kompresorje 15/30°C | - compressor cooling water 15/30°C
| - ustreza proizvod IMI TA tip STAD ali enakovredno | - the product conforms to IMI TA type STAD or equivalent
| DN 40 | DN 40 | kos | 2 |  | 0
2.28 | Kompenzator vibracij iz strojne opreme na cevovod, prirobnična izvedba, PN16, material pocinkano jeklo, EPDM, vključno s pritrdilnim in tesnilnim materialom; | Vibration compensator from hardware to pipeline, flanged version, PN16, material galvanised steel, EPDM, including fixing and sealing material;
| - hladilna voda za kompresorje 15/30°C | - compressor cooling water 15/30°C
| - ustreza proizvod END ARMATUREN tip KP ali enakovredno | - corresponds to END ARMATUREN type KP or equivalent
| DN 40 | DN 40 | kpl | 4 |  | 0
2.29 | Termometer, tekočinski, dolžina skale 100mm, kotni 90°, potopna dolžina 40mm, v zaščitni cevi - tulki, klasa točnosti 1%, navojni priključek 1/2" (DN15), material medenina, aluminij, steklo, nerjavno jeklo, vključno s pritrdilnim in tesnilnim materialom; | Thermometer, liquid, scale length 100mm, angle 90°, immersion length 40mm, in protective tube - sleeves, accuracy class 1%, threaded connection 1/2" (DN15), material brass, aluminium, glass, stainless steel, incl. fixing and sealing material;
| - ustreza proizvod INOL ali enakovredno | - corresponds to INOL or equivalent
| - hladilna voda za kompresorje 15/30°C | - compressor cooling water 15/30°C
| - območjem merjenja: 0 do 100°C | - measuring range: 0 to 100°C | kpl | 6 |  | 0
2.30 | Manometer ø 68 mm, klasa točnosti 1,6% po EN837-1, navojni radialni priključek, material medenina, nerjavno jeklo, steklo / EPDM, komplet z manometrskim ventilom DN15 (1/2"), vključno s pritrdilnim in tesnilnim materialom; | Pressure gauge ø 68 mm, accuracy class 1.6% according to EN837-1, threaded radial connection, material brass, stainless steel, glass / EPDM, complete with pressure gauge valve DN15 (1/2"), incl. mounting and sealing material;
| - ustreza proizvod INOL ali enakovredno | - corresponds to INOL or equivalent
| - hladilna voda za kompresorje 15/30°C | - compressor cooling water 15/30°C
| - območjem merjenja: 0 do 10 bar | - measuring range: 0 to 10 bar | kpl | 7 |  | 0
2.31 | Avtomatski odzračevalnik, PN10 material medenina / PTFE, vključno z navojnim holandcem in tesnilnim materialom; | Automatic vent, PN10 material brass/PTFE, incl. threaded dutch and sealing material;
| - hladilna voda za kompresorje 15/30°C | - compressor cooling water 15/30°C
| DN15 - ustreza proizvod IMI PNEUMATEX tip ZUT ali enakovredno | DN15 - corresponds to IMI PNEUMATEX product type ZUT or equivalent | kpl | 2 |  | 0
2.32 | Odzračitveni lonček, volumen V ≥ 2 litra, izdelan iz cevi DN100, ø114x3,6 mm po EN10216-1 (DIN2448), dolžina L=300mm, z bombiranima zaključkoma, material P235TR2 (St37), vključno z varilnim materialom; | Discharge cup, volume V ≥ 2 litres, made of DN100 pipe, ø114x3,6 mm according to EN10216-1 (DIN2448), length L=300mm, with bomb-coated ends, material P235TR2 (St37), incl. welding consumables;
| - hladilna voda za kompresorje 15/30°C | - compressor cooling water 15/30°C | kpl | 4 |  | 0
2.33 | Jeklene srednje težke šivne cevi izdelane po EN10255 (DIN2440), material S195T (St33.2), vključno z oblikovnimi kosi (loki, redukcije, T kosi, ...) in varilnim materialom, | Medium-weight seamed steel tubes manufactured to EN10255 (DIN2440), material S195T (St33.2), including forming pieces (bows, reducers, T-pieces, etc.) and welding consumables,
| komplet s pocinkanim obešalnim materialom (navojne palice, konzole, sidra, ...) in cevnimi objemkami z oblogo za dušenje hrupa, ustreza proizvod HILTI ali SIKLA, ali enakovredno; | complete with galvanised suspension material (threaded rods, brackets, anchors, etc.) and pipe clamps with noise damping lining, suitable for HILTI or SIKLA, or equivalent;
| - predizolirane obemke za hladilna voda za kompresorje 15/30°C | - pre-insulated cooling water sleeves for 15/30°C compressors
| DN 15, ø 21,3 x 2,65 | DN 15, ø 21,3 x 2,65 | m | 30 |  | 0
| DN 20, ø 26,9 x 2,65 | DN 20, ø 26,9 x 2,65 | m | 6 |  | 0
| DN 25, ø 33,7 x 3,25 | DN 25, ø 33,7 x 3,25 | m | 6 |  | 0
| DN 32, ø 42,4 x 3,25 | DN 32, ø 42,4 x 3,25 | m | 6 |  | 0
| DN 40, ø 48,3 x 3,25 | DN 40, ø 48,3 x 3,25 | m | 60 |  | 0
| DN 50, ø 60,3 x 3,65 | DN 50, ø 60,3 x 3,65 | m | 72 |  | 0
| 90°lok DN 15, ø 21,3 x 2,65 | 90°lok DN 15, ø 21,3 x 2,65 | kos | 7.5 |  | 0
| 90°lok DN 20, ø 26,9 x 2,65 | 90°lok DN 20, ø 26,9 x 2,65 | kos | 1.5 |  | 0
| 90°lok DN 25, ø 33,7 x 3,25 | 90°lok DN 25, ø 33,7 x 3,25 | kos | 1.5 |  | 0
| 90°lok DN 32, ø 42,4 x 3,25 | 90°lok DN 32, ø 42,4 x 3,25 | kos | 1.5 |  | 0
| 90°lok DN 40, ø 48,3 x 3,25 | 90°lok DN 40, ø 48,3 x 3,25 | kos | 15 |  | 0
| 90°lok DN 50, ø 60,3 x 3,65 | 90°lok DN 50, ø 60,3 x 3,65 | kos | 16 |  | 0
| T kos DN 25 / odcep DN 15 | T piece DN 25 / branch DN 15 | kos | 2 |  | 0
| T kos DN 25 / odcep DN 20 | T piece DN 25 / branch DN 20 | kos | 2 |  | 0
| T kos DN 40 / odcep DN 15 | T piece DN 40 / branch DN 15 | kos | 2 |  | 0
| T kos DN 40 / odcep DN 20 | T piece DN 40 / branch DN 20 | kos | 2 |  | 0
| T kos DN 50 / odcep DN 15 | T piece DN 50 / branch DN 15 | kos | 8 |  | 0
| T kos DN 50 / odcep DN 25 | T piece DN 50 / branch DN 25 | kos | 1 |  | 0
| T kos DN 50 / odcep DN 40 | T piece DN 50 / branch DN 40 | kos | 2 |  | 0
| redukcija DN 20 / DN 15 | reduction DN 20 / DN 15 | kos | 2 |  | 0
| redukcija DN 25 / DN 20 | dN 25 / DN 20 reduction | kos | 2 |  | 0
| redukcija DN 32 / DN 25 | dN 32 / DN 25 reduction | kos | 2 |  | 0
| redukcija DN 40 / DN 32 | dN 40 / DN 32 reduction | kos | 2 |  | 0
| redukcija DN 50 / DN 32 | dN 50 / DN 32 reduction | kos | 2 |  | 0
| redukcija DN 50 / DN 40 | dN 50 / DN 40 reduction | kos | 2 |  | 0
| prirobnica DN 32 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 32 to EN1092, PN16, including bolting and sealing material | kpl | 2 |  | 0
| prirobnica DN 40 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 40 to EN1092, PN16, including bolting and sealing material | kpl | 4 |  | 0
| prirobnica DN 50 po EN1092, PN16, vključno z vijačnim in tesnilnim materialom | flange DN 50 to EN1092, PN16, including bolting and sealing material | kpl | 2 |  | 0
2.34 | Čiščenje in barvanje jeklenih podpor iz ogljikovega jekla, odstranitev rje do kovinskega sijaja, dvakratni premaz s temeljnim antikorozijskim barvami ter dvakratni premaz s prekrivno barvo: antikorozijska zaščita s temeljnimi in prekrivnimi barvami mora biti obstojna na temperature v območju od -20 do +80°C in se mora izvesti v skladu z EN ISO 12944 z življenjsko dobo: visoko trajanje H (več kot 15 let). | Cleaning and painting of carbon steel supports, rust removal to a metallic sheen, two coats of anti-corrosion primer and two coats of overcoat: the anti-corrosion protection with primer and overcoat must be resistant to temperatures in the range -20 to +80°C and must be carried out in accordance with EN ISO 12944 with a service life of: high durability H (more than 15 years).
| - hladilna voda za kompresorje 15/30°C | - compressor cooling water 15/30°C | m2 | 32 |  | 0
2.35 | Toplotna izolacija cevovodov in cevnih armatur s parozaporno izolacijo iz elastomerne pene na osnovi sintetične gume po EN14304 z naslednjimi lastnostmi: ne vsebuje CFC, µ≥7000 po EN13469, λ≤0,040W/mK po EN ISO8497, požarna klasifikacija B-s3-d0 po EN13501-1, za temperature -50 do +110°C, lepljeno na cevovode in armature z originalnim lepilom proizvajalca, vključno s trakovi za šive; | Thermal insulation of pipelines and pipe fittings with vapour barrier insulation made of elastomeric foam based on synthetic rubber according to EN14304 with the following properties: CFC-free, µ≥7000 according to EN13469, λ≤0,040W/mK according to EN ISO8497, fire classification B-s3-d0 according to EN13501-1, for temperatures from -50 to +110°C, bonded to pipelines and fittings with the original manufacturer's adhesive, including seam tapes;
| - ustreza proizvod ARMACELL tip Armaflex ACE Plus ali enakovredno | - corresponds to ARMACELL product type Armaflex ACE Plus or equivalent
| DN 15, ø 19 ; debelina 13 mm | DN 15, ø 19 ; thickness 13 mm | m | 40 |  | 0
| DN 20, ø 23 ; debelina 19 mm | DN 20, ø 23 ; thickness 19 mm | m | 8 |  | 0
| DN 25, ø 29 ; debelina 19 mm | DN 25, ø 29 ; thickness 19 mm | m | 8 |  | 0
| DN 32, ø 35 ; debelina 25 mm | DN 32, ø 35 ; thickness 25 mm | m | 8 |  | 0
| DN 40, ø 41 ; debelina 25 mm | DN 40, ø 41 ; thickness 25 mm | m | 80 |  | 0
| DN 50, ø 53 ; debelina 40 mm | DN 50, ø 53 ; thickness 40 mm | m | 100 |  | 0
2.36 | Tlačni preskus trdnosti in tesnenja sistema cevovodov, skladeno z opisom v "IZS Priročnik tlačnih preizkusov strojnih inštalacij", vključno s potrebnim materialom za izvedbo preizkusa, ter izdelavo pisnega poročila o uspešno opravljenem tlačnem preizkusu; | Pressure test of the strength and tightness of the piping system, as described in the "IZS Manual for Pressure Testing of Mechanical Installations", including the necessary materials for the test, and the production of a written report on the successful completion of the pressure test;
| - hladilna voda za kompresorje 15/30°C | - compressor cooling water 15/30°C
| preskusni tlak = 5,0 barg | test pressure = 5,0 barg | kpl | 1 |  | 0
2.37 | Izpiranje cevovodov s sanitarno hladno vodo v celotnem sistemu novoinstaliranih razvodov z namenom odstranjevanja nečistoč v sistemu cevovodov, vključno s čiščenjem lovilnikov nesnage in drugih elementov; | Flushing of sanitary cold water piping throughout the newly installed piping system to remove impurities in the piping system, including cleaning of debris traps and other elements;
| - hladilna voda za kompresorje 15/30°C | - compressor cooling water 15/30°C | kpl | 1 |  | 0
2.38 | Kvalifikacija zvarov ter izdelava dokumentacije o zvarih: | Weld qualification and documentation of welds:
| - zvare lahko izvajajo samo varilci s certifikatom pooblaščenih organizacij, | - welding can only be carried out by welders certified by approved organisations,
| - postopek vizualne kontrole zvarov, kontrolirajo se vsi zvari - 100% zvarov, | - visual weld inspection procedure, all welds are inspected - 100% of welds,
| - označevanje zvarov, izdelava dokumentacije z dokazili o ustreznosti ter slikovnim materialom; | - marking welds, producing documentation with proof of conformity and pictorial material;
| - hladilna voda za kompresorje 15/30°C | - compressor cooling water 15/30°C | kpl | 1 |  | 0
| Skupne postavke | Total items
2.39 | Ognjeodporna tesnilna masa, vgradnja na prehodu cevovodov skozi zid med požarnima sektortjema, požarna odpornost 90 minut, ustreza proizvod HILTI ali enakovredno. | Fire-resistant sealant, for installation at the transition of pipelines through the wall between the two fire sectors, fire resistance 90 minutes, equivalent to HILTI or equivalent.
| Vsak prehod mora biti označen z nalepko ali tablico z osnovnimi požarnimi podatki; | Each passageway must be marked with a sticker or placard with basic fire information; | kpl | 1 |  | 0
2.40 | Preizkusno obratovanje delovanja sistema v obsegu: | Operational test of the system in scope:
| - pregled delovanja kompresorja, kontrola parametrov in nastavitve (delovni tlak, kapaciteta, točka rosišča itd). Aktivnost izvaja pooblaščena oseba s strani dobavitelja kompresorja. | - inspection of the compressor operation, checking parameters and settings (operating pressure, capacity, dew point, etc.). The activity shall be carried out by a person authorised by the compressor supplier.
| - pregled tlačne posode in varnostnega ventila, | - inspection of the pressure vessel and safety valve,
| - pregled delovanja elektronskega odvajalnika kondenzata, | - checking the operation of the electronic condensate drain,
| - pregled filtrov za komprimiran zrak, | - inspection of compressed air filters,
| - pregled inštalacije cevovodov, armatur in opreme | - inspection of piping, fittings and equipment
| - pregled odjemnih mest; | - a review of the customer sites;
| Preizkusno obratovanje traja neprekinjeno 72 ur. | The test operation shall be continuous for 72 hours. | kpl | 1 |  | 0
2.41 | Napisne ploščice iz nerjavne pločevine z vgravirano oznako po shemi za opremo in armature, kompletno z jekleno pritrdilno žico ali visoko kvalotetne nalepke; visoko trajanje H (več kot 15 let) | Stainless steel nameplates with engraved marking according to the scheme for fittings and fixtures, complete with steel fixing wire or high quality labels; high durability H (more than 15 years) | kpl | 1 |  | 0
2.42 | Samolepilne puščice za označitev smeri pretoka ter z napisom vrste medija; visoko trajanje H (več kot 15 let) | Self-adhesive arrows to indicate direction of flow and type of media; high H lifetime (more than 15 years) | kpl | 1 |  | 0
2.43 | Izdelava montažnih risb za izvedbo inštalacij med gradnjo objekta, kot so: detajli priključkov, montažne skice, montažni detajli, ipd. | Preparation of assembly drawings for the installation of services during the construction of the building, such as: connection details, assembly sketches, assembly details, etc. | kpl | 1 |  | 0
2.44 | Kvalifikacije montaže IQ-pregledi (instalation qualification) po GEP Commissioning protokolu in dokumentiranje kvalifikacije montaže, vključno z odpravo prvotnih napak montaže; | Installation qualification IQ-checks (installation qualification) according to the GEP Commissioning Protocol and documentation of installation qualification, including correction of original installation faults; | kpl | 1 |  | 0
2.45 | Meritve delovanja OQ-kvalifikacija (operation qualification) ter dokumentiranje meritev delovanja, vključno z nastavitvijo parametrov; | OQ (operation qualification) measurements and documentation of performance measurements, including parameter settings; | kpl | 1 |  | 0
2.46 | Posnetki izvedenega stanja, sprotno beleženje vseh sprememb nastalih med izvedbo, vrisovanje in vpisovanje v PZI projektno dokumentacijo; | Recording of the as-built condition, keeping a running record of any changes made during the execution, plotting and recording in the PZI project documentation; | kpl | 1 |  | 0
2.47 | Stenska shema sistema, vloženo v zaščitni okvir s prosojnim umetnim steklomo (plastika) ali plastificirano, vključno s pritrditvijo na notranjo steno v strojnici objekta; | Wall diagram of the system, enclosed in a protective frame with transparent plastic or plasticised glass, including fixing to an internal wall in the mechanical room of the building; | kpl | 1 |  | 0
2.48 | Primopredajna dokumentacija, ki mora vsebovati: izjave, dokazilo o zanesljivosti objekta, certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo, obratovanje in vzdrževanje ter ostalo primopredajno dokumantacijo. Predaja se v dveh mapiranih izvodih ter en izvod v elektronski obliki; | The handover documentation, which shall include: declarations, proof of the reliability of the facility, certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use, operation and maintenance, and other handover documentation. It shall be handed over in two mapped copies and one copy in electronic form; | kpl | 1 |  | 0
| KOMPRIMIRAN ZRAK | COMPRESSED AIR |  |  |  | 0

## 4.10.3_TehnicniPlini
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.10 | STROJNA DELA | MECHANICAL WORKS
4.10.3 | TEHNIČNI PLINI | TECHNICAL GAS |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
3 | TEHNIČNI PLINI | TECHNICAL GAS
| Izvajalec del ter dobavitelj opreme in inštalacij tehničnih plinov za laboratorije mora imeti certifikat za delo s tehničnimi plini v Sloveniji. Spisek pooblaščenih podjetij vodi Gospodarsko interesno združenje za tehnične pline Slovenije. | The contractor and the supplier of equipment and installations of technical gases for laboratories must be certified to work with technical gases in Slovenia. The list of certified companies is maintained by the Economic Interest Association for Technical Gases of Slovenia.
| Vse postavke v nadalevanju zajemajo dobavo in montažo (razen tam kjer je to posebej navedeno). | All items below include delivery and installation (except where specifically indicated).
3.1 | Visokotlačna jeklenka za laboratorijski tehnični plin, PN300, za tlak plina 200 bar ali 300 bar, prostornina 50 litrov, označeno po standardu SIST EN 1089-3, dimenzija D x L = ø230 x 1640 mm, teža 80 kg, vsebina 10 Nm3 ali 15 Nm3 tehničnega plina, vključno z zapornim ventilom na jeklenki, varovalnim čepom ter varnostno verigo za pritrditev v varnostno omaro za jeklenke; | High-pressure cylinder for laboratory technical gas, PN300, for gas pressure 200 bar or 300 bar, capacity 50 litres, marked according to SIST EN 1089-3, dimensions D x L = ø230 x 1640 mm, weight 80 kg, capacity 10 Nm3 or 15 Nm3 of technical gas, incl. stop valve on cylinder, safety plug and safety chain for fixing in the cylinder safety cabinet;
| - ustreza proizvod MESSER ali enakovredno; | - corresponds to a MESSER product or equivalent;
| - za laboratorijski tehnični plin: | - for laboratory industrial gas:
| Ar … argon | Ar ... argon | kpl | 14 |  | 0
| Ar 4.6 … argon 4.6 = argon 99,996% | Ar 4.6 ... argon 4.6 = argon 99.996% | kpl | 10 |  | 0
| CH4 … metan | CH4 ... methane | kpl | 2 |  | 0
| CO … ogljikov monoksid | CO ... carbon monoxide | kpl | 1 |  | 0
| CO2 … ogljikov dioksid | CO2 ... carbon dioxide | kpl | 6 |  | 0
| H2 … vodik | H2 ... hydrogen | kpl | 4 |  | 0
| He … helij | He ... helij | kpl | 7 |  | 0
| N2 … dušik | N2 ... nitrogen | kpl | 19 |  | 0
| N2 5.0 … dušik 5.0 = dušik 99,999% | N2 5.0 ... nitrogen 5.0 = nitrogen 99.999% | kpl | 1 |  | 0
| N2O … dušikov oksidul | N2O ... nitrous oxide | kpl | 1 |  | 0
| NH3 … amonjak | NH3 ... ammonia | kpl | 2 |  | 0
| O2 … kisik | O2 ... oxygen | kpl | 11 |  | 0
| SZ … sintetični zrak | SZ ... synthetic air | kpl | 2 |  | 0
3.2 | Visokotlačna nerjavna cevi, za priklop visokotlačne jeklenke na ekspanzijsko reducirno postajo, ustreznost za laboratorijske tehnične pline, material AISI 316L (W.Nr 1.4435), notranja površinska hrapavost Ra≤0,8µm, za tlake 300 bar, vključno s pritrdilnim in tesnilnim materialom; | High-pressure stainless steel hose, for connection of high-pressure cylinder to expansion reduction station, suitable for laboratory technical gases, material AISI 316L (W.Nr 1.4435), internal surface roughness Ra≤0,8µm, for pressures of 300 bar, incl. fastening and sealing material;
| - za laboratorijski tehnični plin: | - for laboratory industrial gas:
| Ar … argon | Ar ... argon | kpl | 14 |  | 0
| Ar 4.6 … argon 4.6 = argon 99,996% | Ar 4.6 ... argon 4.6 = argon 99.996% | kpl | 10 |  | 0
| CH4 … metan | CH4 ... methane | kpl | 2 |  | 0
| CO … ogljikov monoksid | CO ... carbon monoxide | kpl | 1 |  | 0
| CO2 … ogljikov dioksid | CO2 ... carbon dioxide | kpl | 6 |  | 0
| H2 … vodik | H2 ... hydrogen | kpl | 4 |  | 0
| He … helij | He ... helij | kpl | 7 |  | 0
| N2 … dušik | N2 ... nitrogen | kpl | 19 |  | 0
| N2 5.0 … dušik 5.0 = dušik 99,999% | N2 5.0 ... nitrogen 5.0 = nitrogen 99.999% | kpl | 1 |  | 0
| N2O … dušikov oksidul | N2O ... nitrous oxide | kpl | 1 |  | 0
| NH3 … amonjak | NH3 ... ammonia | kpl | 2 |  | 0
| O2 … kisik | O2 ... oxygen | kpl | 11 |  | 0
| SZ … sintetični zrak | SZ ... synthetic air | kpl | 2 |  | 0
3.3 | Ekspanzijska reducirna postaja laboratorijskega tehničnega plina iz tlaka 200 ali 300 bar na 10 bar za priklop ene plinske jeklenke, PN300, izdelano kot kompaktna naprava sestavljeno iz: priklop na jeklenko, visokotlačni zaporni ventil, ventil za izpihovanje, regulator tlaka, manomater tlaka jeklenke, manomater tlaka omreržja, oddušni varnostni ventil, pnevmatski ventil za omrežje (normalno zaprt), priklop na omrežje, vključno s pritrdilnim in tesnilnim materialom; | Expansion reducing station for laboratory technical gas from 200 or 300 bar to 10 bar for connection to one gas cylinder, PN300, manufactured as a compact unit, comprising: cylinder connection, high pressure stop valve, blow-off valve, pressure regulator, cylinder pressure gauge, pressure gauge of the fitting, pressure gauge of the fitting, venting safety valve, pneumatic valve for mains (normally closed), connection to mains, including fitting and sealing material;
| - ustreza proizvod SPECTRON tip BM55-1 ali enakovredno | - corresponds to SPECTRON product type BM55-1 or equivalent
| - za laboratorijski tehnični plin: | - for laboratory industrial gas:
| Ar … argon | Ar ... argon | kpl | 7 |  | 0
| CH4 … metan | CH4 ... methane | kpl | 2 |  | 0
| CO … ogljikov monoksid | CO ... carbon monoxide | kpl | 1 |  | 0
| CO2 … ogljikov dioksid | CO2 ... carbon dioxide | kpl | 6 |  | 0
| H2 … vodik | H2 ... hydrogen | kpl | 4 |  | 0
| He … helij | He ... helij | kpl | 4 |  | 0
| N2 … dušik | N2 ... nitrogen | kpl | 7 |  | 0
| N2 5.0 … dušik 5.0 = dušik 99,999% | N2 5.0 ... nitrogen 5.0 = nitrogen 99.999% | kpl | 1 |  | 0
| N2O … dušikov oksidul | N2O ... nitrous oxide | kpl | 1 |  | 0
| NH3 … amonjak | NH3 ... ammonia | kpl | 2 |  | 0
| O2 … kisik | O2 ... oxygen | kpl | 6 |  | 0
| SZ … sintetični zrak | SZ ... synthetic air | kpl | 2 |  | 0
3.4 | Ekspanzijska reducirna postaja laboratorijskega tehničnega plina iz tlaka 200 bar ali 300 bar na 10 bar za istočasen priklop dveh plinskih jeklenk, z avtomatskim preklopom iz delovne na rezervno jeklenko, PN300, izdelano kot kompaktna naprava sestavljeno iz: priklop na levo in desno jeklenko, dva visokotlačna zaporna ventila, dva ventila za izpihovanje, dva regulatorja tlaka, dva manomatra tlakov jeklenk, manomater tlaka omreržja, oddušni varnostni ventil, pnevmatski ventil za omrežje (normalno zaprt), priklop na omrežje in avtomatska preklopna naprava; | Expansion reduction station for laboratory technical gas from 200 bar or 300 bar to 10 bar for simultaneous connection of two gas cylinders, with automatic change-over from working to reserve cylinder, PN300, designed as a compact unit, comprising: connection to left and right cylinder, two high-pressure stop valves, two blow-off valves, two pressure regulators, two cylinder pressure gauges, a cabinet pressure gauge, a venting safety valve, a pneumatic valve for the mains (normally closed), a connection to the mains and an automatic change-over device;
| - ustreza proizvod SPECTRON tip BM55-2 U ali enakovredno | - corresponds to SPECTRON product type BM55-2 U or equivalent
| - za laboratorijski tehnični plin: | - for laboratory industrial gas:
| Ar … argon | Ar ... argon | kpl | 4 |  | 0
| Ar 4.6 … argon 4.6 = argon 99,996% | Ar 4.6 ... argon 4.6 = argon 99.996% | kpl | 4 |  | 0
| He … helij | He ... helij | kpl | 2 |  | 0
| N2 … dušik | N2 ... nitrogen | kpl | 6 |  | 0
| O2 … kisik | O2 ... oxygen | kpl | 3 |  | 0
3.5 | Visokotlačna ekspanzijska reducirna postaja laboratorijskega tehničnega plina iz tlaka 200 ali 300 bar na 200 bar za priklop ene plinske jeklenke, PN300, izdelano kot kompaktna naprava sestavljeno iz: priklop na jeklenko, visokotlačni zaporni ventil, ventil za izpihovanje, regulator tlaka, manomater tlaka jeklenke, manomater tlaka omreržja, oddušni varnostni ventil, pnevmatski ventil za omrežje (normalno zaprt), priklop na omrežje, vključno s pritrdilnim in tesnilnim materialom; | High-pressure expansion reduction station for laboratory technical gas from 200 or 300 bar to 200 bar for connection to one gas cylinder, PN300, manufactured as a compact unit, comprising: cylinder connection, high-pressure stop valve, blow-off valve, pressure regulator, cylinder pressure gauge, pressure gauge for the cabinet, vent safety valve, pneumatic valve for the mains (normally closed), connection to the mains, including fixing and sealing material;
| - ustreza proizvod SPECTRON ali SWAGELOK ali enakovredno | - corresponds to SPECTRON or SWAGELOK or equivalent
| - za laboratorijski tehnični plin: | - for laboratory industrial gas:
| N2 (200bar) … dušik (200bar) | N2 (200bar) ... nitrogen (200bar) | kpl | 2 |  | 0
3.6 | Varnostna armatura za laboratorijski tehnični plin v skladu z EN 730-1, ISO 5175, z naslednjimi funkcijami: plinski nepovratni ventil NV, plamenska zapora FA, termično varovalo TV, PN15, materiala nerjavno jeklo, vključno z pritrdilnim in tesnilnim materialom; | Safety fittings for laboratory technical gas in accordance with EN 730-1, ISO 5175, with the following functions: gas non-return valve NV, flame arrestor FA, thermal fuse TV, PN15, material stainless steel, including fixing and sealing material;
| - ustreza proizvod IBEDA tip DG91N VA ali enakovredno | - corresponds to IBEDA product type DG91N VA or equivalent
| - za laboratorijski tehnični plin: | - for laboratory industrial gas:
| CH4 … metan | CH4 ... methane | kpl | 13 |  | 0
| CO … ogljikov monoksid | CO ... carbon monoxide | kpl | 4 |  | 0
| H2 … vodik | H2 ... hydrogen | kpl | 15 |  | 0
| NH3 … amonjak | NH3 ... ammonia | kpl | 13 |  | 0
3.7 | Regulacijska grupa laboratorijskega odjemnega mesta tehničnega plina, sestavljeno iz: zapornega ventila, reducirnega ventila z manometrom in igličasti ventil, PN40, materiali kromana medenina / nerjavno jeklo / viton, vstopni tlak 10 bar, izstopni tlak od 0 do 4 bar, vključno s pritrdilnim in tesnilnim materialom; | Control group for laboratory technical gas outlet, consisting of: stop valve, pressure reducing valve with manometer and needle valve, PN40, materials chromed brass/stainless steel/viton, inlet pressure 10 bar, outlet pressure 0 to 4 bar, including fixing and sealing material;
| - ustreza proizvod SPECTRON tip EM55-1 ali enakovredn | - corresponds to SPECTRON product type EM55-1 or equivalent
| - za laboratorijski tehnični plin: | - for laboratory industrial gas:
| Ar … argon | Ar ... argon | kpl | 28 |  | 0
| Ar 4.6 … argon 4.6 = argon 99,996% | Ar 4.6 ... argon 4.6 = argon 99.996% | kpl | 3 |  | 0
| CH4 … metan | CH4 ... methane | kpl | 11 |  | 0
| CO … ogljikov monoksid | CO ... carbon monoxide | kpl | 3 |  | 0
| CO2 … ogljikov dioksid | CO2 ... carbon dioxide | kpl | 15 |  | 0
| H2 … vodik | H2 ... hydrogen | kpl | 15 |  | 0
| He … helij | He ... helij | kpl | 27 |  | 0
| N2 … dušik | N2 ... nitrogen | kpl | 76 |  | 0
| N2 5.0 … dušik 5.0 = dušik 99,999% | N2 5.0 ... nitrogen 5.0 = nitrogen 99.999% | kpl | 16 |  | 0
| N2O … dušikov oksidul | N2O ... nitrous oxide | kpl | 1 |  | 0
| NH3 … amonjak | NH3 ... ammonia | kpl | 11 |  | 0
| O2 … kisik | O2 ... oxygen | kpl | 26 |  | 0
| SZ … sintetični zrak | SZ ... synthetic air | kpl | 10 |  | 0
3.8 | Regulacijska grupa laboratorijskega odjemnega mesta tehničnega plina, sestavljeno iz: zapornega ventila, reducirnega ventila z manometrom in igličasti ventil, PN40, materiali kromana medenina / nerjavno jeklo / viton, vstopni tlak 10 bar, izstopni tlak od 0 do 4 bar, vključno s pritrdilnim in tesnilnim materialom; | Control group for laboratory technical gas outlet, consisting of: stop valve, pressure reducing valve with manometer and needle valve, PN40, materials chromed brass/stainless steel/viton, inlet pressure 10 bar, outlet pressure 0 to 4 bar, including fixing and sealing material;
| - ustreza proizvod SPECTRON tip LE81 ali enakovredn | - corresponds to SPECTRON product type LE81 or equivalent
| DN15 - za laboratorijski tehnični plin: | dN15 - for laboratory technical gas:
| Ar … argon | Ar ... argon | kpl | 1 |  | 0
| Ar 4.6 … argon 4.6 = argon 99,996% | Ar 4.6 ... argon 4.6 = argon 99,996% | kpl | 1 |  | 0
| He … helij | He ... helij | kpl | 1 |  | 0
| N2 … dušik | N2 ... nitrogen | kpl | 1 |  | 0
3.9 | Visokotlačna regulacijska grupa laboratorijskega odjemnega mesta tehničnega plina, sestavljeno iz: zapornega ventila, reducirnega ventila z manometrom in igličasti ventil, PN40, materiali kromana medenina / nerjavno jeklo / viton, vstopni tlak 200 bar, izstopni tlak do 200 bar, vključno s pritrdilnim in tesnilnim materialom; | High pressure control group for laboratory technical gas outlet, consisting of: stop valve, pressure reducing valve with manometer and needle valve, PN40, materials chromed brass/stainless steel/viton, inlet pressure 200 bar, outlet pressure up to 200 bar, including fixing and sealing material;
| - ustreza proizvod SPECTRON ali SWAGELOK ali enakovredno | - corresponds to SPECTRON or SWAGELOK or equivalent
| - za laboratorijski tehnični plin: | - for laboratory industrial gas:
| N2 (200bar) … dušik (200bar) | N2 (200bar) ... nitrogen (200bar) | kpl | 3 |  | 0
3.10 | Jeklene nerjavne cevi, za laboratorijske tehnične pline , material AISI 316L (W.Nr 1.4435), notranja površinska hrapavost Ra≤0,8µm, za tlake 200 bar, metrične dimenzije, vključno z vijačnimi oblikovnimi kosi (loki, redukcije, T kosi, ...) in tesnili za tlake 200 bar; komplet z originalnim pritrdilnim in obešalnim materialom proizvajalca; | Stainless steel tubes, for laboratory technical gases, material AISI 316L (W.Nr 1.4435), internal surface roughness Ra≤0,8µm, for pressures of 200 bar, metric dimensions, incl. screw fittings (bows, reducers, T-pieces, etc.) and gaskets for pressures of 200 bar; complete with original fastening and hanging material of the manufacturer;
| - ustreza proizvod SWAGELOK tip Metric Sizes ali enakovredno | - corresponds to SWAGELOK type Metric Sizes or equivalent
| DN 6, ø 8 x 1 | DN 6, ø 8 x 1 | m | 18 |  | 0
| DN 8, ø 10 x 1 | DN 8, ø 10 x 1 | m | 192 |  | 0
| DN 10, ø 12 x 1 | DN 10, ø 12 x 1 | m | 2460 |  | 0
| DN 15, ø 18 x 1,5 | DN 15, ø 18 x 1,5 | m | 104 |  | 0
| 90°lok DN 10, ø 12 x 1 | 90°lok DN 10, ø 12 x 1 | kos | 520 |  | 0
| 90°lok DN 15, ø 18 x 1,5 | 90°lok DN 15, ø 18 x 1,5 | kos | 12 |  | 0
| T kos DN 10 / odcep DN 10 | T piece DN 10 / branch DN 10 | kos | 240 |  | 0
| T kos DN 15 / odcep DN 10 | T piece DN 15 / branch DN 10 | kos | 2 |  | 0
| redukcija DN 8 / DN 10 | dN 8 / DN 10 reduction | kos | 18 |  | 0
| redukcija DN 10 / DN 8 | dN 10 / DN 8 reduction | kos | 270 |  | 0
| redukcija DN 15 / DN 10 | reduction DN 15 / DN 10 | kos | 2 |  | 0
3.11 | Tlačni preskus trdnosti in tesnenja sistema cevovodov, skladeno z opisom v "IZS Priročnik tlačnih preizkusov strojnih inštalacij", vključno s potrebnim materialom za izvedbo preizkusa, ter izdelavo pisnega poročila o uspešno opravljenem tlačnem preizkusu; | Pressure test of the strength and tightness of the piping system, as described in the "IZS Manual for Pressure Testing of Mechanical Installations", including the necessary materials for the test, and the production of a written report on the successful completion of the pressure test;
| preskusni tlak = 1,1 x 200 bar = 220 bar | test pressure = 1,1 x 200 bar = 220 bar | kpl | 1 |  | 0
| preskusni tlak = 1,1 x 300 bar = 330 bar | test pressure = 1,1 x 300 bar = 330 bar | kpl | 1 |  | 0
| preskusni tlak = 1,5 x 10 bar = 15 bar | test pressure = 1,5 x 10 bar = 15 bar | kpl | 1 |  | 0
3.12 | Izpihovanje cevovodov z zrakom ali inertnim plinom (na primer dušik) v celotnem sistemu z namenom odstranjevanja nečistoč; | Blowing out the piping with air or an inert gas (e.g. nitrogen) throughout the system to remove impurities; | kpl | 1 |  | 0
3.13 | Ognjeodporna tesnilna masa, vgradnja na prehodu cevovodov skozi zid med požarnima sektortjema, požarna odpornost 90 minut, ustreza proizvod HILTI ali enakovredno. | Fire-resistant sealant, for installation at the transition of pipelines through the wall between the two fire sectors, fire resistance 90 minutes, equivalent to HILTI or equivalent.
| Vsak prehod mora biti označen z nalepko ali tablico z osnovnimi požarnimi podatki; | Each passageway must be marked with a sticker or placard with basic fire information; | kpl | 1 |  | 0
3.14 | Preizkusno obratovanje delovanja sistema v obsegu: | Operational test of the system in scope:
| - pregled jeklenk in omar za jeklenke, | - inspection of cylinders and cylinder lockers,
| - pregled ekspanzijskih reducirnih postaj za redukcijo visokega tlaka, | - an overview of expansion reduction stations for high pressure reduction,
| - pregled inštalacije cevovodov, armatur in opreme | - inspection of piping, fittings and equipment
| - pregled delovanja varnostnih funkcij (zapiranje pnevmatskih ventilov, delovanje detektorjev, delovanje prezračevanja omar za jeklenka ipd), | - checking the operation of safety functions (closing of pneumatic valves, operation of detectors, operation of cylinder cabinet ventilation, etc.),
| - pregled odjemnih mest. | - a review of the customer sites.
| Preizkusno obratovanje traja neprekinjeno 72 ur. | The test operation shall be continuous for 72 hours. | kpl | 1 |  | 0
3.15 | Napisne ploščice iz nerjavne pločevine z vgravirano oznako po shemi za opremo in armature, kompletno z jekleno pritrdilno žico ali visoko kvalotetne nalepke; visoko trajanje H (več kot 15 let) | Stainless steel nameplates with engraved marking according to the scheme for fittings and fixtures, complete with steel fixing wire or high quality labels; high durability H (more than 15 years) | kpl | 1 |  | 0
3.16 | Samolepilne puščice za označitev smeri pretoka ter z napisom vrste medija; visoko trajanje H (več kot 15 let) | Self-adhesive arrows to indicate direction of flow and type of media; high H lifetime (more than 15 years) | kpl | 1 |  | 0
3.17 | Izdelava montažnih risb za izvedbo inštalacij med gradnjo objekta, kot so: detajli priključkov, montažne skice, montažni detajli, ipd. | Preparation of assembly drawings for the installation of services during the construction of the building, such as: connection details, assembly sketches, assembly details, etc. | kpl | 1 |  | 0
3.18 | Kvalifikacije montaže IQ-pregledi (instalation qualification) po GEP Commissioning protokolu in dokumentiranje kvalifikacije montaže, vključno z odpravo prvotnih napak montaže; | Installation qualification IQ-checks (installation qualification) according to the GEP Commissioning Protocol and documentation of installation qualification, including correction of original installation faults; | kpl | 1 |  | 0
3.19 | Meritve delovanja OQ-kvalifikacija (operation qualification) ter dokumentiranje meritev delovanja, vključno z nastavitvijo parametrov; | OQ (operation qualification) measurements and documentation of performance measurements, including parameter settings; | kpl | 1 |  | 0
3.20 | Posnetki izvedenega stanja, sprotno beleženje vseh sprememb nastalih med izvedbo, vrisovanje in vpisovanje v PZI projektno dokumentacijo; | Recording of the as-built condition, keeping a running record of any changes made during the execution, plotting and recording in the PZI project documentation; | kpl | 1 |  | 0
3.21 | Stenska shema sistema, vloženo v zaščitni okvir s prosojnim umetnim steklomo (plastika) ali plastificirano, vključno s pritrditvijo na notranjo steno v strojnici objekta; | Wall diagram of the system, enclosed in a protective frame with transparent plastic or plasticised glass, including fixing to an internal wall in the mechanical room of the building; | kpl | 1 |  | 0
3.22 | Primopredajna dokumentacija, ki mora vsebovati: izjave, dokazilo o zanesljivosti objekta, certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo, obratovanje in vzdrževanje ter ostalo primopredajno dokumantacijo. Predaja se v dveh mapiranih izvodih ter en izvod v elektronski obliki; | The handover documentation, which shall include: declarations, proof of the reliability of the facility, certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use, operation and maintenance, and other handover documentation. It shall be handed over in two mapped copies and one copy in electronic form; | kpl | 1 |  | 0
| TEHNIČNI PLINI | TECHNICAL GAS |  |  |  | 0