## 0_Naslovnica
OPOZORILO! Vsi prevodi v angleščino so strojno izdelani in zgolj informativne narave. V primeru kakršnekoli nejasnosti ali dvoma izključno velja izvirno besedilo v slovenščini. WARNING! All translations into English have been produced by machine translation and are provided for informational purposes only. In the event of any ambiguity or uncertainty, the original Slovenian text shall prevail exclusively.
| / | / | [5 empty] | /
| Sprem./Rev.: | Opis spremembe/Description of Changes: | [5 empty] | Datum/Date: | Podpis/Signature:
| Investitor/Investor: |  |  |  |  | Gradnja/Facility
|  |  | Univerza v Ljubljani Kongresni trg 12 1000 Ljubljana, Slovenija |  |  | Fakulteta za strojništvo/Faculty of Mechanical Engineering
| Projektant/Design Engineer: |  |  |  |  | Del objekta/sistem/Building/System:
|  |  | IBE, svetovanje, projektiranje in inženiring Ljubljana, Slovenija |  |  | STAVBA FAKULTETE/FACULTY BUILDING
| Projektant/Design Engineer: |  |  |  |  | Vrsta načrta/Documentation:
4 NAČRT S PODROČJA STROJNIŠTVA/ DOC. IN THE FIELD OF MECHANICAL ENGINEERING
|  | Ime in priimek/Name and Surname: |  |  | Id. št./Id. No: | Vsebina risbe (dokumenta)/Document Title:
| Vodja proj./ Des. Manager: | Boštjan Vuga, univ. dipl. inž. arh., grad. dip. (AA) |  |  | ZAPS 0035 PA PPN | PR. POPIS STROJNIH DEL/BOQ OF MECH. WORKS 4/11 Laboratorij LICEM, oskrba z gorivi/Laboratory LICEM, Fuel supply
| Poobl. strok./ Cert. Profess.: | Simon Vršič, univ. dipl. inž. str. |  |  | IZS S-0141
| Poobl. strok./ Cert. Profess.: |  |  |  |  | Št. proj./ Proj. No.: | 362-19 |  | Vrsta dokument./ Document. Type: | DZR
| Izdelal/ Creator: | Alenka Vreček, mag. inž. str. |  |  | IZS S-2044 | Klas. ozn./ Class. No.: | -- |  | Stran/ Page: | 1/*
| Datum/ Date: | maj/May 2026 |  | Merilo/ Scale: | / | Ident. ozn./ Id. No: | JULFS--6S1102P

## 0_Osebe
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
POOBLAŠČENI STROKOVNJAKI, ODGOVORNI ZA IZDELAVO PROJEKTANTSKEGA POPISA:
Id. št. ZAPS/IZS | Pooblaščeni strokovnjak | Strokovno področje
IZS S-1987 | Simon Vršič, univ. dipl. inž. str. | LICEM, oskrba z gorivi
SODELAVCI PRI IZDELAVI PROJEKTANTSKEGA POPISA:
IZS S-2044 | Alenka Vreček, mag. inž. str. | Priprava popisa
CERTIFIED EXPERTS RESPONSIBLE FOR ELABORATING THE BILL OF QUANTITIES:
Id. No ZAPS/IZS | Certified Expert | Area of Expertise
IZS S-1987 | Simon Vršič, univ. dipl. inž. str. | LICEM, fuel supply
COLABORATORS IN THE ELABORATING THE BILL OF QUANTITIES:
IZS S-2044 | Alenka Vreček, mag. inž. str. | Preparation of the inventory

## 0.1_Uvod-STP
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
0.1 | SPLOŠNI TEHNIČNI POGOJI | GENERAL TECHNICAL CONDITIONS
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic operator with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
0.1.1 | Izvajalec se obveže, da bo upošteval veljavno zakonodajo, ki ureja graditev objektov v Republiki Sloveniji, vključno s povezanimi podzakonskimi akti, predpisi, tehničnimi smernicami, standardi, pravili stroke in dobro gradbeno prakso. Prav tako mora izvajalec upoštevati vse zahteve izdanega integralnega gradbenega dovoljenja in vsa dela izvesti skladno s projektno dokumentacijo ter ostalimi pogoji, objavljenimi v razpisni dokumentaciji. | The Contractor undertakes to comply with the applicable legislation governing the construction of buildings in the Republic of Slovenia, including related by-laws, regulations, technical guidelines, standards, professional rules and good construction practice. The Contractor shall also comply with all the requirements of the integral building permit issued and shall carry out all works in accordance with the project documentation and other conditions published in the tender documentation.
0.1.2 | Dela lahko izvaja samo izvajalec, ki je registriran za opravljanje gradbene dejavnosti in ima za tovrstna dela ustrezno zavarovanje za škodo, certifikate, tehnično izobražen kader, sredstva ter je usposobljen za samostojno pripravo in izvedbo del. | The work may only be carried out by a contractor who is registered to carry out construction work and who has the appropriate insurance for such work, certificates, technically trained staff, resources and is qualified to prepare and carry out the work independently.
0.1.3 | Izvajalec odgovarja za kakovost izvedbe vseh del. | The Contractor shall be responsible for the quality of the execution of all works.
0.1.4 | Izvajalec nosi vso odgovornost za nesreče in škodo, ki nastane na objektu ali v okolici zaradi njegovega dela. | The Contractor shall bear all liability for accidents and damage to the installation or the surrounding area caused by his work.
0.1.5 | Pred oddajo ponudbe se je izvajalec dolžan seznaniti z območjem predvidenim za gradnjo in temu prilagoditi vsa potrebna dela, kar mora biti zajeto v ponudbi. V neposredni bližini predvidene gradnje se nahajajo stavbe, v katerih potekajo izobraževalni in raziskovalni procesi. Zato bo izvajalec moral izvajati kontrolo hrupa in kontrolo vibracij. Dela, ki so hrupna in dela, ki povzročajo vibracije bo izvajalec moral preprečiti oziroma jih izvesti na način, da povzročajo minimalne vplive. Tehnologijo rušenja, pilotiranja in tehnologijo izvedbe ostalih del bo izvajalec moral prilagoditi tako, da bo vpliv minimalen. Izvajalec mora preprečiti in zmanjšati emisije delcev iz gradbišča na najmanjšo možno mero. | Before submitting a tender, the contractor is obliged to familiarise himself with the area to be constructed and to adapt any necessary works accordingly, which must be included in the tender. In the immediate vicinity of the proposed construction, there are buildings in which educational and research processes take place. The contractor will therefore be required to carry out noise and vibration control. Noise and vibration works will have to be avoided or carried out in such a way as to minimise the impact. Demolition, piling and other works will have to be adapted to minimise the impact. The contractor must avoid and minimise the emission of particulates emitted from the construction site as far as is reasonably practicable.
0.1.6 | Izvajalec je pred oddajo ponudbe dolžan pregledati projektno dokumentacijo in ostale pogoje, ki so del razpisne dokumentacije V primeru morebitnih napak in neskladij je izvajalec dolžan na to opozoriti naročnika pred oddajo ponudbe. | The Contractor is obliged to review the project documentation and other conditions forming part of the tender documentation before submitting the tender In case of any errors or inconsistencies, the Contractor is obliged to bring these to the attention of the Contracting Authority before submitting the tender.
0.1.7 | Pred oddajo ponudbe je izvajalec dolžan preveriti ustreznost popisov del in količin v teh popisih ter njihovo skladnost z ostalimi dokumenti projektne dokumentacije, ki so del razpisne dokumentacije. Prav tako je izvajalec dolžan preveriti vse detajle in sheme. Vse izmere je potrebno preveriti po posameznih projektih oz. načrtih, ki sestavljajo razpisno dokumentacijo. V primeru ugotovljenih neskladij je v času priprave ponudbe obvezan o tem obvestiti naročnika. | Before submitting a tender, the Contractor shall check the adequacy of the inventories of works and quantities in these Bills of Quantities and their conformity with the other documents of the project documentation forming part of the tender documentation. The Contractor shall also check all details and diagrams. All measurements shall be checked against the individual projects or plans forming part of the tender documentation. In the event of any discrepancies, the Contractor shall inform the Contracting Authority at the time of preparing the tender.
0.1.8 | Pred oddajo ponudbe je izvajalec dolžan v tem popisu preveriti zmnožke in seštevke ter prenose le-teh v rekapitulacijo. Izvajalec se s pripravo ponudbe obvezuje, da je prebral vse celice in elemente celotnega popisa, vključno z vsemi postavkami in splošnimi navodili ali določili in je preveril pravilnost preračuna ter s tem zagotavlja ponudbeno vrednost. | Before submitting a tender, the Contractor is required to check the products and totals in this Bill of Quantities (BoQ) and their transfer to the recapitulation. The Contractor undertakes, by preparing a tender, to have read all the cells and elements of the complete BoQ, including all headings and general instructions or provisions, and to have checked the correctness of the conversion, thereby guaranteeing the value of the tender.
0.1.9 | Dela bo izvajalec moral izvajati po predloženi projektni dokumentaciji, detajlih in z upoštevanjem navodil in potrditev projektanta, nadzornika in investitorja. Vso potrebno delavniško dokumentacijo zagotovi izvajalec del v okviru ponujene cene. | The Contractor shall carry out the works in accordance with the submitted design documents, details and subject to the instructions and approvals of the Designer, the Supervisor and the Investor. All necessary workshop documentation shall be provided by the Contractor within the scope of the price quoted.
0.1.10 | Pred izvedbo posameznih del je izvajalec dolžan pregledati projektno dokumentacijo za izvedbo gradnje (PZI) in elaborate. Na morebitne napake v dokumentaciji ali neskladja med posameznimi načrti ali deli načrtov (popisi del, tehnična poročila, lokacijski in tehnični prikazi) izvajalec opozori nadzornika in projektanta, in se z njima pravočasno uskladi. | The Contractor shall review the Detailed Design documentation (PZI) and the studies before carrying out the individual works. The Contractor shall draw the attention of the Supervisor and the Designer to any errors in the documentation or discrepancies between the individual designs or parts of designs (BoQ, technical reports, location and technical drawings) and shall coordinate with them in good time.
0.1.11 | Tehnični opisi, prikazi, detajli, sheme ter ostali dokumenti v PZI dokumentaciji predstavljajo dodaten opis popisnih postavk gradbeno obrtniških in inštalacijskih del ter jih je potrebno dosledno upoštevati skupaj s popisom del. | The technical descriptions, illustrations, details, diagrams and other documents in the Detailed Design documentation (PZI) are additional descriptions of the BoQ inventory items of the building, construction and installation works and must be strictly followed together with the BoQ.
0.1.12 | Specifikacije in zahteve, navedene v popisu, se ne smejo upoštevati kot edine zahteve. Izvajalec je dolžan v ceni zajeti in dobaviti vse elemente opreme ter opraviti dela in storitve, ki niso eksplicitno navedeni, a so bistvenega pomena za funkcionalnost, skladnost s predpisi ter kontinuirano, zanesljivo in varno obratovanje opreme. | The specifications and requirements set out in the BoQ shall not be taken as the only requirements. The Contractor shall be obliged to include in the price and supply all items of equipment and to carry out works and services which are not expressly mentioned but which are essential for the functionality, regulatory compliance and continuous, reliable and safe operation of the equipment.
0.1.13 | Vsa dela morajo biti izvedena kvalitetno in iz materialov z zahtevanimi lastnostmi, izvedena skladno z veljavno zakonodajo in z upoštevanjem navodil za vgradnjo za izbrane materiale in opremo, s predložitvijo predpisanih izjav o lastnostih in/ali certifikatov. Vsi gradbeni proizvodi (GP) morajo biti označeni s CE oznako. | All work shall be of good quality and be executed with materials of the required characteristics, in accordance with the applicable legislation and in compliance with the installation instructions for the materials and equipment selected, and shall be accompanied by the prescribed declarations of performance and/or certificates. All construction products (GP) shall bear the CE marking.
0.1.14 | Za vsako opisano delo v popisu je potrebno upoštevati celotno potrebno delo, ves osnovni in pomožni material, prevoz materiala in orodja na objekt, notranje transporte, delovne in pomožne odre, zaključno čiščenje in odstranitev odpadkov po dovršenem delu. | For each work described in the inventory, the total work required, all basic and ancillary materials, the transport of materials and tools to the site, internal transports, working and ancillary scaffolding, final cleaning and the disposal of waste after the work has been completed must be taken into account.
0.1.15 | Vsa delovna sredstva, organizacija in koordinacija del, pripravljalna, spremljajoča in zaključna dela, potrebni montažni in tesnilni materiali ter podkonstrukcije so sestavni del posameznih postavk. | All labour, organisation and coordination of the works, preparatory, accompanying and finishing works, necessary prefabrication and sealing materials and substructures are part of the individual items.
0.1.16 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - načrt organizacije gradbišča s podrobnim terminskim planom in izvedba vseh pripravljalnih del, postavitev, organizacija, zaščita in prijava gradbišča, gradbiščnih objektov, ureditev začasnih deponij, tekoče vzdrževanje, skupaj s plačilom splošnih stroškov pristojbin in davkov upravnih organov, pridobivanju raznih dovoljenj in soglasij za izvedbo, ograditev gradbišča in postavitev gradbene table in prometne signalizacije, zagotavljanje ustrezne varnosti na gradbišču, tekoče vzdrževanje in končna odstranitev gradbišča; - zagotovitev potrebnih začasnih površin za transportne poti in gradnjo izven območja gradbišča s plačilom stroškov za sanacijo in vzpostavitev okoliških zemljišč in objektov v prvotno stanje (soglasja, odškodnine, itd.); - začasni odvoz, deponiranje in vračanje izkopanega materiala, ki ga ne bo možno deponirati na gradbišču; - odvoz in zagotovitev odstranjevanja odpadnega gradbenega materiala skladno z zakonodajo na področju ravnanja z odpadki (odvoz na urejene deponije s plačilom komunalnih prispevkov in taks itd.); - oteženi izkop v mokrem terenu, izkop v vodi, odvod meteorne vode iz gradbene jame in vode, ki se izceja iz bočnih strani izkopov; - ustrezno varovanje izkopa gradbene jame za objekt in ostalih manjših posameznih izkopov za izvedbo komunalne infrastrukture brez posegov na sosednja zemljišča; - ustrezno varovanje obstoječih objektov, infrastrukture in okolice v času gradnje ter dokumentiranje vseh morebitnih škodnih dogodkov; - pripravljalna, spremljajoča in zaključna dela (zakoličbe, zagotovitev potrebnih komunalnih priključkov za potrebe izvajanja gradnje, izvedba začasnih inštalacij, označevanje podzemnih vodov, postavljanje in vzdrževanje zakoličbenih profilov, izvedba in označevanje novih in starih križanj ter morebitna zaščita križanj komunalnih vodov, geodetski posnetki in izdajanje vmesnih posnetkov izvedene infrastrukture naročniku, izdelava zbirnih kart, itd.), v kolikor ni to drugače določeno; - pridobivanje soglasij in izvedba morebitnih zapor na vseh cestah s plačilom stroškov, nadomestil in pristojbin; - zagotovitev oz. postavitev in končna odstranitev po zaključku gradnje začasnih skladišč in začasnega pisarniškega kontejnerskega objekta vključno z opremo za dve delovni mesti in za skupne operativne sestanke vel. ca. 40 m2 za potrebe naročnika, s tekočim vzdrževanjem in čiščenjem. | The following must also be included or taken into account in the uniform prices for individual items: - a construction site organisation plan with a detailed timetable and the execution of all preparatory works, the setting-up, organisation, protection and registration of the construction site, site facilities, the arrangement of temporary storage facilities, ongoing maintenance, including the payment of general costs of fees and taxes of the administrative authorities, the obtaining of various permits and consents for the execution, the fencing of the site and the erection of construction signs and traffic signals, the provision of adequate security on the site, ongoing maintenance and the final dismantling of the construction site; - provision of the necessary temporary areas for transport routes and off-site construction, with costs for restoration and reinstatement of surrounding land and buildings (consents, compensation, etc.); - temporary removal, storage and return of excavated material that cannot be stored on site; - removing and disposing of waste building materials in accordance with waste management legislation (removal to regulated landfill sites with payment of municipal fees and charges, etc.); - difficult excavation in wet ground, excavation in water, drainage of rainwater from the construction pit and water draining from the sides of excavations; - adequate protection of the excavation of the construction pit for the building and other small individual excavations for the implementation of the utility infrastructure without encroaching on neighbouring land; - adequate protection of existing facilities, infrastructure and the surrounding area during construction, and documentation of any damage incidents; - preparatory, accompanying and finishing works (stake-out, provision of the necessary utility connections for the needs of construction, execution of temporary installations, marking of underground lines, installation and maintenance of stake-out profiles, execution and marking of new and old crossings and possible protection of crossings of utility lines, geodetic surveys and issuing of intermediate images of the completed infrastructure to the client, production of summary maps, etc.), unless otherwise specified; - obtaining consents and implementing any road closures, with costs, compensation and fees; - provision or erection and final removal on completion of construction of temporary storage and temporary office container building including equipment for two workstations and for joint operational meetings of approx. 40 m2 for the needs of the client, with ongoing maintenance and cleaning.
0.1.17 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - izdelava montažne tehnične dokumentacije, detajlov izvedbe in vse druge potrebne delavniške dokumentacije (s področja arhitekture, gradbeništva, elektrotehnike, strojništva in zunanje ter krajinske ureditve) ter pridobitev obvezne potrditve s strani projektanta, nadzornika in investitorja; - odprava vseh vrst inštalacijskih kolizij z izvajanjem potrebnih premikov inštalacij in njihovim usklajevanjem na mestu montaže, vse v obsegu, ki ne vpliva na projektirano rešitev ali tip inštalacij oz. opreme; - zagotavljanje kompletnosti elektro-instalacijskih sistemov s področja avtomatike za doseganje njihove popolne funkcionalnosti delovanja; - stroški za nadzor in koordinacijo izvedbe vseh elektro napeljav, ki so predmet končne instalacije proizvoda (senčila, vrata, okna,…); - izdelava montažnih skic in detajlov za izvedbo v dogovoru z vodjo gradnje in nadzornikom; - izdelava in predstavitev vzorcev v ustrezni velikosti za potrditev projektanta, nadzornika in investitorja; - zagotavljanje varnosti in zdravja pri delu, zlasti izvajanje vseh del, ki izhajajo in ukrepov, ki izhajajo iz določil veljavnih predpisov varstva pri delu in zahtev Varnostnega načrta;- stroški garancij, ki jih mora izvajalec predložiti naročniku. | The following must also be included or taken into account in the uniform prices for individual items: - preparation of prefabricated technical documentation, construction details and all other necessary workshop documentation (architectural, civil, electrical, mechanical, exterior and landscaping) and obtaining the mandatory approval of the designer, the supervisor and the investor; - elimination of all types of installation conflicts by carrying out the necessary relocation of installations and their coordination at the installation site, all to the extent that it does not affect the design solution or the type of installation or equipment; - ensuring the completeness of electrical installation systems in the automation sector to achieve their full operational functionality; - the cost of supervising and coordinating the installation of all the electrical installations that are the subject of the final installation of the product (blinds, doors, windows, etc.); - preparation of erection drawings and details for implementation in agreement with the construction manager and supervisor; - production and presentation of samples in appropriate sizes for the approval of the designer, the supervisor and the investor; - ensuring health and safety at work, in particular the implementation of all the works arising from and the measures resulting from the provisions of the applicable occupational safety regulations and the requirements of the Safety Plan; - the cost of the guarantees to be provided by the contractor to the client.
0.1.18 | V enotnih cenah posameznih postavk mora biti zajeto oz. upoštevano tudi naslednje: - strošek vodje del glavnega izvajalca, ki bo izvajal tudi koordinacijo s podizvajalci in z drugimi izvajalci, ki jih bo izbral naročnik in bo opravljal delo vodje gradbišča; - koordinacija del z ostalimi izvajalci oz. podizvajalci del, projektantom, nadzornikom in investitorjem pri medsebojnem usklajevanju organizacije gradbišča in časovnega načrta del ter pri usklajevanju izdelave plana montaže, potrjenih s strani vseh udeležencev gradnje; - stroški koordinacije, sodelovanja in usklajevanja z dobavitelji tehnološke, laboratorijske, eksperimentalne in vse ostale pohištvene ter multimedijske opreme ter z vsemi ostalimi dobavitelji oz. podizvajalci na objektu; - stroški izdelave situacij; - stroški zavarovanja objekta v času izvedbe del in delavcev ter materiala na gradbišču v času izvajanja del, od začetka del do pridobitve uporabnega dovoljenja za objekt. Zavarovanje mora biti sklenjeno pri ustrezni zavarovalni družbi najmanj v višini pogodbene vrednosti ali v zakonsko predpisani vrednosti (v kolikor zavarovanje v višini pogodbene vrednosti presega zakonsko dovoljeno), za ves čas trajanja izvedbe del do uspešne primopredaje objekta; - preizkušanje kvalitete materiala, ki se vgrajuje in dokazovanje kvalitete s certifikati oz. tehničnimi soglasji; - izvedba vseh zahtevanih testov in preizkusov (npr. tlačni preizkusi, termografski pregledi, meritve elektromagnetnega sevanja, hrupa, itd.), poskusnega obratovanja celotnega objekta s poudarkom na vseh inštalacijah ter izvajanje predpisanega monitoringa v skladu s Poročilom o vplivih na okolje (pred gradnjo, med gradnjo in po končani gradnji); - izdelava izkaza požarne varnosti, vključno s sprotnim spremljanjem gradnje in izvajanjem požarnovarnostnih zahtev ter izdelava Požarnega reda z obveznimi prilogami; - izdelava Izkaza zaščite pred hrupom v stavbah; - izdelava Izkaza energijskih lastnosti stavbe in energetske izkaznice; - sodelovanje z izvajalci gradbenega in projektantskega nadzora in investitorjem za izvedbo tehničnega pregleda in priprava primopredaje, ki mora vsebovati vso zahtevano dokumentacijo, predvsem pa: izjave o skladnosti, požarni izkaz in ostale izkaze ter obvezne tabele, dokazilo o zanesljivosti objekta (DZO), certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo in vzdrževanje ter vse ostale dokumente v skladu s predpisi in pogodbenimi določili. | The following must also be included or taken into account in the uniform prices of the individual items: - the cost of a works manager for the main contractor, who will also coordinate with subcontractors and other contractors selected by the client and act as site manager; - coordination of the works with other contractors or subcontractors, the designer, the supervisor and the investor in coordinating the organisation of the construction site and the timetable for the works, and in coordinating the production of an installation plan approved by all the participants in the construction; - the costs of coordination, cooperation and coordination with suppliers of technological, laboratory, experimental and all other furniture and multimedia equipment, as well as with all other suppliers or subcontractors on the site; - the cost of drawing up situations; - the cost of insuring the building during the execution of the works and the workers and materials on site during the execution of the works, from the start of the works until the building has been licensed for occupation. The insurance must be taken out with a suitable insurance company for at least the contract value or the legal value (if the insurance for the contract value exceeds the legal value), for the entire duration of the works until the successful handover of the building; - testing the quality of the material to be installed and proving it with certificates or technical approvals; - carrying out all required tests and trials (e.g. pressure tests, thermographic inspections, electromagnetic radiation measurements, noise measurements, etc.), trial operation of the entire building, with emphasis on all installations, and carrying out the required monitoring in accordance with the Environmental Impact Assessment Report (before, during and after construction); - preparation of a fire safety statement, including ongoing monitoring of construction and implementation of fire safety requirements, and preparation of a Fire Safety Order with mandatory annexes; - preparation of a Noise Protection Statement for buildings; - preparation of the Building Energy Performance Report and Energy Performance Certificate; - cooperation with the construction and design supervision contractors and the investor to carry out the technical inspection and prepare the handover, which must include all the required documentation, in particular: declarations of conformity, fire and other statements and mandatory tables, proof of reliability of the building (DZO), certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use and maintenance, and all other documents in accordance with the regulations and the contractual provisions.
0.1.19 | V enotnih cenah posameznih postavk, ki se nanašajo na opremo in posamezne sisteme, mora biti zajeto oz. upoštevano tudi naslednje: - dobava oz. transport, - stroški za vse delovne stroje za dvigovanje bremen in delovne košare za dostope do delovišč; - morebitni stroški povzročeni upravljavcem GJI, ki bi nastali v zvezi s predmetno gradnjo; - montaža, vključno s pomožnim montažnim materialom (vezni, tesnilni in pritrdilni material, sidra, nosilni profili, podkonstrukcije in podobno) in navodili proizvajalca, - odprava vseh kolizij sistemov s stenami in med sistemi, - izvedba vseh potrebnih tesnjenj, - priključitev in nastavitve, vključno z morebitnim kalibriranjem, - zagon, testiranje in meritve, vključno s poročili, - šolanje uporabnikov oz. vzdrževalnega osebja za uporabo in vzdrževanje sistemov, - navodila za obratovanje in vzdrževanje, - vsi potrebni certifikati, izjave o skladnosti oz. potrdila ter - vsa druga pomožna dela in material, da se zagotovi funkcionalnost posamezne postavke popisa. | The following must also be included or taken into account in the uniform prices for individual items relating to equipment and individual systems: - delivery/transport, - the cost of all lifting machines and work baskets for access to work sites; - any costs incurred to the operators of utility infrastructure (GJI) in connection with the subject construction; - installation, including ancillary installation materials (bonding, sealing and fixing materials, anchors, support profiles, substructures, etc.) and manufacturer's instructions, - eliminating all system-to-wall and system-to-system collisions, - all necessary sealing work, - connection and set-up, including calibration if necessary, - commissioning, testing and measurements, including reports, - training users or maintenance staff in the use and maintenance of the systems, - operating and maintenance instructions, - any necessary certificates, declarations of conformity or attestations; and - all other ancillary works and materials to ensure the functionality of each inventory item.
0.1.20 | Vsi odri morajo biti upoštevani v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All scaffolding must be included in the uniform prices of the items listed, except where specifically mentioned.
0.1.21 | Vsi delovni in pomožni odri, lestve in ostala potrebna pomožna sredstva, kot tudi čiščenje vseh elementov po končanih delih, mora biti upoštevano v enotnih cenah navedenih postavk, razen tistih, ki so posebej navedeni. | All working and auxiliary scaffolding, ladders and other necessary ancillaries, as well as the cleaning of all elements after completion of the works, shall be included in the uniform prices of the items listed, except those specifically mentioned.
0.1.22 | Delavniško dokumentacijo za vse nosilne jeklene konstrukcije in podkonstrukcije izdela izvajalec, strošek izdelave delavniške dokumentacije se upošteva v ponujenih cenah in se ne obračuna posebej. | The cost of the shop drawings for all steelwork and substructures shall be included in the prices quoted and shall not be charged separately.
0.1.23 | V enotnih cenah postavk mora biti vključeno tudi vgrajevanje vseh instalacijskih razvodov v opaže armirano betonskih elementov in izdelava prehodov inštalacij ter dodatno izrezovanje utorov in prebojev v kamnite, zidane ali armirano-betonske stene, ponovno demontiranje in montiranje vseh vrst montažnih sten, vsa dodatna dela za zagotavljanje primernih križanj med posameznimi instalacijskimi vodi, izdelava vseh vrst ojačitev konstrukcij in podobna dela, ki zagotavljajo kakovostno vgradnjo vseh vrst instalacijskih vodov in niso posebej navedena v popisu GOI del. V ponudbi morajo biti upoštevana vsa drobna strojna in elektro instalacijska dela in transporti. | The installation of all installation ducts in the formwork of reinforced concrete elements and the construction of installation penetrations, as well as the additional cutting of grooves and penetrations in stone, masonry or reinforced concrete walls, the reassembly and reinstallation of all types of prefabricated walls, all additional work to ensure adequate crossings between individual installation ducts, the construction of all types of structural reinforcement and similar work to ensure the quality installation of all types of installation ducts and not specifically mentioned in the BoQ of the Construction, installation and finishing works (GOI) shall also be included in the uniform prices of the items. The tender shall take into account all minor mechanical and electrical installation work and transport.
0.1.24 | Vsi kovinski elementi in konstrukcije, ki bi lahko bili izpostavljeni atmosferskim in ostalim korozijskim vplivom, morajo biti ustrezno protikorozijsko zaščiteni. | All metallic elements and structures that could be exposed to atmospheric and other corrosive influences must be adequately protected against corrosion.
0.1.25 | Za vse večje jeklene dele se skladno s predpisi, izdelajo ustrezne ozemljitve, nevidno pritrjene in speljane na splošno ozemljitev objekta. | For all major steel parts, appropriate earth connections shall be made in accordance with the regulations, invisibly attached and connected to the general earth of the building.
0.1.26 | Za vse vidne elemente in serijske elemente je obvezna predhodna uskladitev obdelav, barv in materialov s projektantom na podlagi dostavljenih vzorcev v ustrezni velikosti. Obvezna je preveritev dejanskih mer na licu mesta in posledična prilagoditev elementov in njihove montaže. | For all visible elements and serial elements, it is mandatory to coordinate the finishes, colours and materials with the designer beforehand on the basis of the supplied samples in the appropriate size. It is mandatory to check the actual dimensions on site and to adjust the elements and their installation accordingly.
0.1.27 | Dimenzije obrtniških izdelkov in količine je potrebno pred naročanjem preveriti na objektu. Potrebna je uskladitev vseh elementov (kljuke, okovje, detajlne konstrukcije in obdelave, itd.) s projektantom, nadzornikom in investitorjem. Izvajalec je dolžan pred izdelavo predložiti projektantu v potrditev ustrezne delavniške načrte in detajle. | The dimensions of the workmanship and quantities must be checked on site before ordering. All elements (hooks, fittings, detailed construction and finishes, etc.) must be coordinated with the designer, the supervisor and the investor. The contractor is obliged to submit the relevant workshop plans and details to the designer for approval before manufacture.
0.1.28 | V posameznih postavkah popisa so navedeni proizvajalci in/ali tipi posameznih sistemov, materialov ali opreme, s čimer so zgolj natančno opredeljene zahtevane tehnične lastnosti. Izvajalec del lahko ponudi nadomesten sistem, material ali opremo drugega proizvajalca in tipa, pri čemer morajo biti tehnične lastnosti ponujenega sistema, materiala ali opreme enakovredne ali boljše od opredeljenih v popisu, dimenzijsko pa ne smejo presegati projektiranih dimenzij. Vse funkcijske in tehnične karakteristike nadomestnih sistemov, materialov ali opreme mora izvajalec dokazati z ustrezno dokumentacijo. Vse morebitne posledice zaradi spremembe sistemov, materialov ali opreme vključno z morebitnimi spremembami oz. dopolnitvami BIM modelov in projektne dokumentacije, stroškovno in časovno bremenijo izvajalca. | The individual items of the Inventory shall specify the manufacturers and/or types of the individual systems, materials or equipment, thereby merely specifying the required technical characteristics. The Contractor may offer a substitute system, material or equipment of a different manufacturer and type, provided that the technical characteristics of the offered system, material or equipment shall be equivalent to or better than those specified in the BoQ, and shall not exceed the design dimensions. All functional and technical characteristics of the substitute systems, materials or equipment shall be demonstrated by the Contractor with appropriate documentation. Any consequences resulting from changes to systems, materials or equipment, including any changes or additions to the BIM models and project documentation, shall be borne by the Contractor in terms of cost and time.
0.1.29 | Vsako zamenjavo, uporabo in končni izbor nadomestnih sistemov, materialov, proizvodov in opreme morajo obvezno in pravočasno (pred dobavo in vgradnjo) pisno potrditi projektant (vseh sodelujočih strok), nadzornik in investitor. | Any replacement, use and final selection of alternative systems, materials, products and equipment must be approved in writing by the designer (of all disciplines involved), the supervisor and the investor in a timely manner (prior to delivery and installation).
0.1.30 | Izvajalec mora v ponudbeno ceno vključiti tudi: - ves čas gradnje sprotno beleženje sprememb oz. odstopanj od PZI dokumentacije, vključno z izdelavo tekstualnega opisa sprememb, - pripravo podlog na nivoju PZI, ki so potrebne za posodobitev oz. uskladitev BIM modela z izvedenim stanjem (LOD 500) in izdelavo projektne dokumentacije izvedenih del (PID), - mesečno predajanje potrjenih sprememb opreme in materiala, ki vplivajo na BIM model, v formatu IFC, - vzdrževanje in uporabljanje pri izvedbi zadnje veljavne revizije PZI dokumentacije, vključno z dopolnitvami PZI načrtov, ki so nastali zaradi sprememb med gradnjo. | The contractor must also include in the tender price: - keeping a record of changes or deviations from the construction documentation (PZI) throughout construction, including a textual description of the changes, - preparation of the Detailed Design (PZI) level documents required to update or align the BIM model with the as-built condition (LOD 500) and the preparation of the as-built project documentation for the works (PID), - monthly submission of approved equipment and material changes affecting the BIM model in IFC format, - maintenance and use in the execution of the last valid revision of the construction documentation (PZI), including additions to the construction design documentation (PZI) resulting from changes during construction.

## 0.2_Uvod-DGNB
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
0.2 | SPLOŠNI TEHNIČNI POGOJI ZA PODROČJE DGNB CERTIFICIRANJA | GENERAL TECHNICAL CONDITIONS FOR DGNB CERTIFICATION
| Izvajalec je gospodarski subjekt s katerim naročnik sklene pogodbo o izvedbi javnega naročila in je v fazi oddaje naročila kot ponudnik oddal ekonomsko najugodnejšo ponudbo. | The contractor is the economic entity with which the contracting authority concludes the public procurement contract and which has submitted the most economically advantageous tender as the tenderer in the award phase.
| Splošni pogoji za področje DGNB certificiranja predstavljajo dopolnilo splošnim tehničnim pogojem in ne odpravljajo drugih obveznosti in odgovornosti, ki jih ima izvajalec v skladu s predpisi in pogodbo. | The General Conditions for DGNB Certification are complementary to the General Technical Conditions and do not exclude other obligations and responsibilities that the Contractor has under the Regulations and the Contract.
0.2.1 | Izvajalec mora v svojih ponudbah upoštevati, da se bo objekt certificiral v skladu z zahtevami DGNB sistema certificiranja trajnostne gradnje, ter pravočasno (vsaj 60 dni pred vgradnjo posameznega produkta) dostaviti vso ustrezno dokumentacijo za vse v ponudbi zajete materiale, elemente in opremo. Zahtevana je uporaba materialov, elementov ali opreme, ki so okolju in ljudem prijazni, energetsko učinkoviti in obenem ustrezajo zahtevam DGNB sistema. Zahtevan nivo certifikata je: ZLATI CERTIFIKAT | The Contractor shall take into account in its tenders that the building will be certified in accordance with the requirements of the DGNB Sustainable Building Certification Scheme and shall deliver all relevant documentation for all materials, elements and equipment included in the tender in a timely manner (at least 60 days before the installation of each product). The use of materials, elements or equipment that are environmentally and human friendly, energy efficient and at the same time meet the requirements of the DGNB system is required. The required level of certification is: GOLD CERTIFICATE
0.2.2 | Podrobnejši opis DGNB sistema in navodila za posamezne kriterije so dostopna v dokumentu"DGNB Criteria Set New Construction Buildings, Version 2020 International", ki je na voljo na DGNB spletni strani https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria | A more detailed description of the DGNB system and guidance on the individual criteria is available in the document "DGNB Criteria Set New Construction Buildings, Version 2020 International", available on the DGNB website https://www.dgnb.de/en/certification/important-facts-about-dgnb-certification/criteria
0.2.3 | Izvajalec mora v svojih ponudbah upoštevati, da je potrebno skladno z določili DGNB certifikacijskega sistema, pravočasno (pred pričetkom gradnje) dostaviti vso ustrezno dokumentacijo, za vse v ponudbi zajete materiale, elemente in opremo (tehnični list, varnostni list, izjava o lastnostih, tehnična navodila za ravnanje, servisiranje, vzdrževanje,...) v slovenskem jeziku. Vgradnja kakršnihkoli materialov, elementov ali opreme, se izvede zgolj na podlagi predhodne preveritve posredovane dokumentacije in obenem potrditve s strani nadzornika. | The Contractor must take into account in its tenders that, in accordance with the provisions of the DGNB certification system, all relevant documentation for all materials, elements and equipment included in the tender (technical data sheet, safety data sheet, declaration of properties, technical instructions for handling, servicing, maintenance,...) must be delivered on time (prior to the start of construction) in the Slovene language (in accordance with the provisions of the DGNB certification system). The installation of any materials, elements or equipment shall be subject to prior checking of the submitted documentation and, at the same time, to the approval of the Supervisor.
0.2.4 | Izbrani materiali, elementi, naprave, sistemi in oprema morajo prispevati k večji trajnosti stavbe v smeri zagotavljanja energetske učinkovitosti, ekonomičnega in enostavnega vzdrževanja ter čiščenja, dolge življenjske dobe, uporabe okolju prijaznih materialov ipd. | The materials, elements, appliances, systems and equipment chosen must contribute to the sustainability of the building in terms of energy efficiency, economic and easy maintenance and cleaning, long lifetime, use of environmentally friendly materials, etc.
0.2.5 | Predloženi dokumenti za vse uporabljene materiale, elemente in opremo morajo izpolnjevati zahteve najmanj kakovostne stopnje QS3 (zaželeno QS4), iz dokumenta: DGNB Razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001) | The documents submitted for all materials, components and equipment used shall meet the requirements of at least quality level QS3 (preferably QS4) of the document DGNB Quality Grades for Materials, Components and Equipment (JULFS--7X9001)
0.2.6 | V kolikor izbrani materiali oz. elementi, navedeni v posameznih postavkah, ne ustrezajo vsaj kakovostni stopnji QS3 iz seznama: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), je izvajalec dolžan na to opozoriti projektanta, nadzor in investitorja ter podati predlog ustreznega materiala oz. elementa. | If the selected materials or elements listed in the individual items do not meet at least quality level QS3 of the list of DGNB quality classes for materials, elements and equipment (JULFS--7X9001), the Contractor shall draw this to the attention of the Designer, the Supervisor and the Investor, and shall make a proposal for a suitable material or element.
0.2.7 | Izvajalec lahko v svoji ponudbi predlaga alternativne produkte in rešitve glede na predvidene s projektom, pod pogojem, da le-te prav tako izpolnjujejo vse navedene zahteve. Pri morebitnih predlaganih alternativnih produktih oz. rešitvah je potrebno upoštevati najmanj enake ali boljše lastnosti v smislu življenjske dobe, obstojnosti, ter enostavnosti in stroška čiščenja ter vzdrževanja v primerjavi s projektom predpisanimi rešitvami. Za alternativne rešitve izvajalec pridobi soglasje projektanta, nadzornika in investitorja pred pričetkom gradnje. | The Contractor may propose alternative products and solutions to those envisaged by the project in its tender, provided that they also meet all the requirements set out above. Any alternative products or solutions proposed shall have at least the same or better characteristics in terms of service life, durability, and ease and cost of cleaning and maintenance compared to the solutions envisaged by the project. For alternative solutions, the contractor shall obtain the agreement of the designer, the supervisor and the investor before starting construction.
0.2.8 | Izvajalec med gradnjo dnevno beleži vsa eventualna odstopanja od PZI projektne dokumentacije ter podatke pravočasno posreduje naročniku, nadzoru in projektantu. Potrjene spremembe vnese v podlage za izdelavo PID in posodobitev BIM modelov. | During construction, the Contractor shall record on a daily basis any deviations from the Detailed Design documentation (PZI) and shall provide the information to the Client, Supervision and the Designer in a timely manner. Confirmed changes shall be entered into the basis for the As-built documentation (PID) and BIM model updates.
0.2.9 | Izvajalec med gradnjo sproti izpolnjuje Seznam vseh konstrukcijskih sestav s pripadajočimi vgrajenimi gradbenimi materiali in dokumentira naslednje podatke o vgrajenih materialih (v slovenskem jeziku): - Varnostni list - Tehnični list - Izjavo o lastnostih (če je relevantno) - Izkazovanje morebiti obstoječega okoljskega certifikata (Tip I - okoljski znak ali Tip III - okoljska produktna deklaracija /EPD) - Izjavo proizvajalca ali dobavitelja, da produkt ustreza zahtevam ENV1.2 - Tehnična navodila za ravnanje, servisiranje, vzdrževanje oziroma ostale, z zakonom predpisane dokumente in dokumentacijo. | During construction, the Contractor shall keep a List of all structural assemblies with their associated construction materials and document the following information on the materials installed (in Slovene language): - Safety Data Sheet - Technical Data Sheet - Declaration of performance (if applicable) - Demonstration of any existing environmental certification (Type I - Ecolabel or Type III - Environmental Product Declaration /EPD) - A declaration by the manufacturer or supplier that the product complies with the requirements of ENV1.2 - Technical instructions for handling, servicing, maintenance or other documents and documentation required by law.
0.2.10 | Za vse vgrajene bistvene tehnične sisteme mora izvajalec zagotoviti obstoj pooblaščenega servisa, ki deluje na območju Republike Slovenije, da ima investitor možnost skleniti ustrezno pogodbo o vzdrževanju. Med bistvene tehnične sisteme sodijo npr.: sistemi ogrevanja in hlajenja, priprava tehnoloških medijev, prezračevanje in klimatizacija, sistemi detekcije in gašenja požara, sistemi tehničnega varovanja, BMS in CNS sistemi upravljanja stavbe, razsvetljava, komunikacijski in WI-FI sistemi,... | For all installed essential technical systems, the contractor must ensure the existence of an authorised service centre operating in the territory of the Republic of Slovenia, so that the investor has the possibility of concluding an appropriate maintenance contract. The essential technical systems include, for example: heating and cooling systems, technological media preparation, ventilation and air conditioning, fire detection and extinguishing systems, technical security systems, BMS and CNS building management systems, lighting, communication and WI-FI systems,...
0.2.11 | Zaželeno je, da imajo uporabljeni elementi in materiali okoljsko oznako Tip I. (kot npr. ENCODE, BLUE ANGEL, ipd...). | It is preferable that the elements and materials used have a Type I environmental label (such as ENCODE, BLUE ANGEL, etc...).
0.2.12 | Izvajalec bo za elemente iz lesa moral dokazovati izvor z navedbo izvorne države in tipa lesa, FSC / PEFC certifikat z dodatnim pripadajočim potrdilom Chain of custody-trgovski certifikat dobavitelja - ta se dokazuje z dobavnicami, računi ali enakovredno. Za izdelke iz naravnega kamna iz EU držav je potrebna deklaracija, da je izvor in procesiranje teh izdelkov v celoti v EU državah. Za izdelke iz naravnega kamna, ki prihajajo iz držav izven EU, je potrebno predložiti dokazilo o izpolnjevanju ILO konvencije 182, ki vključuje neodvisna inšpekcijska poročila. | For wood elements, the contractor will be required to provide proof of origin, indicating the country of origin and the type of wood, FSC/PEFC certification with an additional Chain of Custody certificate - the supplier's trade certificate - this shall be evidenced by delivery notes, invoices or equivalent. For natural stone products from EU countries, a declaration that the sourcing and processing of these products is entirely in EU countries is required. For natural stone products from non-EU countries, proof of compliance with ILO Convention 182, including independent inspection reports, is required.
0.2.13 | Izobraževanje udeležencev pri gradnji Izvajalec je dolžan vse udeležence pri gradnji podrobneje seznaniti tudi z relevantnimi koncepti, študijami, elaborati, ki opredelujejo trajnostni način gradnje za naslednja področja: - zaščita pred hrupom (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)) - zaščita pred prašenjem - zaščita tal in podzemne vode (Poročilo o vplivih na okolje št. 100123-11523, z dne 11.5.2023, dopolnitev 13. 11. 2023 in 28. 3. 2024 (E-NET OKOLJE d.o.o. in GIGA-R d.o.o.)), Analiza tveganja za onesnaženje vodnega telesa podzemne vode št. 0346-023/2023, maj 2023 (Geološko projektiranje d.o.o.)) - ravnanje z gradbenimi odpadki (Načrt gospodarjenja z gradbenimi odpadki) Izobraževanja se izvajajo skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.1 1.2, 2.2, 3.2 in 4.2 Training for the parties implementing the construction work | Training of construction participants The contractor is also obliged to inform all construction participants in detail about relevant concepts, studies, elaborations defining sustainable construction methods for the following areas: - noise protection (Environmental Impact Assessment Report No 100123-11523, dated 11.5.2023, supplemented on 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.)) - dust protection - protection of soil and groundwater (Environmental Impact Assessment Report No. 100123-11523, dated 11.5.2023, supplemented 13.11.2023 and 28.3.2024 (E-NET OKOLJE d.o.o. and GIGA-R d.o.o.), Risk analysis for contamination of the groundwater No. 0346-023/2023, May 2023 (Geološko projektiranje d.o.o.)) - construction waste management (Construction Waste Management Plan) The training shall be carried out in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.1 1.2, 2.2, 3.2 and 4.2 Training for the parties implementing the construction work
0.2.14 | Navodila za obratovanje in vzdrževanje objekta Izvajalec pripravi Navodila za obratovanje in vzdrževanje objekta skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilih: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual | Instructions for the operation and maintenance of the facility The Contractor shall prepare the Operation and Maintenance Instructions for the Facility in accordance with the applicable Slovenian legislation and the DGNB System Instructions specified in the Criteria: PRO 1.5 1.1 Production and provision of maintenance, inspection, operating and care instructions 3.1 Production and provision of a facility management manual
0.2.15 | Meritve kontrole kakovosti gradnje Izvajalec mora upoštevati, da se bodo po koncu gradnje izvedle naslednje meritve: - meritve zrakotesnosti - meritve s termokamero (termografija) - meritve akustike - meritve zvočne zaščite ovoja stavbe - meritve zvočne zaščite ločilnih elementov med posameznimi prostori različnih namembnosti - meritve udarnega zvoka - meritve vlažnosti vgrajenih elementov, pred vgradnjo finalnih tlakov - test odvoda dima in toplote Meritve morajo opraviti ustrezno usposobljeni preskusni organi ali strokovnjaki ter rezultate oceniti in primerjati z zahtevami. Obseg opravljenih meritev mora biti sorazmeren z velikostjo zgradbe in mora ustrezno odražati cilj preverjanja kakovosti zgradbe. Smiselno je, da izvajalec del tekom gradnje za sprotno kontrolo kakovosti vgrajenih materialov, elementov in opreme, sam izvaja meritve. Končne meritve (ob primopredaji) izvede tretja oseba kot neodvisna potrditev doseganja zahtev. Meritve se izvajajo skladno z veljavno slovensko zakonodajo in navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 2. Quality control measurements | Construction quality control measurements The contractor must take into account that the following measurements will be carried out after completion of the construction: - airtightness measurements - thermal camera measurements (thermography) - acoustics measurements - measurements of the sound insulation of the building envelope - measurements of the sound insulation of the separating elements between different rooms of different uses - impact sound measurements - moisture measurements of the installed elements, prior to the installation of the final flooring - smoke and heat extraction test The measurements shall be carried out by suitably qualified test bodies or experts and the results evaluated and compared with the requirements. The extent of the measurements carried out shall be proportionate to the size of the building and shall adequately reflect the objective of the building quality verification. It is reasonable for the contractor to carry out his own measurements during construction to check the quality of the materials, elements and equipment installed. Final measurements (at handover) are carried out by a third party as an independent confirmation of compliance with the requirements. The measurements shall be carried out in accordance with the applicable Slovenian legislation and the DGNB system instructions specified in the benchmark: PRO 2.2 2. Quality control measurements
0.2.16 | Zagotavljanje kakovosti za uporabljene gradbene proizvode Izvajalec mora zagotavljati izvajanje primerjav med definiranim in dejansko uporabljenim materialom, elementom ali opremo skladno seznamom: DGNB razredi kakovosti vgrajenih materialov, elementov in opreme (JULFS--7X9001), vključno z dokazno dokumentacijo ugotovitev primerjav ter skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.2 3.1 Quality assurance for the used construction products | Quality assurance for the construction products used The Contractor shall ensure that comparisons are made between the defined and the actual material, element or equipment used in accordance with the list: DGNB Quality Grades of Installed Materials, Elements and Equipment (JULFS--7X9001), including supporting documentation of the findings of the comparisons, and in accordance with the DGNB system instructions defined in the Criterion: PRO 2.2 3.1 Quality assurance for the used construction products
0.2.17 | Zaščita pred vlago Izvajalec predloži dokumentacijo, ki dokazuje, da je bil izveden program prezračevanja, prilagojen stavbi, s čimer se zagotovi pogoje, da so vgrajeni gradbeni elementi ustrezno suhi, skladno z navodili DGNB opredeljenimi v merilu: PRO 2.2 4.1 Mould prevention | Protection against moisture The Contractor shall provide documentation demonstrating that a building-specific ventilation programme has been implemented to ensure that the building elements installed are adequately dry, in accordance with the DGNB guidelines specified in the criteria: PRO 2.2 4.1 Mould prevention
0.2.18 | Preizkusi delovanja sistemov Izvajalec sodeluje pri izvedbi predhodnega in končnega preizkusa delovanja vseh bistvenih tehničnih komponent stavbe in pripravi ustrezne dokazne dokumentacije ter pri usposabljanju vzdrževalcev/upravljalcev stavbe, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators | System performance tests The Contractor shall be involved in the performance of the preliminary and final performance tests of all essential technical components of the building and the preparation of the relevant supporting documentation, as well as in the training of the maintenance/management staff of the building, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 3.1 Performance of a preliminary function test 4.1 Performance and documentation of a function test and training for the operators
0.2.19 | Poročilo o zagonu objekta Izvajalec sodeluje pri pripravi končnega poročila o zagonu objekta, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 5.1 Creation of a detailed final report | Commissioning report The Contractor shall be involved in the preparation of the final commissioning report, in accordance with the DGNB system guidelines defined in the Criterion: PRO 2.3 5.1 Creation of a detailed final report
0.2.20 | Koncept celovitega delovanja sistemov v stavbi Izvajalec sodeluje pri procesu implementiranja stalnega nadzora in nastavitev delovanja stavbe ter usposabljanju vzdrževalcev/upravljalcev stavbe. Navedeno se izvede v skladu z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 6.1 Creation and handover of an integral operating concept | The concept of integrated building systems The contractor is involved in the process of implementing the building's continuous monitoring and settings and training the building's maintenance/management staff. This shall be done in accordance with the DGNB system instructions defined in the benchmark: PRO 2.3 6.1 Creation and handover of an integral operating concept
0.2.21 | Prilagoditev nastavitev sistemov po začetni fazi uporabe objekta Izvajalec sodeluje pri ponovnem pregledu delovanja vseh bistvenih tehničnih sistemov ter eventualni ponovni prilagoditvi teh sistemov s strani strokovnjaka oz. (neodvisne) tretje osebe. Postopek se izvede po približno 10–14 mesecih po zaključku gradnje, skladno z navodili DGNB sistema opredeljenimi v merilu: PRO 2.3 7.1 Readjustment of the system following initial operating phase | Adjusting system settings after the initial phase of use of the building The Contractor shall be involved in the re-examination of the functioning of all essential technical systems and the possible re-adjustment of these systems by an expert or (independent) third party. The procedure shall be carried out approximately 10-14 months after completion of construction, in accordance with the DGNB system guidelines defined in the benchmark: PRO 2.3 7.1 Readjustment of the system following initial operating phase

## 4.11.0_Rekapitulacija
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
| REKAPITULACIJA STROŠKOV STROJNIH DEL | COST SUMMARY OF MECHANICAL WORKS
| 4 NAČRT S PODROČJA STROJNIŠTVA | 4 DOCUMENTATION IN THE FIELD OF MECHANICAL ENGINEERING
| 4/11 Laboratorij LICEM, oskrba z gorivi | 4/11 Laboratory LICEM, Fuel supply
4.11 | STROJNA DELA | MECHANICAL WORKS
4.11.1 | TEKOČE GORIVO - MB95 in D2 | LIQUID FUELS - MB95 and D2 | 0
4.11.2 | OSKRBA S CNG | CNG SUPPLY | 0
4.11.3 | OSKRBA S PROPANOM | PROPANE SUPPLY | 0
4.11.4 | ELEKTRO DELA - IZENAČEVANJE POTENCIALA | ELECTRICAL WORK - EQUIPOTENTIAL BONDING | 0
0
0 | NEPREDVIDENA DELA | UNFORSEEN WORKS | 0
| SKUPAJ STROJNA DELA | TOTAL MECHANICAL WORKS | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT

## 4.11.1_TEKOČE GORIVO - MB95 in
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.11 | STROJNA DELA | MECHANICAL WORKS
4.11.1 | TEKOČE GORIVO - MB95 in D2 | LIQUID FUELS - MB95 and D2 |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
1 | TEKOČE GORIVO - MB95 in D2 | LIQUID FUELS - MB95 and D2
| Namestitev šprinklerskega gasilnega sistema mora biti izvedena v skladu s smernico VdS CEA 4001:2021 s strani izvajalca s VdS pooblastilom za izvajanje šprinklerskih gasilnih sistemov. Če lokalni predpisi za določena dela zahtevajo podizvajalce, jih mora pooblaščeni izvajalec informirati o posebnih zahtevah VdS smernice. | The installation of the sprinkler system must be carried out in accordance with VdS guideline CEA 4001:2021 by a contractor authorised by VdS to carry out sprinkler systems. If local regulations require subcontractors for certain works, the authorised contractor must inform them of the specific requirements of the VdS guideline.
1.1 | Jeklene nerjavne cevi, za laboratorijske tehnične pline , material AISI 316L (W.Nr 1.4435), notranja površinska hrapavost Ra≤0,8µm, za tlake 200 bar, metrične dimenzije, vključno z vijačnimi oblikovnimi kosi (loki, redukcije, T kosi, ...) in tesnili za tlake 200 bar; komplet z originalnim pritrdilnim in obešalnim materialom proizvajalca; | Stainless steel tubes, for laboratory technical gases, material AISI 316L (W.Nr 1.4435), internal surface roughness Ra≤0,8µm, for pressures of 200 bar, metric dimensions, incl. screw fittings (bows, reducers, T-pieces, etc.) and gaskets for pressures of 200 bar; complete with original fixing and hanging material of the manufacturer;
| - ustreza proizvod SWAGELOK tip Metric Sizes ali enakovredno | - corresponds to SWAGELOK type Metric Sizes or equivalent
| DN 4, ø 6 x 1 | DN 4, ø 6 x 1 | m | 6 |  | 0
| DN 10, ø 12 x 1 | DN 10, ø 12 x 1 | m | 180 |  | 0
| 90°lok DN 4, ø 6 x 1 | 90°lok DN 4, ø 6 x 1 | kos | 4 |  | 0
| 90°lok DN 10, ø 12 x 1 | 90°lok DN 10, ø 12 x 1 | kos | 135 |  | 0
| T kos DN 10 / odcep DN 4 | T piece DN 10 / branch DN 4 | kos | 5 |  | 0
| T kos DN 10 / odcep DN 10 | T piece DN 10 / branch DN 10 | kos | 10 |  | 0
| T kos DN 20 / odcep DN 15 | T piece DN 20 / branch DN 15 | kos | 6 |  | 0
| T kos DN 20 / odcep DN 20 | T piece DN 20 / branch DN 20 | kos | 2 |  | 0
| redukcija DN 10 / DN 8 | reduction DN 10 / DN 8 | kos | 5 |  | 0
| spojka ø 12 "male connector" -12M0-1-8 | connector ø 12 "male connector" -12M0-1-8 | kos | 3 |  | 0
| spojka ø 12 "male connector" -12M0-1-8 | connector ø 12 "male connector" -12M0-1-8 | kos | 4 |  | 0
| spojka ø 12 "male connector" -12M0-1-4 | connector ø 12 "male connector" -12M0-1-4 | kos | 2 |  | 0
| reducirna spojka 1/2 / 1/4 "male to Female NPT" -8-RB-4 | reducing coupling 1/2 / 1/4 "male to female NPT" -8-RB-4 | kos | 3 |  | 0
| spojka ø 12 | coupling ø 12 | kos | 40 |  | 0
| čep DN 20 - female | plug DN 20 - female | kos | 4 |  | 0
1.2 | Dvokomponentna membranska črpalka (AODD), z zračnim pogon, z dovodnim in odvodnim priključkom goriva 1/4” NPT, priklop za komprimiran zrak R 1/8”. volumski pretok do 19 l/min (merjeno za vodo pri 20°C, maksimalna tlačna višina 7 bar, sesalne višine 9 metrov (mokro) in suho 1 meter. Ohišje in sedeži ventilov znotraj črpalke sestavljeni iz prevodni PE UHMW, kroglici ventili PTFE, membrana iz PTFE "over-molded". Temperaturno območje delovanja do 100°C. ATEX certifikat, EX II 2GD c II B Tx | Air-operated double diaphragm pump (AODD), with fuel inlet and outlet 1/4" NPT, compressed air connection R 1/8".Volumetric flow up to 19 l/min (measured for water at 20°C, maximum pressure head 7 bar, suction head 9 metres (wet) and 1 metre dry. Housing and valve seats inside the pump made of conductive PE UHMW, PTFE ball valves, PTFE "over-molded" diaphragm. Operating temperature range up to 100°C. ATEX certified, EX II 2GD c II B Tx
| - ustreza proizvod Verderair PURE VA‑P08GG GG TF TO TN PD ali enakovredno | - corresponds to Verderair PURE VA-P08GG GG TF TO TN PD or equivalent | kos | 2 |  | 0
1.3 | Aktivni dušilec pulzacij za membranske črpalke. Življenjska funkcija: zmanjšanje pulzacij do 95 %. Nameščen na izhodno stran črpalke. Primerno za agresivne medije. Minimalna poraba stisnjenega zraka. tekočinski del ohišje iz konduktivni PE UHMW, zračni del ohišja iz konduktivni polietilen PE UHMW, membrana iz PTFE "overmolded", priključki za kompr. zrak R1/8", priključek za tekoče gorivo 3/8" NPT moški, maksimalni obratovalni tlak 7 bar. ATEX certifikat, EX II 2GD c II B Tx | Active pulsation damper for diaphragm pumps. Lifetime function: pulsation reduction up to 95%. Mounted on the outlet side of the pump. Suitable for aggressive media. Minimum compressed air consumption. liquid part housing made of conductive PE UHMW, air part housing made of conductive polyethylene PE UHMW, diaphragm made of PTFE "overmolded", air connections R1/8", liquid fuel connection 3/8" NPT male, maximum operating pressure 7 bar. ATEX certified, EX II 2GD c II B Tx
| - ustreza proizvod Verderair PD-P08GG TO TN ali enakovredno | - corresponds to Verderair PD-P08GG TO TN or equivalent | kos | 2 |  | 0
1.4 | Protipovratni ventil,, nerjavno jeklo 316, 12 mm Tube Fitting obe strani; razporka (cracking pressure) 1,8 bar (navedena izvedba); tesnila iz PTFE | Check valve,, 316 stainless steel, 12 mm Tube Fitting both sides; cracking pressure 1,8 bar (version specified); PTFE seals
| - ustreza proizvod Swagelok SS‑12C‑MM-25 Poppet Check Valve ali enakovredno | - corresponds to Swagelok SS-12C-MM-25 Poppet Check Valve or equivalent | kos | 2 |  | 0
1.5 | Sesalni čep, 1.4301, navoj ISO 228. Čep se prevrta, vstavi sesalna/povratna cev dimenzije in ustrezno privari, da se zagotovi zrakotesnost soda in inštalacije | Suction plug, 1.4301, thread ISO 228. The plug shall be overturned, a suction/return hose of the dimension inserted and welded in place to ensure the airtightness of the barrel and the installation
| 2" | 2" | kos | 2 |  | 0
1.6 | Prestrujni ventil, – ventil za srednji pretok iz nerjavečega jekla 316 SS, cevni priključki obe strani, 6 mm, CV max 0,03, ročaj z reliefnim vzorcem (knurled), delovna temperatura od ‑23 °C do +204 °C, standard čiščenja SC‑10. Namenjen za fino uravnavanje pretoka v procesnih sistemih. | Pressure valve, - medium flow valve made of 316 SS stainless steel, hose connections both sides, 6 mm, CV max 0,03, handle with knurled pattern, operating temperature from -23 °C to +204 °C, cleaning standard SC-10. Designed for fine flow control in process systems.
| - ustreza proizvod Swagelok SS‑6MG‑MM ali enakovredno | - corresponds to Swagelok SS-6MG-MM or equivalent | kos | 2 |  | 0
1.7 | Hidravlična hitra spojka z vtičem in tlačno razbremenitvijo (eliminatorjem), 1.4404, NPT 1/4” notranji navoj (Female), ISO 7241-1, tip B, Jeklo (karbon jeklo), površinsko zaščiteno (cinkano ali s Cr6-free premazom), NBR (nitrilna guma), temperaturno območje -25°C - 200°C | Hydraulic quick coupling with plug and pressure relief (eliminator), 1.4404, NPT 1/4" female thread (Female), ISO 7241-1, Type B, Steel (carbon steel), surface protected (zinc plated or Cr6-free coating), NBR (nitrile rubber), temperature range -25°C - 200°C
| - ustreza proizvod Landfeld, VAM 14 ES- VAS 14 ES ali enakovredno | - corresponds to Landfeld, VAM 14 EC- VAS 14 EC or equivalent | kos | 6 |  | 0
1.8 | Gibka, fleksibilna cev “Yellow Band” Elaflex HD 10, ID 10 mm (3/8”), dolžine 5,00 m, brez spirale, za tlačno točenje naftnih derivatov in letalskih goriv. Notranja plast NBR, zunanji ovoj CR, antistatična (<10⁶ Ω), delovni tlak do 25 bar, temperaturno območje –30 do +90 °C. Opremljena z nerjavnima priključkoma MC10–3/8” SS (notranji navoj), tesnilo PTFE, objemke iz nerjavečega jekla SPANNLOC. Odobreno po EN 1761, EN 12115 in VG 95 955 Typ D. | Elaflex HD 10 "Yellow Band" flexible hose, ID 10 mm (3/8"), 5,00 m (5,00 m) length, without spiral, for pressure dispensing of petroleum products and aviation fuels. NBR inner layer, CR outer sheath, antistatic (<10⁶ Ω), working pressure up to 25 bar, temperature range -30 to +90 °C. Fitted with MC10-3/8" SS stainless steel connectors (internal thread), PTFE gasket, SPANNLOC stainless steel clamps. Approved according to EN 1761, EN 12115 and VG 95 955 Type D.
| - ustreza proizvod Elaflex HD 13 L1=4m MC 10-3/8" SS/SS ¦ MC 10 3/8" SS/SS ali enakovredno | - corresponds to Elaflex HD 13 L1=4m MC 10-3/8" SS/SS ¦ MC 10 3/8" SS/SS or equivalent | kos | 2 |  | 0
| - ustreza proizvod Elaflex HD 13 L1=1,0m MC 10-3/8" SS/SS ¦ MC 10 3/8" SS/SS ali enakovredno | - corresponds to Elaflex HD 13 L1=1,0m MC 10-3/8" SS/SS ¦ MC 10 3/8" SS/SS or equivalent | kos | 2 |  | 0
1.9 | Kroglični ventil s ročnim odpiranjem in zapiranjem – nerjaveče jeklo, 1/2", SS, R-PTFE, Krogla iz nerjavečega jekla, sedež iz ojačan PTFE (R-PTFE) | Ball valve with manual opening and closing - Stainless steel, 1/2", SS, R-PTFE, Stainless steel ball, PTFE reinforced seat (R-PTFE)
| - ustreza proizvod SWAGELOK tip SS‑63TF8 ali enakovredno | - corresponds to SWAGELOK product type SS-63TF8 or equivalent | kos | 6 |  | 0
1.10 | Instrumentni dvo‑ventilski blok (manifold), 2 ventila, 2 ventila, material telesa nerjaveče jeklo (316 SS), 12 mm cevno fitting (tube fitting) dodatni priključek / izpuh (bleed): 1/4" FEMALE NPT (navoj notranji , FKM (fluorokarbon) | Instrument two-valve block (manifold), 2 valves, 2 valves, body material stainless steel (316 SS), 12 mm pipe fitting (tube fitting) additional connection / bleed: 1/4" FEMALE NPT (threaded internal , FKM (fluorocarbon)
| - ustreza proizvod SWAGELOK tip SS‑V2BFS12MM‑FL (Swagelok V‑serija, 2 ventila) ali enakovredno | - corresponds to SWAGELOK product type SS-V2BFS12MM-FL (Swagelok V-series, 2 valves) or equivalent | kos | 2 |  | 0
1.11 | Manometer za tekoče gorivo za območje merjanja od 0 do 10 bar, premer skale ø 50 mm, izdelan iz materiala nerjavno jeklo AISI 316L / EPDM, 1/4" NPT (notranji navoj), Tesnila: NBR | Liquid fuel pressure gauge for measuring range from 0 to 10 bar, scale diameter ø 50 mm, made of stainless steel AISI 316L / EPDM, 1/4" NPT (internal thread), Gaskets: NBR
| - ustreza proizvod SWAGELOK tip PGI-50M-BG10-L-AO-X) ali enakovredno | - corresponds to SWAGELOK product type PGI-50M-BG10-L-AO-X) or equivalent | kos | 2 |  | 0
1.12 | Regulacijska grupa komprimiranega zraka za krmiljenje in pogon mebranske črpalke Sestavljena iz: 3/2 zapornega ventila ON/OFF električno vodenega 24 V DC filtra in regulatorja tlaka, maksimalni pretok KZ 1500 l/min, obratovalni tlak 0,5-16 bar, priključek 1/4" BSP dušilni ventil maksimalni pretok KZ 1100 l/min, priključek 1/4" BSP Ventil za mehki zagon, Maksimalni pretok 1000 l/min, priključek KZ 1/4" BSP, | Compressed air control group for control and drive of mebran pump Consisting of: 3/2 ON/OFF shut-off valve electrically controlled 24 V DC filter and pressure regulator, max. flow rate KZ 1500 l/min, operating pressure 0,5-16 bar, connection 1/4" BSP throttle valve max. flow KZ 1100 l/min, 1/4" BSP connection Soft start valve, max. flow 1000 l/min, connection KZ 1/4" BSP,
| - ustreza proizvod Verderair tip ACP1/4-CV24V-FR-TV-ST-CK(3)-MB2 ali enakovredno | - corresponds to Verderair product type ACP1/4-CV24V-FR-TV-ST-CK(3)-MB2 or equivalent | kpl | 2 |  | 0
1.13 | Varnostni ventil, za uravnavanje podtlaka in nadtlaka v sodu goriva. Ventil omogoča nastavitev tlaka odpiranja v območju od 5 do 500 mbar in je opremljen z navojnimi priključki G ½ . Ohišje izdelano iz nerjavečega jekla, disk pa iz materiala NBR. Standardno temperaturno območje delovanja znaša od -30 °C do +100 °C, pri posebni izvedbi z nerjavečim diskom pa do +270 °C. Ventil za nazivni tlak PN10 in izpolnjuje zahteve standarda DIN EN ISO 4126‑1 ter evropske direktive o tlačni opremi PED 2014/68/EU. Namesti se dva ventil nasprotno nameščena, eden služi za odpiranje pri podtlaku, drugi za odpiranje pri nadtlaku | Safety valve for regulating the vacuum and overpressure in a fuel drum. The valve allows the opening pressure to be adjusted from 5 to 500 mbar and is equipped with threaded connections G ½ . The body is made of stainless steel and the disc is made of NBR material. The standard operating temperature range is -30 °C to +100 °C, and up to +270 °C for the special version with stainless disc. The valve is rated for a pressure of PN10 and complies with the requirements of DIN EN ISO 4126-1 and with the European Pressure Equipment Directive (PED) PED 2014/68/EU. The valve is installed with two valves mounted in opposite positions, one for the vacuum opening and the other for the overpressure opening
| - ustreza proizvod WITT tip Ultravent15 ali enakovredno | - corresponds to WITT product type Ultravent15 or equivalent | kpl | 4 |  | 0
1.14 | Tlačni preskus trdnosti in tesnenja sistema cevovodov, skladeno z opisom v "IZS Priročnik tlačnih preizkusov strojnih inštalacij", vključno s potrebnim materialom za izvedbo preizkusa, ter izdelavo pisnega poročila o uspešno opravljenem tlačnem preizkusu; | Pressure test of the strength and tightness of the piping system, as described in the "IZS Manual for Pressure Testing of Mechanical Installations", including the necessary materials for the test, and the production of a written report on the successful completion of the pressure test;
| preskusni tlak = 1,43 x 8 bar = 11,44 bar(n) | test pressure = 1,43 x 8 bar = 11,44 bar(n) | kpl | 2 |  | 0
1.15 | Izpihovanje cevovodov z zrakom ali inertnim plinom (na primer dušik) v celotnem sistemu z namenom odstranjevanja nečistoč; | Blowing out the piping with air or an inert gas (e.g. nitrogen) throughout the system to remove impurities; | kpl | 2 |  | 0
1.16 | Ognjeodporna tesnilna masa, vgradnja na prehodu cevovodov skozi zid med požarnima sektortjema, požarna odpornost 90 minut, ustreza proizvod HILTI ali enakovredno. | Fire-resistant sealant, for installation at the transition of pipelines through the wall between the two fire sectors, fire resistance 90 minutes, equivalent to HILTI or equivalent.
| Vsak prehod mora biti označen z nalepko ali tablico z osnovnimi požarnimi podatki; | Each passageway must be marked with a sticker or placard with basic fire information; | kpl | 8 |  | 0
1.17 | Priprava na delo, ki mora obsegati pregled projektne dokumentacije za izvedbo (PZI) del, identifikacijo morebitnih neskladij, napak ali pomanjkljivosti ter pravočasno pisno obveščanje projektanta o ugotovljenih nepravilnostih. V sklop priprave sodijo tudi vsi usklajevalni sestanki, tehnična priprava na izvedbo, izdelava montažnih in delavniških risb ter razreševanje kolizij, ki ne vplivajo na delovanje sistema, kot so lokalni odmiki cevi zaradi ovir, prilagajanje višine, smeri ali naklona, zagotavljanje praznjenja ali odzračevanja. O spremembah je treba obveščati nadzornika. | Preparation for the work, which shall include review of the design documentation for the execution (PZI) of the works, identification of any discrepancies, defects or deficiencies, and timely written notification to the designer of any identified anomalies. Preparation shall also include all coordination meetings, technical preparation for execution, preparation of erection and shop drawings, and resolution of conflicts that do not affect the operation of the system, such as local deviations of pipes due to obstructions, adjustments to height, direction or slope, provision of emptying, or venting. Changes shall be notified to the supervisor. | kpl | 1 |  | 0
1.18 | Preizkusno obratovanje delovanja sistema v obsegu: | Operational test of the system in scope:
| - pregled jeklenk in omar za jeklenke, | - inspection of cylinders and cylinder lockers,
| - pregled ekspanzijskih reducirnih postaj za redukcijo visokega tlaka, | - an overview of expansion reduction stations for high pressure reduction,
| - pregled inštalacije cevovodov, armatur in opreme | - inspection of piping, fittings and equipment
| - pregled delovanja varnostnih funkcij (zapiranje pnevmatskih ventilov, delovanje detektorjev, delovanje prezračevanja omar za jeklenka ipd), | - checking the operation of safety functions (closing of pneumatic valves, operation of detectors, operation of cylinder cabinet ventilation, etc.),
| - pregled odjemnih mest. | - a review of the customer sites.
| Preizkusno obratovanje traja neprekinjeno 72 ur. | The test operation shall be continuous for 72 hours. | kpl | 1 |  | 0
1.19 | Napisne ploščice iz nerjavne pločevine z vgravirano oznako po shemi za opremo in armature, kompletno z jekleno pritrdilno žico ali visoko kvalotetne nalepke; visoko trajanje H (več kot 15 let) | Stainless steel nameplates with engraved marking according to the scheme for fittings and fixtures, complete with steel fixing wire or high quality labels; high durability H (more than 15 years) | kpl | 1 |  | 0
1.20 | Samolepilne puščice za označitev smeri pretoka ter z napisom vrste medija; visoko trajanje H (več kot 15 let) | Self-adhesive arrows to indicate direction of flow and type of media; high H lifetime (more than 15 years) | kpl | 1 |  | 0
1.21 | Izdelava montažnih risb za izvedbo inštalacij med gradnjo objekta, kot so: detajli priključkov, montažne skice, montažni detajli, ipd. | Preparation of assembly drawings for the installation of services during the construction of the building, such as: connection details, assembly sketches, assembly details, etc. | kpl | 1 |  | 0
1.22 | Kvalifikacije montaže IQ-pregledi (instalation qualification) po GEP Commissioning protokolu in dokumentiranje kvalifikacije montaže, vključno z odpravo prvotnih napak montaže; | Installation qualification IQ-checks (installation qualification) according to the GEP Commissioning Protocol and documentation of installation qualification, including correction of original installation faults; | kpl | 1 |  | 0
1.23 | Meritve delovanja OQ-kvalifikacija (operation qualification) ter dokumentiranje meritev delovanja, vključno z nastavitvijo parametrov; | OQ (operation qualification) measurements and documentation of performance measurements, including parameter setting; | kpl | 1 |  | 0
1.24 | Posnetki izvedenega stanja, sprotno beleženje vseh sprememb nastalih med izvedbo, vrisovanje in vpisovanje v PZI projektno dokumentacijo; | Recording of the as-built condition, keeping a running record of any changes made during execution, plotting and entering into the PZI project documentation; | kpl | 1 |  | 0
1.25 | Stenska shema sistema, vloženo v zaščitni okvir s prosojnim umetnim steklomo (plastika) ali plastificirano, vključno s pritrditvijo na notranjo steno v strojnici objekta; | Wall diagram of the system, enclosed in a protective frame with transparent plastic or plasticised glass, including fixing to an internal wall in the mechanical room of the building; | kpl | 1 |  | 0
1.26 | Primopredajna dokumentacija, ki mora vsebovati: izjave, dokazilo o zanesljivosti objekta, certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo, obratovanje in vzdrževanje ter ostalo primopredajno dokumantacijo. Predaja se v dveh mapiranih izvodih ter en izvod v elektronski obliki; | The handover documentation, which shall include: declarations, proof of the reliability of the facility, certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use, operation and maintenance, and other handover documentation. It shall be handed over in two mapped copies and one copy in electronic form; | kpl | 1 |  | 0
1.27 | Elaborat eksplozijske ogroženosti z oceno tveganja - faza PID | Explosion Hazard Laboratory with Risk Assessment - PID phase | kpl | 1 |  | 0
1.28 | Certificiranje EX elaborata | Certification of the EX study | kpl | 1 |  | 0
| TEKOČE GORIVO - MB95 in D2 | LIQUID FUELS - MB95 and D2 |  |  |  | 0

## 4.11.2_OSKRBA Z CNG
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.11 | STROJNA DELA | MECHANICAL WORKS
4.11.2 | OSKRBA S CNG | CNG SUPPLY |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
2 | OSKRBA S CNG | CNG SUPPLY
| Izvajalec del ter dobavitelj opreme in inštalacij tehničnih plinov za laboratorije mora imeti certifikat za delo s tehničnimi plini v Sloveniji. Spisek pooblaščenih podjetij vodi Gospodarsko interesno združenje za tehnične pline Slovenije. | The contractor and the supplier of equipment and installations of technical gases for laboratories must be certified to work with technical gases in Slovenia. The list of certified companies is maintained by the Economic Interest Association for Technical Gases of Slovenia.
| Vse postavke v nadalevanju zajemajo dobavo in montažo (razen tam kjer je to posebej navedeno). | All items below include delivery and installation (except where specifically indicated).
2.1 | Visokotlačni boks z štirimi jeklenkami v paketu za CNG, PN300, za tlak plina 200 bar ali 300 bar, prostornina 150 litrov, označeno po standardu SIST EN 1089-3, dimenzija D x L = ø930 x 1950 mm, teža 1100 kg, vsebina 120 Nm3 ali 180 Nm3 tehničnega plina, vključno z zapornim ventilom na boksu, varovalnim čepom. | High pressure box with four cylinders in package for CNG, PN300, for gas pressure 200 bar or 300 bar, volume 150 litres, marked according to SIST EN 1089-3, dimensions L x L = ø930 x 1950 mm, weight 1100 kg, capacity 120 Nm3 or 180 Nm3 of technical gas, incl. shut-off valve on box, safety plug.
| - ustreza proizvod MESSER MEGAPACK C4 ali enakovredno; | - corresponds to MESSER MEGAPACK C4 or equivalent;
| CH4 … metan - CNG | CH4 ... methane - CNG | kpl | 1 |  | 0
2.2 | Visokotlačna nerjavna cevi, za priklop paketa visokotlačnih jeklenk na ekspanzijsko reducirno postajo, ustreznost za laboratorijske tehnične pline, material AISI 316L (W.Nr 1.4435), notranja površinska hrapavost Ra≤0,8µm, za tlake 300 bar, vključno s pritrdilnim in tesnilnim materialom; | High-pressure stainless steel hose, for connection of a bundle of high-pressure cylinders to an expansion reduction station, suitable for laboratory technical gases, material AISI 316L (W.Nr 1.4435), internal surface roughness Ra≤0,8µm, for pressures of 300 bar, incl. fastening and sealing material;
| CH4 … metan - CNG | CH4 ... methane - CNG | kpl | 1 |  | 0
2.3 | Ekspanzijska reducirna postaja laboratorijskega tehničnega plina iz tlaka 200 ali 300 bar na 10 bar za priklop celotnega paketa jeklenk, za visoke pretoke, PN300, izdelano kot kompaktna naprava sestavljeno iz: priklop na jeklenko, visokotlačni zaporni ventil, ventil za izpihovanje, regulator tlaka, manomater tlaka jeklenke, manomater tlaka omreržja, oddušni varnostni ventil, pnevmatski ventil za omrežje (normalno zaprt), priklop na omrežje, vključno s pritrdilnim in tesnilnim materialom; | Expansion reducing station for laboratory technical gas from 200 or 300 bar to 10 bar for connection of a complete cylinder package, for high flows, PN300, manufactured as a compact unit, comprising: cylinder connection, high pressure stop valve, blow-off valve, pressure regulator, cylinder pressure gauge, pressure gauge of the fitting, vent safety valve, pneumatic valve for mains (normally closed), connection to mains, including fitting and sealing material;
| - ustreza proizvod SPECTRON tip BU13 ali enakovredno | - corresponds to SPECTRON product type BU13 or equivalent
| CH4 … metan - CNG | CH4 ... methane - CNG | kpl | 2 |  | 0
2.4 | Varnostna armatura za laboratorijski tehnični plin v skladu z EN 730-1, ISO 5175, z naslednjimi funkcijami: plinski nepovratni ventil NV, plamenska zapora FA, termično varovalo TV, PN15, materiala nerjavno jeklo, vključno z pritrdilnim in tesnilnim materialom; | Safety fittings for laboratory technical gas in accordance with EN 730-1, ISO 5175, with the following functions: gas non-return valve NV, flame arrestor FA, thermal fuse TV, PN15, material stainless steel, including fixing and sealing material;
| - ustreza proizvod IBEDA tip DG91N VA ali enakovredno | - corresponds to IBEDA product type DG91N VA or equivalent
| CH4 … metan - CNG | CH4 ... methane - CNG | kpl | 6 |  | 0
2.5 | Kroglični ventil s ročnim odpiranjem in zapiranjem – nerjaveče jeklo, 1", SS, R-PTFE, Krogla iz nerjavečega jekla, sedež iz ojačan PTFE (R-PTFE) | Ball valve with manual opening and closing - stainless steel, 1", SS, R-PTFE, Stainless steel ball, PTFE reinforced seat (R-PTFE)
| - ustreza proizvod SWAGELOK tip SS-65TS25MM ali enakovredno | - corresponds to SWAGELOK product type SS-65TS25MM or equivalent | kos | 3 |  | 0
2.6 | Hidravlična hitra spojka z vtičem in tlačno razbremenitvijo (eliminatorjem), 1.4404, NPT 1/4” notranji navoj (Female), ISO 7241-1, tip B, Jeklo (karbon jeklo), površinsko zaščiteno (cinkano ali s Cr6-free premazom), NBR (nitrilna guma), temperaturno območje -25°C - 200°C | Hydraulic quick coupling with plug and pressure relief (eliminator), 1.4404, NPT 1/4" female thread (Female), ISO 7241-1, Type B, Steel (carbon steel), surface protected (zinc plated or Cr6-free coating), NBR (nitrile rubber), temperature range -25°C - 200°C
| - ustreza proizvod Landfeld, VAM 14 ES- VAS 14 ES ali enakovredno | - corresponds to Landfeld, VAM 14 EC- VAS 14 EC or equivalent | kos | 6 |  | 0
2.7 | Jeklene nerjavne cevi, za laboratorijske tehnične pline , material AISI 316L (W.Nr 1.4435), notranja površinska hrapavost Ra≤0,8µm, za tlake 200 bar, metrične dimenzije, vključno z vijačnimi oblikovnimi kosi (loki, redukcije, T kosi, ...) in tesnili za tlake 200 bar; komplet z originalnim pritrdilnim in obešalnim materialom proizvajalca; | Stainless steel tubes, for laboratory technical gases, material AISI 316L (W.Nr 1.4435), internal surface roughness Ra≤0,8µm, for pressures of 200 bar, metric dimensions, incl. screw fittings (bows, reducers, T-pieces, etc.) and gaskets for pressures of 200 bar; complete with original fixing and hanging material of the manufacturer;
| - ustreza proizvod SWAGELOK tip Metric Sizes ali enakovredno | - corresponds to SWAGELOK type Metric Sizes or equivalent
| DN 20, ø 25 x 2,5 | DN 20, ø 25 x 2,5 | m | 60 |  | 0
| 90°lok DN 20, ø 25 x 2,5 | 90°lok DN 20, ø 25 x 2,5 | kos | 40 |  | 0
| T kos DN 20 / odcep DN 20 | T piece DN 20 / branch DN 20 | kos | 5 |  | 0
| redukcija DN 20 / DN 8 | reduction DN 20 / DN 8 | kos | 3 |  | 0
2.8 | Tlačni preskus trdnosti in tesnenja sistema cevovodov, skladeno z opisom v "IZS Priročnik tlačnih preizkusov strojnih inštalacij", vključno s potrebnim materialom za izvedbo preizkusa, ter izdelavo pisnega poročila o uspešno opravljenem tlačnem preizkusu; | Pressure test of the strength and tightness of the piping system, as described in the "IZS Manual for Pressure Testing of Mechanical Installations", including the necessary materials for the test, and the production of a written report on the successful completion of the pressure test;
| preskusni tlak = 1,1 x 200 bar = 220 bar | test pressure = 1,1 x 200 bar = 220 bar | kpl | 1 |  | 0
| preskusni tlak = 1,1 x 300 bar = 330 bar | test pressure = 1,1 x 300 bar = 330 bar | kpl | 1 |  | 0
| preskusni tlak = 1,5 x 10 bar = 15 bar | test pressure = 1,5 x 10 bar = 15 bar | kpl | 1 |  | 0
2.9 | Izpihovanje cevovodov z zrakom ali inertnim plinom (na primer dušik) v celotnem sistemu z namenom odstranjevanja nečistoč; | Blowing out the piping with air or an inert gas (e.g. nitrogen) throughout the system to remove impurities; | kpl | 1 |  | 0
2.10 | Ognjeodporna tesnilna masa, vgradnja na prehodu cevovodov skozi zid med požarnima sektortjema, požarna odpornost 90 minut, ustreza proizvod HILTI ali enakovredno. | Fire-resistant sealant, for installation at the transition of pipelines through the wall between the two fire sectors, fire resistance 90 minutes, equivalent to HILTI or equivalent.
| Vsak prehod mora biti označen z nalepko ali tablico z osnovnimi požarnimi podatki; | Each passageway must be marked with a sticker or placard with basic fire information; | kpl | 1 |  | 0
2.11 | Preizkusno obratovanje delovanja sistema v obsegu: | Operational test of the system in scope:
| - pregled jeklenk in omar za jeklenke, | - inspection of cylinders and cylinder lockers,
| - pregled ekspanzijskih reducirnih postaj za redukcijo visokega tlaka, | - an overview of expansion reduction stations for high pressure reduction,
| - pregled inštalacije cevovodov, armatur in opreme | - inspection of piping, fittings and equipment
| - pregled delovanja varnostnih funkcij (zapiranje pnevmatskih ventilov, delovanje detektorjev, delovanje prezračevanja omar za jeklenka ipd), | - checking the operation of safety functions (closing of pneumatic valves, operation of detectors, operation of cylinder cabinet ventilation, etc.),
| - pregled odjemnih mest. | - a review of the customer sites.
| Preizkusno obratovanje traja neprekinjeno 72 ur. | The test operation shall be continuous for 72 hours. | kpl | 1 |  | 0
2.12 | Napisne ploščice iz nerjavne pločevine z vgravirano oznako po shemi za opremo in armature, kompletno z jekleno pritrdilno žico ali visoko kvalotetne nalepke; visoko trajanje H (več kot 15 let) | Stainless steel nameplates with engraved marking according to the scheme for fittings and fixtures, complete with steel fixing wire or high quality labels; high durability H (more than 15 years) | kpl | 1 |  | 0
2.13 | Samolepilne puščice za označitev smeri pretoka ter z napisom vrste medija; visoko trajanje H (več kot 15 let) | Self-adhesive arrows to indicate direction of flow and type of media; high H lifetime (more than 15 years) | kpl | 1 |  | 0
2.14 | Izdelava montažnih risb za izvedbo inštalacij med gradnjo objekta, kot so: detajli priključkov, montažne skice, montažni detajli, ipd. | Preparation of assembly drawings for the installation of services during the construction of the building, such as: connection details, assembly sketches, assembly details, etc. | kpl | 1 |  | 0
2.15 | Kvalifikacije montaže IQ-pregledi (instalation qualification) po GEP Commissioning protokolu in dokumentiranje kvalifikacije montaže, vključno z odpravo prvotnih napak montaže; | Installation qualification IQ-checks (installation qualification) according to the GEP Commissioning Protocol and documentation of installation qualification, including correction of original installation faults; | kpl | 1 |  | 0
2.16 | Meritve delovanja OQ-kvalifikacija (operation qualification) ter dokumentiranje meritev delovanja, vključno z nastavitvijo parametrov; | OQ (operation qualification) measurements and documentation of performance measurements, including parameter settings; | kpl | 1 |  | 0
2.17 | Posnetki izvedenega stanja, sprotno beleženje vseh sprememb nastalih med izvedbo, vrisovanje in vpisovanje v PZI projektno dokumentacijo; | Recording of the as-built condition, keeping a running record of any changes made during the execution, plotting and recording in the PZI project documentation; | kpl | 1 |  | 0
2.18 | Stenska shema sistema, vloženo v zaščitni okvir s prosojnim umetnim steklomo (plastika) ali plastificirano, vključno s pritrditvijo na notranjo steno v strojnici objekta; | Wall diagram of the system, enclosed in a protective frame with transparent plastic or plasticised glass, including fixing to an internal wall in the mechanical room of the building; | kpl | 1 |  | 0
2.19 | Primopredajna dokumentacija, ki mora vsebovati: izjave, dokazilo o zanesljivosti objekta, certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo, obratovanje in vzdrževanje ter ostalo primopredajno dokumantacijo. Predaja se v dveh mapiranih izvodih ter en izvod v elektronski obliki; | The handover documentation, which shall include: declarations, proof of the reliability of the facility, certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use, operation and maintenance, and other handover documentation. It shall be handed over in two mapped copies and one copy in electronic form; | kpl | 1 |  | 0
2.20 | Elaborat eksplozijske ogroženosti z oceno tveganja - faza PID | Explosion Hazard Laboratory with Risk Assessment - PID phase | kpl | 1 |  | 0
2.21 | Certificiranje EX elaborata | Certification of the EX Study | kpl | 1 |  | 0
| SKUPAJ TEHNIČNI PLINI | SKUPAJ TEHNIČNI PLINI |  |  |  | 0

## 4.11.3_OSKRBA S PROPANOM
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.11 | STROJNA DELA | MECHANICAL WORKS
4.11.3 | OSKRBA S PROPANOM | PROPANE SUPPLY |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
3 | OSKRBA S PROPANOM | PROPANE SUPPLY
| Izvajalec del ter dobavitelj opreme in inštalacij tehničnih plinov za laboratorije mora imeti certifikat za delo s tehničnimi plini v Sloveniji. Spisek pooblaščenih podjetij vodi Gospodarsko interesno združenje za tehnične pline Slovenije. | The contractor and the supplier of equipment and installations of technical gases for laboratories must be certified to work with technical gases in Slovenia. The list of certified companies is maintained by the Economic Interest Association for Technical Gases of Slovenia.
| Vse postavke v nadalevanju zajemajo dobavo in montažo (razen tam kjer je to posebej navedeno). | All items below include delivery and installation (except where specifically indicated).
3.1 | Plinska jeklenka - propan, C3H8, 14 bar, prostornina 150 litrov, označeno po standardu SIST EN 1142:2017, EU direktiva 2010/35/EU, dimenzija D x L = ø183 x 1145 mm, teža 35 kg, vsebina 87 L tehničnega plina, vključno z zapornim ventilom na jeklenki, varovalnim čepom in varnostnim ventilom. | Gas cylinder - propane, C3H8, 14 bar, capacity 150 litres, marked according to SIST EN 1142:2017, EU Directive 2010/35/EU, dimensions L x D = ø183 x 1145 mm, weight 35 kg, 87 L of technical gas, incl. cylinder stop valve, safety plug and safety valve.
| - ustreza proizvod Messer ali enakovredno; | - corresponds to a Messer product or equivalent;
| C3H8 … propan | C3H8 ... propane | kpl | 1 |  | 0
3.2 | Visokotlačna nerjavna cevi, za priklop paketa visokotlačnih jeklenk na ekspanzijsko reducirno postajo, ustreznost za laboratorijske tehnične pline, material AISI 316L (W.Nr 1.4435), notranja površinska hrapavost Ra≤0,8µm, za tlake 300 bar, vključno s pritrdilnim in tesnilnim materialom; | High-pressure stainless steel hose, for connection of a bundle of high-pressure cylinders to an expansion reduction station, suitable for laboratory technical gases, material AISI 316L (W.Nr 1.4435), internal surface roughness Ra≤0,8µm, for pressures of 300 bar, incl. fastening and sealing material;
| C3H8 … propan | C3H8 ... propane | kpl | 1 |  | 0
3.3 | Kroglični ventil s ročnim odpiranjem in zapiranjem – nerjaveče jeklo, 1", SS, R-PTFE, Krogla iz nerjavečega jekla, sedež iz ojačan PTFE (R-PTFE) | Ball valve with manual opening and closing - stainless steel, 1", SS, R-PTFE, Stainless steel ball, PTFE reinforced seat (R-PTFE)
| - ustreza proizvod SWAGELOK tip SS-65TS25MM ali enakovredno | - corresponds to SWAGELOK product type SS-65TS25MM or equivalent | kos | 3 |  | 0
3.4 | Varnostna armatura za laboratorijski tehnični plin v skladu z EN 730-1, ISO 5175, z naslednjimi funkcijami: plinski nepovratni ventil NV, plamenska zapora FA, termično varovalo TV, maksimalni tlak 4 bar za propan, materiala nerjavno jeklo, vključno z pritrdilnim in tesnilnim materialom; | Safety fitting for laboratory technical gas in accordance with EN 730-1, ISO 5175, with the following functions: gas non-return valve NV, flame arrestor FA, thermal fuse TV, maximum pressure 4 bar for propane, material stainless steel, incl. fixing and sealing material;
| - ustreza proizvod WITT ali 85-20 enakovredno | - corresponds to WITT or 85-20 equivalent
| C3H8 … propan | C3H8 ... propane | kpl | 6 |  | 0
3.5 | Regulacijska grupa laboratorijskega odjemnega mesta tehničnega plina, sestavljeno iz: zapornega ventila, reducirnega ventila z manometrom in igličasti ventil, PN40, materiali kromana medenina / nerjavno jeklo / viton, vstopni tlak 10 bar, izstopni tlak od 0 do 4 bar, vključno s pritrdilnim in tesnilnim materialom; | Control group for laboratory technical gas outlet, consisting of: stop valve, pressure reducing valve with manometer and needle valve, PN40, materials chromed brass/stainless steel/viton, inlet pressure 10 bar, outlet pressure 0 to 4 bar, including fixing and sealing material;
| - ustreza proizvod SPECTRON tip EU11 ali enakovredn | - sPECTRON product type EU11 or equivalent
| C3H8 … propan | C3H8 ... propane | kpl | 3 |  | 0
3.6 | Membranski zaporni ventil, ki omogoča avtomatizirano zapiranje pri tlaku upravljanja 6–8 bar, Največji dovoljeni delovni tlak je do 300 bar, Priključki so v izvedbi 1/2″ NPT ženski vhod in izhod. Normalno zaprt | Diaphragm stop valve allowing automated closing at a control pressure of 6-8 bar, Maximum allowable working pressure is up to 300 bar, Connections are 1/2″ NPT female inlet and outlet. Normally closed
| - ustreza proizvod SPECTRON tip MV3-E ali enakovredn | - corresponds to SPECTRON product type MV3-E or equivalent
| C3H8 … propan | C3H8 ... propane | kpl | 1 |  | 0
3.7 | Jeklene nerjavne cevi, za laboratorijske tehnične pline , material AISI 316L (W.Nr 1.4435), notranja površinska hrapavost Ra≤0,8µm, za tlake 200 bar, metrične dimenzije, vključno z vijačnimi oblikovnimi kosi (loki, redukcije, T kosi, ...) in tesnili za tlake 200 bar; komplet z originalnim pritrdilnim in obešalnim materialom proizvajalca; | Stainless steel tubes, for laboratory technical gases, material AISI 316L (W.Nr 1.4435), internal surface roughness Ra≤0,8µm, for pressures of 200 bar, metric dimensions, incl. screw fittings (bows, reducers, T-pieces, etc.) and gaskets for pressures of 200 bar; complete with original fastening and hanging material of the manufacturer;
| - ustreza proizvod SWAGELOK tip Metric Sizes ali enakovredno | - corresponds to SWAGELOK type Metric Sizes or equivalent
| DN 16, ø 20 x 2 | DN 16, ø 20 x 2 | m | 60 |  | 0
| 90°lok DN 16, ø 20 x 2 | 90°lok DN 16, ø 20 x 2 | kos | 40 |  | 0
| T kos DN 15 / odcep DN 15 | T piece DN 15 / branch DN 15 | kos | 15 |  | 0
3.8 | Tlačni preskus trdnosti in tesnenja sistema cevovodov, skladeno z opisom v "IZS Priročnik tlačnih preizkusov strojnih inštalacij", vključno s potrebnim materialom za izvedbo preizkusa, ter izdelavo pisnega poročila o uspešno opravljenem tlačnem preizkusu; | Pressure test of the strength and tightness of the piping system, as described in the "IZS Manual for Pressure Testing of Mechanical Installations", including the necessary materials for the test, and the production of a written report on the successful completion of the pressure test;
| preskusni tlak = 1,5 x 15 bar = 22,5 bar(n) | test pressure = 1,5 x 15 bar = 22,5 bar(n) | kpl | 1 |  | 0
3.9 | Izpihovanje cevovodov z zrakom ali inertnim plinom (na primer dušik) v celotnem sistemu z namenom odstranjevanja nečistoč; | Blowing out the piping with air or an inert gas (e.g. nitrogen) throughout the system to remove impurities; | kpl | 1 |  | 0
3.10 | Ognjeodporna tesnilna masa, vgradnja na prehodu cevovodov skozi zid med požarnima sektortjema, požarna odpornost 90 minut, ustreza proizvod HILTI ali enakovredno. | Fire-resistant sealant, for installation at the transition of pipelines through the wall between the two fire sectors, fire resistance 90 minutes, equivalent to HILTI or equivalent.
| Vsak prehod mora biti označen z nalepko ali tablico z osnovnimi požarnimi podatki; | Each passageway must be marked with a sticker or placard with basic fire information; | kpl | 1 |  | 0
3.11 | Preizkusno obratovanje delovanja sistema v obsegu: | Operational test of the system in scope:
| - pregled jeklenk in omar za jeklenke, | - inspection of cylinders and cylinder lockers,
| - pregled ekspanzijskih reducirnih postaj za redukcijo visokega tlaka, | - an overview of expansion reduction stations for high pressure reduction,
| - pregled inštalacije cevovodov, armatur in opreme | - inspection of piping, fittings and equipment
| - pregled delovanja varnostnih funkcij (zapiranje pnevmatskih ventilov, delovanje detektorjev, delovanje prezračevanja omar za jeklenka ipd), | - checking the operation of safety functions (closing of pneumatic valves, operation of detectors, operation of cylinder cabinet ventilation, etc.),
| - pregled odjemnih mest. | - a review of the customer sites.
| Preizkusno obratovanje traja neprekinjeno 72 ur. | The test operation shall be continuous for 72 hours. | kpl | 1 |  | 0
3.12 | Napisne ploščice iz nerjavne pločevine z vgravirano oznako po shemi za opremo in armature, kompletno z jekleno pritrdilno žico ali visoko kvalotetne nalepke; visoko trajanje H (več kot 15 let) | Stainless steel nameplates with engraved marking according to the scheme for fittings and fixtures, complete with steel fixing wire or high quality labels; high durability H (more than 15 years) | kpl | 1 |  | 0
3.13 | Samolepilne puščice za označitev smeri pretoka ter z napisom vrste medija; visoko trajanje H (več kot 15 let) | Self-adhesive arrows to indicate direction of flow and type of media; high H lifetime (more than 15 years) | kpl | 1 |  | 0
3.14 | Izdelava montažnih risb za izvedbo inštalacij med gradnjo objekta, kot so: detajli priključkov, montažne skice, montažni detajli, ipd. | Preparation of assembly drawings for the installation of services during the construction of the building, such as: connection details, assembly sketches, assembly details, etc. | kpl | 1 |  | 0
3.15 | Kvalifikacije montaže IQ-pregledi (instalation qualification) po GEP Commissioning protokolu in dokumentiranje kvalifikacije montaže, vključno z odpravo prvotnih napak montaže; | Installation qualification IQ-checks (installation qualification) according to the GEP Commissioning Protocol and documentation of installation qualification, including correction of original installation faults; | kpl | 1 |  | 0
3.16 | Meritve delovanja OQ-kvalifikacija (operation qualification) ter dokumentiranje meritev delovanja, vključno z nastavitvijo parametrov; | OQ (operation qualification) measurements and documentation of performance measurements, including parameter settings; | kpl | 1 |  | 0
3.17 | Posnetki izvedenega stanja, sprotno beleženje vseh sprememb nastalih med izvedbo, vrisovanje in vpisovanje v PZI projektno dokumentacijo; | Recording of the as-built condition, keeping a running record of any changes made during the execution, plotting and recording in the PZI project documentation; | kpl | 1 |  | 0
3.18 | Stenska shema sistema, vloženo v zaščitni okvir s prosojnim umetnim steklomo (plastika) ali plastificirano, vključno s pritrditvijo na notranjo steno v strojnici objekta; | Wall diagram of the system, enclosed in a protective frame with transparent plastic or plasticised glass, including fixing to an internal wall in the mechanical room of the building; | kpl | 1 |  | 0
3.19 | Primopredajna dokumentacija, ki mora vsebovati: izjave, dokazilo o zanesljivosti objekta, certifikate in ateste za vgrajene materiale in opremo, zapisnike preizkusov in meritev, navodila za uporabo, obratovanje in vzdrževanje ter ostalo primopredajno dokumantacijo. Predaja se v dveh mapiranih izvodih ter en izvod v elektronski obliki; | The handover documentation, which shall include: declarations, proof of the reliability of the facility, certificates and attestations for the materials and equipment installed, records of tests and measurements, instructions for use, operation and maintenance, and other handover documentation. It shall be handed over in two mapped copies and one copy in electronic form; | kpl | 1 |  | 0
3.20 | Elaborat eksplozijske ogroženosti z oceno tveganja - faza PID | Explosion Hazard Laboratory with Risk Assessment - PID phase | kpl | 1 |  | 0
3.21 | Certificiranje EX elaborata | Certification of the EX study | kpl | 1 |  | 0
| SKUPAJ TEHNIČNI PLINI | SKUPAJ TEHNIČNI PLINI |  |  |  | 0

## 4.11.4_ELEKTRO DELA - IZENAČEVA
Investitor: | UNIVERZA V LJUBLJANI | UNIVERSITY IN LJUBLJANA
Gradnja: | Fakulteta za strojništvo | Faculty of Mechanical Engineering
Objekt: | STAVBA FAKULTETE | FACULTY BUILDING
4.11 | STROJNA DELA | MECHANICAL WORKS
4.11.4 | ELEKTRO DELA - IZENAČEVANJE POTENCIALA | ELECTRICAL WORK - EQUIPOTENTIAL BONDING |  |  |  | 0
Opomba: Cene so v EUR brez DDV-ja / Note: Prices are in EUR excluding VAT
Poz. | Opis | Description | EM | Količina | Cena/EM | Cena
4 | ELEKTRO DELA - IZENAČEVANJE POTENCIALA | ELECTRICAL WORK - EQUIPOTENTIAL BONDING
4.1 | Dobava in vgradnja glavne zbiralke za izenačitev potenciala s pokrovom - GIP | Supply and installation of main busbar for equipotential bonding with cover - GIP
| - za 12 priključnih mest, kot naprimer.: 472 239 + 472 299, DEHN | - for 12 connection points, e.g. 472 239 + 472 299, DEHN | kos | 1 |  | 0
4.2 | Dobava in vgradnja zbiralke za izenačitev potenciala s pokrovom - ZIP | Supply and installation of a potential equalisation busbar with cover - ZIP
| - za 14 priključnih mest, kot naprimer: 563 030 + 1x563 013 + 13x563 011 + 563 015, DEHN R15 | - for 14 connection points, e.g. 563 030 + 1x563 013 + 13x563 011 + 563 015, DEHN R15 | kos | 1 |  | 0
4.3 | Dobava in polaganje: Vodnik za izenačevanje potenciala, deloma položene na police, deloma uvlečen v zaščitne cevi vključno z označevalnimi ploščicami, odziv na ogenj vsaj Cca s1 d2 a1. Kabli brez halogena. N2XH-J, rumeno/zelena. | Supply and installation: Potential equalisation conductor, partly laid on shelves, partly enclosed in protective tubes including marker plates, reaction to fire not less than Cca s1 d2 a1. N2XH-J, yellow/green.
| - 1x 6 mm2 | - 1x 6 mm2 | m | 20 |  | 0
| - 1x 16 mm2 | - 1x 16 mm2 | m | 50 |  | 0
| - 1x 35 mm2 | - 1x 35 mm2 | m | 10 |  | 0
4.4 | Izdelava spojev za izenačitve potencialov (premostitveni spoj iz dveh kabelskih čevljelj), kovinske mase - podboji, okvirji vrat, tehnološke opreme, ograj, kovinski fasadni elementi itd. | Making joints for equipotential bonding (bridging joint made of two cable shoes), metal masses - soffits, door frames, technological equipment, fences, metal façade elements, etc. | ur | 20 |  | 0
4.5 | Premostitveni spoj izdelan iz dveh kabelskih čevljev in 0,25m žice N2HX-J 1x16mm2. Odziv na ogenj vsaj Cca s1 d2 a1. Kabel brez halogena. | Bridging joint made of two cable shoes and 0,25m of N2HX-J 1x16mm2 wire. Fire response at least Cca s1 d2 a1. | kos | 10 |  | 0
4.6 | CuSn pletenica 50 mm2, dolžina do 20 cm, komplet s kabel čevelj in vijačnim priborom | CuSn stranded wire 50 mm2, length up to 20 cm, complete with cable shoe and screw fittings | kos | 5 |  | 0
4.7 | Gibljiva zaščitna cev fi 10-20 kot naprimer EVROFLEX, komplet s priborom in s pritrdilnim materialom. | Flexible protection hose fi 10-20 such as EVROFLEX, complete with fittings and fixing material. | m | 5 |  | 0
4.8 | Nerjaveče INOX kovinske zaščitne cevi fi 16-32 s priborom za sestavo in montažo. | Stainless INOX metal protection pipes fi 16-32 with accessories for assembly and installation. | m | 5 |  | 0
4.9 | Ozemljitveni sistem sestavljen iz inox ozemljitvene plošče, 2x ru/ze spiralne žice 4mm2 dolžine 10 m zaključene s kabelskim čevljem M8 in 2x inox ozemljitvenih klešč. 1x navojni priključek M8 za priključek na ozemljilni sistem z vodnikom Cu 35 mm2. | Earthing system consisting of an inox earthing plate, 2x 4mm2 stranded wires (10 m long) terminated with an M8 cable lug and 2x inox earthing pliers. 1x M8 threaded connector for connection to the earthing system with a Cu 35 mm2 conductor. | kos | 1 |  | 0
4.10 | Tipska omarica za kontrolirano ozemljevanje avtocisterne, skupaj s signalizacijo ustreznosti ozemljitve, v izvedbi IP66, Cu ozemljilno žico dolžine 10 m, konektor - krokodilček, pritrdilnim priborom. Newson Gale - Eart-Rite II RTR, oziroma podobno | Type box for controlled earthing of a tanker, including earthing signal, IP66 version, 10 m Cu earthing wire, crocodile connector, fixing accessories. Newson Gale - Eart-Rite II RTR, or similar | kos | 1 |  | 0
| SKUPAJ TEHNIČNI PLINI | SKUPAJ TEHNIČNI PLINI |  |  |  | 0